## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-30 | Thursday
|  |  | Date (day): | 2021-09-30 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14109.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15149 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-29 | 2021-09-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 400 | 341 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 331 | 321 | 340 | 340 | 20
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 340 | 340 | 340 | 110 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 275 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 50 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 48 | 68 | 68 |  | 32 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 255 | 254 | 240 | 240 | 95 |  | DP high
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 51 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 280 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 130 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 105 | 100 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 84 | 94 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2970 | 3332 | 3714 | 3989 | 892 | 802
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 116 | 159 | 157 | 157 | 73 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 34 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 40 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 18 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 5 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 58 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 51 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 53 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1005 | 1450 | 1512 | 1565 | 133 | 671
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 80 | 80 | 135 | 0
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 214 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 310 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 270 | 310 | 340 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 130 | 135 | 137 |  | 13 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 141 | 140 | 140 |  | 23 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 136 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 36 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 50 | 100 | 100 | 100
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 50 | 96 | 90 | 98 |  | 15 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1543 | 1927 | 2147 | 2389 | 450 | 118
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 164 | 155 | 150 | 155 | 47 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 35 | 165 | 170 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 34 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 368 | 479 | 530.6 | 514 | 47 | 95
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 130 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 161 | 160 | 160 | 170 |  | GT-1 under maint
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 80 | 81 | 81 |  | 5 | Engine problem
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 193 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 270 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 303 | 316 | 316 | 316 | 84 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 321 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1561 | 1686 | 1817 | 1817 | 317 | 222
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 719 | 717 | 734 | 734
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 7 | 0 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 170 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 320 | 400 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 45 | 103 | 70 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1238 | 1317 | 1579 | 1739 | 0 | 98
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 30 | 30 | 30
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 87 | 88 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 22 | 22 | 22 | 22 | 73 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 480 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 224 | 228 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 651 | 864 | 1092 | 1242 | 73 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 36 | 34 | 35 |  | 36 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 28 | 28 | 22 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 24 | 0 | 50 |  |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 174 | 166 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 172 | 167 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 336 | 330 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30 |  | 20 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 95 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 783 | 1255 | 1519 | 1678 | 402 | 76
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 78 | 78
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 117 | 193 | 199 | 216 | 0 | 374
|  | Total |  |  |  |  | 22031 | 21180 | 10236 | 12503 | 14109.6 | 15149 | 2314 | 2562
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9741.5152 | 11899 | 13427.9877 | 14417.176
| A. |  | 2021-09-29 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 12503 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9031 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12503 | MW
| 3 | Day peak Generation : |  |  | 10236 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11899 | MW
| 4 | Evening peak Generation : |  |  | 12503 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 261.4472 | MKWHr | By Solar | 0.54384 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 161.7333 | MKWHr |  | By Oil: | 64.4644 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.7144 | MKWHr |  | By Hydro: | 3.1953 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2314 | MW | Dhaka | 4425 | 4425 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2562 | MW | Chittagong | 1242 | 1242 |  | 0 |  | 18:00 |  | 128
|  |  |  | Total = |  |  | 4876 | MW | Khulna | 1301 | 1301 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1186.2 | MMCFD |  |  | Rajshahi | 1228 | 1228 |  | 0 |  | 19:00 |  | 136
| 8 | Fuel Cost : | i) Gas : | Taka | 166024257.784 | ii) Oil : | Taka | 505877410.61 | Comilla | 1103 | 1103 |  | 0 |  | 19:30 |  | 136
|  |  | iii) Coal : |  | 54504168 | Total | Taka | 726405836.394 | Mymensingh | 1021 | 1021 |  | 0 |  | 20:00 |  | 134
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.976 | MKWHr. | Sylhet | 543 | 543 |  | 0 |  | 21:00 |  | 130
|  | ii) During Peak Demand : |  |  | -126 | MW (E to W) at | 19:00 | hrs | Barisal | 311 | 311 |  | 0 |  | 22:00 |  | 128
|  | iii) Maximum : |  |  | -176 | MW at | 18:30 | hrs | Rangpur | 725 | 725 |  | 0 |  | 23:00 |  | 126
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.2° C |  |  | Total | 11899 | 11899 |  | 0
| B. |  | 2021-09-30 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15149 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 2149 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 271.8398 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9254 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2865 | MKWHr. | ii) HVDC Flow at Peak Time |  | 717 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5094 | MKWHr. | iii) Maximum HVDC Flow : |  | 720 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.5 |  | (b) Today: | 106.56 |  | (c) Rule Curve: |  | 105.76
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 404 | 332 |  | 0 | 320 | 275 | 0 | 0 | 45 | 258 | 0 | 0 | 0 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 43 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 12 | 21 | 37 | 0 | 0 | 0 | 310 | 300 | 214 | 83 | 140 | 23 | 55 | 0 | 35 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 116 | 200 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 130 | 161 | 45 | 78 | 0 | 220 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 194 | 0 | 115 | 0 | 100 | 200 | 132 | 317 | 115 | 0 | 105 | 0 | 305 | 54 | 17 | 70 | 48 | 100 | 320 | 70 | 0 | 162 | 108 | 0 | 36 | 0 |  | 710 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 12 | 0 | 188 | 0 | 387 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 222 | 0 | 0 | 0 |  | 8014 | 3136 | 11150 | 4508 | 710 | 2349 | 0 | 2657 | 487 | 118 | 120 | 85 | 116 | 0 | 0 | 106.5
2:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 404 | 332 |  | 0 | 320 | 285 | 0 | 0 | 55 | 253 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 43 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 31 | 0 | 0 | 0 | 315 | 300 | 213 | 83 | 141 | 23 | 56 | 0 | 35 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 116 | 200 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 130 | 160 | 45 | 78 | 0 | 220 | 18 | 0 | 9 | 285 | 16 | 8 | 0 | 170 | 0 | 0 | 194 | 0 | 115 | 0 | 100 | 200 | 10 | 318 | 115 | 0 | 105 | 0 | 305 | 54 | 17 | 70 | 49 | 100 | 321 | 25 | 0 | 17 | 108 | 0 | 36 | 0 |  | 709 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 12 | 0 | 188 | 0 | 403 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 223 | 0 | 0 | 0 |  | 7638 | 3164 | 10802 | 4520 | 709 | 2374 | 0 | 2307 | 486 | 118 | 120 | 52 | 116 | 0 | 0 | 106.5
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 404 | 333 |  | 0 | 320 | 275 | 0 | 0 | 55 | 254 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 31 | 0 | 0 | 0 | 310 | 305 | 214 | 83 | 138 | 23 | 56 | 0 | 35 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 110 | 207 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 130 | 160 | 45 | 78 | 0 | 220 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 145 | 0 | 0 | 160 | 0 | 115 | 0 | 100 | 200 | 10 | 318 | 115 | 0 | 68 | 0 | 305 | 54 | 17 | 70 | 48 | 100 | 320 | 17 | 0 | 17 | 108 | 0 | 36 | 0 |  | 709 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 12 | 0 | 188 | 0 | 380 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 410 | 224 | 0 | 0 | 0 |  | 7485 | 3068 | 10553 | 4528 | 709 | 2338 | 0 | 2124 | 487 | 117 | 120 | 20 | 110 | 0 | 0 | 106.5
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 404 | 333 |  | 0 | 320 | 290 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 29 | 0 | 0 | 0 | 310 | 305 | 214 | 83 | 138 | 23 | 56 | 0 | 35 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 108 | 211 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 130 | 160 | 45 | 78 | 0 | 220 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 145 | 0 | 0 | 120 | 0 | 115 | 0 | 100 | 200 | 10 | 316 | 115 | 0 | 68 | 0 | 305 | 54 | 17 | 45 | 47 | 100 | 320 | 17 | 0 | 17 | 72 | 0 | 36 | 0 |  | 710 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 12 | 0 | 187 | 0 | 308 | 0 | 0 | 113 | 0 | 70 | 0 | 0 | 35 | 370 | 227 | 0 | 0 | 0 |  | 7397 | 2917 | 10314 | 4529 | 710 | 2283 | 0 | 1979 | 448 | 117 | 120 | 20 | 108 | 0 | 0 | 106.5
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 404 | 331 |  | 0 | 320 | 290 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 37 | 0 | 0 | 0 | 325 | 320 | 212 | 83 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 45 | 22 | 11 | 33 | 21 | 106 | 210 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 130 | 160 | 45 | 78 | 0 | 220 | 18 | 0 | 9 | 290 | 16 | 8 | 0 | 145 | 0 | 0 | 100 | 0 | 115 | 0 | 100 | 200 | 0 | 316 | 115 | 0 | 17 | 0 | 305 | 54 | 0 | 0 | 48 | 100 | 320 | 0 | 0 | 0 | 72 | 0 | 36 | 0 |  | 710 | 0 | 375 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 12 | 0 | 179 | 0 | 348 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 340 | 227 | 0 | 0 | 0 |  | 7224 | 2753 | 9977 | 4560 | 710 | 2332 | 0 | 1610 | 418 | 117 | 120 | 4 | 106 | 0 | 0 | 106.5
6:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 402 | 332 |  | 0 | 320 | 290 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 7 | 0 | 0 | 0 | 315 | 305 | 213 | 83 | 136 | 20 | 56 | 0 | 35 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 96 | 211 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 110 | 160 | 45 | 78 | 0 | 178 | 18 | 0 | 9 | 270 | 16 | 8 | 0 | 145 | 0 | 0 | 35 | 0 | 115 | 1 | 70 | 180 | 0 | 316 | 85 | 0 | 17 | 0 | 251 | 54 | 0 | 0 | 48 | 100 | 320 | 0 | 0 | 0 | 17 | 0 | 36 | 0 |  | 710 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 12 | 0 | 172 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 174 | 0 | 0 | 0 |  | 6778 | 2480 | 9258 | 4391 | 710 | 2171 | 0 | 1270 | 378 | 117 | 120 | 4 | 96 | 1 | 0 | 106.5
7:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 364 | 331 |  | 0 | 320 | 270 | 0 | 0 | 55 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 41 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 27 | 0 | 0 | 0 | 315 | 315 | 212 | 83 | 138 | 20 | 56 | 0 | 35 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 78 | 210 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 110 | 161 | 45 | 75 | 0 | 179 | 18 | 0 | 9 | 270 | 16 | 8 | 0 | 152 | 0 | 0 | 35 | 0 | 102 | 5 | 20 | 136 | 0 | 316 | 55 | 0 | 17 | 1 | 178 | 54 | 0 | 0 | 48 | 100 | 320 | 0 | 9 | 0 | 17 | 0 | 17 | 5 |  | 710 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 12 | 0 | 170 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 172 | 0 | 0 | 0 |  | 6523 | 2508 | 9031 | 4355 | 710 | 2202 | 0 | 1048 | 378 | 116 | 120 | 4 | 78 | 20 | 0 | 106.5
8:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 363 | 333 |  | 0 | 320 | 275 | 0 | 0 | 55 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 40 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 21 | 2 | 0 | 0 | 0 | 310 | 305 | 212 | 83 | 140 | 20 | 56 | 0 | 35 | 0 | 0 | 8 | 19 | 2 | 33 | 18 | 68 | 205 | 0 | 21 | 1 | 43 | 0 | 47 | 0 | 110 | 159 | 45 | 75 | 0 | 179 | 18 | 0 | 9 | 290 | 16 | 8 | 0 | 250 | 0 | 0 | 35 | 0 | 102 | 10 | 20 | 141 | 0 | 316 | 55 | 0 | 17 | 3 | 176 | 54 | 0 | 0 | 49 | 100 | 320 | 2 | 17 | 0 | 17 | 0 | 17 | 1 |  | 720 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 11 | 0 | 171 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 172 | 0 | 0 | 2 |  | 6636 | 2521 | 9157 | 4331 | 720 | 2198 | 0 | 1189 | 377 | 115 | 120 | 4 | 68 | 35 | 0 | 106.51
9:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 364 | 333 |  | 0 | 320 | 310 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 27 | 33 | 33 | 16 | 0 | 41 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 2 | 0 | 0 | 0 | 345 | 350 | 210 | 83 | 140 | 20 | 56 | 0 | 35 | 0 | 0 | 16 | 19 | 2 | 33 | 12 | 76 | 184 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 110 | 159 | 45 | 75 | 0 | 179 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 250 | 0 | 0 | 35 | 0 | 102 | 18 | 30 | 178 | 0 | 316 | 55 | 0 | 17 | 2 | 178 | 54 | 0 | 0 | 48 | 100 | 321 | 17 | 17 | 1 | 17 | 0 | 17 | 3 |  | 720 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 11 | 0 | 179 | 0 | 352 | 0 | 0 | 0 | 0 | 15 | 0 | 1 | 0 | 300 | 202 | 0 | 0 | 1 |  | 6846 | 2632 | 9478 | 4436 | 720 | 2284 | 0 | 1302 | 377 | 116 | 120 | 4 | 76 | 43 | 0 | 106.51
10:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 363 | 333 |  | 0 | 320 | 290 | 0 | 0 | 55 | 254 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 27 | 33 | 33 | 16 | 0 | 41 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 290 | 350 | 201 | 55 | 142 | 20 | 55 | 0 | 35 | 0 | 0 | 25 | 6 | 5 | 33 | 12 | 80 | 171 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 163 | 161 | 50 | 75 | 0 | 206 | 18 | 0 | 9 | 290 | 16 | 8 | 0 | 255 | 0 | 0 | 35 | 0 | 132 | 12 | 50 | 180 | 0 | 317 | 60 | 52 | 17 | 3 | 178 | 54 | 7 | 0 | 49 | 100 | 320 | 17 | 25 | 20 | 17 | 0 | 17 | 4 |  | 719 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 21 | 0 | 173 | 0 | 377 | 0 | 0 | 12 | 0 | 35 | 0 | 4 | 0 | 300 | 223 | 0 | 0 | 1 |  | 6995 | 2695 | 9690 | 4359 | 719 | 2333 | 0 | 1534 | 375 | 116 | 120 | 4 | 80 | 50 | 0 | 106.51
11:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 385 | 332 |  | 0 | 320 | 280 | 0 | 0 | 55 | 256 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 21 | 25 | 27 | 25 | 33 | 25 | 0 | 41 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 280 | 310 | 183 | 26 | 140 | 20 | 52 | 0 | 35 | 0 | 0 | 25 | 18 | 8 | 6 | 12 | 86 | 171 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 163 | 160 | 57 | 75 | 0 | 220 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 260 | 0 | 0 | 35 | 0 | 132 | 6 | 76 | 180 | 0 | 318 | 108 | 52 | 35 | 3 | 302 | 54 | 31 | 20 | 48 | 100 | 320 | 52 | 45 | 79 | 37 | 0 | 17 | 18 |  | 720 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 22 | 0 | 173 | 0 | 295 | 3 | 0 | 35 | 0 | 35 | 0 | 4 | 25 | 300 | 218 | 0 | 0 | 2 |  | 7345 | 2657 | 10002 | 4309 | 720 | 2195 | 0 | 1997 | 376 | 116 | 120 | 4 | 86 | 79 | 0 | 106.52
12:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 331 |  | 0 | 320 | 290 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 25 | 33 | 0 | 0 | 41 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 270 | 285 | 207 | 8 | 140 | 20 | 52 | 0 | 35 | 0 | 0 | 36 | 19 | 0 | 25 | 19 | 90 | 164 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 0 | 160 | 61 | 75 | 0 | 220 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 275 | 0 | 0 | 35 | 0 | 130 | 0 | 100 | 200 | 20 | 303 | 115 | 52 | 51 | 4 | 305 | 54 | 51 | 50 | 50 | 100 | 321 | 84 | 34 | 162 | 53 | 0 | 17 | 24 |  | 719 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 22 | 0 | 172 | 0 | 336 | 45 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 300 | 224 | 0 | 0 | 2 |  | 7447 | 2789 | 10236 | 4347 | 719 | 2070 | 0 | 2323 | 380 | 116 | 120 | 4 | 90 | 67 | 0 | 106.52
13:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 333 |  | 0 | 320 | 280 | 0 | 0 | 43 | 254 | 0 | 0 | 0 | 24 | 0 | 10 | 0 | 0 | 0 | 0 | 55 | 55 | 22 | 25 | 27 | 25 | 33 | 17 | 0 | 42 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 260 | 270 | 210 | 8 | 140 | 20 | 52 | 0 | 35 | 0 | 0 | 52 | 19 | 8 | 33 | 19 | 90 | 149 | 0 | 19 | 2 | 43 | 0 | 50 | 0 | 10 | 160 | 62 | 78 | 0 | 220 | 18 | 0 | 9 | 310 | 16 | 8 | 0 | 276 | 0 | 0 | 35 | 0 | 90 | 7 | 100 | 200 | 71 | 316 | 115 | 52 | 66 | 0 | 305 | 54 | 61 | 50 | 56 | 100 | 320 | 94 | 25 | 162 | 75 | 0 | 17 | 31 |  | 717 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 21 | 0 | 202 | 0 | 364 | 65 | 0 | 40 | 0 | 35 | 0 | 4 | 55 | 330 | 224 | 0 | 0 | 4 |  | 7568 | 2932 | 10500 | 4377 | 717 | 2135 | 0 | 2458 | 409 | 117 | 120 | 4 | 90 | 73 | 0 | 106.52
14:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 371 | 302 |  | 0 | 320 | 290 | 0 | 0 | 40 | 252 | 0 | 0 | 0 | 24 | 0 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 27 | 25 | 33 | 25 | 0 | 42 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 18 | 21 | 6 | 20 | 0 | 0 | 260 | 270 | 209 | 8 | 137 | 20 | 51 | 0 | 36 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 102 | 149 | 0 | 19 | 2 | 43 | 0 | 47 | 0 | 70 | 163 | 61 | 78 | 0 | 220 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 195 | 0 | 0 | 35 | 0 | 149 | 5 | 100 | 170 | 100 | 318 | 115 | 17 | 105 | 0 | 305 | 54 | 85 | 34 | 49 | 100 | 320 | 93 | 24 | 162 | 108 | 0 | 17 | 31 |  | 717 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 22 | 0 | 181 | 0 | 347 | 70 | 0 | 70 | 0 | 34 | 0 | 6 | 70 | 340 | 226 | 0 | 0 | 3 |  | 7652 | 2910 | 10562 | 4291 | 717 | 2132 | 0 | 2588 | 420 | 117 | 120 | 4 | 102 | 71 | 0 | 106.53
15:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 389 | 333 |  | 0 | 320 | 280 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 24 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 25 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 21 | 2 | 35 | 0 | 0 | 285 | 270 | 207 | 8 | 138 | 20 | 53 | 0 | 43 | 0 | 0 | 45 | 22 | 8 | 33 | 8 | 98 | 150 | 0 | 19 | 2 | 43 | 0 | 47 | 0 | 70 | 161 | 62 | 75 | 0 | 221 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 195 | 0 | 0 | 35 | 0 | 149 | 4 | 100 | 170 | 108 | 316 | 115 | 17 | 105 | 0 | 305 | 54 | 85 | 34 | 48 | 100 | 320 | 94 | 42 | 162 | 108 | 0 | 17 | 16 |  | 717 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 22 | 0 | 174 | 0 | 414 | 70 | 0 | 70 | 0 | 35 | 0 | 4 | 70 | 340 | 225 | 0 | 0 | 0 |  | 7834 | 3005 | 10839 | 4388 | 717 | 2241 | 0 | 2606 | 419 | 162 | 120 | 20 | 98 | 68 | 0 | 106.53
16:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 360 | 328 |  | 0 | 320 | 285 | 0 | 0 | 55 | 254 | 0 | 0 | 0 | 24 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 25 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 21 | 4 | 60 | 0 | 0 | 300 | 285 | 207 | 8 | 139 | 20 | 53 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 8 | 96 | 154 | 0 | 21 | 1 | 44 | 0 | 49 | 0 | 70 | 160 | 61 | 79 | 0 | 221 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 160 | 0 | 0 | 35 | 0 | 149 | 2 | 100 | 170 | 108 | 316 | 115 | 17 | 105 | 0 | 305 | 54 | 85 | 34 | 48 | 100 | 320 | 93 | 6 | 162 | 108 | 0 | 17 | 1 |  | 717 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 186 | 0 | 415 | 35 | 0 | 35 | 0 | 35 | 0 | 3 | 35 | 340 | 224 | 0 | 0 | 1 |  | 7783 | 2937 | 10720 | 4456 | 717 | 2244 | 0 | 2472 | 419 | 162 | 120 | 20 | 96 | 14 | 0 | 106.53
17:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 349 | 282 |  | 0 | 340 | 270 | 0 | 0 | 40 | 254 | 0 | 0 | 0 | 24 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 25 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 19 | 7 | 65 | 0 | 0 | 280 | 270 | 210 | 8 | 139 | 20 | 54 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 102 | 157 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 110 | 161 | 62 | 79 | 0 | 220 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 160 | 0 | 0 | 35 | 0 | 149 | 1 | 50 | 170 | 122 | 316 | 115 | 17 | 51 | 0 | 215 | 54 | 51 | 34 | 49 | 100 | 320 | 72 | 5 | 162 | 108 | 0 | 17 | 1 |  | 716 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 2 | 0 | 0 | 87 | 19 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 22 | 0 | 182 | 0 | 308 | 35 | 0 | 35 | 0 | 38 | 0 | 1 | 35 | 340 | 154 | 0 | 0 | 0 |  | 7502 | 2720 | 10222 | 4377 | 716 | 2067 | 0 | 2226 | 420 | 162 | 120 | 24 | 102 | 8 | 0 | 106.54
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 303 | 282 |  | 0 | 340 | 250 | 0 | 0 | 52 | 255 | 0 | 0 | 0 | 64 | 115 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 13 | 33 | 33 | 32 | 0 | 87 | 75 | 120 | 0 | 6 | 0 | 0 | 0 | 0 |  | 4 | 0 | 102 | 35 | 32 | 24 | 18 | 8 | 70 | 0 | 0 | 280 | 270 | 212 | 8 | 139 | 20 | 55 | 0 | 43 | 0 | 50 | 45 | 22 | 8 | 33 | 19 | 128 | 155 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 110 | 160 | 62 | 80 | 0 | 193 | 18 | 0 | 9 | 270 | 24 | 8 | 0 | 183 | 0 | 0 | 53 | 0 | 149 | 0 | 90 | 175 | 130 | 316 | 115 | 33 | 70 | 0 | 305 | 54 | 60 | 76 | 87 | 100 | 320 | 76 | 0 | 162 | 114 | 0 | 17 | 0 |  | 716 | 0 | 320 | 0 | 0 | 160 | 0 | 0 | 14 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 31 | 30 | 94 | 27 | 0 | 27 | 14 | 16 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 22 | 0 | 167 | 0 | 297 | 35 | 0 | 41 | 0 | 97 | 0 | 0 | 70 | 360 | 141 | 0 | 3 | 0 |  | 8130 | 3073 | 11203 | 4271 | 716 | 2014 | 0 | 2834 | 439 | 162 | 160 | 479 | 128 | 0 | 0 | 106.54
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 341 | 321 |  | 0 | 340 | 275 | 0 | 0 | 50 | 254 | 0 | 0 | 0 | 102 | 150 | 48 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 40 | 58 | 50 | 18 | 5 | 80 | 0 | 0 | 280 | 270 | 214 | 8 | 141 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 136 | 155 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 161 | 63 | 80 | 0 | 193 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 280 | 0 | 0 | 165 | 0 | 149 | 0 | 100 | 200 | 130 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 100 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 | 0 |  | 717 | 0 | 320 | 0 | 0 | 170 | 0 | 0 | 7 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 50 | 36 | 94 | 27 | 24 | 39 | 52 | 29 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 22 | 0 | 167 | 0 | 330 | 103 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 480 | 228 | 0 | 17 | 0 |  | 8874 | 3629 | 12503 | 4342 | 717 | 2219 | 0 | 3693 | 560 | 159 | 170 | 507 | 136 | 0 | 0 | 106.55
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 347 | 332 |  | 0 | 340 | 295 | 0 | 0 | 55 | 253 | 0 | 0 | 0 | 64 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 25 | 0 | 84 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 10 | 12 | 50 | 18 | 16 | 80 | 0 | 0 | 285 | 285 | 213 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 136 | 155 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 161 | 62 | 81 | 0 | 213 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 280 | 0 | 0 | 175 | 0 | 149 | 0 | 100 | 200 | 130 | 316 | 115 | 52 | 105 | 0 | 305 | 54 | 110 | 100 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 716 | 0 | 360 | 0 | 0 | 170 | 0 | 0 | 4 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 50 | 36 | 94 | 27 | 0 | 39 | 52 | 30 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 22 | 0 | 168 | 0 | 397 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 228 | 0 | 17 | 0 |  | 8741 | 3738 | 12479 | 4436 | 716 | 2359 | 0 | 3473 | 559 | 159 | 170 | 471 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 347 | 331 |  | 0 | 340 | 267 | 0 | 0 | 55 | 253 | 0 | 0 | 0 | 64 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 23 | 33 | 33 | 25 | 0 | 84 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 10 | 12 | 50 | 18 | 18 | 80 | 0 | 0 | 285 | 295 | 213 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 134 | 157 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 63 | 81 | 0 | 213 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 278 | 0 | 0 | 175 | 0 | 149 | 0 | 100 | 200 | 127 | 316 | 115 | 52 | 105 | 0 | 305 | 54 | 110 | 100 | 97 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 716 | 0 | 360 | 0 | 0 | 170 | 0 | 0 | 7 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 50 | 36 | 94 | 27 | 0 | 39 | 52 | 28 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 22 | 0 | 173 | 0 | 369 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 228 | 0 | 17 | 0 |  | 8740 | 3719 | 12459 | 4451 | 716 | 2328 | 0 | 3469 | 560 | 159 | 170 | 472 | 134 | 0 | 0 | 106.55
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 347 | 332 |  | 0 | 340 | 280 | 0 | 0 | 55 | 251 | 0 | 0 | 0 | 32 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 30 | 33 | 25 | 0 | 84 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 10 | 11 | 50 | 21 | 20 | 80 | 0 | 0 | 285 | 300 | 212 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 0 | 44 | 22 | 8 | 33 | 21 | 130 | 162 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 162 | 63 | 81 | 0 | 213 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 187 | 0 | 149 | 0 | 100 | 200 | 127 | 317 | 115 | 52 | 105 | 0 | 305 | 54 | 110 | 70 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 | 0 |  | 717 | 0 | 360 | 0 | 0 | 180 | 0 | 0 | 8 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 50 | 36 | 94 | 27 | 0 | 36 | 52 | 28 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 22 | 0 | 185 | 0 | 398 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 228 | 0 | 17 | 0 |  | 8539 | 3769 | 12308 | 4477 | 717 | 2372 | 0 | 3277 | 560 | 159 | 180 | 436 | 130 | 0 | 0 | 106.55
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 346 | 332 |  | 0 | 340 | 265 | 0 | 0 | 55 | 252 | 0 | 0 | 0 | 16 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 27 | 30 | 33 | 25 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 10 | 9 | 50 | 21 | 27 | 80 | 0 | 0 | 285 | 300 | 212 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 44 | 22 | 8 | 33 | 21 | 128 | 163 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 158 | 62 | 81 | 0 | 219 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 145 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 200 | 133 | 316 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 70 | 95 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 0 | 0 |  | 717 | 0 | 360 | 0 | 0 | 165 | 0 | 0 | 4 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 50 | 20 | 94 | 27 | 0 | 36 | 52 | 28 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 22 | 0 | 184 | 0 | 369 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 228 | 0 | 17 | 0 |  | 8457 | 3707 | 12164 | 4481 | 717 | 2330 | 0 | 3207 | 561 | 159 | 165 | 416 | 128 | 0 | 0 | 106.55
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 347 | 332 |  | 0 | 340 | 265 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 16 | 133 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 27 | 30 | 33 | 25 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 10 | 0 | 50 | 21 | 29 | 80 | 0 | 0 | 280 | 300 | 212 | 8 | 139 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 126 | 162 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 63 | 81 | 0 | 220 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 190 | 0 | 149 | 0 | 100 | 200 | 140 | 318 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 70 | 95 | 100 | 320 | 93 | 0 | 162 | 112 | 0 | 14 | 0 |  | 718 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 27 | 0 | 0 | 52 | 28 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 22 | 0 | 188 | 0 | 367 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 226 | 0 | 0 | 0 |  | 8441 | 3523 | 11964 | 4487 | 718 | 2333 | 0 | 3205 | 540 | 159 | 120 | 276 | 126 | 0 | 0 | 106.56
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 349 | 332 |  | 0 | 340 | 262 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 16 | 115 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 29 | 30 | 33 | 25 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 50 | 21 | 32 | 80 | 0 | 0 | 280 | 300 | 213 | 8 | 139 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 122 | 174 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 159 | 63 | 81 | 0 | 220 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 145 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 200 | 140 | 317 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 70 | 55 | 100 | 320 | 93 | 0 | 162 | 114 | 0 | 17 | 0 |  | 717 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 22 | 0 | 191 | 0 | 369 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 222 | 0 | 0 | 0 |  | 8394 | 3421 | 11815 | 4507 | 717 | 2340 | 0 | 3117 | 520 | 159 | 120 | 213 | 122 | 0 | 0 | 106.56
KWH | 0 | 0 | 0 | 0 | 7417909 | 0 | 0 | 9029640 | 7818000 |  | 0 | 7707000 | 6744436 | 0 | 0 | 1284435 | 6136194 | 0 | 0 | 0 | 565632 | 1096800 | 224009 | 0 | 0 | 0 | 1303560 | 973780 | 724409 | 435780 | 600000 | 635040 | 758700 | 832200 | 398400 | 0 | 1375283 | 1820000 | 2800000 | 0 | 51661 | 0 | 0 | 0 | 0 |  | 179760 | 0 | 327558 | 203280 | 125760 | 551520 | 476736 | 373920 | 721678 | 0 | 0 | 7423200 | 7286000 | 5074000 | 1003636 | 3329510 | 466128 | 1315680 | 0 | 910026 | 0 | 49760 | 874718 | 478296 | 185940 | 759300 | 488540 | 2509440 | 4134960 | 0 | 452376 | 9500 | 1025000 | 0 | 1159800 | 0 | 3105085 | 3654000 | 1313184 | 1854720 | 0 | 5063250 | 393000 | 0 | 214380 | 7083000 | 474968 | 192384 | 0 | 4967998 | 0 | 0 | 2409600 | 0 | 3150720 | 75735 | 2031360 | 4487040 | 1709527 | 7610000 | 2521200 | 634800 | 1785636 | 18959 | 6676691 | 1301193 | 1337344 | 1077300 | 1468320 | 2435520 | 7601200 | 1431360 | 267520 | 2520000 | 2018564 | 0 | 553320 | 126313 |  | 17286545 | 0 | 8473248 | 0 | 0 | 3262080 | 0 | 0 | 100800 | 0 | 0 | 2102435 | 535494 | 0 | 0 | 0 | 0 | 241597 | 156693 | 606592 | 177800 | 26829 | 151640 | 358560 | 166461 | 504720 | 0 | 236772 | 1876800 | 0 | 0 | 0 | 0 | 0 | 0 | 4416882 | 0 | 444192 | 0 | 4596082 | 0 | 8786836 | 1058880 | 0 | 1599264 | 0 | 1576656 | 0 | 26790 | 1437984 | 9837600 | 5097845 | 0 | 90000 | 19020 |  | 186194081 | 75253097 | 261447178 | 107074532 | 17286545 | 54658770 | 0 | 58304390 | 11714400 | 3195283 | 3262080 | 2897901 | 2509440 | 543837 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8233878.99 | 0 | 0 | 9119936.4 | 8052540 |  | 0 | 8400630 | 7486323.96 | 0 | 0 | 10866320.1 | 6381641.76 | 0 | 0 | 0 | 5158563.84 | 10792512 | 2065362.98 | 0 | 0 | 0 | 9515988 | 7527319.4 | 7142672.74 | 326835 | 450000 | 0 | 0 | 0 | 3852528 | 0 | 371326.41 | 491400 | 5068000 | 0 | 479930.69 | 0 | 0 | 0 | 0 |  | 0 | 0 | 3177312.6 | 1941324 | 1094112 | 4368038.4 | 600687.36 | 1110542.4 | 1068083.44 | 0 | 0 | 5493168 | 7286000 | 4668080 | 1294690.44 | 3828936.5 | 526724.64 | 1841952 | 0 | 1556144.46 | 0 | 502576 | 8353556.9 | 607435.92 | 139455 | 1328775 | 366405 | 18820800 | 4383057.6 | 0 | 574517.52 | 151430 | 1681000 | 0 | 2064444 | 0 | 3539796.9 | 3800160 | 2586972.48 | 3542515.2 | 0 | 8759422.5 | 860670 | 0 | 437335.2 | 7153830 | 356226 | 146211.84 | 0 | 37558064.88 | 0 | 0 | 12529920 | 0 | 31003084.8 | 885342.15 | 16555584 | 48684384 | 12052165.35 | 7077300 | 22993344 | 5998860 | 15552889.56 | 0 | 50475783.96 | 11333391.03 | 11755253.76 | 10751454 | 12583502.4 | 16220563.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99570499.2 | 0 | 8896910.4 | 0 | 0 | 45212428.8 | 0 | 0 | 1057392 | 0 | 0 | 2375751.55 | 830015.7 | 0 | 0 | 0 | 0 | 2377314.48 | 1592000.88 | 5368339.2 | 1369060 | 362728.08 | 1469391.6 | 3474446.4 | 1614671.7 | 969062.4 | 0 | 179236.404 | 11317104 | 0 | 0 | 0 | 0 | 0 | 0 | 5830284.24 | 0 | 666288 | 0 | 5377415.94 | 0 | 8698967.64 | 11054707.2 | 0 | 15177015.36 | 0 | 12234850.56 | 0 | 296029.5 | 10626701.76 | 43187064 | 0 | 0 | 0 | 0 |  | 545806986.66 | 301185676.994 | 846992663.654 | 108379179.484 | 99570499.2 | 57645078.3 | 0 | 432713471.35 | 54504168 | 862726.41 | 45212428.8 | 27951510.46 | 18820800 | 1332801.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 331 |  | 0 | 320 | 290 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 25 | 33 | 0 | 0 | 41 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 270 | 285 | 207 | 8 | 140 | 20 | 52 | 0 | 35 | 0 | 0 | 36 | 19 | 0 | 25 | 19 | 90 | 164 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 0 | 160 | 61 | 75 | 0 | 220 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 275 | 0 | 0 | 35 | 0 | 130 | 0 | 100 | 200 | 20 | 303 | 115 | 52 | 51 | 4 | 305 | 54 | 51 | 50 | 50 | 100 | 321 | 84 | 34 | 162 | 53 | 0 | 17 | 24 |  | 719 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 22 | 0 | 172 | 0 | 336 | 45 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 300 | 224 | 0 | 0 | 2 |  | 10236 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 341 | 321 | 0 | 0 | 340 | 275 | 0 | 0 | 50 | 254 | 0 | 0 | 0 | 102 | 150 | 48 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 102 | 40 | 58 | 50 | 18 | 5 | 80 | 0 | 0 | 280 | 270 | 214 | 8 | 141 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 136 | 155 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 161 | 63 | 80 | 0 | 193 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 280 | 0 | 0 | 165 | 0 | 149 | 0 | 100 | 200 | 130 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 100 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 | 0 |  | 717 | 0 | 320 | 0 | 0 | 170 | 0 | 0 | 7 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 50 | 36 | 94 | 27 | 24 | 39 | 52 | 29 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 22 | 0 | 167 | 0 | 330 | 103 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 480 | 228 | 0 | 17 | 0 |  | 12503 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 340 | 0 | 0 | 340 | 305 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 82 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 21 | 15 | 135 | 0 | 0 | 330 | 340 | 210 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 155 | 0 | 22 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 60 | 81 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 137 | 316 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 100 | 98 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 734 | 0 | 410 | 0 | 0 | 225 | 0 | 0 | 25 | 40 | 0 | 88 | 30 | 110 | 0 | 0 | 0 | 50 | 35 | 94 | 28 | 50 | 40 | 52 | 30 | 22 | 0 | 11 | 78 | 0 | 0 | 15 | 10 | 0 | 0 | 220 | 0 | 22 | 100 | 220 | 0 | 400 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 340 | 0 | 0 | 340 | 305 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 82 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 34 | 100 | 90 | 50 | 21 | 5 | 80 | 0 | 0 | 310 | 310 | 210 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 150 | 0 | 22 | 1.6 | 43 | 0 | 50 | 0 | 163 | 160 | 60 | 81 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 100 | 90 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 734 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 110 | 0 | 0 | 0 | 50 | 34 | 90 | 28 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 50 | 200 | 0 | 400 | 70 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 358 | 283 | 0 | 0 | 340 | 295 | 0 | 0 | 40 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 18 | 25 | 27 | 28 |  | 8 | 0 | 82 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 21 | 8 | 80 | 0 | 0 | 280 | 330 | 184 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 96 | 198 | 0 | 21 | 1 | 43 | 0 | 50 | 0 | 110 | 161 | 40 | 81 | 0 | 166 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 86 | 0 | 60 | 200 | 80 | 317 | 115 | 0 | 0 | 2 | 195 | 54 | 0 | 0 | 49 | 85 | 320 | 93 | 31 | 90 | 17 | 0 | 17 | 17 | 0 | 721 | 0 | 290 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 88 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 12 | 0 | 182 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 201 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 9031 | 7:00
| Highest Generation |  | 12503 | 19:00
| Day Peak Generation |  | 10236 | 12:00
| Evening Peak Generation |  | 12503 | 19:00
| HVDC Max Flow |  | 720 | 8:00
| HVDC EvPeak Flow |  | 717 | 19:00
| Load factor L.F |  | 87.13%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-30
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10236 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9254 | MW
Evening Peak Generation : |  | 12503 | MW Hour : | 19:00 | Available Max Generation : |  | 15149 | MW
E.P. Demand (at gen end) : |  | 12503 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12503 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2149 | MW
Total Gen. (MKWH) : |  | 261.4472 | System Load Factor : | 87.13% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -176 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-30
Actual : | 106.56 | Ft.(MSL) , | Rule curve : | 105.76 | Ft.( MSL )
Gas Consumed : | Total = | 1186.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 166024257.784
: |  | Coal : | 54504168 | Oil : | 505877410.61 | Total : | 726405836.394
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4598.0565 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1568.3071 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1405.991 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1270.7296 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1148.1756 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 926.5489 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.0152 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 238.4009 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 714.6296 |  |  | 0 | 0%
Total | 0 |  | 12382.8544 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Fenchuganj 3,4
7) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar 230/132 kV To2 transformer was under shut down from 09:42 to 12:06 for A/M.
b) Mymensingh-Kishoreganj 132 kV Ckt-2 was shut down at 07:36(30/9/2021) for C/M.
c) Ashuganj-Cumilla(N) 230 kV Ckt-2 was shut down at 09:24 for C/M and was switched on at 22:20
from Comilla(N) end.
d) Dohazari-Cox'sbazar 132 kv Ckt-2 was under shut down from 10:06 to 16:01 for D/W.
e) Feni 132/33 kV T-1 transformer was under shut down from 09:37 to10:42 for C/M.
f) Manikganj 132/33 kV T-3 transformer along with Kabirpur 132 kV Ckt-1 were under shut down from
09:25 to 11:28 for R/h maintenance at Manikganj end.
g) Mymensingh 132/33 kV T-1 & T-2 transformers tripped at 10:30 due to 33 kV Akua feeder fault and |  |  |  |  | About 126 MW power interruption occurred under Mymensingh S/S area
were switched on at 10:36. |  |  |  |  | from 10:30 to 10:36.
h) Satkhira132/33 kV T-1 transformer was under shut down from 08:10 to09:26 for C/M.
i) Savar 132/33 kV T-3 transformer was under shut down from 08:39 to15:18 for D/W.
j) After maintenance Tongi-Ghorashal 230 kV Ckt-2 was switched on at 10:07.
k) Meghnaghat-Aminbazar 230 kV Ckt-1 was under shut down from 12:14 to 16:16 for C/M.
l) Feni 132/33 kV T-2 transformer was under shut down from 10:44 to12:02 for C/M.
m) Feni-Chauddagram 132 kv Ckt-2 was under shut down from 12:25 to 13:25 for C/M.
n) Kodda 132/33 kV T-2 & T-4 transformers tripped at 12:01 due to 33 kV I-3,I-5,I-14 feeder fault and |  |  |  |  | About 100 MW power interruption occurred under Kodda S/S area
were switched on at 12:14. |  |  |  |  | from 12:01 to 12:14.
o) Purbachal 132 kV Bus-1 & 2 were energized at 12:15 for 1st time.
p) Purbachal 132/33 kV T-1 transformer was energized at 13:07.
q) Purbachal 132/33 kV T-2 transformer was energized at 12:28.
r) Kushiara 163 MW tripped at 11:49 due to tripping of exhaust fan and GT was synchronized at 12:58.
s) Ashuganj unit-3 synchronized at 12:45.
t) Feni-Chowmuhani 132 kv Ckt-2 was under shut down from 14:57 to 15:44 for C/M.
u) Hathazari-Kaptai 132 kV Ckt-1 tripped at 14:02 from both ends showing Dist.Z1,B at Hathazari end
and E/F,B at Kaptai end and was switched on at 14:44.
v) Hathazari-Kaptai 132 kV Ckt-2 tripped at 14:02 from both ends showing General trip,Y,B at Hathazari end
and E/F,Y,B at Kaptai end and was switched on at 14:46.
w) Sylhet 132/33 kV T-1A & T-1B transformers were under shut down from 20:50 to 21:48 for R/H maint. |  |  |  |  | About 30 MW power interruption occurred under Sylhet S/S area
at B-phase,isolator of 33 kV side. |  |  |  |  | from 20:50 to 21:48.
x) Chowmuhoni 132/33 kV T-3 transformer was under shut down from 11:30 to 16:37 for C/M.
y) Mirpur 132 kV reserve Bus was switched on at 21:11.
z) Dohazari-Cox'sbazar 132 kv Ckt-1 & 2 were shut down at 05:43(30/9/2021) for D/W and Ckt-1 & 2 |  |  |  |  | About 100 MW power interruption occurred under Matarbari &
were switched on at 10:36 & 11:48 respectively. |  |  |  |  | Cox'sbazar S/S areas from 05:43(30/9/2021) to 10:36.
aa) Mymensingh-Kishoreganj 132 kV Ckt-2 was shut down at 07:36(30/9/2021) for C/M.
ab) Sreenagar 132/33 kV T-1 transformer was under shut down from 07:25(30/9/2021) to 09:11 for |  |  |  |  | About 15 MW power interruption occurred under Sreenagar S/S area
R/H maintenance at R,Bus isolator of 33 kV PBS feeder-1. |  |  |  |  | from 07:25(30/9/2021) to 09:11.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7417909 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 341 | 9029640 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 321 | 7818000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 7707000 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6744436 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 50 | 1284435
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 48 | 224009 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 435780 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 254 | 6136194 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 565632
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1303560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1096800
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 973780
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 724409
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1235040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 758700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 832200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 398400
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 4967998 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3150720
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 634800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 1431360 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2520000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 126313
| Dhaka area Total |  |  |  | 5719 | 3332 | 67517115
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 51661
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 75735
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 551520
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 159 | 3195283 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1785636
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 327558
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 203280 | Engine problem
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2031360
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 476736
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 373920
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 58 | 125760 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18959
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 6676691
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1301193
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1337344
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2435520
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2018564
| Chattogram area Total |  |  |  | 2382 | 1450 | 25786720
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 721678 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 5074000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7423200 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7286000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 466128 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1315680
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1003636 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 910026 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 1709527 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 49760 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 141 | 3329510 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 4487040
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 478296
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 185940
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 2509440
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 759300
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 874718
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 488540 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1077300 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1468320 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 553320 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1927 | 42171359
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 155 | 4134960 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 452376
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9500
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 165 | 2409600 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2521200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 267520
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 179760
| Mymensingh Area Total |  |  |  | 709 | 479 | 9974916
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1025000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3105085
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 161 | 3654000 | GT-2 under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1159800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1313184 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1854720
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 193 | 5063250 | Gas shortage
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 393000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 474968
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7083000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 7610000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 214380
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7601200 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1686 | 40743971
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 717 | 17286545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 7 | 100800 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 170 | 3262080 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8473248 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 103 | 1058880
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1317 | 30181553
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 535494 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2102435 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 444192 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 9837600 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 228 | 5097845
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 90000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 864 | 18107566
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 241597
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 36 | 156693 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 177800 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 24 | 26829 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 151640 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 166 | 4416882 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 167 | 4596082 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 330 | 8786836 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 166461 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 504720
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236772
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 358560
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 606592 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 95 | 1599264 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1437984
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19020
| Rajshahi Area Total |  |  |  | 2179 | 1255 | 23483732
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1876800
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1576656
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26790
| Rangpur Area Total |  |  |  | 605 | 193 | 3480246
| Total |  |  |  | 21180 | 12503 | 261447178
| Eastern Grid Total |  |  |  | 14221 | 8874 | 186194081
| Western Grid Total |  |  |  | 6959 | 3629 | 75253097
| National Grid Total |  |  |  | 21180 | 12503 | 261447178
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-29
(a) ENTIRE EASTERN GRID : |  | 8334 | MW | (b) ENTIRE WESTERN GRID : |  | 3565 | MW
i) Dhaka area |  | 4425 | MW | i) Khulna area |  | 1301 | MW
ii) Chittagong area |  | 1242 | MW | ii) Rajshahi area |  | 1228 | MW
iii) Comilla area |  | 1103 | MW | iii) Barisal area |  | 311 | MW
iv) Mymensingh area |  | 1021 | MW | iv) Rangpur area |  | 725 | MW
v) Sylhet area |  | 543 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11899 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 15:00 | Kishoreganj | 130 | 21:00 | Jessore | 91 | 18:30
Munsiganj | 92 | 0:00 | Netrokona | 118 | 19:00 | Benapol | 48 | 18:30
Sonargaon | 78 | 0:00 | Jamalpur | 153 | 21:00 | Jhenida(Old) | 98 | 18:30
Shyampur | 188 | 0:00 | Sherpur | 136 | 20:00 | Bottail | 116 | 18:30
Bhulta | 198 | 0:00 | Srimongal | 52 | 18:30 | G.K Project | 50 | 19:30
Madanganj | 51 | 13:00 | Shahjibazar | 118 | 21:00 | Faridpur | 127 | 20:00
Shitalakhya | 117 | 11:00 | Fenchuganj | 52 | 18:00 | Rajbari | 48 | 18:30
Rahim steel | 16 | 12:00 | Kulawara | 50 | 18:00 | Madaripur | 85 | 20:00
Matuail | 66 | 14:00 | Sylhet | 148 | 18:00 | Sariatpur | 58 | 19:30
Ghorasal | 80 | 23:00 | Chatak | 35 | 21:00 | Gopalganj | 74 | 22:00
Narsingdi | 179 | 21:00 | Sunamganj | 56 | 21:00 | Bagerhat | 81 | 18:30
Haripur (SBU) | 125 | 21:00 | Biani Bazar | 70 | 19:30 | Mongla | 34 | 9:00
Sreenagar | 36 | 18:30 | Comilla (S) | 136 | 18:30 | Satkhira | 81 | 18:30
Ullon | 71 | 18:00 | Comilla(N) | 155 | 13:00 | Gallamari | 29 | 19:00
Hasnabad | 83 | 19:30 | Chandpur | 70 | 23:00 | Magura | 48 | 18:30
Magbazar | 89 | 15:00 | Feni | 115 | 18:00 | Norail | 42 | 18:30
Maniknagar | 70 | 13:00 | Chowmuhani | 188 | 21:00 | Chuadanga | 83 | 18:30
Bangabhaban | 12 | 10:00 | Ashuganj | 44 | 23:00 | Barisal(N) | 38 | 20:00
Motijheel | 27 | 12:00 | Daudkandi | 144 | 21:00 | Barisal (S) | 98 | 18:00
Narinda | 64 | 13:00 | B.Baria | 156 | 21:00 | Patuakhali | 95 | 21:00
Kazla | 81 | 19:30 | Ramganj | 78 | 22:00 | Bhandaria | 44 | 19:30
Dhanmondi | 200 | 13:00 | Chaddagram | 44 | 23:00 | Borguna | 14 | 18:00
Lalbag | 78 | 13:00 | PHP | 10 | 19:30 | Borhan Uddin | 37 | 22:00
Madartek | 70 | 23:00 | Kochua | 60 | 18:30 | Ishurdi | 64 | 19:00
Dhaka University | 35 | 12:00 | Madunaghat | 55 | 11:00 | Ruppur Paromanobik | 4 | 20:00
Aftabnagar | 14 | 11:00 | Hathazari | 96 | 18:30 | Natore | 116 | 21:00
Fatullah | 59 | 11:00 | Khulshi | 198 | 12:00 | Bogra | 160 | 21:00
Nawabganj | 48 | 20:00 | Halishahar | 141 | 17:00 | Noagaon | 98 | 20:00
Keraniganj | 68 | 19:00 | Baraulia | 146 | 0:00 | Rajshahi | 137 | 20:00
Mirpur | 117 | 12:00 | Sikalbaha | 42 | 15:00 | Rajshahi New | 16 | 20:00
Kalyanpur | 90 | 18:00 | Dohazari | 92 | 19:30 | C.Nawabganj | 53 | 20:00
Gulshan | 116 | 14:00 | Cox'sbazar | 92 | 18:30 | Amnura | 43 | 20:00
Uttara | 77 | 14:00 | Chandraghona | 26 | 18:30 | Pabna | 101 | 19:00
Uttara New | 27 | 11:00 | Kaptai | 4.5 | 18:00 | Shahjadpur | 82 | 20:00
Kamrangirchar | 96 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 101 | 20:00
Savar | 169 | 17:00 | Bakulia | 114 | 18:00 | Niyamatpur | 65 | 1:00
Bhasantec | 130 | 12:00 | Julda | 20 | 12:00 | Joypurhat | 56 | 20:00
Agargaon | 82 | 13:00 | TK chemical | 27.5 | 18:30 | Sherpur(Bogura) | 56 | 18:30
Satmosjid | 103 | 20:00 | Modern Steel | 5 | 16:00 | Mohastangor | 64 | 19:00
Tongi | 126 | 12:00 | Shahmirpur | 24.5 | 18:00 | Bhangura | 28 | 20:00
Kabirpur | 245 | 16:00 | Khagrachhari | 26 | 18:00 | Rangpur | 126 | 21:00
Basundhara | 173 | 14:00 | Matarbari | 36 | 19:30 | Lalmonirhat | 40 | 19:00
Manikganj | 66 | 19:00 | Baroiar Hat | 46 | 18:00 | Saidpur | 90 | 19:30
Joydevpur | 170 | 18:30 | Rangamati | 13 | 18:00 | Purbasadipur | 95 | 20:00
New Tongi | 90 | 10:00 | Abul Khair 230 | 179 | 16:00 | Thakurgaon | 79 | 20:00
Kodda | 265 | 18:30 | BSRM | 150 | 13:00 | Palashbari | 116 | 20:00
Dhamrai | 102 | 18:30 | GPH Ispat | 95 | 9:00 | Barapukuria | 48 | 21:00
Rajendrapur | 104 | 19:00 | Agrabad | 0 | 1:00 | Panchagar | 53 | 19:00
Valuka | 104 | 18:00 | Goalpara | 27 | 19:00 | Joldhaka | 56 | 21:00
Tangail | 207 | 20:00 | Central S/S | 81 | 18:30 | Kurigram | 57 | 20:00
Mymensing | 222 | 19:00 | Noapara | 43 | 18:30 | Mithapukur | 29 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 4:00 | 402 | 15:00 | Kaliakoir | 397 | 0.33333 | 386 | 0.625
| Bheramara | 406 | 1:00 | 398 | 19:30 | Bhulta | 387 | 0.041667 | 377 | 0.66667
| Ashuganj(N) | 394 | 9:00 | 385 | 16:00 | Gopalganj | 407 | 0.625 | 390 | 0.91667
| Payra | 413 | 18:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 13:00 | 230 | 1:00 | Hathazari | 238 | 18:30 | 227 | 6:00
| Ishurdi | 235 | 18:00 | 227 | 1:00 | Megnaghat | 233 | 6:00 | 230 | 11:00
| Ashuganj | 241 | 1:00 | 236 | 12:00 | Fenchuganj | 244 | 1:00 | 240 | 12:00
| Serajganj | 230 | 18:00 | 224 | 21:00 | Siddhirganj | 232 | 1:00 | 227 | 9:00
| Baghabari | 231 | 17:00 | 227 | 20:00 | Maniknagar | 230 | 1:00 | 224 | 16:00
| Barapukuria | 235 | 18:00 | 223 | 21:00 | Agargaon | 228 | 6:00 | 221 | 16:00
| Bogra | 226 | 18:00 | 213 | 21:00 | Barisal | 243 | 18:00 | 231 | 19:30
| Rajshahi | 230 | 8:00 | 220 | 1:00 | Bhola 225 MW | 244 | 6:00 | 236 | 22:00
| Khulna South | 234 | 6:00 | 224 | 1:00 | AKSML | 234 | 18:00 | 221 | 9:00
| Rampura | 230 | 1:00 | 225 | 15:00 | BSRM | 235 | 18:00 | 221 | 9:00
| Haripur | 229 | 2:00 | 225 | 15:00 | Bibiyana | 242 | 2:00 | 238 | 17:00
| Hasnabad | 228 | 1:00 | 220 | 11:00 | Bhulta | 232 | 1:00 | 227 | 10:00
| Shyampur | 228 | 18:00 | 222 | 16:00 | Ashuganj (S) | 238 | 1:00 | 233 | 15:00
| Aminbazar | 229 | 1:00 | 224 | 2:00 | Kaliakoir | 229 | 7:00 | 223 | 15:00
| Tongi | 228 | 1:00 | 220 | 15:00 | GPH | 236 | 18:00 | 221 | 9:00
| Comilla (N) | 233 | 18:00 | 227 | 9:00 | Jhenaidah | 230 | 11:00 | 221 | 3:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 18:00 | 130 | 14:00 | Madanhat | 139 | 0.75 | 128 | 0.375
| Munsiganj | 134 | 3:00 | 130 | 10:00 | Hathazari | 138 | 0.77083 | 133 | 0.20833
| Sonargaon | 133 | 18:00 | 128 | 10:00 | Khulshi | 136 | 0.75 | 126 | 0.41667
| Shyampur | 136 | 4:00 | 132 | 10:00 | Halishahar | 137 | 0.75 | 126 | 0.41667
| Bhulta | 128 | 18:00 | 125 | 5:00 | Baraulia | 138 | 0.75 | 127 | 0.29167
| Madanganj | 133 | 3:00 | 129 | 15:00 | Sikalbaha | 139 | 0.75 | 127 | 0.41667
| Shitalakhya | 135 | 18:00 | 130 | 10:00 | Dohazari | 133 | 0.75 | 124 | 0.33333
| Rahim steal | 133 | 1:00 | 130 | 10:00 | Cox'sbazar | 124 | 0.75 | 110 | 0.45833
| Matuail | 134 | 18:00 | 130 | 14:00 | Chandraghona | 137 | 0.75 | 128 | 0.41667
| Ghorasal | 138 | 1:00 | 137 | 9:00 | Kaptai | 135 | 0.041667 | 132 | 0.25
| Narsinghdi | 133 | 7:00 | 124 | 21:00 | A. Khaer Stl. | 135 | 0.79167 | 129 | 0.20833
| Haripur (SBU) | 133 | 1:00 | 130 | 15:00 | Bakulia | 138 | 0.75 | 129 | 0.41667
| Sreenagar | 133 | 3:00 | 130 | 10:00 | Julda | 138 | 0.77083 | 127 | 0.41667
| Ullon | 135 | 6:00 | 129 | 16:00 | TK Chemical | 138 | 0.77083 | 127 | 0.41667
| Hasnabad | 135 | 1:00 | 133 | 9:00 | Modern Steel | 137 | 0.75 | 125 | 0.41667
| Magbazar | 135 | 1:00 | 130 | 10:00 | Shahmirpur | 139 | 0.77083 | 127 | 0.41667
| Maniknagar | 135 | 3:00 | 130 | 16:00 | Khagrachhari | 136 | 0.75 | 128 | 0.41667
| Bangabhaban | 135 | 3:00 | 130 | 16:00 | Matarbari | 129 | 0.79167 | 110 | 0.41667
| Motijheel | 135 | 3:00 | 130 | 16:00 | Baroiar Hat | 134 | 0.58333 | 131 | 0.20833
| Narinda | 135 | 3:00 | 130 | 16:00 | Rangamati | 137 | 18:30 | 128 | 10:00
| Kazla | 135 | 3:00 | 130 | 16:00 | Agrabad | 0 | #N/A | 0 | #N/A
| Dhanmondi | 133 | 1:00 | 129 | 16:00 | Goalpara S/S | 138 | 17:00 | 134 | 0.041667
| Lalbag | 134 | 1:00 | 129 | 16:00 | Khulna Central S/S | 138 | 18:00 | 134 | 0.77083
| Madartek | 135 | 4:00 | 129 | 15:00 | Noapara | 136 | 6:00 | 130 | 0.041667
| Dhaka University | 134 | 1:00 | 129 | 16:00 | Jessore | 132 | 17:00 | 126 | 0.041667
| Aftabnagar | 135 | 2:00 | 129 | 15:00 | Benapol | 134 | 0.25 | 125 | 0.79167
| Fatullah | 136 | 18:00 | 131 | 16:00 | Jhenida(Old) | 133 | 6:00 | 123 | 0.8125
| Nawabganj | 134 | 7:00 | 130 | 16:00 | Bottail | 134 | 0.25 | 128 | 0.041667
| Keraniganj | 134 | 1:00 | 130 | 15:00 | G.K Project | 138 | 0.29167 | 135 | 0.041667
| Mirpur | 132 | 1:00 | 127 | 9:00 | Faridpur | 137 | 0.29167 | 128 | 0.8125
| Kalyanpur | 132 | 18:00 | 127 | 10:00 | Rajbari | 136 | 0.25 | 128 | 0.79167
| Gulshan | 135 | 6:00 | 129 | 15:00 | Madaripur | 140 | 0.25 | 132 | 0.8125
| Uttara | 136 | 19:00 | 128 | 3:00 | Shariyatpur S/S | 140 | 7:00 | 131 | 0.875
| Uttara New | 131 | 11:00 | 125 | 3:00 | Gopalganj | 144 | 0.70833 | 134 | 0.79167
| Kamrangirchar | 133 | 1:00 | 130 | 12:00 | Bagerhat | 136 | 15:00 | 130 | 0.041667
| Savar | 133 | 18:00 | 126 | 9:00 | Mongla | 135 | 16:00 | 129 | 0.041667
| Bhasantec | 135 | 1:00 | 130 | 15:00 | Satkhira | 137 | 6:00 | 131 | 18:30
| Agargaon | 136 | 1:00 | 132 | 9:00 | Gallamari | 139 | 0.75 | 133 | 1:00
| Satmosjid | 135 | 1:00 | 130 | 16:00 | Magura | 134 | 6:00 | 121 | 0.77083
| Tongi | 138 | 1:00 | 131 | 15:00 | Narail | 131 | 0.25 | 120 | 0.875
| Kabirpur | 136 | 7:00 | 128 | 9:00 | Chuadanga | 137 | 6:00 | 128 | 0.041667
| Basundhara | 136 | 18:00 | 129 | 15:00 | Barisal(N) | 142 | 6:00 | 132 | 0.95833
| Manikganj | 140 | 7:00 | 133 | 9:00 | Barisal (S) | 139 | 7:00 | 131 | 21:00
| Joydevpur | 138 | 19:00 | 132 | 14:00 | Patuakhali(S) | 137 | 0.29167 | 127 | 0.95833
| New Tongi | 138 | 4:00 | 129 | 16:00 | Bhandaria | 136 | 0.29167 | 126 | 0.875
| Kodda | 136 | 19:00 | 125 | 15:00 | Borguna | 138 | 0.375 | 129 | 0.95833
| Dhamrai | 137 | 17:00 | 133 | 21:00 | Jhenaidah(230kV S/S) | 140 | 18:00 | 122 | 1:00
| Rajendrapur | 134 | 18:30 | 123 | 16:00 | Ishurdi | 137 | 18:00 | 132 | 20:00
| Valuka | 123 | 11:00 | 109 | 22:00 | Ruppur Paromanobik | 135 | 17:00 | 132 | 19:30
| Tangail | 130 | 11:00 | 122 | 23:00 | Natore | 137 | 18:00 | 129 | 1:00
| Mymensing | 126 | 11:00 | 115 | 19:00 | Bogra | 136 | 18:00 | 125 | 20:00
| Kishorganj | 129 | 11:00 | 118 | 22:00 | Noagaon | 128 | 18:00 | 120 | 20:00
| Netrokona | 123 | 11:00 | 109 | 22:00 | Rajshahi | 136 | 18:00 | 129 | 1:00
| Jamalpur | 129 | 18:00 | 121 | 6:00 | Rajshahi New | 136 | 18:00 | 128 | 1:00
| Sherpur | 125 | 2:00 | 117 | 7:00 | C.Nawabganj | 139 | 18:00 | 128 | 1:00
| Srimongal | 138 | 7:00 | 132 | 21:00 | Amnura | 138 | 18:00 | 126 | 1:00
| Shahjibazar | 136 | 9:00 | 131 | 19:00 | Pabna | 135 | 18:00 | 129 | 20:00
| Fenchuganj | 136 | 7:00 | 133 | 1:00 | Shahjadpur | 136 | 18:00 | 133 | 20:00
| Khulawara | 136 | 7:00 | 131 | 19:30 | Serajganj | 132 | 18:00 | 128 | 20:00
| Sylhet | 131 | 1:00 | 129 | 19:30 | Niyamatpur | 130 | 18:00 | 116 | 20:00
| Chatak | 132 | 7:00 | 128 | 18:30 | Joypurhat | 133 | 18:00 | 119 | 20:00
| Sunamganj | 130 | 8:00 | 123 | 20:00 | Sherpur(Bogura) | 134 | 18:00 | 126 | 20:00
| Biani Bazar | 132 | 10:00 | 125 | 19:30 | Mohastangor | 133 | 18:00 | 122 | 20:00
| Comilla(s) | 129 | 6:00 | 125 | 14:00 | Bangura | 137 | 18:00 | 132 | 20:00
| Comilla(n) | 138 | 18:00 | 133 | 10:00 | Rangpur | 127 | 18:00 | 114 | 21:00
| Chandpur | 142 | 11:00 | 137 | 23:00 | Lalmonirhat | 128 | 18:00 | 115 | 21:00
| Feni | 136 | 18:00 | 129 | 10:00 | Saidpur | 132 | 18:00 | 117 | 21:00
| Chowmuhani | 136 | 19:00 | 130 | 1:00 | Purbasadipur | 128 | 17:00 | 110 | 21:00
| Ashuganj | 139 | 11:00 | 134 | 19:00 | Thakurgaon | 131 | 17:00 | 112 | 21:00
| Daudkandi | 134 | 18:00 | 128 | 21:00 | Palashbari | 131 | 18:00 | 120 | 1:00
| B.Baria | 134 | 11:00 | 127 | 21:00 | Barapukuria | 135 | 18:00 | 123 | 21:00
| Ramganj | 136 | 17:00 | 130 | 23:00 | Panchagar | 134 | 0.75 | 112 | 0.875
| Chaddagram | 137 | 18:00 | 132 | 4:00 | Joldhaka | 126 | 0.70833 | 109 | 0.875
| PHP | 136 | 18:00 | 128 | 10:00 | Kurigram | 131 | 0.45833 | 116 | 0.041667
| Kochua | 138 | 4:00 | 134 | 7:00 | Mithapukur | 131 | 0.70833 | 119 | 0.875
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 46 | 8394 | 3421 | 11815 |  |  |  | QF-LDC-11
0:30 | 98 | 8204 | 3278.5 | 11482.5 | Date: | 2021-09-29
1:00 | 150 | 8014 | 3136 | 11150
1:30 | 115 | 7826 | 3150 | 10976
2:00 | 80 | 7638 | 3164 | 10802
2:30 | 56 | 7561.5 | 3116 | 10677.5 | [5 empty] | Gen. at Eve. Peak | 12503 | 12503 MW (19:00 )
3:00 | 32 | 7485 | 3068 | 10553 | [6 empty] | 19:00
3:30 | 50 | 7441 | 2992.5 | 10433.5 | [5 empty] | Gen. at Day Peak | 10236 | 10236 MW (12:00 )
4:00 | 68 | 7397 | 2917 | 10314 | [6 empty] | 12:00
4:30 | 76 | 7310.5 | 2835 | 10145.5 | [5 empty] | Highest Generation | 12503
5:00 | 84 | 7224 | 2753 | 9977 | [6 empty] | 19:00
5:30 | 53 | 7001 | 2616.5 | 9617.5
6:00 | 22 | 6778 | 2480 | 9258
6:30 | 47 | 6650.5 | 2494 | 9144.5
7:00 | 72 | 6523 | 2508 | 9031
7:30 | 61 | 6579.5 | 2514.5 | 9094
8:00 | 50 | 6636 | 2521 | 9157
8:30 | 100 | 6741 | 2576.5 | 9317.5
9:00 | 150 | 6846 | 2632 | 9478
9:30 | 195 | 6920.5 | 2663.5 | 9584
10:00 | 240 | 6995 | 2695 | 9690
10:30 | 168 | 7170 | 2676 | 9846
11:00 | 96 | 7345 | 2657 | 10002
11:30 | 83 | 7396 | 2723 | 10119
12:00 | 70 | 7447 | 2789 | 10236
12:30 | 76 | 7507.5 | 2860.5 | 10368
13:00 | 82 | 7568 | 2932 | 10500
13:30 | 57 | 7610 | 2921 | 10531
14:00 | 32 | 7652 | 2910 | 10562
14:30 | 145 | 7743 | 2957.5 | 10700.5
15:00 | 258 | 7834 | 3005 | 10839
15:30 | 279 | 7808.5 | 2971 | 10779.5
16:00 | 300 | 7783 | 2937 | 10720
16:30 | 221 | 7642.5 | 2828.5 | 10471
17:00 | 142 | 7502 | 2720 | 10222
17:30 | 126 | 7816 | 2896.5 | 10712.5
18:00 | 110 | 8130 | 3073 | 11203
18:30 | 118 | 8502 | 3351 | 11853
19:00 | 126 | 8874 | 3629 | 12503
19:30 | 32 | 8741 | 3738 | 12479
20:00 | 80 | 8740 | 3719 | 12459 |  |  |  | Executive Engineer
20:30 | 53 | 8639.5 | 3744 | 12383.5 |  |  |  | Network Operation Division
21:00 | 26 | 8539 | 3769 | 12308
21:30 | 20 | 8498 | 3738 | 12236
22:00 | 14 | 8457 | 3707 | 12164 |  |  |  |  | Page 6 of 7
22:30 | 31 | 8449 | 3615 | 12064
23:00 | 48 | 8441 | 3523 | 11964
23:30 | 47 | 8417.5 | 3472 | 11889.5
24:00 | 46 | 8394 | 3421 | 11815
12503 MW (19:00 )
10236 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-29 |  | Energy |  | 261447178
[13 empty] | 2021-09-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4507 | 717 | 2340 | 0 | 3117 | 520 | 159 | 120 | 213 | 122 | 0 | 0
0:30 | 4507.5 | 713.5 | 2344.5 | 0 | 2887 | 503.5 | 138.5 | 120 | 149 | 119 | 0 | 0 | Date: | 2021-09-29
1:00 | 4508 | 710 | 2349 | 0 | 2657 | 487 | 118 | 120 | 85 | 116 | 0 | 0
1:30 | 4514 | 709.5 | 2361.5 | 0 | 2482 | 486.5 | 118 | 120 | 68.5 | 116 | 0 | 0 | [8 empty] | Total Energy | 261.4472 | Total Energy Gen 261.447 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.447 MKWHr
2:00 | 4520 | 709 | 2374 | 0 | 2307 | 486 | 118 | 120 | 52 | 116 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4524 | 709 | 2356 | 0 | 2215.5 | 486.5 | 117.5 | 120 | 36 | 113 | 0 | 0 | [8 empty] | Energy Requirement | 261.4472
3:00 | 4528 | 709 | 2338 | 0 | 2124 | 487 | 117 | 120 | 20 | 110 | 0 | 0
3:30 | 4528.5 | 709.5 | 2310.5 | 0 | 2051.5 | 467.5 | 117 | 120 | 20 | 109 | 0 | 0 | [6 empty] | Shortage
4:00 | 4529 | 710 | 2283 | 0 | 1979 | 448 | 117 | 120 | 20 | 108 | 0 | 0
4:30 | 4544.5 | 710 | 2307.5 | 0 | 1794.5 | 433 | 117 | 120 | 12 | 107 | 0 | 0
5:00 | 4560 | 710 | 2332 | 0 | 1610 | 418 | 117 | 120 | 4 | 106 | 0 | 0
5:30 | 4475.5 | 710 | 2251.5 | 0 | 1440 | 398 | 117 | 120 | 4 | 101 | 0.5 | 0
6:00 | 4391 | 710 | 2171 | 0 | 1270 | 378 | 117 | 120 | 4 | 96 | 1 | 0
6:30 | 4373 | 710 | 2186.5 | 0 | 1159 | 378 | 116.5 | 120 | 4 | 87 | 10.5 | 0 |  |  |  |  | Coal
7:00 | 4355 | 710 | 2202 | 0 | 1048 | 378 | 116 | 120 | 4 | 78 | 20 | 0
7:30 | 4343 | 715 | 2200 | 0 | 1118.5 | 377.5 | 115.5 | 120 | 4 | 73 | 27.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4331 | 720 | 2198 | 0 | 1189 | 377 | 115 | 120 | 4 | 68 | 35 | 0
8:30 | 4383.5 | 720 | 2241 | 0 | 1245.5 | 377 | 115.5 | 120 | 4 | 72 | 39 | 0
9:00 | 4436 | 720 | 2284 | 0 | 1302 | 377 | 116 | 120 | 4 | 76 | 43 | 0
9:30 | 4397.5 | 719.5 | 2308.5 | 0 | 1418 | 376 | 116 | 120 | 4 | 78 | 46.5 | 0
10:00 | 4359 | 719 | 2333 | 0 | 1534 | 375 | 116 | 120 | 4 | 80 | 50 | 0
10:30 | 4334 | 719.5 | 2264 | 0 | 1765.5 | 375.5 | 116 | 120 | 4 | 83 | 64.5 | 0
11:00 | 4309 | 720 | 2195 | 0 | 1997 | 376 | 116 | 120 | 4 | 86 | 79 | 0
11:30 | 4328 | 719.5 | 2132.5 | 0 | 2160 | 378 | 116 | 120 | 4 | 88 | 73 | 0
12:00 | 4347 | 719 | 2070 | 0 | 2323 | 380 | 116 | 120 | 4 | 90 | 67 | 0
12:30 | 4362 | 718 | 2102.5 | 0 | 2390.5 | 394.5 | 116.5 | 120 | 4 | 90 | 70 | 0
13:00 | 4377 | 717 | 2135 | 0 | 2458 | 409 | 117 | 120 | 4 | 90 | 73 | 0
13:30 | 4377 | 717 | 2135 | 0 | 2458 | 409 | 117 | 120 | 4 | 90 | 73 | 0
14:00 | 4377 | 717 | 2135 | 0 | 2458 | 409 | 117 | 120 | 4 | 90 | 73 | 0
14:30 | 4382.5 | 717 | 2188 | 0 | 2532 | 414 | 139.5 | 120 | 12 | 94 | 70.5 | 0
15:00 | 4388 | 717 | 2241 | 0 | 2606 | 419 | 162 | 120 | 20 | 98 | 68 | 0
15:30 | 4422 | 717 | 2242.5 | 0 | 2539 | 419 | 162 | 120 | 20 | 97 | 41 | 0
16:00 | 4456 | 717 | 2244 | 0 | 2472 | 419 | 162 | 120 | 20 | 96 | 14 | 0
16:30 | 4416.5 | 716.5 | 2155.5 | 0 | 2349 | 419.5 | 162 | 120 | 22 | 99 | 11 | 0
17:00 | 4377 | 716 | 2067 | 0 | 2226 | 420 | 162 | 120 | 24 | 102 | 8 | 0
17:30 | 4324 | 716 | 2040.5 | 0 | 2530 | 429.5 | 162 | 140 | 251.5 | 115 | 4 | 0
18:00 | 4271 | 716 | 2014 | 0 | 2834 | 439 | 162 | 160 | 479 | 128 | 0 | 0
18:30 | 4306.5 | 716.5 | 2116.5 | 0 | 3263.5 | 499.5 | 160.5 | 165 | 493 | 132 | 0 | 0
19:00 | 4342 | 717 | 2219 | 0 | 3693 | 560 | 159 | 170 | 507 | 136 | 0 | 0
19:30 | 4436 | 716 | 2359 | 0 | 3473 | 559 | 159 | 170 | 471 | 136 | 0 | 0
20:00 | 4451 | 716 | 2328 | 0 | 3469 | 560 | 159 | 170 | 472 | 134 | 0 | 0
20:30 | 4464 | 716.5 | 2350 | 0 | 3373 | 560 | 159 | 175 | 454 | 132 | 0 | 0
21:00 | 4477 | 717 | 2372 | 0 | 3277 | 560 | 159 | 180 | 436 | 130 | 0 | 0
21:30 | 4479 | 717 | 2351 | 0 | 3242 | 560.5 | 159 | 172.5 | 426 | 129 | 0 | 0
22:00 | 4481 | 717 | 2330 | 0 | 3207 | 561 | 159 | 165 | 416 | 128 | 0 | 0
22:30 | 4484 | 717.5 | 2331.5 | 0 | 3206 | 550.5 | 159 | 142.5 | 346 | 127 | 0 | 0
23:00 | 4487 | 718 | 2333 | 0 | 3205 | 540 | 159 | 120 | 276 | 126 | 0 | 0
23:30 | 4497 | 717.5 | 2336.5 | 0 | 3161 | 530 | 159 | 120 | 244.5 | 124 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.2° C
24:00 | 4507 | 717 | 2340 | 0 | 3117 | 520 | 159 | 120 | 213 | 122 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 261.447 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.447 MKWHr
Note on W13: Author:

## Generation
g | 2021-09-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 43 | 43 | 42 | 42 | 42 | 42 | 41 | 40 | 41 | 41 | 41 | 41 | 42 | 42 | 87 | 87 | 87 | 87 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1375283
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1820000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 6 |  | 8 | 8 | 8 | 8 |  |  | 0 | 51661
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 18 | 12 | 6 |  | 7 | 5 | 4 | 2 | 1 | [9 empty] | 75735
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [16 empty] | 102 |  | 102 | 68 | 68 | 34 | 34 | 17 | 0 | 327558
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 68 | 68 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 51 | 66 | 105 | 105 | 105 | 51 | 70 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1785636
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 50 | [7 empty] | 0 | 49760
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 258 | 253 | 254 | 255 | 255 | 255 | 253 | 254 | 255 | 254 | 256 | 255 | 254 | 252 | 255 | 254 | 254 | 255 |  | 254 | 253 | 253 | 251 | 252 | 250 | 250 | 6136194
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 170 | 145 | 145 | 145 | 145 | 152 | 250 | 250 | 255 | 260 | 275 | 276 | 195 | 195 | 160 | 160 | 183 |  | 280 | 280 | 278 | 145 | 145 | 145 | 145 | 4967998
19 | Ashuganj 195MW PP (APSCL-United) | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 55 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1003636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7417909
26
28 | Ashuganj TPP Unit- 3 | [13 empty] | 20 | 35 | 60 | 65 | 70 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 721678
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 466128
33 | Ashuganj 225 MW CCPP | 214 | 213 | 214 | 214 | 212 | 213 | 212 | 212 | 210 | 201 | 183 | 207 | 210 | 209 | 207 | 207 | 210 | 212 |  | 214 | 213 | 213 | 212 | 212 | 212 | 213 | 5074000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 305 | 305 | 320 | 305 | 315 | 305 | 350 | 350 | 310 | 285 | 270 | 270 | 270 | 285 | 270 | 270 |  | 270 | 285 | 295 | 300 | 300 | 300 | 300 | 7286000
| Ashuganj 450 MW CCPP(North) | 310 | 315 | 310 | 310 | 325 | 315 | 315 | 310 | 345 | 290 | 280 | 270 | 260 | 260 | 285 | 300 | 280 | 280 |  | 280 | 285 | 285 | 285 | 285 | 280 | 280 | 7423200
35 | Ashuganj 55 MW PP (Precision) | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 52 | 52 | 52 | 51 | 53 | 53 | 54 | 55 |  | 55 | 55 | 55 | 55 | 56 | 56 | 56 | 1315680
36 | Chandpur 150 MW CCPP | 140 | 141 | 138 | 138 | 140 | 136 | 138 | 140 | 140 | 142 | 140 | 140 | 140 | 137 | 138 | 139 | 139 | 139 |  | 141 | 140 | 140 | 139 | 140 | 139 | 139 | 3329510
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 404 | 404 | 404 | 404 | 404 | 402 | 364 | 363 | 364 | 363 | 385 | 400 | 399 | 371 | 389 | 360 | 349 | 303 |  | 341 | 347 | 347 | 347 | 346 | 347 | 349 | 9029640
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 7707000
41 | Haripur 360MW CCPP(HPL) | 332 | 332 | 333 | 333 | 331 | 332 | 331 | 333 | 333 | 333 | 332 | 331 | 333 | 302 | 333 | 328 | 282 | 282 |  | 321 | 332 | 331 | 332 | 332 | 332 | 332 | 7818000
42 | RPCL 210MW CCPP | 200 | 200 | 207 | 211 | 210 | 211 | 210 | 205 | 184 | 171 | 171 | 164 | 149 | 149 | 150 | 154 | 157 | 155 |  | 155 | 155 | 157 | 162 | 163 | 162 | 174 | 4134960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 9 | 17 | 17 | 25 | 45 | 34 | 25 | 24 | 42 | 6 | 5 | [9 empty] | 267520
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1025000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 161 | 160 | 160 | 160 | 160 | 160 | 161 | 159 | 159 | 161 | 160 | 160 | 160 | 163 | 161 | 160 | 161 | 160 |  | 161 | 161 | 160 | 162 | 158 | 160 | 159 | 3654000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 57 | 61 | 62 | 61 | 62 | 61 | 62 | 62 |  | 63 | 62 | 63 | 63 | 62 | 63 | 63 | 1313184
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 75 | 79 | 79 | 80 |  | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 1854720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 178 | 179 | 179 | 179 | 206 | 220 | 220 | 220 | 220 | 221 | 221 | 220 | 193 |  | 193 | 213 | 213 | 213 | 219 | 220 | 220 | 5063250
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 393000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 214380
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 47 | 47 | 49 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1159800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 474968
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 280 | 280 | 290 | 270 | 270 | 290 | 300 | 290 | 280 | 280 | 310 | 280 | 300 | 295 | 290 | 270 |  | 270 | 300 | 290 | 290 | 285 | 290 | 300 | 7083000
| Bibiyana South 400 MW | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7601200
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 724409
59 | Tangail Palli Power Gen 22 MW | 24 | [16 empty] | 4 |  | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 179760
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 18 |  | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 476736
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 22 | 22 | 21 | 21 | 21 | 19 | 18 |  | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 435780
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 452376
63 | Impoprt (Tripura) | 116 | 116 | 110 | 108 | 106 | 96 | 78 | 68 | 76 | 80 | 86 | 90 | 90 | 102 | 98 | 96 | 102 | 128 |  | 136 | 136 | 134 | 130 | 128 | 126 | 122 | 2509440
64 | Malancha, Ctg. EPZ (United) | 37 | 31 | 31 | 29 | 37 | 7 | 27 | 2 | 2 | 2 | 2 | 2 | 2 | 6 | 2 | 4 | 7 | 8 |  | 5 | 16 | 18 | 20 | 27 | 29 | 32 | 373920
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 6 | 18 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 478296
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 2 | 2 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 185940
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 6 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 759300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 18 | 12 | 12 | 12 | 19 | 19 | 19 | 8 | 8 | 19 | 19 |  | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 488540
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 26 | 20 | 13 |  | 26 | 26 | 23 | 27 | 27 | 27 | 29 | 635040
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 758700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 832200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 70 | 70 | 70 | 45 | [6 empty] | 20 | 50 | 50 | 34 | 34 | 34 | 34 | 76 |  | 100 | 100 | 100 | 70 | 70 | 70 | 70 | 1077300
| Chowmuhani 113 MW | 48 | 49 | 48 | 47 | 48 | 48 | 48 | 49 | 48 | 49 | 48 | 50 | 56 | 49 | 48 | 48 | 49 | 87 |  | 96 | 96 | 97 | 96 | 95 | 95 | 55 | 1468320
| Manikgonj 162MW PP(MPGL) | 162 | 17 | 17 | 17 |  |  |  |  | 1 | 20 | 79 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2520000
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 16 | 16 | 25 |  | 17 | 25 | 25 | 25 | 25 | 32 |  | 51 | 25 | 25 | 25 | 25 | 25 | 25 | 398400
79 | Kodda 150MW PP | 64 | 48 | 16 | 16 | [10 empty] | 16 | 16 | 16 | 115 |  | 150 | 150 | 150 | 150 | 150 | 133 | 115 | 1096800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 45 | 8 | 8 | 8 | 16 | 25 | 25 | 36 | 52 | 52 | 45 | 52 | 52 | 45 |  | 52 | 52 | 52 | 44 | 44 | 52 | 52 | 874718
| Gazipur 100 MW PP | [9 empty] | 52 | 52 | 52 | 52 | 17 | 17 | 17 | 17 | 33 |  | 105 | 52 | 52 | 52 | 17 | 17 | 17 | 634800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 2 | 3 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 18959
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1301193
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | [5 empty] | 7 | 31 | 51 | 61 | 85 | 85 | 85 | 51 | 60 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1337344
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 10 | 10 | 10 | 10 | 10 | 40 |  | 48 | 10 | 10 | 10 | 10 | 10 | 10 | 224009
86 | Meghnaghat CCPP ( Summit) | 275 | 285 | 275 | 290 | 290 | 290 | 270 | 275 | 310 | 290 | 280 | 290 | 280 | 290 | 280 | 285 | 270 | 250 |  | 275 | 295 | 267 | 280 | 265 | 265 | 262 | 6744436
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 70 | 25 | 17 | 17 |  |  |  | 2 | 17 | 17 | 52 | 84 | 94 | 93 | 94 | 93 | 72 | 76 |  | 94 | 93 | 93 | 94 | 93 | 93 | 93 | 1431360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 35 |  | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 203280
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 910026
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | [5 empty] | 7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 64 |  | 102 | 64 | 64 | 32 | 16 | 16 | 16 | 565632
95 | Patenga 50MW PP (Baraka) | 12 | 12 | 12 | 12 |  |  |  | 2 | 12 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 24 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 551520
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 32 |  | 58 | 12 | 12 | 11 | 9 |  | 0 | 125760
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 43 | 40 | 55 | 55 | 40 | 52 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 1284435
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 |  |  |  | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 973780
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 163 | 163 |  | 10 | 70 | 70 | 70 | 110 | 110 |  | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 3105085
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 9500
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1303560
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 194 | 194 | 160 | 120 | 100 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 53 |  | 165 | 175 | 175 | 187 | 191 | 190 | 192 | 2409600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 115 | 115 | 115 | 115 | 115 | 115 | 102 | 102 | 102 | 132 | 132 | 130 | 90 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3150720
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 70 | 20 | 20 | 30 | 50 | 76 | 100 | 100 | 100 | 100 | 100 | 50 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2031360
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 180 | 136 | 141 | 178 | 180 | 180 | 200 | 200 | 170 | 170 | 170 | 170 | 175 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4487040
117 | Ashuganj 150MW PP (Midland) | 132 | 10 | 10 | 10 | [7 empty] | 20 | 71 | 100 | 108 | 108 | 122 | 130 |  | 130 | 130 | 127 | 127 | 133 | 140 | 140 | 1709527
118 | Bibiyana-III 400 MW CCPP | 317 | 318 | 318 | 316 | 316 | 316 | 316 | 316 | 316 | 317 | 318 | 303 | 316 | 318 | 316 | 316 | 316 | 316 |  | 316 | 316 | 316 | 317 | 316 | 318 | 317 | 7610000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 85 | 55 | 55 | 55 | 60 | 108 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2521200
| Anwara 300 MW PP (United) | 305 | 305 | 305 | 305 | 305 | 251 | 178 | 176 | 178 | 178 | 302 | 305 | 305 | 305 | 305 | 305 | 215 | 305 |  | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 6676691
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2435520
| Anlima Energy Ltd. | 108 | 108 | 108 | 72 | 72 | 17 | 17 | 17 | 17 | 17 | 37 | 53 | 75 | 108 | 108 | 108 | 108 | 114 |  | 116 | 116 | 116 | 116 | 116 | 112 | 114 | 2018564
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  | 14 | 17 | 553320
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 1 | 3 | 4 | 18 | 24 | 31 | 31 | 16 | 1 | 1 | [9 empty] | 126313
120 | Eastern Zone Total | 8014 | 7638 | 7485 | 7397 | 7224 | 6778 | 6523 | 6636 | 6846 | 6995 | 7345 | 7447 | 7568 | 7652 | 7834 | 7783 | 7502 | 8130 |  | 8874 | 8741 | 8740 | 8539 | 8457 | 8441 | 8394 | 186194081
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 14 |  | 7 | 4 | 7 | 8 | 4 | 4 | 4 | 100800
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 |  | 170 | 170 | 170 | 180 | 165 | 120 | 120 | 3262080
129 | Rupsha 105 MW PP (Orion rupsha) | [10 empty] | 3 | 45 | 65 | 70 | 70 | 35 | 35 | 35 |  | 103 | 105 | 105 | 105 | 105 | 105 | 105 | 1058880
130
131
132 | United Payra Power Ltd. | [17 empty] | 3 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 90000
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 223 | 224 | 227 | 227 | 174 | 172 | 172 | 202 | 223 | 218 | 224 | 224 | 226 | 225 | 224 | 154 | 141 |  | 228 | 228 | 228 | 228 | 228 | 226 | 222 | 5097845
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 21 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 444192
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 85 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 2102435
140 | Bhola 33 MW PP (Venture) | 25 | 24 | 24 | 25 | 18 | 17 | 16 | 16 | 18 | 17 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 27 |  | 30 | 30 | 31 | 30 | 30 | 30 | 29 | 535494
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 710 | 709 | 709 | 710 | 710 | 710 | 710 | 720 | 720 | 719 | 720 | 719 | 717 | 717 | 717 | 717 | 716 | 716 |  | 717 | 716 | 716 | 717 | 717 | 718 | 717 | 17286545
147 | Bheramara 410 MW CCPP | 355 | 355 | 355 | 355 | 375 | 300 | 300 | 300 | 320 | 320 | 320 | 350 | 350 | 320 | 360 | 360 | 320 | 320 |  | 320 | 360 | 360 | 360 | 360 | 360 | 360 | 8473248
148 | Payra 1320 MW | 410 | 410 | 410 | 370 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 340 | 340 | 340 | 340 | 360 |  | 480 | 480 | 480 | 480 | 480 | 460 | 440 | 9837600
149
150 | Barapukuria TPP Unit-1 | 77 | 76 | 77 | 78 | 78 | 78 | 78 | 77 | 77 | 75 | 76 | 80 | 79 | 80 | 79 | 79 | 80 | 79 |  | 80 | 79 | 80 | 80 | 81 | 80 | 80 | 1876800
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 31 |  | 50 | 50 | 50 | 50 | 50 |  |  | 241597
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 1 | 1 | 2 | 2 | 4 | 3 | 0 | 1 | 0 | [9 empty] | 19020
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 168 | 182 | 185 | 184 | 174 | 164 | 162 | 168 | 199 | 181 | 174 | 174 | 186 | 157 | 155 | 180 | 179 | 165 |  | 166 | 175 | 176 | 177 | 179 | 183 | 185 | 4416882
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 188 | 188 | 188 | 187 | 179 | 172 | 170 | 171 | 179 | 173 | 173 | 172 | 202 | 181 | 174 | 186 | 182 | 167 |  | 167 | 168 | 173 | 185 | 184 | 188 | 191 | 4596082
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 387 | 403 | 380 | 308 | 348 | 310 | 348 | 343 | 352 | 377 | 295 | 336 | 364 | 347 | 414 | 415 | 308 | 297 |  | 330 | 397 | 369 | 398 | 369 | 367 | 369 | 8786836
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 6 | 30 |  | 36 | 36 | 36 | 36 | 20 |  |  | 156693
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504720
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236772
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 0 | 177800
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 24 | [6 empty] | 26829
167 | Katakhali 50 MW Peaking PP | [17 empty] | 27 |  | 39 | 39 | 39 | 36 | 36 |  |  | 151640
168 | Santahar 50 MW Peaking PP | [17 empty] | 16 |  | 29 | 30 | 28 | 28 | 28 | 28 | 0 | 166461
169 | Natore 52 MW PP (Rajlanka) | [13 empty] | 8 | 8 | 8 | 8 | 14 |  | 52 | 52 | 52 | 52 | 52 | 52 | 24 | 358560
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 606592
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | [5 empty] | 12 | 35 | 35 | 40 | 70 | 70 | 35 | 35 | 41 |  | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 1599264
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 35 | 35 | [6 empty] | 25 | 35 | 55 | 70 | 70 | 35 | 35 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1437984
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 70 | 49 |  |  |  | 15 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 38 | 97 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1576656
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 4 | 4 | 2 | 4 | 6 | 4 | 3 | 1 | 0 | [8 empty] | 26790
178
178