## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-02 | Saturday
|  |  | Date (day): | 2021-10-02 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13586.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14718 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-01 | 2021-10-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 305 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 362 | 395 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 318 | 340 | 340 | 20
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 305 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 33 | 68 | 68 |  | 32 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 145 | 189 | 190 | 190 | 20
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under S/D.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 64 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 133 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 51 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 5 | 195 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 53 | 52 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 52 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 48 | 93 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 119 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2259 | 2906 | 3574 | 3844 | 1032 | 802
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 12 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 25 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 159 | 160 | 126 | 126 | 104 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 65 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 34 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 90 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 35 | 31 | 10 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 286 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 18 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 112 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 801 | 1328 | 1451 | 1524 | 174 | 671
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 110 | 110 | 110 | 110
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 179 | 206 | 170 | 170 | 51 |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 315 | 315 | 340 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 315 | 310 | 350 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 54 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 118 | 127 | 135 | 137 |  | 13 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 139 | 141 | 141 |  | 22 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 152 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 132 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 100 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 95 | 87 | 95 |  | 18 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1747 | 2070 | 2140 | 2356 | 501 | 120
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 205 | 205 | 200 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 160 | 200 | 170 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 551 | 559 | 580.6 | 559 | 0 | 95
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 20 | 160 | 170 |  | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 36 | 51 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81 |  | 5 | Engine problem
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 192 | 220 | 0 | 0 |  | 231 | Under maint
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 316 | 316 | 316 | 316 | 84 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1560 | 1615 | 1457 | 1597 | 317 | 453
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 708 | 707 | 722 | 722
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 4 | 0 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 180 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 370 | 400 | 410 |  |  | FGMO
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 32 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1187 | 1398 | 1602 | 1727 | 0 | 98
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 32 | 30 | 30
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 86 | 82 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 18 | 17 | 22 | 22 | 73 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 530 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 223 | 224 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 643 | 906 | 1086 | 1242 | 73 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 34 | 35 |  | 36 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 28 | 28 | 22 |  | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 25 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 190 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 181 | 192 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 404 | 414 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 0 | 30 |  | 20 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 11 | 94 | 94 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 20 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 829 | 1338 | 1500 | 1678 | 402 | 76
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 77 | 75 | 75 | 78
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 116 | 188 | 196 | 191 | 0 | 399
|  | Total |  |  |  |  | 22031 | 21180 | 9693 | 12308 | 13586.6 | 14718 | 2499 | 2820
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9298.4442 | 11807 | 13033.5543 | 14118.9004
| A. |  | 2021-10-01 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12425 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8983 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12308 | MW
| 3 | Day peak Generation : |  |  | 9693 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11807 | MW
| 4 | Evening peak Generation : |  |  | 12308 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 258.8568 | MKWHr | By Solar | 0.79297 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 153.5216 | MKWHr |  | By Oil: | 68.007 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.7471 | MKWHr |  | By Hydro: | 3.7974 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2499 | MW | Dhaka | 3992 | 3992 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2820 | MW | Chittagong | 1210 | 1210 |  | 0 |  | 18:00 |  | 124
|  |  |  | Total = |  |  | 5319 | MW | Khulna | 1494 | 1494 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1160.24 | MMCFD |  |  | Rajshahi | 1260 | 1260 |  | 0 |  | 19:00 |  | 126
| 8 | Fuel Cost : | i) Gas : | Taka | 159623793.302 | ii) Oil : | Taka | 518458685.99 | Comilla | 1179 | 1179 |  | 0 |  | 19:30 |  | 130
|  |  | iii) Coal : |  | 58938878.43 | Total | Taka | 737021357.722 | Mymensingh | 1035 | 1035 |  | 0 |  | 20:00 |  | 132
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.043 | MKWHr. | Sylhet | 565 | 565 |  | 0 |  | 21:00 |  | 132
|  | ii) During Peak Demand : |  |  | -188 | MW (E to W) at | 21:00 | hrs | Barisal | 339 | 339 |  | 0 |  | 22:00 |  | 136
|  | iii) Maximum : |  |  | #VALUE! | MW at | #VALUE! | hrs | Rangpur | 733 | 733 |  | 0 |  | 23:00 |  | 134
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 11807 | 11807 |  | 0
| B. |  | 2021-10-02 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14718 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10100 | MW
| 4 | Reserve(Generation end) |  |  |  | 1918 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 266.6694 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9633 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1156 | MKWHr. | ii) HVDC Flow at Peak Time |  | 707 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8752 | MKWHr. | iii) Maximum HVDC Flow : |  | 717 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.5 |  | (b) Today: | 106.4 |  | (c) Rule Curve: |  | 106.09
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 326 |  | 0 | 250 | 250 | 0 | 0 | 55 | 235 | 0 | 0 | 0 | 102 | 115 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 68 | 92 | 86 | 50 | 21 | 32 | 80 | 0 | 0 | 330 | 330 | 211 | 8 | 137 | 23 | 56 | 0 | 43 | 0 | 25 | 52 | 22 | 8 | 33 | 21 | 122 | 203 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 159 | 62 | 81 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 296 | 0 | 0 | 182 | 0 | 149 | 0 | 100 | 200 | 137 | 316 | 115 | 105 | 105 | 0 | 306 | 54 | 110 | 98 | 48 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 717 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 0 | 30 | 52 | 29 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 12 | 0 | 188 | 0 | 380 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 490 | 226 | 0 | 0 | 0 |  | 8522 | 3594 | 12116 | 4179 | 717 | 2182 | 0 | 3702 | 567 | 159 | 120 | 368 | 122 | 0 | 0 | 106.53
2:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 5 | 332 |  | 0 | 250 | 265 | 0 | 0 | 55 | 233 | 0 | 0 | 0 | 102 | 82 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 65 | 50 | 21 | 33 | 80 | 0 | 0 | 330 | 305 | 210 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 134 | 208 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 160 | 36 | 81 | 0 | 140 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 296 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 200 | 136 | 317 | 115 | 52 | 105 | 0 | 306 | 54 | 110 | 98 | 47 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 708 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 12 | 0 | 189 | 0 | 395 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 490 | 226 | 0 | 0 | 0 |  | 8253 | 3403 | 11656 | 4160 | 708 | 2216 | 0 | 3505 | 566 | 161 | 120 | 86 | 134 | 0 | 0 | 106.52
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 7 | 332 |  | 0 | 250 | 275 | 0 | 0 | 55 | 235 | 0 | 0 | 0 | 64 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 42 | 0 | 50 | 21 | 33 | 80 | 0 | 0 | 310 | 310 | 210 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 132 | 208 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 159 | 36 | 81 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 296 | 0 | 0 | 192 | 0 | 131 | 0 | 100 | 200 | 137 | 317 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 85 | 48 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 12 | 0 | 192 | 0 | 397 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 470 | 226 | 0 | 0 | 0 |  | 8015 | 3313 | 11328 | 4095 | 708 | 2239 | 0 | 3240 | 547 | 161 | 120 | 86 | 132 | 0 | 0 | 106.51
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 49 | 329 |  | 0 | 250 | 280 | 0 | 0 | 55 | 230 | 0 | 0 | 0 | 24 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 21 | 33 | 80 | 0 | 0 | 315 | 315 | 210 | 8 | 139 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 128 | 208 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 160 | 36 | 81 | 0 | 165 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 192 | 0 | 105 | 0 | 100 | 200 | 135 | 317 | 115 | 0 | 105 | 0 | 305 | 54 | 110 | 17 | 48 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 707 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 192 | 0 | 402 | 70 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 450 | 226 | 0 | 0 | 0 |  | 7812 | 3273 | 11085 | 4183 | 707 | 2255 | 0 | 2919 | 526 | 161 | 120 | 86 | 128 | 0 | 0 | 106.51
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 86 | 329 |  | 0 | 250 | 275 | 0 | 0 | 40 | 226 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 21 | 34 | 80 | 0 | 0 | 310 | 320 | 211 | 8 | 141 | 23 | 56 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 21 | 120 | 211 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 160 | 37 | 81 | 0 | 192 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 130 | 0 | 0 | 140 | 0 | 80 | 0 | 100 | 200 | 137 | 317 | 115 | 0 | 105 | 0 | 305 | 54 | 110 | 17 | 48 | 100 | 321 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 12 | 0 | 189 | 0 | 362 | 17 | 0 | 113 | 0 | 81 | 0 | 0 | 113 | 450 | 224 | 0 | 0 | 0 |  | 7616 | 3148 | 10764 | 4247 | 708 | 2187 | 0 | 2642 | 527 | 161 | 120 | 52 | 120 | 0 | 0 | 106.5
6:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 202 | 330 |  | 0 | 250 | 250 | 0 | 0 | 15 | 175 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 26 | 33 | 16 | 0 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 21 | 35 | 80 | 0 | 0 | 310 | 305 | 211 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 21 | 108 | 213 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 0 | 37 | 81 | 0 | 191 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 60 | 0 | 0 | 140 | 0 | 80 | 0 | 100 | 155 | 135 | 317 | 115 | 0 | 68 | 0 | 305 | 54 | 85 | 1 | 47 | 100 | 320 | 75 | 0 | 54 | 72 | 0 | 17 | 0 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 12 | 0 | 188 | 0 | 354 | 17 | 0 | 70 | 0 | 40 | 0 | 0 | 35 | 450 | 220 | 0 | 0 | 0 |  | 6917 | 2968 | 9885 | 4113 | 708 | 2138 | 0 | 1990 | 527 | 161 | 120 | 20 | 108 | 0 | 0 | 106.5
7:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 378 | 328 |  | 0 | 250 | 270 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 38 | 80 | 0 | 0 | 310 | 310 | 210 | 8 | 144 | 23 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 106 | 211 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 0 | 37 | 81 | 0 | 192 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 148 | 0 | 80 | 5 | 60 | 155 | 133 | 318 | 115 | 0 | 68 | 1 | 142 | 54 | 34 | 0 | 42 | 100 | 320 | 55 | 1 | 54 | 72 | 0 | 17 | 6 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 12 | 0 | 189 | 0 | 391 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 380 | 200 | 0 | 0 | 1 |  | 6595 | 2821 | 9416 | 4134 | 708 | 2192 | 0 | 1517 | 458 | 162 | 120 | 4 | 106 | 15 | 0 | 106.49
8:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 404 | 329 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 26 | 33 | 0 | 0 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 38 | 80 | 0 | 0 | 280 | 365 | 211 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 100 | 207 | 0 | 21 | 1 | 43 | 0 | 44 | 0 | 110 | 0 | 37 | 81 | 0 | 192 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 15 | 0 | 0 | 160 | 0 | 84 | 11 | 60 | 120 | 125 | 316 | 115 | 0 | 51 | 2 | 0 | 35 | 34 | 0 | 44 | 70 | 320 | 55 | 23 | 54 | 53 | 0 | 17 | 17 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 12 | 0 | 181 | 0 | 307 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 350 | 202 | 0 | 0 | 3 |  | 6383 | 2710 | 9093 | 4183 | 708 | 2067 | 0 | 1265 | 426 | 162 | 120 | 4 | 100 | 58 | 0 | 106.49
9:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 363 | 328 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 20 | 33 | 17 | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 285 | 305 | 211 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 6 | 22 | 8 | 33 | 17 | 100 | 204 | 0 | 21 | 1 | 43 | 0 | 44 | 0 | 110 | 0 | 37 | 78 | 0 | 192 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 15 | 0 | 0 | 160 | 0 | 85 | 16 | 60 | 120 | 125 | 316 | 107 | 0 | 51 | 3 | 0 | 35 | 34 | 0 | 48 | 70 | 322 | 55 | 39 | 54 | 53 | 0 | 18 | 26 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 166 | 0 | 308 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 300 | 201 | 0 | 0 | 4 |  | 6356 | 2627 | 8983 | 4095 | 708 | 2060 | 0 | 1269 | 376 | 160 | 120 | 4 | 100 | 91 | 0 | 106.48
10:00 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 353 | 329 |  | 0 | 250 | 275 | 0 | 0 | 15 | 0 | 0 | 115 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 20 | 33 | 17 | 0 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 36 | 80 | 0 | 0 | 305 | 305 | 179 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 17 | 104 | 203 | 0 | 21 | 1 | 44 | 0 | 44 | 0 | 130 | 0 | 36 | 78 | 0 | 192 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 63 | 20 | 60 | 120 | 123 | 316 | 106 | 0 | 51 | 2 | 0 | 37 | 17 | 0 | 48 | 100 | 320 | 25 | 46 | 53 | 55 | 0 | 35 | 31 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 7 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 19 | 0 | 173 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 300 | 180 | 0 | 0 | 4 |  | 6387 | 2624 | 9011 | 4122 | 708 | 2152 | 0 | 1154 | 378 | 158 | 120 | 7 | 104 | 108 | 0 | 106.48
11:00 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 360 | 323 |  | 0 | 250 | 280 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 13 | 33 | 25 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 80 | 0 | 0 | 340 | 310 | 183 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 18 | 108 | 201 | 0 | 21 | 1 | 43 | 0 | 44 | 0 | 130 | 0 | 36 | 78 | 0 | 192 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 53 | 20 | 74 | 123 | 132 | 316 | 115 | 52 | 51 | 2 | 0 | 54 | 17 | 0 | 52 | 100 | 320 | 20 | 42 | 65 | 78 | 0 | 35 | 35 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 19 | 0 | 188 | 0 | 365 | 0 | 0 | 0 | 0 | 35 | 0 | 5 | 0 | 300 | 180 | 0 | 0 | 1 |  | 6626 | 2670 | 9296 | 4198 | 708 | 2157 | 0 | 1359 | 377 | 159 | 120 | 4 | 108 | 106 | 0 | 106.48
12:00 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 362 | 322 |  | 0 | 250 | 270 | 0 | 0 | 40 | 0 | 0 | 145 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 13 | 33 | 25 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 110 | 0 | 0 | 335 | 305 | 179 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 18 | 108 | 205 | 0 | 21 | 1 | 43 | 0 | 44 | 0 | 163 | 0 | 36 | 78 | 0 | 192 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 5 | 0 | 0 | 160 | 0 | 53 | 12 | 100 | 152 | 118 | 316 | 115 | 52 | 65 | 5 | 0 | 54 | 18 | 0 | 47 | 100 | 320 | 48 | 49 | 119 | 112 | 0 | 35 | 35 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 18 | 0 | 181 | 0 | 404 | 0 | 0 | 11 | 0 | 35 | 0 | 4 | 20 | 300 | 223 | 0 | 0 | 2 |  | 6918 | 2775 | 9693 | 4240 | 708 | 2264 | 0 | 1605 | 377 | 159 | 120 | 4 | 108 | 108 | 0 | 106.47
13:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 348 | 283 |  | 0 | 250 | 270 | 0 | 0 | 40 | 0 | 0 | 185 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 13 | 33 | 25 | 8 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 11 | 21 | 36 | 110 | 0 | 0 | 335 | 275 | 178 | 8 | 140 | 23 | 54 | 0 | 43 | 0 | 0 | 22 | 22 | 8 | 33 | 18 | 114 | 202 | 0 | 21 | 1 | 43 | 0 | 47 | 0 | 110 | 0 | 36 | 78 | 0 | 166 | 18 | 0 | 9 | 275 | 24 | 11 | 0 | 116 | 0 | 0 | 120 | 0 | 25 | 20 | 100 | 183 | 125 | 316 | 115 | 105 | 90 | 4 | 0 | 54 | 99 | 9 | 48 | 100 | 320 | 84 | 28 | 162 | 116 | 0 | 35 | 33 |  | 708 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 18 | 0 | 179 | 0 | 333 | 0 | 0 | 78 | 0 | 35 | 0 | 4 | 100 | 330 | 220 | 0 | 0 | 2 |  | 7173 | 2878 | 10051 | 4195 | 708 | 2075 | 0 | 2176 | 408 | 159 | 120 | 4 | 114 | 92 | 0 | 106.47
14:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 344 | 252 |  | 0 | 225 | 280 | 0 | 0 | 50 | 0 | 0 | 125 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 11 | 33 | 25 | 8 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 21 | 36 | 110 | 0 | 0 | 280 | 280 | 179 | 8 | 141 | 23 | 54 | 0 | 43 | 0 | 0 | 24 | 22 | 8 | 33 | 20 | 120 | 200 | 0 | 21 | 1 | 43 | 0 | 47 | 0 | 110 | 0 | 35 | 78 | 0 | 166 | 17 | 0 | 9 | 280 | 24 | 11 | 0 | 188 | 0 | 0 | 100 | 0 | 0 | 17 | 100 | 200 | 83 | 316 | 115 | 105 | 90 | 4 | 0 | 54 | 108 | 0 | 48 | 100 | 320 | 93 | 49 | 162 | 116 | 0 | 35 | 29 |  | 708 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 84 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 18 | 0 | 166 | 0 | 351 | 0 | 0 | 94 | 0 | 34 | 0 | 3 | 113 | 330 | 153 | 0 | 0 | 5 |  | 7069 | 2853 | 9922 | 4067 | 708 | 1986 | 0 | 2240 | 409 | 160 | 120 | 4 | 120 | 108 | 0 | 106.47
15:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 367 | 303 |  | 0 | 225 | 275 | 0 | 0 | 55 | 0 | 0 | 130 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 11 | 33 | 25 | 8 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 36 | 110 | 0 | 0 | 315 | 310 | 182 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 20 | 122 | 200 | 0 | 21 | 1 | 44 | 0 | 47 | 0 | 110 | 0 | 50 | 78 | 0 | 166 | 17 | 0 | 9 | 300 | 24 | 11 | 0 | 190 | 0 | 0 | 100 | 0 | 0 | 13 | 100 | 200 | 117 | 316 | 106 | 105 | 90 | 3 | 0 | 54 | 110 | 0 | 48 | 100 | 321 | 93 | 7 | 162 | 116 | 0 | 35 | 22 |  | 707 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 85 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 18 | 0 | 181 | 0 | 398 | 0 | 0 | 94 | 0 | 34 | 0 | 5 | 113 | 330 | 152 | 0 | 0 | 2 |  | 7210 | 2911 | 10121 | 4172 | 707 | 2098 | 0 | 2276 | 409 | 160 | 120 | 4 | 122 | 53 | 0 | 106.46
16:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 393 | 303 |  | 0 | 250 | 250 | 0 | 0 | 55 | 0 | 0 | 125 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 11 | 33 | 8 | 8 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 24 | 110 | 0 | 0 | 280 | 305 | 178 | 8 | 141 | 23 | 54 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 20 | 112 | 201 | 0 | 21 | 1 | 44 | 0 | 44 | 0 | 163 | 0 | 51 | 78 | 0 | 166 | 17 | 0 | 9 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 100 | 0 | 0 | 8 | 76 | 200 | 118 | 316 | 106 | 105 | 99 | 2 | 0 | 54 | 110 | 0 | 48 | 90 | 320 | 86 | 22 | 162 | 116 | 0 | 35 | 14 |  | 707 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 18 | 0 | 176 | 0 | 360 | 0 | 0 | 50 | 50 | 34 | 0 | 4 | 50 | 330 | 152 | 0 | 0 | 2 |  | 7120 | 2788 | 9908 | 4117 | 707 | 2086 | 0 | 2143 | 407 | 159 | 120 | 4 | 112 | 53 | 0 | 106.46
17:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 365 | 251 |  | 0 | 250 | 225 | 0 | 0 | 55 | 0 | 0 | 67 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 11 | 33 | 25 | 8 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 38 | 110 | 0 | 0 | 280 | 275 | 177 | 8 | 139 | 23 | 54 | 0 | 35 | 0 | 0 | 25 | 22 | 8 | 33 | 20 | 102 | 203 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 110 | 0 | 52 | 30 | 0 | 166 | 17 | 0 | 9 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 100 | 0 | 23 | 2 | 50 | 155 | 118 | 316 | 115 | 52 | 105 | 0 | 0 | 54 | 110 | 0 | 48 | 50 | 320 | 39 | 2 | 162 | 116 | 0 | 35 | 4 |  | 707 | 0 | 300 | 0 | 0 | 150 | 0 | 0 | 4 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 18 | 0 | 176 | 0 | 291 | 2 | 0 | 50 | 50 | 34 | 0 | 3 | 50 | 300 | 106 | 0 | 0 | 0 |  | 6629 | 2613 | 9242 | 3954 | 707 | 1791 | 0 | 1982 | 377 | 159 | 150 | 9 | 102 | 11 | 0 | 106.46
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 294 | 262 |  | 0 | 250 | 285 | 0 | 0 | 55 | 0 | 0 | 70 | 0 | 32 | 50 | 8 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 8 | 33 | 25 | 8 | 0 | 85 | 75 | 120 | 0 | 3 | 0 | 0 | 0 | 0 |  | 2 | 0 | 95 | 20 | 11 | 47 | 21 | 38 | 110 | 0 | 0 | 315 | 330 | 200 | 8 | 140 | 23 | 54 | 0 | 43 | 0 | 35 | 28 | 22 | 8 | 33 | 20 | 124 | 203 | 0 | 21 | 0 | 44 | 0 | 16 | 0 | 110 | 0 | 50 | 78 | 0 | 190 | 17 | 0 | 9 | 270 | 24 | 11 | 0 | 163 | 0 | 0 | 122 | 0 | 59 | 0 | 50 | 140 | 120 | 317 | 115 | 58 | 81 | 0 | 0 | 54 | 85 | 65 | 76 | 50 | 320 | 35 | 0 | 162 | 116 | 0 | 35 | 0 |  | 707 | 0 | 320 | 0 | 0 | 150 | 0 | 0 | 4 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 43 | 24 | 75 | 27 | 16 | 34 | 3 | 12 | 21 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 18 | 0 | 157 | 0 | 372 | 38 | 0 | 50 | 50 | 100 | 0 | 0 | 90 | 310 | 129 | 0 | 6 | 0 |  | 7155 | 3111 | 10266 | 4030 | 707 | 1993 | 0 | 2344 | 386 | 160 | 150 | 372 | 124 | 0 | 0 | 106.45
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 381 | 332 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 128 | 0 | 74 | 133 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 17 | 0 | 102 | 50 | 25 | 19 | 21 | 39 | 110 | 0 | 0 | 305 | 305 | 208 | 8 | 138 | 23 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 126 | 205 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 0 | 52 | 81 | 0 | 206 | 17 | 0 | 9 | 270 | 24 | 11 | 0 | 245 | 0 | 0 | 199 | 0 | 106 | 0 | 90 | 200 | 125 | 316 | 115 | 52 | 105 | 0 | 230 | 54 | 110 | 114 | 86 | 100 | 320 | 76 | 0 | 162 | 116 | 0 | 17 | 0 |  | 707 | 0 | 360 | 0 | 0 | 145 | 0 | 0 | 10 | 0 | 0 | 85 | 31 | 0 | 0 | 0 | 0 | 50 | 17 | 93 | 27 | 43 | 40 | 52 | 20 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 17 | 0 | 186 | 0 | 356 | 98 | 0 | 81 | 50 | 113 | 0 | 0 | 113 | 420 | 226 | 0 | 17 | 0 |  | 8387 | 3626 | 12013 | 4267 | 707 | 2238 | 0 | 3410 | 495 | 160 | 145 | 465 | 126 | 0 | 0 | 106.44
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 332 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 130 | 0 | 64 | 133 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 70 | 10 | 0 | 18 | 21 | 37 | 110 | 0 | 0 | 325 | 330 | 205 | 8 | 140 | 23 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 130 | 204 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 0 | 51 | 81 | 0 | 220 | 17 | 0 | 9 | 315 | 24 | 11 | 0 | 195 | 0 | 0 | 198 | 0 | 65 | 0 | 90 | 200 | 125 | 316 | 115 | 52 | 105 | 0 | 272 | 54 | 110 | 114 | 95 | 100 | 320 | 92 | 0 | 162 | 116 | 0 | 17 | 0 |  | 707 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 31 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 27 | 43 | 40 | 52 | 20 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 17 | 0 | 186 | 0 | 395 | 105 | 0 | 94 | 38 | 113 | 0 | 0 | 113 | 520 | 224 | 0 | 17 | 0 |  | 8369 | 3776 | 12145 | 4411 | 707 | 2333 | 0 | 3278 | 595 | 160 | 120 | 411 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 326 |  | 0 | 250 | 315 | 0 | 0 | 55 | 0 | 0 | 186 | 0 | 64 | 133 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 71 | 10 | 0 | 18 | 21 | 40 | 110 | 0 | 0 | 345 | 350 | 204 | 8 | 140 | 23 | 53 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 132 | 204 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 0 | 51 | 81 | 0 | 220 | 17 | 0 | 9 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 198 | 0 | 60 | 0 | 90 | 200 | 127 | 316 | 115 | 52 | 105 | 0 | 282 | 54 | 110 | 114 | 95 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 707 | 0 | 400 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 27 | 25 | 40 | 52 | 20 | 21 | 0 | 11 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 17 | 0 | 187 | 0 | 410 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 520 | 224 | 0 | 17 | 0 |  | 8462 | 3783 | 12245 | 4528 | 707 | 2330 | 0 | 3262 | 594 | 160 | 120 | 412 | 132 | 0 | 0 | 106.45
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 318 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 189 | 0 | 64 | 133 | 33 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 40 | 0 | 19 | 21 | 31 | 110 | 0 | 0 | 315 | 315 | 206 | 45 | 139 | 23 | 54 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 132 | 205 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 0 | 51 | 81 | 0 | 220 | 17 | 0 | 9 | 310 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 52 | 0 | 90 | 200 | 127 | 316 | 115 | 52 | 105 | 0 | 286 | 54 | 110 | 114 | 95 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 707 | 0 | 370 | 0 | 0 | 180 | 0 | 0 | 4 | 0 | 0 | 86 | 32 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 27 | 25 | 36 | 52 | 20 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 17 | 0 | 192 | 0 | 414 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 530 | 224 | 0 | 17 | 0 |  | 8478 | 3830 | 12308 | 4439 | 707 | 2367 | 0 | 3314 | 605 | 160 | 180 | 404 | 132 | 0 | 0 | 106.44
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 322 |  | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 187 | 0 | 64 | 133 | 40 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 40 | 0 | 19 | 21 | 40 | 110 | 0 | 0 | 320 | 315 | 207 | 45 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 136 | 205 | 0 | 22 | 0 | 43 | 20 | 44 | 0 | 163 | 0 | 51 | 81 | 0 | 220 | 17 | 0 | 9 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 52 | 0 | 100 | 200 | 127 | 316 | 115 | 52 | 105 | 0 | 286 | 54 | 110 | 114 | 95 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 707 | 0 | 370 | 0 | 0 | 180 | 0 | 0 | 4 | 0 | 0 | 75 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 27 | 25 | 36 | 52 | 27 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 17 | 0 | 195 | 0 | 418 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 540 | 160 | 0 | 42 | 0 |  | 8508 | 3801 | 12309 | 4452 | 707 | 2312 | 0 | 3336 | 615 | 160 | 180 | 411 | 136 | 0 | 0 | 106.44
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 322 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 189 | 0 | 64 | 133 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 40 | 0 | 19 | 21 | 40 | 110 | 0 | 0 | 325 | 320 | 208 | 45 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 12 | 134 | 206 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 163 | 0 | 51 | 81 | 0 | 220 | 17 | 0 | 9 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 50 | 0 | 100 | 200 | 133 | 316 | 115 | 52 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 385 | 0 | 0 | 180 | 0 | 0 | 4 | 0 | 0 | 75 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 27 | 25 | 36 | 52 | 27 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 17 | 0 | 195 | 0 | 417 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 540 | 160 | 0 | 90 | 0 |  | 8558 | 3867 | 12425 | 4481 | 708 | 2308 | 0 | 3428 | 615 | 160 | 180 | 411 | 134 | 0 | 0 | 106.44
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 324 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 75 | 133 | 43 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 18 | 0 | 68 | 100 | 0 | 19 | 21 | 40 | 110 | 0 | 0 | 310 | 305 | 208 | 45 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 130 | 206 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 163 | 0 | 51 | 81 | 0 | 0 | 0 | 0 | 9 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 60 | 0 | 100 | 200 | 136 | 317 | 106 | 60 | 105 | 0 | 306 | 54 | 110 | 98 | 58 | 100 | 320 | 94 | 0 | 162 | 112 | 0 | 17 | 0 |  | 707 | 0 | 355 | 0 | 0 | 210 | 0 | 0 | 4 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 27 | 25 | 30 | 52 | 27 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 17 | 0 | 191 | 0 | 401 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 530 | 225 | 0 | 72 | 0 |  | 8304 | 3888 | 12192 | 4175 | 707 | 2360 | 0 | 3440 | 605 | 160 | 210 | 405 | 130 | 0 | 0 | 106.43
KWH | 0 | 0 | 0 | 0 | 7312627 | 0 | 0 | 7162840 | 7580000 |  | 0 | 5941550 | 6591884 | 0 | 0 | 1109382 | 1443564 | 0 | 1082000 | 0 | 1048608 | 1320480 | 299941 | 0 | 0 | 0 | 1285956 | 1107159 | 1041295 | 315648 | 600000 | 511740 | 810300 | 668900 | 134918 | 0 | 1993385 | 1804000 | 2900000 | 0 | 97345 | 0 | 0 | 0 | 0 |  | 148800 | 0 | 563380 | 557040 | 190992 | 572640 | 486672 | 840000 | 2362754 | 0 | 0 | 7812200 | 7520000 | 4845000 | 351272 | 3315230 | 543312 | 1317600 | 0 | 984360 | 0 | 82232 | 784930 | 511920 | 181800 | 768700 | 503640 | 2875200 | 4737200 | 0 | 489672 | 10250 | 1027000 | 45000 | 1065000 | 0 | 3518521 | 829000 | 1060320 | 1847040 | 0 | 4335130 | 380000 | 0 | 228600 | 7100000 | 564744 | 264000 | 0 | 3703417 | 0 | 0 | 3900000 | 0 | 1630512 | 142560 | 2050560 | 4236960 | 3032654 | 7607000 | 2684400 | 1224852 | 2187090 | 31850 | 3658004 | 1251781 | 2155158 | 1086420 | 1414560 | 2250240 | 7554000 | 1803840 | 290110 | 3356640 | 2476473 | 0 | 621720 | 250334 |  | 17115636 | 0 | 9035712 | 0 | 0 | 3333120 | 0 | 0 | 95520 | 0 | 0 | 2061435 | 601494 | 0 | 0 | 0 | 0 | 359817 | 71312 | 561030 | 193400 | 180054 | 256504 | 411840 | 177620 | 473040 | 0 | 244386 | 1816581 | 0 | 0 | 0 | 0 | 0 | 0 | 4408982 | 0 | 377844 | 14400 | 4718464 | 0 | 8969200 | 1124160 | 0 | 1861344 | 385632 | 1594915 | 0 | 34809 | 2011104 | 10930500 | 4713327 | 0 | 304800 | 33060 |  | 180385808 | 78471042 | 258856850 | 101020892 | 17115636 | 52500732 | 14400 | 61171536 | 12747081 | 3797385 | 3333120 | 3487895 | 2875200 | 792973 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8117015.97 | 0 | 0 | 7234468.4 | 7807400 |  | 0 | 6476289.5 | 7316991.24 | 0 | 0 | 9385371.72 | 1501306.56 | 0 | 1871860 | 0 | 9563304.96 | 12993523.2 | 2765456.02 | 0 | 0 | 0 | 9387478.8 | 8558339.07 | 10267168.7 | 236736 | 450000 | 0 | 0 | 0 | 1304657.06 | 0 | 538213.95 | 487080 | 5249000 | 0 | 904335.05 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5464786 | 5319732 | 1661630.4 | 4535308.8 | 613206.72 | 2494800 | 3496875.92 | 0 | 0 | 5781028 | 7520000 | 4457400 | 453140.88 | 3812514.5 | 613942.56 | 1844640 | 0 | 1683255.6 | 0 | 830543.2 | 7496081.5 | 650138.4 | 136350 | 1345225 | 377730 | 21564000 | 5021432 | 0 | 621883.44 | 163385 | 1684280 | 72000 | 1895700 | 0 | 4011113.94 | 862160 | 2088830.4 | 3527846.4 | 0 | 7499774.9 | 832200 | 0 | 466344 | 7171000 | 423558 | 200640 | 0 | 27997832.52 | 0 | 0 | 20280000 | 0 | 16044238.08 | 1666526.4 | 16712064 | 45971016 | 21380210.7 | 7074510 | 24481728 | 11574851.4 | 19049553.9 | 0 | 27654510.24 | 10903012.51 | 18943838.82 | 10842471.6 | 12122779.2 | 14986598.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98586063.36 | 0 | 9487497.6 | 0 | 0 | 46197043.2 | 0 | 0 | 1002004.8 | 0 | 0 | 2329421.55 | 932315.7 | 0 | 0 | 0 | 0 | 3540599.28 | 724529.92 | 4965115.5 | 1489180 | 2434330.08 | 2485523.76 | 3990729.6 | 1722914 | 908236.8 | 0 | 185000.202 | 10953983.43 | 0 | 0 | 0 | 0 | 0 | 0 | 5819856.24 | 0 | 566766 | 244944 | 5520602.88 | 0 | 8879508 | 11736230.4 | 0 | 17664154.56 | 3640366.08 | 12376540.4 | 0 | 384639.45 | 14862058.56 | 47984895 | 0 | 0 | 0 | 0 |  | 538796215.53 | 321615050.352 | 860411265.882 | 103188445.242 | 98586063.36 | 56435348.06 | 244944 | 438287159.13 | 58938878.43 | 1025293.95 | 46197043.2 | 33729539.66 | 21564000 | 2214550.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 362 | 322 |  | 0 | 250 | 270 | 0 | 0 | 40 | 0 | 0 | 145 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 13 | 33 | 25 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 110 | 0 | 0 | 335 | 305 | 179 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 18 | 108 | 205 | 0 | 21 | 1 | 43 | 0 | 44 | 0 | 163 | 0 | 36 | 78 | 0 | 192 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 5 | 0 | 0 | 160 | 0 | 53 | 12 | 100 | 152 | 118 | 316 | 115 | 52 | 65 | 5 | 0 | 54 | 18 | 0 | 47 | 100 | 320 | 48 | 49 | 119 | 112 | 0 | 35 | 35 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 18 | 0 | 181 | 0 | 404 | 0 | 0 | 11 | 0 | 35 | 0 | 4 | 20 | 300 | 223 | 0 | 0 | 2 |  | 9693 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 318 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 189 | 0 | 64 | 133 | 33 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 68 | 40 | 0 | 19 | 21 | 31 | 110 | 0 | 0 | 315 | 315 | 206 | 45 | 139 | 23 | 54 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 132 | 205 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 0 | 51 | 81 | 0 | 220 | 17 | 0 | 9 | 310 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 52 | 0 | 90 | 200 | 127 | 316 | 115 | 52 | 105 | 0 | 286 | 54 | 110 | 114 | 95 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 707 | 0 | 370 | 0 | 0 | 180 | 0 | 0 | 4 | 0 | 0 | 86 | 32 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 27 | 25 | 36 | 52 | 20 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 17 | 0 | 192 | 0 | 414 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 530 | 224 | 0 | 17 | 0 |  | 12308 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 340 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 190 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 40 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 21 | 15 | 110 | 0 | 0 | 340 | 350 | 170 | 8 | 141 | 23 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 200 | 0 | 22 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 60 | 81 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 137 | 316 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 95 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 722 | 0 | 410 | 0 | 0 | 225 | 0 | 0 | 25 | 40 | 0 | 88 | 30 | 110 | 0 | 0 | 0 | 50 | 35 | 94 | 28 | 50 | 40 | 52 | 30 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 22 | 100 | 220 | 0 | 400 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 340 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 190 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 40 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 34 | 100 | 90 | 25 | 21 | 10 | 110 | 0 | 0 | 315 | 310 | 170 | 8 | 141 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 200 | 0 | 22 | 1.6 | 43 | 0 | 50 | 0 | 163 | 20 | 60 | 81 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 100 | 87 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 722 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 82 | 30 | 110 | 0 | 0 | 0 | 50 | 34 | 90 | 28 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 361 | 333 | 0 | 0 | 250 | 280 | 0 | 0 | 30 | 0 | 0 | 129 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 20 | 25 | 26 | 33 |  | 0 | 0 | 86 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 10 | 110 | 0 | 0 | 310 | 310 | 167 | 45 | 141 | 20 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 20 | 100 | 206 | 0 | 22 | 1 | 43 | 0 | 39 | 0 | 130 | 0 | 52 | 72 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 30 | 0 | 0 | 150 | 0 | 66 | 2 | 100 | 200 | 110 | 317 | 115 | 17 | 51 | 1 | 179 | 54 | 51 | 17 | 47 | 100 | 320 | 55 | 27 | 162 | 53 | 0 | 17 | 19 | 0 | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 17 | 0 | 172 | 0 | 330 | 70 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 380 | 184 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 8983 | 9:00
| Highest Generation |  | 12425 | 23:00
| Day Peak Generation |  | 9693 | 12:00
| Evening Peak Generation |  | 12308 | 21:00
| HVDC Max Flow |  | 717 | 1:00
| HVDC EvPeak Flow |  | 707 | 21:00
| Load factor L.F |  | 86.81%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-02
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9693 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9633 | MW
Evening Peak Generation : |  | 12308 | MW Hour : | 21:00 | Available Max Generation : |  | 14718 | MW
E.P. Demand (at gen end) : |  | 12308 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 12425 | MW Hour : | 23:00 | Reserve(Generation end) |  | 1918 | MW
Total Gen. (MKWH) : |  | 258.8568 | System Load Factor : | 86.81% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | #VALUE! | MW at | #VALUE! | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-02
Actual : | 106.4 | Ft.(MSL) , | Rule curve : | 106.09 | Ft.( MSL )
Gas Consumed : | Total = | 1160.24 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 159623793.302
: |  | Coal : | 58938878.43 | Oil : | 518458685.99 | Total : | 737021357.722
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4563.1835 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1556.1955 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1395.0943 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1260.8676 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1139.2722 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 919.3636 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 508.3229 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 236.5595 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 709.0863 |  |  | 0 | 0%
Total | 0 |  | 12287.9454 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Fenchuganj 3,4
7) Raozan #02
8) Shajibazar 330 Mw GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bhaluka 132/33 kV T-1 and T-2 transformers were under shut down from 08:31 to 12:32 for D/W. |  |  |  |  | About 50 MW power interruption occurred under Bhaluka S/S area
from 08:31 to 12:32.
b) Bagerhat 132/33 kV T-1 transformer was under shut down from 07:36 to 08:19 for C/M. |  |  |  |  | About 14 MW power interruption occurred under Bagerhat S/S area
from 07:36 to 08:19.
c) Shariatpur 132/33 kV T-2 transformer was under shut down from 08:36 to 10:06 for C/M. |  |  |  |  | About 15 MW power interruption occurred under Shariatpur S/S area
from 08:36 to 10:06.
d) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down from 09:05 to 17:25 for C/M.
e) Ashuganj-B.Baria 132 kV Ckt-2 was under shut down from 09:57 to 11:00 for C/M.
f) Hasnabad-Sitalakkhya 132 kV Ckt was under shut down from 10:11 to 15:15 for D/W.
g) Hasnabad-Bramhangaon 132 kV Ckt was under shut down from 10:29 to 15:14 for D/W.
h) Meghnaghat 450 MW GT-2 tripped at 13:04 due to voltage fluctuation and was synchronized at 15:38.
i) Meghnaghat-Haripur 230 kV Ckt-1 tripped at 13:04 from both ends showing Dist.Z1,CN,A,B,C at
Haripur end due to B-phase,LA burst and was switched on at 18:26.
j) Bhulta-Rampura 230 kV Ckt-4 tripped at 13:04 from Bhulta end showing Dist.Z3,OC,E/F and was
switched on at 13:29.
k) Siddhirganj Peaking GT-2 was synchronized at 08:07.
l) Gopalganj-Gollamari 132 kV Ckt-1 was switched on at 16:55.
m) Ghorashal-Ishurdi 230 kv Ckt-1 tripped at 18:38 showing Dist.Z1,B at Ghorashal end and was
switched on at 18:50.
n) Sikalbaha-Anwara 230 kv Ckt-2 was charged from Anwara end.
o) Barishal(N) 230/132 kV TO2 transformer was under shut down from 21:50 to 23:06 for R/H maintenance
at HT side bushing.
p) Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-3 tripped at 03:55(02/10/2021) and was switched
on at 05:16.
q) Fenchuganj-Srimangal 132 kV Ckt-2 tripped at 05:05(02/10/2021) from Srimangal end showing Dist.A
and was switched on at 05:15.
r) Sylhet 225 MW CCPP tripped at 23:17 due to problem with control system.
s) Cox'sbazar-Dohazari 132 kV Ckt-2 was shut down at 06:34(02/10/2021) for D/W.
t) Lalbag-Kallyanpur 132 kV Ckt-1 tripped at 06:05(02/10/2021) showing Dirctional O/C relay at Lalbag end and was switched on at 07:04.
u) Mymensingh-Kishoreganj 132 kV Ckt-2 was shut down at 07:24(02/10/2021) for C/M.
v) Rampura-Bashundhara 132 kV Ckt-2 was under shut down from 07:12(02/10/20210 to 09:53 for C/M.
w) Thakurgaon-Purbasadipur 132 kV Ckt-2 was shut down at 07:20(02/10/2021) for C/M.
x) Shahjibazar 330 MW GT-1 was synchronized at 08:01(02/10/2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7312627 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 395 | 7162840 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 318 | 7580000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 5941550 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 305 | 6591884 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1109382
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 33 | 299941 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 315648
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 189 | 1082000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1443564 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 1048608 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1285956
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1320480 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1107159
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1041295
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1111740 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 810300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 668900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 134918 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 3703417 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 52 | 1630512 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 1224852 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 1803840 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3356640
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 250334
| Dhaka area Total |  |  |  | 5719 | 2906 | 59338387
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 97345 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 142560
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 572640 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 160 | 3797385 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2187090
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 563380 | Low demand
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 557040 | Low demand
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2050560 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 486672
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 840000
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 190992 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31850
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 286 | 3658004 | Engine problem
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1251781
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2155158
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2250240
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2476473
| Chattogram area Total |  |  |  | 2382 | 1328 | 26209170
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 110 | 2362754 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4845000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7812200 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7520000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 543312 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1317600
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 351272 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 984360 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 127 | 3032654 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 82232 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 139 | 3315230 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 4236960
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 511920
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 181800 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 2875200
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 768700
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 784930
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 503640 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1086420
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 1414560 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 621720 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2070 | 45152464
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 205 | 4737200
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 489672
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10250
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3900000
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2684400
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 290110
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 148800
| Mymensingh Area Total |  |  |  | 709 | 559 | 12260432
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1027000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 45000 | Under maint.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3518521
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 829000 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1065000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000 | Engine problem
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 51 | 1060320
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1847040
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 4335130
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 380000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 564744
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7100000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 7607000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 228600
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7554000 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1615 | 37425355
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 707 | 17115636
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 95520
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 180 | 3333120 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 9035712 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 14400 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1124160
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 32 | 385632 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1398 | 31104180
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 601494
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2061435 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 377844 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 10930500 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 4713327
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 304800 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 906 | 18989400
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 359817
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 71312 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 193400 | Low demand
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 180054 | Low demand
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 256504 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4408982 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 192 | 4718464 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8969200 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 177620 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 473040
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244386
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 411840
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 561030 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1861344 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2011104
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33060
| Rajshahi Area Total |  |  |  | 2179 | 1338 | 24931157
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1816581
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1594915
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34809
| Rangpur Area Total |  |  |  | 605 | 188 | 3446305
| Total |  |  |  | 21180 | 12308 | 258856850
| Eastern Grid Total |  |  |  | 14221 | 8478 | 180385808
| Western Grid Total |  |  |  | 6959 | 3830 | 78471042
| National Grid Total |  |  |  | 21180 | 12308 | 258856850
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-01
(a) ENTIRE EASTERN GRID : |  | 7981 | MW | (b) ENTIRE WESTERN GRID : |  | 3826 | MW
i) Dhaka area |  | 3992 | MW | i) Khulna area |  | 1494 | MW
ii) Chittagong area |  | 1210 | MW | ii) Rajshahi area |  | 1260 | MW
iii) Comilla area |  | 1179 | MW | iii) Barisal area |  | 339 | MW
iv) Mymensingh area |  | 1035 | MW | iv) Rangpur area |  | 733 | MW
v) Sylhet area |  | 565 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11807 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 1:00 | Kishoreganj | 146 | 19:30 | Jessore | 98 | 20:00
Munsiganj | 104 | 0:00 | Netrokona | 119 | 18:30 | Benapol | 68 | 18:30
Sonargaon | 73 | 1:00 | Jamalpur | 148 | 20:00 | Jhenida(Old) | 114 | 18:30
Shyampur | 182 | 0:00 | Sherpur | 134 | 22:00 | Bottail | 108 | 18:30
Bhulta | 196 | 5:00 | Srimongal | 55 | 20:00 | G.K Project | 55 | 19:00
Madanganj | 42 | 9:00 | Shahjibazar | 119 | 21:00 | Faridpur | 143 | 21:00
Shitalakhya | 92 | 1:00 | Fenchuganj | 46 | 22:00 | Rajbari | 54 | 18:30
Rahim steel | 12 | 1:00 | Kulawara | 50 | 20:00 | Madaripur | 107 | 22:00
Matuail | 54 | 3:00 | Sylhet | 136 | 21:00 | Sariatpur | 68 | 21:00
Ghorasal | 76 | 2:00 | Chatak | 36 | 21:00 | Gopalganj | 94 | 18:30
Narsingdi | 184 | 21:00 | Sunamganj | 56 | 21:00 | Bagerhat | 95 | 20:00
Haripur (SBU) | 109 | 2:00 | Biani Bazar | 72 | 20:00 | Mongla | 37 | 23:00
Sreenagar | 42 | 21:00 | Comilla (S) | 136 | 22:00 | Satkhira | 101 | 21:00
Ullon | 67 | 1:00 | Comilla(N) | 141 | 19:00 | Gallamari | 37 | 23:00
Hasnabad | 84 | 13:00 | Chandpur | 77 | 22:00 | Magura | 56 | 18:30
Magbazar | 78 | 18:00 | Feni | 125 | 21:00 | Norail | 45 | 18:30
Maniknagar | 58 | 22:00 | Chowmuhani | 208 | 22:00 | Chuadanga | 96 | 21:00
Bangabhaban | 4 | 1:00 | Ashuganj | 46 | 0:00 | Barisal(N) | 45 | 22:00
Motijheel | 18 | 19:30 | Daudkandi | 148 | 1:00 | Barisal (S) | 100 | 23:00
Narinda | 44 | 18:30 | B.Baria | 170 | 21:00 | Patuakhali | 120 | 23:00
Kazla | 75 | 23:00 | Ramganj | 90 | 21:00 | Bhandaria | 50 | 20:00
Dhanmondi | 150 | 19:00 | Chaddagram | 46 | 22:00 | Borguna | 18 | 23:00
Lalbag | 64 | 1:00 | PHP | 9 | 23:00 | Borhan Uddin | 44 | 23:00
Madartek | 75 | 23:00 | Kochua | 62 | 21:00 | Ishurdi | 64 | 21:00
Dhaka University | 23 | 12:00 | Madunaghat | 56 | 22:00 | Ruppur Paromanobik | 4 | 9:00
Aftabnagar | 15 | 20:00 | Hathazari | 96 | 18:00 | Natore | 120 | 20:00
Fatullah | 52 | 1:00 | Khulshi | 199 | 0:00 | Bogra | 162 | 21:00
Nawabganj | 54 | 22:00 | Halishahar | 117 | 20:00 | Noagaon | 102 | 19:00
Keraniganj | 61 | 1:00 | Baraulia | 126 | 8:00 | Rajshahi | 148 | 20:00
Mirpur | 122 | 0:00 | Sikalbaha | 32 | 11:00 | Rajshahi New | 18 | 22:00
Kalyanpur | 93 | 23:00 | Dohazari | 114 | 19:30 | C.Nawabganj | 57 | 22:00
Gulshan | 92 | 18:00 | Cox'sbazar | 100 | 20:00 | Amnura | 48 | 20:00
Uttara | 81 | 18:00 | Chandraghona | 28 | 18:30 | Pabna | 105 | 20:00
Uttara New | 25 | 1:00 | Kaptai | 4.2 | 18:30 | Shahjadpur | 83 | 19:00
Kamrangirchar | 85 | 1:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 94 | 19:30
Savar | 141 | 16:00 | Bakulia | 102 | 1:00 | Niyamatpur | 74 | 21:00
Bhasantec | 128 | 18:30 | Julda | 19 | 1:00 | Joypurhat | 58 | 20:00
Agargaon | 75 | 23:00 | TK chemical | 19 | 1:00 | Sherpur(Bogura) | 58 | 19:00
Satmosjid | 107 | 20:00 | Modern Steel | 0.1 | 7:00 | Mohastangor | 64 | 21:00
Tongi | 109 | 1:00 | Shahmirpur | 21 | 1:00 | Bhangura | 32 | 19:30
Kabirpur | 196 | 22:00 | Khagrachhari | 28 | 1:00 | Rangpur | 122 | 24:00
Basundhara | 172 | 18:00 | Matarbari | 36 | 18:00 | Lalmonirhat | 43 | 18:30
Manikganj | 72 | 21:00 | Baroiar Hat | 48 | 18:30 | Saidpur | 83 | 1:00
Joydevpur | 146 | 21:00 | Rangamati | 14 | 18:30 | Purbasadipur | 99 | 19:00
New Tongi | 67 | 22:00 | Abul Khair 230 | 144 | 4:00 | Thakurgaon | 82 | 19:30
Kodda | 210 | 1:00 | BSRM | 149 | 6:00 | Palashbari | 116 | 20:00
Dhamrai | 96 | 0:00 | GPH Ispat | 90 | 6:00 | Barapukuria | 48 | 18:30
Rajendrapur | 96 | 1:00 | Agrabad | 0 | 1:00 | Panchagar | 54 | 18:30
Valuka | 102 | 21:00 | Goalpara | 31 | 23:00 | Joldhaka | 64 | 19:00
Tangail | 225 | 20:00 | Central S/S | 84 | 20:00 | Kurigram | 61 | 18:30
Mymensing | 220 | 19:00 | Noapara | 45 | 18:30 | Mithapukur | 30 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 18:30 | 402 | 24:00 | Kaliakoir | 398 | 0.75 | 388 | 0.8125
| Bheramara | 403 | 17:00 | 396 | 18:30 | Bhulta | 387 | 0.70833 | 382 | 0.41667
| Ashuganj(N) | 395 | 17:00 | 389 | 10:00 | Gopalganj | 410 | 0.625 | 391 | 0.875
| Payra | 414 | 17:00 | 405 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 23:00 | 230 | 1:00 | Hathazari | 236 | 19:00 | 221 | 11:00
| Ishurdi | 235 | 17:00 | 224 | 20:00 | Megnaghat | 236 | 18:30 | 230 | 4:00
| Ashuganj | 242 | 6:00 | 239 | 19:30 | Fenchuganj | 244 | 17:00 | 237 | 24:00
| Serajganj | 229 | 17:00 | 225 | 10:00 | Siddhirganj | 233 | 6:00 | 229 | 10:00
| Baghabari | 233 | 16:00 | 225 | 20:00 | Maniknagar | 231 | 6:00 | 228 | 7:00
| Barapukuria | 237 | 17:00 | 225 | 20:00 | Agargaon | 230 | 7:00 | 225 | 10:00
| Bogra | 226 | 17:00 | 213 | 20:00 | Barisal | 240 | 22:00 | 231 | 21:00
| Rajshahi | 230 | 18:00 | 220 | 2:00 | Bhola 225 MW | 244 | 7:00 | 237 | 19:30
| Khulna South | 234 | 17:00 | 220 | 21:00 | AKSML | 234 | 22:00 | 220 | 10:00
| Rampura | 231 | 18:30 | 227 | 1:00 | BSRM | 238 | 18:30 | 225 | 10:00
| Haripur | 231 | 17:00 | 228 | 11:00 | Bibiyana | 244 | 16:00 | 238 | 24:00
| Hasnabad | 228 | 15:00 | 224 | 1:00 | Bhulta | 236 | 19:00 | 230 | 7:00
| Shyampur | 230 | 17:00 | 224 | 10:00 | Ashuganj (S) | 239 | 17:00 | 235 | 20:00
| Aminbazar | 231 | 1:00 | 226 | 2:00 | Kaliakoir | 231 | 18:00 | 224 | 10:00
| Tongi | 236 | 5:00 | 224 | 10:00 | GPH | 237 | 18:30 | 223 | 9:00
| Comilla (N) | 234 | 18:30 | 228 | 10:00 | Jhenaidah | 230 | 17:00 | 216 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 13:00 | 132 | 1:00 | Madanhat | 138 | 0.70833 | 131 | 0.58333
| Munsiganj | 137 | 17:00 | 133 | 1:00 | Hathazari | 136 | 0.70833 | 130 | 0.45833
| Sonargaon | 136 | 18:30 | 132 | 1:00 | Khulshi | 135 | 0.041667 | 127 | 0.45833
| Shyampur | 138 | 17:00 | 135 | 1:00 | Halishahar | 137 | 0.041667 | 129 | 0.33333
| Bhulta | 132 | 17:00 | 125 | 1:00 | Baraulia | 136 | 0.041667 | 129 | 0.41667
| Madanganj | 136 | 16:00 | 130 | 2:00 | Sikalbaha | 138 | 0.77083 | 129 | 0.41667
| Shitalakhya | 138 | 18:30 | 133 | 11:00 | Dohazari | 131 | 0.77083 | 123 | 0.5
| Rahim steal | 135 | 13:00 | 132 | 1:00 | Cox'sbazar | 124 | 0.75 | 114 | 0.45833
| Matuail | 135 | 13:00 | 132 | 1:00 | Chandraghona | 137 | 0.041667 | 131 | 0.41667
| Ghorasal | 140 | 18:00 | 134 | 13:00 | Kaptai | 135 | 0.041667 | 132 | 0.54167
| Narsinghdi | 134 | 6:00 | 124 | 21:00 | A. Khaer Stl. | 135 | 0.041667 | 128 | 0.41667
| Haripur (SBU) | 136 | 18:30 | 131 | 1:00 | Bakulia | 137 | 0.77083 | 128 | 0.375
| Sreenagar | 135 | 17:00 | 132 | 1:00 | Julda | 139 | 0.75 | 128 | 0.29167
| Ullon | 134 | 4:00 | 132 | 10:00 | TK Chemical | 137 | 0.79167 | 128 | 0.41667
| Hasnabad | 136 | 1:00 | 134 | 8:00 | Modern Steel | 136 | 0.041667 | 127 | 0.41667
| Magbazar | 135 | 4:00 | 132 | 10:00 | Shahmirpur | 137 | 0.041667 | 128 | 0.375
| Maniknagar | 135 | 3:00 | 133 | 10:00 | Khagrachhari | 136 | 0.041667 | 129 | 0.45833
| Bangabhaban | 135 | 3:00 | 133 | 10:00 | Matarbari | 130 | 0.54167 | 119 | 0.5
| Motijheel | 135 | 3:00 | 133 | 10:00 | Baroiar Hat | 134 | 0.041667 | 130 | 0.41667
| Narinda | 135 | 3:00 | 133 | 10:00 | Rangamati | 137 | 18:30 | 130 | 11:00
| Kazla | 135 | 3:00 | 133 | 10:00 | Agrabad | 0 | #N/A | 0 | #N/A
| Dhanmondi | 135 | 17:00 | 132 | 1:00 | Goalpara S/S | 140 | 17:00 | 132 | 0.83333
| Lalbag | 136 | 16:00 | 133 | 1:00 | Khulna Central S/S | 138 | 17:00 | 131 | 0.83333
| Madartek | 135 | 5:00 | 131 | 20:00 | Noapara | 138 | 17:00 | 128 | 0.83333
| Dhaka University | 135 | 4:00 | 132 | 10:00 | Jessore | 136 | 8:00 | 125 | 0.83333
| Aftabnagar | 135 | 5:00 | 132 | 10:00 | Benapol | 136 | 0.375 | 124 | 0.83333
| Fatullah | 138 | 17:00 | 133 | 8:00 | Jhenida(Old) | 138 | 17:00 | 127 | 0.83333
| Nawabganj | 136 | 17:00 | 131 | 1:00 | Bottail | 136 | 0.70833 | 129 | 0.83333
| Keraniganj | 136 | 18:30 | 133 | 1:00 | G.K Project | 138 | 0.29167 | 134 | 0.083333
| Mirpur | 132 | 3:00 | 127 | 10:00 | Faridpur | 138 | 0.75 | 130 | 0.83333
| Kalyanpur | 132 | 17:00 | 130 | 8:00 | Rajbari | 137 | 0.70833 | 129 | 0.875
| Gulshan | 135 | 6:00 | 131 | 20:00 | Madaripur | 140 | 0.375 | 132 | 0.91667
| Uttara | 132 | 3:00 | 128 | 10:00 | Shariyatpur S/S | 140 | 10:00 | 130 | 0.875
| Uttara New | 132 | 1:00 | 127 | 10:00 | Gopalganj | 144 | 0.70833 | 133 | 0.875
| Kamrangirchar | 136 | 17:00 | 132 | 10:00 | Bagerhat | 137 | 17:00 | 129 | 0.83333
| Savar | 135 | 18:30 | 128 | 10:00 | Mongla | 134 | 4:00 | 128 | 0.83333
| Bhasantec | 136 | 5:00 | 132 | 11:00 | Satkhira | 138 | 17:00 | 126 | 21:00
| Agargaon | 137 | 5:00 | 131 | 13:00 | Gallamari | 140 | 0.70833 | 131 | 20:00
| Satmosjid | 137 | 17:00 | 133 | 10:00 | Magura | 139 | 17:00 | 125 | 0.83333
| Tongi | 141 | 18:00 | 135 | 10:00 | Narail | 135 | 0.70833 | 123 | 0.91667
| Kabirpur | 137 | 17:00 | 129 | 22:00 | Chuadanga | 134 | 17:00 | 119 | 0.83333
| Basundhara | 139 | 18:30 | 132 | 10:00 | Barisal(N) | 139 | 7:00 | 132 | 0.875
| Manikganj | 141 | 13:00 | 134 | 21:00 | Barisal (S) | 138 | 17:00 | 130 | 21:00
| Joydevpur | 138 | 18:30 | 135 | 23:00 | Patuakhali(S) | 136 | 0.95833 | 126 | 0.8125
| New Tongi | 140 | 21:00 | 134 | 11:00 | Bhandaria | 136 | 0.29167 | 125 | 0.83333
| Kodda | 139 | 18:00 | 125 | 10:00 | Borguna | 137 | 0.375 | 130 | 0.041667
| Dhamrai | 140 | 17:00 | 134 | 22:00 | Jhenaidah(230kV S/S)
| Rajendrapur | 138 | 18:30 | 124 | 11:00 | Ishurdi | 137 | 17:00 | 131 | 20:00
| Valuka | 131 | 9:00 | 106 | 20:00 | Ruppur Paromanobik | 137 | 18:00 | 131 | 19:30
| Tangail | 133 | 8:00 | 123 | 19:30 | Natore | 136 | 18:00 | 129 | 20:00
| Mymensing | 132 | 9:00 | 114 | 19:00 | Bogra | 133 | 6:00 | 126 | 19:30
| Kishorganj | 132 | 11:00 | 117 | 20:00 | Noagaon | 132 | 17:00 | 118 | 20:00
| Netrokona | 128 | 12:00 | 107 | 19:00 | Rajshahi | 135 | 18:00 | 128 | 2:00
| Jamalpur | 139 | 9:00 | 121 | 20:00 | Rajshahi New | 136 | 18:00 | 129 | 2:00
| Sherpur | 138 | 9:00 | 118 | 20:00 | C.Nawabganj | 135 | 18:00 | 129 | 20:00
| Srimongal | 139 | 8:00 | 132 | 20:00 | Amnura | 134 | 18:00 | 126 | 3:00
| Shahjibazar | 137 | 7:00 | 129 | 23:00 | Pabna | 136 | 17:00 | 128 | 20:00
| Fenchuganj | 136 | 6:00 | 129 | 24:00 | Shahjadpur | 140 | 17:00 | 134 | 7:00
| Khulawara | 135 | 7:00 | 128 | 24:00 | Serajganj | 133 | 18:00 | 125 | 21:00
| Sylhet | 133 | 7:00 | 123 | 24:00 | Niyamatpur | 130 | 17:00 | 114 | 20:00
| Chatak | 132 | 5:00 | 122 | 24:00 | Joypurhat | 131 | 17:00 | 117 | 20:00
| Sunamganj | 130 | 7:00 | 122 | 24:00 | Sherpur(Bogura) | 134 | 17:00 | 125 | 20:00
| Biani Bazar | 132 | 8:00 | 120 | 24:00 | Mohastangor | 134 | 17:00 | 122 | 20:00
| Comilla(s) | 129 | 6:00 | 125 | 15:00 | Bangura | 136 | 17:00 | 132 | 2:00
| Comilla(n) | 137 | 18:00 | 134 | 22:00 | Rangpur | 130 | 17:00 | 116 | 20:00
| Chandpur | 139 | 18:00 | 137 | 22:00 | Lalmonirhat | 131 | 17:00 | 117 | 21:00
| Feni | 137 | 18:30 | 127 | 15:00 | Saidpur | 132 | 6:00 | 119 | 20:00
| Chowmuhani | 134 | 18:00 | 128 | 9:00 | Purbasadipur | 131 | 17:00 | 112 | 20:00
| Ashuganj | 140 | 17:00 | 135 | 19:30 | Thakurgaon | 133 | 17:00 | 114 | 20:00
| Daudkandi | 134 | 18:30 | 128 | 1:00 | Palashbari | 132 | 18:00 | 122 | 1:00
| B.Baria | 135 | 8:00 | 127 | 22:00 | Barapukuria | 137 | 17:00 | 125 | 20:00
| Ramganj | 135 | 18:30 | 130 | 15:00 | Panchagar | 136 | 0.25 | 114 | 0.875
| Chaddagram | 138 | 18:30 | 130 | 15:00 | Joldhaka | 129 | 0.70833 | 111 | 0.91667
| PHP | 135 | 18:30 | 128 | 12:00 | Kurigram | 131 | 0.70833 | 116 | 0.83333
| Kochua | 137 | 18:30 | 134 | 20:00 | Mithapukur | 132 | 0.70833 | 120 | 0.83333
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-10-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 52 | 8304 | 3888 | 12192 |  |  |  | QF-LDC-11
0:30 | 72 | 8413 | 3741 | 12154 | Date: | 2021-10-01
1:00 | 92 | 8522 | 3594 | 12116
1:30 | 114 | 8387.5 | 3498.5 | 11886
2:00 | 136 | 8253 | 3403 | 11656
2:30 | 97 | 8134 | 3358 | 11492 | [5 empty] | Gen. at Eve. Peak | 12308 | 12308 MW (21:00 )
3:00 | 58 | 8015 | 3313 | 11328 | [6 empty] | 21:00
3:30 | 57 | 7913.5 | 3293 | 11206.5 | [5 empty] | Gen. at Day Peak | 9693 | 9693 MW (12:00 )
4:00 | 56 | 7812 | 3273 | 11085 | [6 empty] | 12:00
4:30 | 38 | 7714 | 3210.5 | 10924.5 | [5 empty] | Highest Generation | 12425
5:00 | 20 | 7616 | 3148 | 10764 | [6 empty] | 23:00
5:30 | 68 | 7266.5 | 3058 | 10324.5
6:00 | 116 | 6917 | 2968 | 9885
6:30 | 114 | 6756 | 2894.5 | 9650.5
7:00 | 112 | 6595 | 2821 | 9416
7:30 | 65 | 6489 | 2765.5 | 9254.5
8:00 | 18 | 6383 | 2710 | 9093
8:30 | 20 | 6369.5 | 2668.5 | 9038
9:00 | 22 | 6356 | 2627 | 8983
9:30 | 36 | 6371.5 | 2625.5 | 8997
10:00 | 50 | 6387 | 2624 | 9011
10:30 | 40 | 6506.5 | 2647 | 9153.5
11:00 | 30 | 6626 | 2670 | 9296
11:30 | 26 | 6772 | 2722.5 | 9494.5
12:00 | 22 | 6918 | 2775 | 9693
12:30 | 88 | 7045.5 | 2826.5 | 9872
13:00 | 154 | 7173 | 2878 | 10051
13:30 | 139 | 7121 | 2865.5 | 9986.5
14:00 | 124 | 7069 | 2853 | 9922
14:30 | 115 | 7139.5 | 2882 | 10021.5
15:00 | 106 | 7210 | 2911 | 10121
15:30 | 60 | 7165 | 2849.5 | 10014.5
16:00 | 14 | 7120 | 2788 | 9908
16:30 | 22 | 6874.5 | 2700.5 | 9575
17:00 | 30 | 6629 | 2613 | 9242
17:30 | 41 | 6892 | 2862 | 9754
18:00 | 52 | 7155 | 3111 | 10266
18:30 | #VALUE! | 7771 | 3368.5 | 11139.5
19:00 | #VALUE! | 8387 | 3626 | 12013
19:30 | 192 | 8369 | 3776 | 12145
20:00 | 200 | 8462 | 3783 | 12245 |  |  |  | Executive Engineer
20:30 | 194 | 8470 | 3806.5 | 12276.5 |  |  |  | Network Operation Division
21:00 | 188 | 8478 | 3830 | 12308
21:30 | 154 | 8493 | 3815.5 | 12308.5
22:00 | 120 | 8508 | 3801 | 12309 |  |  |  |  | Page 6 of 7
22:30 | 110 | 8533 | 3834 | 12367
23:00 | 100 | 8558 | 3867 | 12425
23:30 | 76 | 8431 | 3877.5 | 12308.5
24:00 | 52 | 8304 | 3888 | 12192
12308 MW (21:00 )
9693 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-01 |  | Energy |  | 258856850
[13 empty] | 2021-10-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4175 | 707 | 2360 | 0 | 3440 | 605 | 160 | 210 | 405 | 130 | 0 | 0
0:30 | 4177 | 712 | 2271 | 0 | 3571 | 586 | 159.5 | 165 | 386.5 | 126 | 0 | 0 | Date: | 2021-10-01
1:00 | 4179 | 717 | 2182 | 0 | 3702 | 567 | 159 | 120 | 368 | 122 | 0 | 0
1:30 | 4169.5 | 712.5 | 2199 | 0 | 3603.5 | 566.5 | 160 | 120 | 227 | 128 | 0 | 0 | [8 empty] | Total Energy | 258.8569 | Total Energy Gen 258.857 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.857 MKWHr
2:00 | 4160 | 708 | 2216 | 0 | 3505 | 566 | 161 | 120 | 86 | 134 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4127.5 | 708 | 2227.5 | 0 | 3372.5 | 556.5 | 161 | 120 | 86 | 133 | 0 | 0 | [8 empty] | Energy Requirement | 258.8569
3:00 | 4095 | 708 | 2239 | 0 | 3240 | 547 | 161 | 120 | 86 | 132 | 0 | 0
3:30 | 4139 | 707.5 | 2247 | 0 | 3079.5 | 536.5 | 161 | 120 | 86 | 130 | 0 | 0 | [6 empty] | Shortage
4:00 | 4183 | 707 | 2255 | 0 | 2919 | 526 | 161 | 120 | 86 | 128 | 0 | 0
4:30 | 4215 | 707.5 | 2221 | 0 | 2780.5 | 526.5 | 161 | 120 | 69 | 124 | 0 | 0
5:00 | 4247 | 708 | 2187 | 0 | 2642 | 527 | 161 | 120 | 52 | 120 | 0 | 0
5:30 | 4180 | 708 | 2162.5 | 0 | 2316 | 527 | 161 | 120 | 36 | 114 | 0 | 0
6:00 | 4113 | 708 | 2138 | 0 | 1990 | 527 | 161 | 120 | 20 | 108 | 0 | 0
6:30 | 4123.5 | 708 | 2165 | 0 | 1753.5 | 492.5 | 161.5 | 120 | 12 | 107 | 7.5 | 0 |  |  |  |  | Coal
7:00 | 4134 | 708 | 2192 | 0 | 1517 | 458 | 162 | 120 | 4 | 106 | 15 | 0
7:30 | 4158.5 | 708 | 2129.5 | 0 | 1391 | 442 | 162 | 120 | 4 | 103 | 36.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4183 | 708 | 2067 | 0 | 1265 | 426 | 162 | 120 | 4 | 100 | 58 | 0
8:30 | 4139 | 708 | 2063.5 | 0 | 1267 | 401 | 161 | 120 | 4 | 100 | 74.5 | 0
9:00 | 4095 | 708 | 2060 | 0 | 1269 | 376 | 160 | 120 | 4 | 100 | 91 | 0
9:30 | 4108.5 | 708 | 2106 | 0 | 1211.5 | 377 | 159 | 120 | 5.5 | 102 | 99.5 | 0
10:00 | 4122 | 708 | 2152 | 0 | 1154 | 378 | 158 | 120 | 7 | 104 | 108 | 0
10:30 | 4160 | 708 | 2154.5 | 0 | 1256.5 | 377.5 | 158.5 | 120 | 5.5 | 106 | 107 | 0
11:00 | 4198 | 708 | 2157 | 0 | 1359 | 377 | 159 | 120 | 4 | 108 | 106 | 0
11:30 | 4219 | 708 | 2210.5 | 0 | 1482 | 377 | 159 | 120 | 4 | 108 | 107 | 0
12:00 | 4240 | 708 | 2264 | 0 | 1605 | 377 | 159 | 120 | 4 | 108 | 108 | 0
12:30 | 4217.5 | 708 | 2169.5 | 0 | 1890.5 | 392.5 | 159 | 120 | 4 | 111 | 100 | 0
13:00 | 4195 | 708 | 2075 | 0 | 2176 | 408 | 159 | 120 | 4 | 114 | 92 | 0
13:30 | 4195 | 708 | 2075 | 0 | 2176 | 408 | 159 | 120 | 4 | 114 | 92 | 0
14:00 | 4195 | 708 | 2075 | 0 | 2176 | 408 | 159 | 120 | 4 | 114 | 92 | 0
14:30 | 4183.5 | 707.5 | 2086.5 | 0 | 2226 | 408.5 | 159.5 | 120 | 4 | 118 | 72.5 | 0
15:00 | 4172 | 707 | 2098 | 0 | 2276 | 409 | 160 | 120 | 4 | 122 | 53 | 0
15:30 | 4144.5 | 707 | 2092 | 0 | 2209.5 | 408 | 159.5 | 120 | 4 | 117 | 53 | 0
16:00 | 4117 | 707 | 2086 | 0 | 2143 | 407 | 159 | 120 | 4 | 112 | 53 | 0
16:30 | 4035.5 | 707 | 1938.5 | 0 | 2062.5 | 392 | 159 | 135 | 6.5 | 107 | 32 | 0
17:00 | 3954 | 707 | 1791 | 0 | 1982 | 377 | 159 | 150 | 9 | 102 | 11 | 0
17:30 | 3992 | 707 | 1892 | 0 | 2163 | 381.5 | 159.5 | 150 | 190.5 | 113 | 5.5 | 0
18:00 | 4030 | 707 | 1993 | 0 | 2344 | 386 | 160 | 150 | 372 | 124 | 0 | 0
18:30 | 4148.5 | 707 | 2115.5 | 0 | 2877 | 440.5 | 160 | 147.5 | 418.5 | 125 | 0 | 0
19:00 | 4267 | 707 | 2238 | 0 | 3410 | 495 | 160 | 145 | 465 | 126 | 0 | 0
19:30 | 4411 | 707 | 2333 | 0 | 3278 | 595 | 160 | 120 | 411 | 130 | 0 | 0
20:00 | 4528 | 707 | 2330 | 0 | 3262 | 594 | 160 | 120 | 412 | 132 | 0 | 0
20:30 | 4483.5 | 707 | 2348.5 | 0 | 3288 | 599.5 | 160 | 150 | 408 | 132 | 0 | 0
21:00 | 4439 | 707 | 2367 | 0 | 3314 | 605 | 160 | 180 | 404 | 132 | 0 | 0
21:30 | 4445.5 | 707 | 2339.5 | 0 | 3325 | 610 | 160 | 180 | 407.5 | 134 | 0 | 0
22:00 | 4452 | 707 | 2312 | 0 | 3336 | 615 | 160 | 180 | 411 | 136 | 0 | 0
22:30 | 4466.5 | 707.5 | 2310 | 0 | 3382 | 615 | 160 | 180 | 411 | 135 | 0 | 0
23:00 | 4481 | 708 | 2308 | 0 | 3428 | 615 | 160 | 180 | 411 | 134 | 0 | 0
23:30 | 4328 | 707.5 | 2334 | 0 | 3434 | 610 | 160 | 195 | 408 | 132 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.8° C
24:00 | 4175 | 707 | 2360 | 0 | 3440 | 605 | 160 | 210 | 405 | 130 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 258.857 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.857 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 84 | 86 | 86 | 86 | 86 | 86 | 87 | 87 | 85 | 83 | 84 | 84 | 84 | 85 | 85 | 84 | 84 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1993385
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1804000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [16 empty] | 3 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 97345
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 11 | 16 | 20 | 20 | 12 | 20 | 17 | 13 | 8 | 2 | [9 empty] | 142560
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | [16 empty] | 95 |  | 102 | 70 | 71 | 68 | 68 | 68 | 68 | 563380
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 68 | 68 | 51 | 51 | 51 | 51 | 65 | 90 | 90 | 90 | 99 | 105 | 81 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2187090
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 25 | [16 empty] | 35 | [8 empty] | 82232
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [7 empty] | 37 | 70 | 115 | 120 | 145 | 185 | 125 | 130 | 125 | 67 | 70 |  | 128 | 130 | 186 | 189 | 187 | 189 | 185 | 1082000
17 | Siddhirganj 335 MW CCPP | 235 | 233 | 235 | 230 | 226 | 175 | [19 empty] | 0 | 1443564
18 | Kodda 300 MW PP Unit-2 (Summit) | 296 | 296 | 296 | 195 | 130 | 60 | 15 | 15 | 15 |  |  | 5 | 116 | 188 | 190 | 145 | 145 | 163 |  | 245 | 195 | 195 | 195 | 195 | 195 | 195 | 3703417
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 45 | 45 | 45 | 45 | 351272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 305 | 305 | 305 | 300 | 300 | 300 | 300 | 300 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7312627
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2362754
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 543312
33 | Ashuganj 225 MW CCPP | 211 | 210 | 210 | 210 | 211 | 211 | 210 | 211 | 211 | 179 | 183 | 179 | 178 | 179 | 182 | 178 | 177 | 200 |  | 208 | 205 | 204 | 206 | 207 | 208 | 208 | 4845000
34 | Ashuganj 450 MW CCPP(South) | 330 | 305 | 310 | 315 | 320 | 305 | 310 | 365 | 305 | 305 | 310 | 305 | 275 | 280 | 310 | 305 | 275 | 330 |  | 305 | 330 | 350 | 315 | 315 | 320 | 305 | 7520000
| Ashuganj 450 MW CCPP(North) | 330 | 330 | 310 | 315 | 310 | 310 | 310 | 280 | 285 | 305 | 340 | 335 | 335 | 280 | 315 | 280 | 280 | 315 |  | 305 | 325 | 345 | 315 | 320 | 325 | 310 | 7812200
35 | Ashuganj 55 MW PP (Precision) | 56 | 55 | 56 | 56 | 56 | 55 | 55 | 56 | 56 | 56 | 55 | 55 | 54 | 54 | 55 | 54 | 54 | 54 |  | 52 | 52 | 53 | 54 | 55 | 56 | 56 | 1317600
36 | Chandpur 150 MW CCPP | 137 | 139 | 140 | 139 | 141 | 140 | 144 | 140 | 140 | 140 | 140 | 140 | 140 | 141 | 139 | 141 | 139 | 140 |  | 138 | 140 | 140 | 139 | 140 | 140 | 140 | 3315230
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP |  | 5 | 7 | 49 | 86 | 202 | 378 | 404 | 363 | 353 | 360 | 362 | 348 | 344 | 367 | 393 | 365 | 294 |  | 381 | 394 | 396 | 395 | 395 | 397 | 395 | 7162840
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 225 | 225 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5941550
41 | Haripur 360MW CCPP(HPL) | 326 | 332 | 332 | 329 | 329 | 330 | 328 | 329 | 328 | 329 | 323 | 322 | 283 | 252 | 303 | 303 | 251 | 262 |  | 332 | 332 | 326 | 318 | 322 | 322 | 324 | 7580000
42 | RPCL 210MW CCPP | 203 | 208 | 208 | 208 | 211 | 213 | 211 | 207 | 204 | 203 | 201 | 205 | 202 | 200 | 200 | 201 | 203 | 203 |  | 205 | 204 | 204 | 205 | 205 | 206 | 206 | 4737200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 23 | 39 | 46 | 42 | 49 | 28 | 49 | 7 | 22 | 2 | [9 empty] | 290110
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 44 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1027000
45 | Fenchugonj CCPP Phase-2 | [23 empty] | 20 | 20 | 20 | 45000
46 | Shajibazar 330 MW CCPP | 159 | 160 | 159 | 160 | 160 | 0 |  |  | 0 | [17 empty] | 829000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 36 | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 36 | 36 | 35 | 50 | 51 | 52 | 50 |  | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 1060320
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 30 | 78 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1847040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 165 | 192 | 191 | 192 | 192 | 192 | 192 | 192 | 192 | 166 | 166 | 166 | 166 | 166 | 190 |  | 206 | 220 | 220 | 220 | 220 | 220 | 0 | 4335130
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 380000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 228600
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 47 | 47 | 47 | 44 | 47 | 16 |  | 50 | 50 | 50 | 50 | 44 | 45 | 45 | 1065000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 564744
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 290 | 300 | 280 | 270 | 290 | 280 | 275 | 290 | 300 | 305 | 275 | 280 | 300 | 290 | 280 | 270 |  | 270 | 315 | 290 | 310 | 300 | 300 | 300 | 7100000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 320 | 322 | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7554000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 |  |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 1041295
59 | Tangail Palli Power Gen 22 MW | 19 | [16 empty] | 2 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 148800
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 486672
61 | Narshingdi 22 MW PP (Doreen) |  | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 15 | 15 | [5 empty] | 19 | 20 | 19 | 19 | 20 | 0 | 315648
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 489672
63 | Impoprt (Tripura) | 122 | 134 | 132 | 128 | 120 | 108 | 106 | 100 | 100 | 104 | 108 | 108 | 114 | 120 | 122 | 112 | 102 | 124 |  | 126 | 130 | 132 | 132 | 136 | 134 | 130 | 2875200
64 | Malancha, Ctg. EPZ (United) | 32 | 33 | 33 | 33 | 34 | 35 | 38 | 38 | 40 | 36 | 34 | 35 | 36 | 36 | 36 | 24 | 38 | 38 |  | 39 | 37 | 40 | 31 | 40 | 40 | 40 | 840000
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511920
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 181800
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 768700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 12 | 21 | 503640
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 29 | 26 | 29 | 29 | 26 | 28 | 26 | 20 | 20 | 13 | 13 | 13 | 11 | 11 | 11 | 11 | 8 |  | 25 | 27 | 28 | 26 | 26 | 28 | 29 | 511740
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 16 | 33 |  | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 8 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 668900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 98 | 98 | 85 | 17 | 17 | 1 | [6 empty] | 9 |  |  |  |  | 65 |  | 114 | 114 | 114 | 114 | 114 | 114 | 98 | 1086420
| Chowmuhani 113 MW | 48 | 47 | 48 | 48 | 48 | 47 | 42 | 44 | 48 | 48 | 52 | 47 | 48 | 48 | 48 | 48 | 48 | 76 |  | 86 | 95 | 95 | 95 | 95 | 96 | 58 | 1414560
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 54 | 54 | 54 | 54 | 53 | 65 | 119 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3356640
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 51 | [11 empty] | 8 | 8 | 8 | 8 | 8 | 8 | [8 empty] | 134918
79 | Kodda 150MW PP | 115 | 82 | 82 | 82 | 48 | 16 | [11 empty] | 50 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 1320480
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 25 | 25 |  |  | 6 | 8 | 8 | 8 | 22 | 24 | 25 | 25 | 25 | 28 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 784930
| Gazipur 100 MW PP | 105 | 52 | 17 | [7 empty] | 52 | 52 | 105 | 105 | 105 | 105 | 52 | 58 |  | 52 | 52 | 52 | 52 | 52 | 52 | 60 | 1224852
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 2 | 2 | 5 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 31850
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 37 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1251781
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 85 | 34 | 34 | 34 | 17 | 17 | 18 | 99 | 108 | 110 | 110 | 110 | 85 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2155158
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 25 | 25 | [15 empty] | 8 |  | 50 | 10 | 10 | 33 | 40 | 40 | 43 | 299941
86 | Meghnaghat CCPP ( Summit) | 250 | 265 | 275 | 280 | 275 | 250 | 270 | 260 | 260 | 275 | 280 | 270 | 270 | 280 | 275 | 250 | 225 | 285 |  | 290 | 305 | 315 | 305 | 310 | 305 | 305 | 6591884
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 93 | 93 | 93 | 93 | 93 | 75 | 55 | 55 | 55 | 25 | 20 | 48 | 84 | 93 | 93 | 86 | 39 | 35 |  | 76 | 92 | 93 | 93 | 93 | 93 | 94 | 1803840
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 42 | 10 | 10 | 10 | [11 empty] | 20 |  | 50 | 10 | 10 | 40 | 40 | 40 | 100 | 557040
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 984360
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 64 | 24 | 8 | 8 |  |  |  | 7 | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 74 | 64 | 64 | 64 | 64 | 64 | 75 | 1048608
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 50 | 19 | [6 empty] | 11 | 24 | 25 | 25 | 35 | 47 |  | 19 | 18 | 18 | 19 | 19 | 19 | 19 | 572640
96 | Chattogram 108 MW PP (ECPV) | 86 | 65 | [15 empty] | 11 |  | 25 | [5 empty] | 0 | 190992
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 40 | 15 | 15 | 15 | 15 | 15 | 40 | 40 | 40 | 50 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1109382
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1107159
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 130 | 130 | 163 | 110 | 110 | 110 | 163 | 110 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3518521
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 10250
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1285956
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 182 | 192 | 192 | 192 | 140 | 140 | 148 | 160 | 160 | 160 | 160 | 160 | 120 | 100 | 100 | 100 | 100 | 122 |  | 199 | 198 | 198 | 200 | 200 | 200 | 200 | 3900000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 131 | 105 | 80 | 80 | 80 | 84 | 85 | 63 | 53 | 53 | 25 |  |  |  | 23 | 59 |  | 106 | 65 | 60 | 52 | 52 | 50 | 60 | 1630512
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 74 | 100 | 100 | 100 | 100 | 76 | 50 | 50 |  | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 2050560
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 155 | 155 | 120 | 120 | 120 | 123 | 152 | 183 | 200 | 200 | 200 | 155 | 140 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4236960
117 | Ashuganj 150MW PP (Midland) | 137 | 136 | 137 | 135 | 137 | 135 | 133 | 125 | 125 | 123 | 132 | 118 | 125 | 83 | 117 | 118 | 118 | 120 |  | 125 | 125 | 127 | 127 | 127 | 133 | 136 | 3032654
118 | Bibiyana-III 400 MW CCPP | 316 | 317 | 317 | 317 | 317 | 317 | 318 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 317 |  | 316 | 316 | 316 | 316 | 316 | 316 | 317 | 7607000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 107 | 106 | 115 | 115 | 115 | 115 | 106 | 106 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 106 | 2684400
| Anwara 300 MW PP (United) | 306 | 306 | 305 | 305 | 305 | 305 | 142 | [12 empty] | 230 | 272 | 282 | 286 | 286 | 305 | 306 | 3658004
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2250240
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 72 | 72 | 53 | 53 | 55 | 78 | 112 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 112 | 2476473
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 621720
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 6 | 17 | 26 | 31 | 35 | 35 | 33 | 29 | 22 | 14 | 4 | [9 empty] | 250334
120 | Eastern Zone Total | 8522 | 8253 | 8015 | 7812 | 7616 | 6917 | 6595 | 6383 | 6356 | 6387 | 6626 | 6918 | 7173 | 7069 | 7210 | 7120 | 6629 | 7155 |  | 8387 | 8369 | 8462 | 8478 | 8508 | 8558 | 8304 | 180385808
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 10 | 4 | 4 | 4 | 4 | 4 | 4 | 95520
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 150 |  | 145 | 120 | 120 | 180 | 180 | 180 | 210 | 3333120
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 70 | 17 | 17 | [10 empty] | 2 | 38 |  | 98 | 105 | 105 | 105 | 105 | 105 | 105 | 1124160
130
131
132 | United Payra Power Ltd. | [17 empty] | 6 |  | 17 | 17 | 17 | 17 | 42 | 90 | 72 | 304800
133 | Bhola Nutan Biddut BD LTD (GAS) | 226 | 226 | 226 | 226 | 224 | 220 | 200 | 202 | 201 | 180 | 180 | 223 | 220 | 153 | 152 | 152 | 106 | 129 |  | 226 | 224 | 224 | 224 | 160 | 160 | 225 | 4713327
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 377844
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 84 | 85 | 86 | 86 | 87 |  | 85 | 86 | 86 | 86 | 75 | 75 | 88 | 2061435
140 | Bhola 33 MW PP (Venture) | 32 | 30 | 30 | 29 | 27 | 24 | 20 | 15 | 16 | 16 | 17 | 16 | 23 | 24 | 24 | 22 | 20 | 30 |  | 31 | 31 | 30 | 32 | 34 | 34 | 34 | 601494
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 14400
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [15 empty] | 50 | 50 | 50 |  | 50 | 38 | 32 | 32 | 32 | 32 | 32 | 385632
146 | Bheramara HVDC | 717 | 708 | 708 | 707 | 708 | 708 | 708 | 708 | 708 | 708 | 708 | 708 | 708 | 708 | 707 | 707 | 707 | 707 |  | 707 | 707 | 707 | 707 | 707 | 708 | 707 | 17115636
147 | Bheramara 410 MW CCPP | 410 | 410 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 350 | 360 | 370 | 360 | 300 | 320 |  | 360 | 390 | 400 | 370 | 370 | 385 | 355 | 9035712
148 | Payra 1320 MW | 490 | 490 | 470 | 450 | 450 | 450 | 380 | 350 | 300 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 300 | 310 |  | 420 | 520 | 520 | 530 | 540 | 540 | 530 | 10930500
149
150 | Barapukuria TPP Unit-1 | 77 | 76 | 77 | 76 | 77 | 77 | 78 | 76 | 76 | 78 | 77 | 77 | 78 | 79 | 79 | 77 | 77 | 76 |  | 75 | 75 | 74 | 75 | 75 | 75 | 75 | 1816581
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | [16 empty] | 43 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 359817
| Sirajgonj 6.55 MW Solar | [6 empty] | 1 | 3 | 4 | 4 | 1 | 2 | 2 | 5 | 2 | 2 | 0 | [9 empty] | 33060
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 166 | 166 | 167 | 180 | 179 | 177 | 175 | 189 | 169 | 174 | 178 | 180 | 181 | 178 | 167 | 157 | 154 | 151 |  | 162 | 183 | 190 | 190 | 185 | 188 | 185 | 4408982
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 188 | 189 | 192 | 192 | 189 | 188 | 189 | 181 | 166 | 173 | 188 | 181 | 179 | 166 | 181 | 176 | 176 | 157 |  | 186 | 186 | 187 | 192 | 195 | 195 | 191 | 4718464
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 395 | 397 | 402 | 362 | 354 | 391 | 307 | 308 | 367 | 365 | 404 | 333 | 351 | 398 | 360 | 291 | 372 |  | 356 | 395 | 410 | 414 | 418 | 417 | 401 | 8969200
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 24 |  | 17 | [6 empty] | 71312
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 18 | 18 | 17 | 18 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 473040
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244386
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 193400
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 16 |  | 43 | 43 | 25 | 25 | 25 | 25 | 25 | 180054
167 | Katakhali 50 MW Peaking PP | 30 | [16 empty] | 34 |  | 40 | 40 | 40 | 36 | 36 | 36 | 30 | 256504
168 | Santahar 50 MW Peaking PP | 29 | [16 empty] | 12 |  | 20 | 20 | 20 | 20 | 27 | 27 | 27 | 177620
169 | Natore 52 MW PP (Rajlanka) | 52 | 16 | [15 empty] | 3 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 411840
170 | Chapainawabganj 100 MW Peaking PP | 47 | [16 empty] | 75 |  | 93 | 94 | 94 | 93 | 93 | 93 | 93 | 561030
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 35 |  |  | 11 | 78 | 94 | 94 | 50 | 50 | 50 |  | 81 | 94 | 94 | 94 | 94 | 94 | 94 | 1861344
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 |  |  | 20 | 100 | 113 | 113 | 50 | 50 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2011104
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 107 | 107 | 81 | 40 |  |  |  |  | 35 | 35 | 35 | 34 | 34 | 34 | 34 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1594915
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 4 | 5 | 4 | 4 | 3 | 5 | 4 | 3 | [9 empty] | 34809
178
178