## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-03 | Sunday
|  |  | Date (day): | 2021-10-03 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13900.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14955 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-02 | 2021-10-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 290 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 401 | 399 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 320 | 340 | 340 | 20 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 310 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 8 | 45 | 68 | 68 |  | 32 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 145 | 185 | 150 | 185 | 25
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under S/D.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 93 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 51 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 208 | 281 | 250 | 290 |  |  | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 50 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 58 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 93 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2772 | 3289 | 3544 | 3839 | 1037 | 792
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 19 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 1 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 50 | 25 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 124 | 161 | 126 | 161 | 69 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 87 | 34 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 17 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 8 | 86 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 304 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 71 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 108 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1183 | 1538 | 1451 | 1564 | 134 | 671
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100 |  |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 206 | 200 | 210 | 51 |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 330 | 300 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 320 | 300 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 45 | 45 | 150 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 123 | 123 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 139 | 141 | 141 |  | 22 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 142 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 32 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 82 | 114 | 100 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 48 | 87 | 87 | 95 |  | 18 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1836 | 2065 | 2172 | 2391 | 464 | 122
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 182 | 200 | 200 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 168 | 199 | 170 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 57 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 3 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 548 | 560 | 580.6 | 559 | 0 | 95
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 20 | 20 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 7 | 160 | 160 | 160 | 170 |  | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 47 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 31 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81 |  | 5 | Engine problem
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 145 | 150 | 150
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 316 | 316 | 316 | 316 | 84 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1338 | 1678 | 1767 | 1767 | 317 | 222
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 708 | 700 | 713 | 713
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 27 | 5 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 224 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 395 | 400 | 410 |  |  | FGMO
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1292 | 1451 | 1598 | 1718 | 0 | 98
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 33 | 30 | 30
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 82 | 82 | 82 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 17 | 17 | 22 | 22 | 73 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 580 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 181 | 224 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 649 | 971 | 1086 | 1242 | 73 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 33 | 34 | 35 |  | 36 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 28 | 28 | 22 |  | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 192 | 193 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 191 | 196 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 392 | 414 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 2 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 92 | 113 | 94 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1019 | 1432 | 1500 | 1681 | 402 | 73
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 79 | 81 | 81 | 81
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 87 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 168 | 194 | 202 | 194 | 0 | 399
|  | Total |  |  |  |  | 22031 | 21180 | 10805 | 13178 | 13900.6 | 14955 | 2427 | 2578
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10346.6607 | 12619 | 13310.9479 | 14320.6211
| A. |  | 2021-10-02 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13178 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 9633 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13178 | MW
| 3 | Day peak Generation : |  |  | 10805 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12619 | MW
| 4 | Evening peak Generation : |  |  | 13178 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 276.0795 | MKWHr | By Solar | 0.70897 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 156.0352 | MKWHr |  | By Oil: | 82.4654 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.607 | MKWHr |  | By Hydro: | 3.4104 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2427 | MW | Dhaka | 4562 | 4562 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2578 | MW | Chittagong | 1243 | 1243 |  | 0 |  | 18:00 |  | 132
|  |  |  | Total = |  |  | 5005 | MW | Khulna | 1561 | 1561 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1177.78 | MMCFD |  |  | Rajshahi | 1342 | 1342 |  | 0 |  | 19:00 |  | 140
| 8 | Fuel Cost : | i) Gas : | Taka | 161270194.226 | ii) Oil : | Taka | 644360641.58 | Comilla | 1232 | 1232 |  | 0 |  | 19:30 |  | 142
|  |  | iii) Coal : |  | 62763257.7 | Total | Taka | 868394093.506 | Mymensingh | 1045 | 1045 |  | 0 |  | 20:00 |  | 142
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.4335 | MKWHr. | Sylhet | 536 | 536 |  | 0 |  | 21:00 |  | 140
|  | ii) During Peak Demand : |  |  | -144 | MW (E to W) at | 20:00 | hrs | Barisal | 375 | 375 |  | 0 |  | 22:00 |  | 138
|  | iii) Maximum : |  |  | -316 | MW at | 22:00 | hrs | Rangpur | 723 | 723 |  | 0 |  | 23:00 |  | 134
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.2° C |  |  | Total | 12619 | 12619 |  | 0
| B. |  | 2021-10-03 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14955 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 1155 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 289.1104 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9621 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0676 | MKWHr. | ii) HVDC Flow at Peak Time |  | 700 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.785 | MKWHr. | iii) Maximum HVDC Flow : |  | 709 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.4 |  | (b) Today: | 106.38 |  | (c) Rule Curve: |  | 106.18
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 327 |  | 0 | 250 | 255 | 0 | 0 | 55 | 0 | 0 | 147 | 0 | 102 | 133 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 100 | 20 | 24 | 21 | 40 | 110 | 0 | 0 | 310 | 305 | 208 | 45 | 137 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 124 | 210 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 130 | 0 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 270 | 24 | 11 | 0 | 240 | 0 | 0 | 200 | 0 | 107 | 0 | 100 | 200 | 133 | 318 | 106 | 70 | 105 | 0 | 305 | 54 | 110 | 114 | 48 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 708 | 0 | 355 | 0 | 0 | 222 | 0 | 0 | 4 | 0 | 0 | 86 | 32 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 52 | 27 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 17 | 0 | 185 | 0 | 345 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 530 | 202 | 0 | 54 | 0 |  | 8293 | 3699 | 11992 | 4144 | 708 | 2167 | 0 | 3510 | 605 | 159 | 222 | 353 | 124 | 0 | 0 | 106.43
2:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 395 | 329 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 50 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 50 | 24 | 25 | 21 | 42 | 110 | 0 | 0 | 310 | 305 | 209 | 45 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 43 | 22 | 8 | 33 | 21 | 124 | 207 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 130 | 0 | 51 | 81 | 0 | 0 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 278 | 0 | 0 | 200 | 0 | 99 | 0 | 100 | 200 | 123 | 317 | 106 | 17 | 105 | 0 | 305 | 54 | 110 | 70 | 47 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 708 | 0 | 355 | 0 | 0 | 221 | 0 | 0 | 4 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 17 | 0 | 185 | 0 | 396 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 500 | 222 | 0 | 17 | 0 |  | 8026 | 3456 | 11482 | 4155 | 708 | 2257 | 0 | 3147 | 575 | 159 | 221 | 136 | 124 | 0 | 0 | 106.42
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 329 |  | 0 | 250 | 255 | 0 | 0 | 55 | 0 | 0 | 153 | 0 | 50 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 25 | 21 | 42 | 110 | 0 | 0 | 310 | 305 | 209 | 45 | 137 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 120 | 208 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 130 | 0 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 278 | 0 | 0 | 200 | 0 | 80 | 0 | 100 | 200 | 123 | 318 | 115 | 0 | 105 | 0 | 305 | 54 | 110 | 52 | 47 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 709 | 0 | 355 | 0 | 0 | 190 | 0 | 0 | 4 | 0 | 0 | 81 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 17 | 0 | 184 | 0 | 361 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 490 | 211 | 0 | 0 | 0 |  | 7930 | 3353 | 11283 | 4172 | 709 | 2216 | 0 | 3050 | 565 | 159 | 190 | 102 | 120 | 0 | 0 | 106.42
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 330 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 153 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 42 | 110 | 0 | 0 | 310 | 305 | 208 | 45 | 140 | 23 | 54 | 0 | 43 | 0 | 0 | 34 | 22 | 8 | 33 | 21 | 120 | 208 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 130 | 0 | 52 | 81 | 0 | 0 | 18 | 0 | 0 | 280 | 24 | 11 | 0 | 180 | 0 | 0 | 200 | 0 | 64 | 0 | 100 | 200 | 127 | 317 | 115 | 0 | 105 | 0 | 305 | 54 | 110 | 17 | 48 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 708 | 0 | 335 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 17 | 0 | 184 | 0 | 374 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 450 | 211 | 0 | 0 | 0 |  | 7631 | 3235 | 10866 | 4153 | 708 | 2234 | 0 | 2795 | 525 | 159 | 120 | 52 | 120 | 0 | 0 | 106.41
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 331 |  | 0 | 250 | 280 | 0 | 0 | 30 | 0 | 0 | 153 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 42 | 110 | 0 | 0 | 310 | 305 | 208 | 45 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 34 | 22 | 8 | 33 | 21 | 110 | 207 | 0 | 22 | 0 | 43 | 0 | 26 | 0 | 130 | 0 | 51 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 50 | 0 | 100 | 200 | 130 | 317 | 115 | 0 | 105 | 0 | 305 | 54 | 85 | 17 | 47 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 708 | 0 | 335 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 81 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 17 | 0 | 185 | 0 | 392 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 35 | 430 | 211 | 0 | 0 | 0 |  | 7302 | 3134 | 10436 | 4130 | 708 | 2253 | 0 | 2431 | 505 | 159 | 120 | 20 | 110 | 0 | 0 | 106.41
6:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 332 |  | 0 | 250 | 280 | 0 | 0 | 30 | 0 | 0 | 148 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 20 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 42 | 110 | 0 | 0 | 305 | 305 | 209 | 45 | 138 | 23 | 56 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 21 | 104 | 211 | 0 | 22 | 0 | 43 | 0 | 39 | 0 | 130 | 0 | 52 | 20 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 50 | 0 | 100 | 200 | 128 | 317 | 115 | 0 | 51 | 0 | 250 | 54 | 51 | 17 | 48 | 100 | 320 | 60 | 0 | 162 | 53 | 0 | 17 | 0 |  | 708 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 81 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 17 | 0 | 189 | 0 | 350 | 70 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 420 | 220 | 0 | 0 | 0 |  | 6952 | 2981 | 9933 | 4126 | 708 | 2171 | 0 | 2030 | 495 | 159 | 120 | 20 | 104 | 0 | 0 | 106.4
7:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 363 | 332 |  | 0 | 250 | 290 | 0 | 0 | 30 | 0 | 0 | 129 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 20 | 25 | 29 | 33 | 17 | 0 | 0 | 85 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 38 | 110 | 0 | 0 | 340 | 340 | 183 | 45 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 21 | 96 | 206 | 0 | 22 | 0 | 43 | 0 | 36 | 0 | 130 | 0 | 51 | 72 | 0 | 0 | 18 | 0 | 9 | 295 | 24 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 50 | 0 | 100 | 200 | 130 | 317 | 115 | 0 | 51 | 0 | 178 | 54 | 51 | 17 | 47 | 100 | 320 | 55 | 4 | 162 | 53 | 0 | 17 | 6 |  | 709 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 81 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 17 | 0 | 181 | 0 | 350 | 70 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 400 | 180 | 0 | 0 | 1 |  | 6875 | 2869 | 9744 | 4084 | 709 | 2185 | 0 | 1918 | 475 | 125 | 120 | 20 | 96 | 12 | 0 | 106.4
8:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 361 | 333 |  | 0 | 250 | 280 | 0 | 0 | 30 | 0 | 0 | 129 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 20 | 25 | 26 | 33 | 33 | 0 | 0 | 86 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 10 | 110 | 0 | 0 | 310 | 310 | 167 | 45 | 141 | 20 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 20 | 100 | 206 | 0 | 22 | 1 | 43 | 0 | 39 | 0 | 130 | 0 | 52 | 72 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 8 | 0 | 30 | 0 | 0 | 150 | 0 | 66 | 2 | 100 | 200 | 110 | 317 | 115 | 17 | 51 | 1 | 179 | 54 | 51 | 17 | 47 | 100 | 320 | 55 | 27 | 162 | 53 | 0 | 17 | 19 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 17 | 0 | 172 | 0 | 330 | 70 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 380 | 184 | 0 | 0 | 2 |  | 6809 | 2824 | 9633 | 4010 | 708 | 2125 | 0 | 1932 | 455 | 126 | 120 | 4 | 100 | 53 | 0 | 106.39
9:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 361 | 320 |  | 0 | 250 | 295 | 0 | 0 | 55 | 0 | 0 | 70 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 20 | 25 | 25 | 33 | 33 | 25 | 0 | 88 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 2 | 110 | 0 | 0 | 320 | 350 | 164 | 8 | 140 | 17 | 56 | 0 | 43 | 0 | 0 | 16 | 19 | 8 | 33 | 20 | 90 | 202 | 0 | 22 | 1 | 43 | 0 | 39 | 0 | 130 | 6 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 62 | 0 | 0 | 150 | 0 | 105 | 1 | 90 | 200 | 125 | 316 | 115 | 17 | 51 | 0 | 179 | 54 | 51 | 17 | 48 | 100 | 320 | 53 | 41 | 162 | 53 | 0 | 17 | 20 |  | 709 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 17 | 0 | 171 | 0 | 361 | 73 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 350 | 183 | 0 | 0 | 4 |  | 6892 | 2838 | 9730 | 3999 | 709 | 2127 | 0 | 2060 | 425 | 128 | 120 | 4 | 90 | 68 | 0 | 106.39
10:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 362 | 320 |  | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 128 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 20 | 25 | 25 | 33 | 33 | 25 | 0 | 86 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 2 | 110 | 0 | 0 | 340 | 345 | 158 | 8 | 141 | 20 | 54 | 0 | 43 | 0 | 0 | 16 | 19 | 5 | 33 | 18 | 92 | 201 | 0 | 22 | 2 | 43 | 0 | 39 | 0 | 130 | 7 | 51 | 75 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 5 | 0 | 95 | 0 | 0 | 150 | 0 | 140 | 4 | 90 | 200 | 130 | 316 | 115 | 17 | 51 | 1 | 250 | 54 | 51 | 17 | 48 | 100 | 320 | 53 | 54 | 162 | 53 | 0 | 17 | 32 |  | 709 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 17 | 0 | 178 | 0 | 391 | 103 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 340 | 181 | 0 | 0 | 1 |  | 7118 | 2923 | 10041 | 4087 | 709 | 2158 | 0 | 2235 | 415 | 126 | 120 | 4 | 92 | 95 | 0 | 106.38
11:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 397 | 320 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 25 | 33 | 33 | 25 | 0 | 86 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 2 | 80 | 0 | 0 | 310 | 310 | 190 | 8 | 140 | 20 | 51 | 0 | 43 | 0 | 0 | 16 | 19 | 5 | 33 | 20 | 80 | 202 | 0 | 22 | 3 | 43 | 0 | 42 | 0 | 130 | 6 | 51 | 75 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 100 | 0 | 0 | 150 | 0 | 149 | 1 | 90 | 200 | 128 | 316 | 115 | 17 | 67 | 1 | 285 | 54 | 51 | 17 | 41 | 100 | 320 | 67 | 54 | 162 | 66 | 0 | 17 | 36 |  | 708 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 6 | 0 | 0 | 81 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 17 | 0 | 190 | 0 | 414 | 105 | 0 | 55 | 0 | 35 | 0 | 1 | 100 | 340 | 181 | 0 | 0 | 5 |  | 7203 | 3037 | 10240 | 4077 | 708 | 2151 | 0 | 2452 | 419 | 126 | 120 | 6 | 80 | 101 | 0 | 106.38
12:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 401 | 320 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 145 | 0 | 40 | 0 | 8 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 25 | 33 | 17 | 25 | 0 | 84 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 70 | 8 | 25 | 21 | 2 | 80 | 0 | 0 | 310 | 310 | 198 | 8 | 138 | 23 | 55 | 0 | 43 | 0 | 0 | 32 | 19 | 5 | 33 | 20 | 92 | 182 | 0 | 22 | 1 | 43 | 0 | 42 | 0 | 130 | 7 | 51 | 78 | 0 | 0 | 18 | 0 | 9 | 295 | 24 | 5 | 0 | 208 | 0 | 0 | 168 | 0 | 149 | 1 | 100 | 200 | 123 | 316 | 115 | 58 | 105 | 2 | 304 | 54 | 71 | 82 | 48 | 90 | 320 | 92 | 57 | 162 | 96 | 0 | 17 | 35 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 17 | 0 | 191 | 0 | 392 | 105 | 0 | 92 | 0 | 87 | 0 | 2 | 113 | 350 | 181 | 0 | 0 | 5 |  | 7677 | 3128 | 10805 | 4052 | 708 | 2122 | 0 | 3051 | 429 | 124 | 120 | 4 | 92 | 103 | 0 | 106.37
13:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 377 | 320 |  | 0 | 250 | 265 | 0 | 0 | 55 | 0 | 0 | 127 | 0 | 85 | 16 | 32 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 25 | 33 | 33 | 25 | 0 | 84 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 70 | 30 | 25 | 0 | 2 | 80 | 0 | 0 | 310 | 310 | 180 | 8 | 137 | 23 | 54 | 0 | 43 | 0 | 0 | 52 | 19 | 5 | 33 | 20 | 86 | 166 | 0 | 22 | 1 | 43 | 0 | 44 | 0 | 130 | 107 | 50 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 250 | 0 | 0 | 184 | 0 | 149 | 0 | 100 | 200 | 117 | 316 | 115 | 90 | 105 | 2 | 304 | 54 | 97 | 100 | 42 | 90 | 320 | 92 | 50 | 162 | 105 | 0 | 17 | 34 |  | 709 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 17 | 0 | 192 | 0 | 395 | 105 | 0 | 92 | 0 | 100 | 0 | 3 | 113 | 380 | 181 | 0 | 0 | 5 |  | 7937 | 3189 | 11126 | 4074 | 709 | 2130 | 0 | 3308 | 460 | 124 | 120 | 20 | 86 | 95 | 0 | 106.37
14:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 325 | 317 |  | 0 | 250 | 295 | 0 | 0 | 55 | 0 | 0 | 127 | 0 | 93 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 25 | 33 | 33 | 25 | 0 | 84 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 20 | 12 | 25 | 15 | 2 | 80 | 0 | 0 | 280 | 295 | 205 | 8 | 141 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 5 | 33 | 20 | 82 | 164 | 0 | 19 | 1 | 43 | 0 | 44 | 0 | 110 | 107 | 29 | 81 | 0 | 0 | 18 | 0 | 9 | 295 | 24 | 5 | 0 | 245 | 0 | 0 | 160 | 0 | 149 | 5 | 100 | 200 | 122 | 316 | 115 | 70 | 85 | 0 | 304 | 54 | 51 | 52 | 47 | 90 | 320 | 92 | 12 | 162 | 108 | 0 | 17 | 29 |  | 708 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 17 | 0 | 181 | 0 | 349 | 105 | 0 | 92 | 0 | 71 | 0 | 7 | 113 | 350 | 181 | 0 | 0 | 5 |  | 7594 | 3091 | 10685 | 3975 | 708 | 2099 | 0 | 3066 | 432 | 124 | 120 | 20 | 82 | 59 | 0 | 106.38
15:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 376 | 317 |  | 0 | 250 | 255 | 0 | 0 | 55 | 0 | 0 | 184 | 0 | 102 | 25 | 23 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 24 | 33 | 33 | 35 | 0 | 84 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 100 | 14 | 36 | 21 | 2 | 80 | 0 | 0 | 300 | 310 | 183 | 8 | 138 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 5 | 33 | 20 | 102 | 165 | 0 | 19 | 1 | 43 | 20 | 44 | 0 | 163 | 158 | 31 | 81 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 5 | 0 | 260 | 0 | 0 | 175 | 0 | 149 | 5 | 100 | 200 | 120 | 316 | 115 | 75 | 90 | 0 | 304 | 54 | 77 | 98 | 47 | 92 | 320 | 92 | 9 | 162 | 108 | 0 | 17 | 19 |  | 709 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 17 | 0 | 188 | 0 | 392 | 105 | 0 | 94 | 0 | 99 | 0 | 7 | 113 | 370 | 218 | 0 | 0 | 4 |  | 8054 | 3250 | 11304 | 4192 | 709 | 2198 | 0 | 3334 | 451 | 124 | 120 | 29 | 102 | 45 | 0 | 106.38
16:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 401 | 317 |  | 0 | 250 | 275 | 0 | 0 | 48 | 0 | 0 | 149 | 0 | 58 | 32 | 42 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 24 | 33 | 33 | 42 | 0 | 84 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 100 | 20 | 50 | 21 | 2 | 80 | 0 | 0 | 280 | 280 | 206 | 8 | 141 | 23 | 56 | 0 | 43 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 102 | 168 | 0 | 19 | 1 | 43 | 20 | 42 | 0 | 130 | 158 | 30 | 80 | 0 | 0 | 18 | 0 | 9 | 270 | 24 | 2 | 0 | 210 | 0 | 0 | 183 | 0 | 120 | 5 | 90 | 200 | 120 | 317 | 115 | 105 | 105 | 0 | 303 | 54 | 110 | 114 | 42 | 100 | 320 | 92 | 11 | 162 | 108 | 0 | 17 | 15 |  | 709 | 0 | 400 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 17 | 0 | 196 | 0 | 400 | 105 | 0 | 70 | 0 | 105 | 0 | 5 | 50 | 400 | 218 | 0 | 0 | 2 |  | 7987 | 3227 | 11214 | 4186 | 709 | 2160 | 0 | 3258 | 480 | 124 | 120 | 36 | 102 | 39 | 0 | 106.38
17:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 401 | 287 |  | 0 | 250 | 245 | 0 | 0 | 42 | 0 | 0 | 182 | 0 | 58 | 32 | 42 | 0 | 0 | 0 | 54 | 17 | 35 | 20 | 25 | 24 | 33 | 33 | 51 | 0 | 85 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 60 | 24 | 25 | 21 | 2 | 80 | 0 | 0 | 280 | 280 | 209 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 110 | 183 | 0 | 21 | 0 | 43 | 20 | 42 | 0 | 130 | 160 | 31 | 81 | 0 | 20 | 18 | 0 | 9 | 300 | 24 | 0 | 0 | 210 | 0 | 0 | 170 | 0 | 100 | 1 | 100 | 155 | 123 | 316 | 115 | 105 | 85 | 0 | 270 | 54 | 68 | 104 | 47 | 100 | 320 | 60 | 8 | 162 | 72 | 0 | 17 | 4 |  | 708 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 22 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 17 | 0 | 191 | 0 | 292 | 88 | 0 | 70 | 0 | 113 | 0 | 3 | 50 | 400 | 218 | 0 | 0 | 0 |  | 7689 | 3044 | 10733 | 4193 | 708 | 2022 | 0 | 2920 | 479 | 125 | 120 | 40 | 110 | 16 | 0 | 106.38
18:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 335 | 270 |  | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 127 | 0 | 72 | 130 | 53 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 14 | 33 | 33 | 42 | 0 | 86 | 40 | 110 | 0 | 2 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 92 | 58 | 31 | 21 | 3 | 80 | 0 | 0 | 280 | 280 | 206 | 8 | 139 | 23 | 56 | 0 | 43 | 0 | 33 | 31 | 19 | 11 | 29 | 20 | 132 | 180 | 0 | 21 | 0 | 43 | 20 | 42 | 0 | 110 | 159 | 31 | 81 | 0 | 140 | 18 | 0 | 9 | 280 | 24 | 5 | 30 | 235 | 40 | 30 | 183 | 31 | 111 | 0 | 100 | 164 | 122 | 316 | 115 | 105 | 73 | 0 | 290 | 54 | 85 | 100 | 85 | 100 | 320 | 70 | 0 | 162 | 74 | 0 | 17 | 0 |  | 700 | 0 | 375 | 0 | 0 | 160 | 0 | 0 | 4 | 0 | 0 | 82 | 29 | 0 | 0 | 0 | 0 | 23 | 8 | 94 | 12 | 24 | 29 | 30 | 18 | 21 | 0 | 11 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 17 | 4 | 176 | 0 | 377 | 88 | 22 | 80 | 0 | 113 | 0 | 0 | 90 | 400 | 217 | 0 | 4 | 0 |  | 8347 | 3451 | 11798 | 4188 | 700 | 2113 | 157 | 3310 | 471 | 126 | 160 | 441 | 132 | 0 | 0 | 106.38
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 395 | 320 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 93 | 150 | 53 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 26 | 33 | 33 | 51 | 0 | 86 | 75 | 120 | 0 | 22 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 100 | 86 | 50 | 21 | 6 | 80 | 0 | 0 | 285 | 305 | 208 | 8 | 138 | 23 | 55 | 0 | 43 | 0 | 42 | 52 | 19 | 11 | 10 | 8 | 140 | 186 | 0 | 21 | 0 | 43 | 20 | 47 | 0 | 163 | 161 | 31 | 81 | 0 | 150 | 18 | 0 | 9 | 280 | 24 | 11 | 30 | 260 | 12 | 25 | 198 | 100 | 149 | 0 | 100 | 200 | 125 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 91 | 0 | 162 | 106 | 0 | 17 | 0 |  | 701 | 0 | 360 | 0 | 0 | 223 | 0 | 0 | 32 | 0 | 0 | 82 | 33 | 0 | 0 | 0 | 0 | 50 | 34 | 94 | 27 | 43 | 37 | 52 | 31 | 21 | 0 | 11 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 17 | 0 | 188 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 223 | 0 | 35 | 0 |  | 9127 | 3890 | 13017 | 4359 | 701 | 2261 | 167 | 3863 | 570 | 161 | 223 | 572 | 140 | 0 | 0 | 106.38
19:30 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 399 | 320 |  | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 93 | 150 | 52 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 26 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 100 | 100 | 87 | 50 | 21 | 7 | 80 | 0 | 0 | 295 | 305 | 206 | 8 | 138 | 23 | 55 | 0 | 43 | 0 | 42 | 52 | 19 | 11 | 33 | 21 | 142 | 182 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 160 | 31 | 81 | 0 | 145 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 280 | 0 | 0 | 199 | 50 | 149 | 0 | 100 | 200 | 125 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 91 | 0 | 162 | 108 | 0 | 17 | 0 |  | 701 | 0 | 380 | 0 | 0 | 222 | 0 | 0 | 32 | 0 | 0 | 82 | 33 | 0 | 0 | 0 | 0 | 50 | 33 | 94 | 27 | 43 | 40 | 52 | 33 | 18 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 17 | 0 | 193 | 0 | 412 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 223 | 0 | 35 | 0 |  | 9098 | 4022 | 13120 | 4424 | 701 | 2306 | 50 | 3881 | 659 | 161 | 222 | 574 | 142 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 399 | 320 |  | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 93 | 150 | 45 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 26 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 19 | 0 | 0 | 0 | 0 |  | 24 | 0 | 87 | 100 | 86 | 50 | 21 | 17 | 80 | 0 | 0 | 330 | 320 | 206 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 42 | 52 | 19 | 11 | 33 | 21 | 142 | 200 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 160 | 31 | 81 | 0 | 145 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 281 | 0 | 0 | 199 | 50 | 149 | 0 | 100 | 200 | 123 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 87 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 700 | 0 | 395 | 0 | 0 | 224 | 0 | 0 | 27 | 0 | 0 | 82 | 33 | 0 | 0 | 0 | 0 | 50 | 33 | 93 | 27 | 43 | 40 | 52 | 33 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 17 | 0 | 196 | 0 | 414 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 224 | 0 | 35 | 0 |  | 9130 | 4048 | 13178 | 4516 | 700 | 2302 | 50 | 3867 | 661 | 161 | 224 | 555 | 142 | 0 | 0 | 106.38
21:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 395 | 322 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 181 | 0 | 93 | 150 | 48 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 26 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 23 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 100 | 86 | 50 | 21 | 22 | 80 | 0 | 0 | 335 | 300 | 208 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 42 | 52 | 19 | 11 | 33 | 21 | 140 | 198 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 159 | 32 | 81 | 0 | 145 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 285 | 0 | 0 | 199 | 0 | 149 | 0 | 100 | 200 | 123 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 85 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 701 | 0 | 400 | 0 | 0 | 210 | 0 | 0 | 29 | 0 | 0 | 82 | 34 | 0 | 0 | 0 | 0 | 50 | 33 | 93 | 27 | 43 | 36 | 52 | 33 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 17 | 0 | 192 | 0 | 390 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 224 | 0 | 35 | 0 |  | 9082 | 4014 | 13096 | 4499 | 701 | 2271 | 0 | 3876 | 670 | 161 | 210 | 568 | 140 | 0 | 0 | 106.38
22:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 321 |  | 0 | 250 | 285 | 0 | 0 | 55 | 0 | 0 | 182 | 0 | 93 | 150 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 28 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 100 | 86 | 50 | 21 | 28 | 80 | 0 | 0 | 330 | 295 | 209 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 42 | 44 | 19 | 11 | 33 | 21 | 138 | 198 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 161 | 32 | 81 | 0 | 145 | 18 | 0 | 9 | 285 | 24 | 11 | 0 | 281 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 123 | 317 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 92 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 700 | 0 | 405 | 0 | 0 | 150 | 0 | 0 | 29 | 0 | 0 | 82 | 34 | 0 | 0 | 0 | 0 | 50 | 32 | 93 | 0 | 0 | 36 | 52 | 34 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 17 | 0 | 178 | 0 | 354 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 224 | 0 | 54 | 0 |  | 9058 | 3850 | 12908 | 4480 | 700 | 2225 | 0 | 3815 | 671 | 161 | 150 | 568 | 138 | 0 | 0 | 106.38
23:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 322 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 182 | 0 | 93 | 150 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 29 | 33 | 33 | 25 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 92 | 86 | 50 | 21 | 34 | 80 | 0 | 0 | 310 | 295 | 210 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 44 | 19 | 11 | 33 | 21 | 134 | 198 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 161 | 52 | 81 | 0 | 145 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 288 | 0 | 0 | 200 | 0 | 140 | 0 | 100 | 200 | 122 | 316 | 115 | 52 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 701 | 0 | 405 | 0 | 0 | 150 | 0 | 0 | 29 | 0 | 0 | 82 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 0 | 0 | 36 | 52 | 35 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 17 | 0 | 170 | 0 | 370 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 224 | 0 | 54 | 0 |  | 8937 | 3823 | 12760 | 4461 | 701 | 2259 | 0 | 3730 | 670 | 160 | 150 | 495 | 134 | 0 | 0 | 106.38
24:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 321 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 150 | 38 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 92 | 53 | 50 | 21 | 40 | 80 | 0 | 0 | 310 | 295 | 210 | 8 | 140 | 20 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 130 | 198 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 162 | 52 | 81 | 0 | 145 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 288 | 0 | 0 | 190 | 0 | 149 | 0 | 100 | 200 | 123 | 316 | 115 | 52 | 105 | 0 | 305 | 54 | 110 | 114 | 62 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 701 | 0 | 405 | 0 | 0 | 130 | 0 | 0 | 29 | 0 | 0 | 81 | 34 | 0 | 0 | 0 | 0 | 43 | 0 | 93 | 0 | 0 | 30 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 17 | 0 | 168 | 0 | 366 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 225 | 0 | 54 | 0 |  | 8849 | 3781 | 12630 | 4456 | 701 | 2257 | 0 | 3646 | 670 | 159 | 130 | 481 | 130 | 0 | 0 | 106.38
KWH | 0 | 0 | 0 | 0 | 7229600 | 0 | 0 | 9337000 | 7690000 |  | 0 | 6159750 | 6683549 | 0 | 0 | 1234800 | 0 | 0 | 5184000 | 0 | 1402272 | 1566720 | 531332 | 0 | 0 | 0 | 1274760 | 1082343 | 1030273 | 385812 | 600000 | 611100 | 817800 | 767400 | 515040 | 0 | 2014407 | 1396000 | 2700000 | 0 | 136285 | 0 | 0 | 0 | 0 |  | 312000 | 0 | 738696 | 1265880 | 711360 | 805920 | 457200 | 487200 | 2293552 | 0 | 0 | 7806800 | 7455000 | 4797000 | 518545 | 3304150 | 497232 | 1321440 | 0 | 993526 | 0 | 185272 | 943186 | 464508 | 188280 | 758400 | 498650 | 2784960 | 4549280 | 0 | 485496 | 12650 | 1025000 | 262080 | 1004400 | 0 | 3453136 | 1715000 | 1050720 | 1736640 | 0 | 911010 | 382000 | 0 | 206820 | 7118960 | 561576 | 185808 | 102720 | 4907780 | 67118 | 70532 | 4320000 | 182300 | 2808720 | 19305 | 2354880 | 4699200 | 2984132 | 7610000 | 2703600 | 1338000 | 2204654 | 8760 | 6762000 | 1299265 | 2243961 | 1662120 | 1405320 | 2375040 | 7662000 | 2023680 | 366650 | 3941280 | 2258182 | 0 | 443520 | 238237 |  | 17067636 | 0 | 9051264 | 0 | 0 | 3716160 | 0 | 0 | 216480 | 0 | 0 | 1991435 | 628054 | 0 | 0 | 0 | 0 | 346832 | 137662 | 688616 | 105220 | 168154 | 232487 | 490560 | 238360 | 483840 | 0 | 250938 | 1846690 | 0 | 0 | 0 | 0 | 0 | 0 | 4626064 | 0 | 424162 | 28800 | 4662773 | 0 | 9039400 | 2341920 | 15891 | 2063232 | 53424 | 2195337 | 0 | 30129 | 2160096 | 11760300 | 4949809 | 0 | 372000 | 33240 |  | 193662532 | 82416965 | 276079497 | 103135928 | 17067636 | 52899231 | 467361 | 73930728 | 13606990 | 3410407 | 3716160 | 4351125 | 2784960 | 708971 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8024856 | 0 | 0 | 9430370 | 7920700 |  | 0 | 6714127.5 | 7418739.39 | 0 | 0 | 10446408 | 0 | 0 | 8968320 | 0 | 12788720.64 | 15416524.8 | 4898881.04 | 0 | 0 | 0 | 9305748 | 8366511.39 | 10158491.78 | 289359 | 450000 | 0 | 0 | 0 | 4980436.8 | 0 | 543889.89 | 376920 | 4887000 | 0 | 1266087.65 | 0 | 0 | 0 | 0 |  | 0 | 0 | 7165351.2 | 12089154 | 6188832 | 6382886.4 | 576072 | 1446984 | 3394456.96 | 0 | 0 | 5777032 | 7455000 | 4413240 | 668923.05 | 3799772.5 | 561872.16 | 1850016 | 0 | 1698929.46 | 0 | 1871247.2 | 9007426.3 | 589925.16 | 141210 | 1327200 | 373987.5 | 20887200 | 4822236.8 | 0 | 616579.92 | 201641 | 1681000 | 419328 | 1787832 | 0 | 3936575.04 | 1783600 | 2069918.4 | 3316982.4 | 0 | 1576047.3 | 836580 | 0 | 421912.8 | 7190149.6 | 421182 | 141214.08 | 1747267.2 | 37102816.8 | 1139663.64 | 1179295.04 | 22464000 | 3048056 | 27637804.8 | 225675.45 | 19192272 | 50986320 | 21038130.6 | 7077300 | 24656832 | 12644100 | 19202536.34 | 0 | 51120720 | 11316598.15 | 19724417.19 | 16587957.6 | 12043592.4 | 15817766.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98309583.36 | 0 | 9503827.2 | 0 | 0 | 51505977.6 | 0 | 0 | 2270875.2 | 0 | 0 | 2250321.55 | 973483.7 | 0 | 0 | 0 | 0 | 3412826.88 | 1398645.92 | 6094251.6 | 810194 | 2273442.08 | 2252799.03 | 4753526.4 | 2312092 | 928972.8 | 0 | 189960.066 | 11135540.7 | 0 | 0 | 0 | 0 | 0 | 0 | 6106404.48 | 0 | 636243 | 489888 | 5455444.41 | 0 | 8949006 | 24449644.8 | 270305.91 | 19580071.68 | 504322.56 | 17035815.12 | 0 | 332925.45 | 15963109.44 | 51627717 | 0 | 0 | 0 | 0 |  | 637494710.72 | 351777217.936 | 989271928.656 | 105410617.486 | 98309583.36 | 55859576.74 | 7874475.79 | 542785574.36 | 62763257.7 | 920809.89 | 51505977.6 | 42194613.83 | 20887200 | 760241.9 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 401 | 320 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 145 | 0 | 40 | 0 | 8 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 25 | 33 | 17 | 25 | 0 | 84 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 70 | 8 | 25 | 21 | 2 | 80 | 0 | 0 | 310 | 310 | 198 | 8 | 138 | 23 | 55 | 0 | 43 | 0 | 0 | 32 | 19 | 5 | 33 | 20 | 92 | 182 | 0 | 22 | 1 | 43 | 0 | 42 | 0 | 130 | 7 | 51 | 78 | 0 | 0 | 18 | 0 | 9 | 295 | 24 | 5 | 0 | 208 | 0 | 0 | 168 | 0 | 149 | 1 | 100 | 200 | 123 | 316 | 115 | 58 | 105 | 2 | 304 | 54 | 71 | 82 | 48 | 90 | 320 | 92 | 57 | 162 | 96 | 0 | 17 | 35 |  | 708 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 17 | 0 | 191 | 0 | 392 | 105 | 0 | 92 | 0 | 87 | 0 | 2 | 113 | 350 | 181 | 0 | 0 | 5 |  | 10805 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 399 | 320 | 0 | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 93 | 150 | 45 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 26 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 87 | 100 | 86 | 50 | 21 | 17 | 80 | 0 | 0 | 330 | 320 | 206 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 42 | 52 | 19 | 11 | 33 | 21 | 142 | 200 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 160 | 31 | 81 | 0 | 145 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 281 | 0 | 0 | 199 | 50 | 149 | 0 | 100 | 200 | 123 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 87 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 700 | 0 | 395 | 0 | 0 | 224 | 0 | 0 | 27 | 0 | 0 | 82 | 33 | 0 | 0 | 0 | 0 | 50 | 33 | 93 | 27 | 43 | 40 | 52 | 33 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 17 | 0 | 196 | 0 | 414 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 224 | 0 | 35 | 0 |  | 13178 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 340 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 21 | 15 | 100 | 0 | 0 | 330 | 330 | 210 | 45 | 141 | 23 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 200 | 0 | 22 | 0 | 43 | 20 | 50 | 0 | 163 | 160 | 60 | 81 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 290 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 95 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 713 | 0 | 410 | 0 | 0 | 225 | 0 | 0 | 25 | 40 | 0 | 88 | 30 | 110 | 0 | 0 | 0 | 50 | 35 | 94 | 28 | 50 | 40 | 52 | 33 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 22 | 100 | 220 | 0 | 400 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 340 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 34 | 100 | 90 | 25 | 21 | 5 | 100 | 0 | 0 | 300 | 300 | 200 | 45 | 141 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 200 | 0 | 22 | 1.6 | 43 | 20 | 50 | 0 | 163 | 160 | 60 | 81 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 100 | 87 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 713 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 5 | 0 | 0 | 82 | 30 | 110 | 0 | 0 | 0 | 50 | 34 | 90 | 28 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 306 | 303 | 0 | 0 | 250 | 265 | 0 | 0 | 30 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 |  | 2 | 0 | 85 | 35 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 7 | 80 | 0 | 0 | 260 | 270 | 179 | 45 | 139 | 20 | 54 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 90 | 208 | 0 | 22 | 0 | 43 | 20 | 39 | 0 | 130 | 161 | 52 | 78 | 0 | 0 | 18 | 0 | 9 | 275 | 16 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 117 | 0 | 90 | 100 | 103 | 317 | 98 | 0 | 51 | 2 | 304 | 54 | 51 | 0 | 57 | 100 | 320 | 104 | 12 | 162 | 53 | 0 | 17 | 8 | 0 | 701 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 17 | 0 | 167 | 0 | 321 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 440 | 181 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 9633 | 8:00
| Highest Generation |  | 13178 | 20:00
| Day Peak Generation |  | 10805 | 12:00
| Evening Peak Generation |  | 13178 | 20:00
| HVDC Max Flow |  | 709 | 3:00
| HVDC EvPeak Flow |  | 700 | 20:00
| Load factor L.F |  | 87.29%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-03
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10805 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9621 | MW
Evening Peak Generation : |  | 13178 | MW Hour : | 20:00 | Available Max Generation : |  | 14955 | MW
E.P. Demand (at gen end) : |  | 13178 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 13178 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1155 | MW
Total Gen. (MKWH) : |  | 276.0795 | System Load Factor : | 87.29% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -316 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-03
Actual : | 106.38 | Ft.(MSL) , | Rule curve : | 106.18 | Ft.( MSL )
Gas Consumed : | Total = | 1177.78 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161270194.226
: |  | Coal : | 62763257.7 | Oil : | 644360641.58 | Total : | 868394093.506
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4907.0959 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1675.6381 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1502.5553 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1358.1254 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1227.0756 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 990.2242 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 544.7361 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 254.7193 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 763.7529 |  |  | 0 | 0%
Total | 0 |  | 13223.9225 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Fenchuganj 3,4
7) Raozan #02
8) Shajibazar 330 Mw GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Chandraghona 132/33 kV T-2 tripped at 08:17 showing main protection trip and was switched
on at 10:17.
b) Abul Khair-Hathazari 230 kV Ckt tripped at 08:30 showing CB spring discharge at Abul Khair end
and was switched on at 08:37.
c) Sherpur(Bogura) 33 kV full Bas was shut down from 08:30 to 10:40 due to red hot maintenance |  |  |  |  | About 40 MW power interruption occurred under Sherpur S/S area
at B-phase sectionalizer isolator. |  |  |  |  | from 08:30 to 10:40.
d) Jhenaidah(N)-Chuadanga 132 kV Ckt-2 was under shut down from 08:21 to 10:44 for D/W. |  |  |  |  | About 50 MW power interruption occurred under Jhenaidah(N) S/S
area from 08:21 to 10:44.
e) Rangamati-Khagrachori 132 kV Ckt-1 was under shut down from 08:23 to 15:22 for A/M.
f) Tongi-Kodda 300 MW P/P 230 kV Ckt was under shut down from 09:21 to 17:02 for A/M.
g) Lalmonirhat 132/33 kV T-2 transformer was under shut down from 08:15 to 15:55 for A/M.
h) Naogaon 132/33 kV T-3 transformer was under shut down at 09:20 for C/M.
i) Shahjibazar 330 MW CCPP ST was synchronized at 12:12.
j) Madanganj 132 kV main Bus was under shut down from 12:38 to 13:54 for C/M.
k) Barapukuria 132/33 kV T-3 & T4 transformers tripped at 14:47 due to 33 kV feeder fault and was |  |  |  |  | About 40 MW power interruption occurred under Barapukuria S/S
switched on at 15:25. |  |  |  |  | area from 14:47 to 15:25.
l) Cumilla(N) 132/33 kV T-3 & T4 transformers tripped at 17:54 due to 33 kV PBS feeder fault and
were switched on at 18:26,18:09 respectively.
m) Sylhet 225 MW GT was synchronized at 16:52.
n) Kaptai unit-5 was synchronized at 18:23.
o) Mymensing-Kishoreganj 132 kV Ckt-2 was shut down at 07:09(03/10/20210 for C/M.
p) Purbasadipur-Thakurgaon 132 kV Ckt-1 tripped at 06:46(03-10-2021) showing Dist. C-phase
relay at Purbasadipur end and was switched on at 07:27(03-10-20210)
q) Kabirpur 132/33 kV T-1 & T-2 transformers tripped at 06:05(03-10-2021) due to 33 kV |  |  |  |  | About 88 MW power interruption occurred under Kabirpur S/S
Kashempur-2 feeder fault and was switched on at 06:45(03-10-2021). |  |  |  |  | area from 06:05(03-10-2021) to 06:45(03-10-2021).
r) Sylhet 225 MW CCPP GT tripped at 07:01(03-10-2021) due to generator protection operated.
s) Kaptai unit-4 was shut down at 07:01(03-10-2021) due to emergency maintenance of rotor
spoke support inspection.
t) Niyamatpur 132/33 kV T2 transformer was shut down at 07:41(03-10-2021) for C/M. |  |  |  |  | About 08 MW power interruption occurred under Niyamatpur S/S
area from 07:41(03-10-2021) to till.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 290 | 7229600 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9337000
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7690000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6159750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 310 | 6683549 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1234800
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 45 | 531332 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 385812
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 5184000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1402272 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1274760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1566720
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1082343
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1030273
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1211100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 767400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 515040
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 281 | 4907780 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 67118 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 70532 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 182300 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2808720
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1338000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 2023680 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3941280
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 238237
| Dhaka area Total |  |  |  | 5719 | 3289 | 69681198
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 19 | 136285 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 19305
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 805920
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 161 | 3410407 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2204654
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 87 | 738696 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1265880
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2354880
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 457200
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 487200
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 86 | 711360 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 8760
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 6762000
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1299265
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2243961
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2375040
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2258182 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1538 | 30238995
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2293552 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4797000
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7806800 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7455000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 497232 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1321440
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 518545 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 993526 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 2984132 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 185272 | Engine problem
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 139 | 3304150 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 4699200
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 464508
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 188280
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 142 | 2784960
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 758400
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 943186
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 498650
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 102720 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1662120
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 87 | 1405320 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2065 | 46107513
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 200 | 4549280
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 485496
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12650
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 199 | 4320000
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2703600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 366650
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 312000
| Mymensingh Area Total |  |  |  | 709 | 560 | 12749676
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1025000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 262080 | Engine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3453136
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 1715000 | Machine problem
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1004400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 185808
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 31 | 1050720 | Machine problem
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1736640
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 911010 | ST under maint
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 382000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 561576
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7118960 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 7610000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 206820
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7662000 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1678 | 34885150
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 700 | 17067636
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 216480
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 224 | 3716160
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 395 | 9051264 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 28800 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2341920
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 53424 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1451 | 32475684
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 628054
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 82 | 1991435 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 424162 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 11760300 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 4949809
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 372000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 971 | 20125760
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 346832
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 33 | 137662 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 105220 | Low demand
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 168154 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 232487 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4626064 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 196 | 4662773 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9039400 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 238360 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 483840
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250938
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 490560
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 688616 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 15891 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2063232
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2160096
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33240
| Rajshahi Area Total |  |  |  | 2179 | 1432 | 25743365
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1846690
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2195337
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30129
| Rangpur Area Total |  |  |  | 605 | 194 | 4072156
| Total |  |  |  | 21180 | 13178 | 276079497
| Eastern Grid Total |  |  |  | 14221 | 9130 | 193662532
| Western Grid Total |  |  |  | 6959 | 4048 | 82416965
| National Grid Total |  |  |  | 21180 | 13178 | 276079497
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-02
(a) ENTIRE EASTERN GRID : |  | 8618 | MW | (b) ENTIRE WESTERN GRID : |  | 4001 | MW
i) Dhaka area |  | 4562 | MW | i) Khulna area |  | 1561 | MW
ii) Chittagong area |  | 1243 | MW | ii) Rajshahi area |  | 1342 | MW
iii) Comilla area |  | 1232 | MW | iii) Barisal area |  | 375 | MW
iv) Mymensingh area |  | 1045 | MW | iv) Rangpur area |  | 723 | MW
v) Sylhet area |  | 536 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12619 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 18:00 | Kishoreganj | 148 | 21:00 | Jessore | 119 | 19:00
Munsiganj | 100 | 0:00 | Netrokona | 116 | 18:00 | Benapol | 60 | 1:00
Sonargaon | 80 | 21:00 | Jamalpur | 155 | 18:30 | Jhenida(Old) | 116 | 20:00
Shyampur | 188 | 11:00 | Sherpur | 130 | 18:30 | Bottail | 122 | 21:00
Bhulta | 202 | 23:00 | Srimongal | 55 | 18:30 | G.K Project | 58 | 19:00
Madanganj | 48 | 10:00 | Shahjibazar | 117 | 19:30 | Faridpur | 148 | 19:30
Shitalakhya | 116 | 12:00 | Fenchuganj | 45 | 21:00 | Rajbari | 56 | 19:00
Rahim steel | 17 | 18:00 | Kulawara | 48 | 19:30 | Madaripur | 105 | 22:00
Matuail | 66 | 12:00 | Sylhet | 137 | 18:00 | Sariatpur | 70 | 21:00
Ghorasal | 82 | 21:00 | Chatak | 32 | 19:30 | Gopalganj | 97 | 21:00
Narsingdi | 184 | 20:00 | Sunamganj | 51 | 20:00 | Bagerhat | 91 | 19:30
Haripur (SBU) | 132 | 14:00 | Biani Bazar | 63 | 20:00 | Mongla | 42 | 10:00
Sreenagar | 42 | 21:00 | Comilla (S) | 142 | 19:30 | Satkhira | 104 | 22:00
Ullon | 70 | 23:00 | Comilla(N) | 135 | 22:00 | Gallamari | 49 | 18:00
Hasnabad | 91 | 23:00 | Chandpur | 80 | 20:00 | Magura | 58 | 18:30
Magbazar | 100 | 13:00 | Feni | 126 | 20:00 | Norail | 47 | 18:30
Maniknagar | 64 | 13:00 | Chowmuhani | 210 | 19:30 | Chuadanga | 102 | 19:30
Bangabhaban | 7 | 11:00 | Ashuganj | 45 | 1:00 | Barisal(N) | 47 | 21:00
Motijheel | 25 | 13:00 | Daudkandi | 156 | 18:30 | Barisal (S) | 112 | 20:00
Narinda | 62 | 17:00 | B.Baria | 167 | 19:30 | Patuakhali | 118 | 22:00
Kazla | 72 | 0:00 | Ramganj | 92 | 23:00 | Bhandaria | 52 | 19:00
Dhanmondi | 188 | 13:00 | Chaddagram | 42 | 21:00 | Borguna | 18 | 19:30
Lalbag | 73 | 12:00 | PHP | 10 | 16:00 | Borhan Uddin | 46 | 22:00
Madartek | 78 | 23:00 | Kochua | 62 | 21:00 | Ishurdi | 68 | 21:00
Dhaka University | 39 | 12:00 | Madunaghat | 66 | 18:00 | Ruppur Paromanobik | 4 | 9:00
Aftabnagar | 16 | 23:00 | Hathazari | 90 | 19:00 | Natore | 127 | 21:00
Fatullah | 62 | 16:00 | Khulshi | 213 | 16:00 | Bogra | 169 | 21:00
Nawabganj | 54 | 22:00 | Halishahar | 136 | 14:00 | Noagaon | 108 | 21:00
Keraniganj | 73 | 18:30 | Baraulia | 128 | 16:00 | Rajshahi | 158 | 21:00
Mirpur | 143 | 18:30 | Sikalbaha | 39 | 10:00 | Rajshahi New | 20 | 12:00
Kalyanpur | 99 | 18:00 | Dohazari | 106 | 1:00 | C.Nawabganj | 64 | 20:00
Gulshan | 110 | 15:00 | Cox'sbazar | 94 | 1:00 | Amnura | 41 | 21:00
Uttara | 87 | 18:00 | Chandraghona | 26 | 19:30 | Pabna | 102 | 18:30
Uttara New | 29 | 18:00 | Kaptai | 4.2 | 18:30 | Shahjadpur | 100 | 19:30
Kamrangirchar | 102 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 107 | 19:30
Savar | 163 | 18:30 | Bakulia | 117 | 13:00 | Niyamatpur | 75 | 21:00
Bhasantec | 124 | 18:00 | Julda | 19 | 1:00 | Joypurhat | 61 | 20:00
Agargaon | 80 | 13:00 | TK chemical | 18 | 21:00 | Sherpur(Bogura) | 62 | 18:30
Satmosjid | 113 | 18:30 | Modern Steel | 7 | 8:00 | Mohastangor | 66 | 21:00
Tongi | 127 | 19:00 | Shahmirpur | 21 | 19:00 | Bhangura | 32 | 19:00
Kabirpur | 238 | 18:00 | Khagrachhari | 22 | 13:00 | Rangpur | 138 | 19:30
Basundhara | 196 | 18:00 | Matarbari | 35 | 1:00 | Lalmonirhat | 41 | 20:00
Manikganj | 76 | 21:00 | Baroiar Hat | 44 | 18:00 | Saidpur | 93 | 18:30
Joydevpur | 182 | 18:30 | Rangamati | 12 | 18:30 | Purbasadipur | 96 | 19:00
New Tongi | 94 | 15:00 | Abul Khair 230 | 156 | 4:00 | Thakurgaon | 76 | 19:30
Kodda | 284 | 17:00 | BSRM | 150 | 19:30 | Palashbari | 111 | 1:00
Dhamrai | 102 | 19:30 | GPH Ispat | 85 | 8:00 | Barapukuria | 48 | 19:30
Rajendrapur | 106 | 21:00 | Agrabad | 0 | 1:00 | Panchagar | 45 | 1:00
Valuka | 128 | 15:00 | Goalpara | 32 | 13:00 | Joldhaka | 59 | 18:00
Tangail | 224 | 21:00 | Central S/S | 105 | 19:30 | Kurigram | 54 | 1:00
Mymensing | 219 | 19:30 | Noapara | 50 | 19:00 | Mithapukur | 28 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 3:00 | 400 | 18:30 | Kaliakoir | 395 | 0.375 | 384 | 0.70833
| Bheramara | 402 | 15:00 | 397 | 19:30 | Bhulta | 388 | 0.041667 | 377 | 0.45833
| Ashuganj(N) | 395 | 4:00 | 382 | 10:00 | Gopalganj | 404 | 0.625 | 381 | 0.91667
| Payra | 410 | 1:00 | 399 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 14:00 | Hathazari | 237 | 13:00 | 228 | 9:00
| Ishurdi | 234 | 17:00 | 224 | 20:00 | Megnaghat | 234 | 8:00 | 229 | 11:00
| Ashuganj | 242 | 6:00 | 236 | 14:00 | Fenchuganj | 242 | 3:00 | 238 | 1:00
| Serajganj | 230 | 11:00 | 224 | 23:00 | Siddhirganj | 233 | 1:00 | 226 | 10:00
| Baghabari | 232 | 15:00 | 224 | 19:30 | Maniknagar | 231 | 1:00 | 224 | 11:00
| Barapukuria | 236 | 17:00 | 223 | 19:00 | Agargaon | 230 | 7:00 | 222 | 11:00
| Bogra | 226 | 17:00 | 212 | 19:30 | Barisal | 240 | 13:00 | 232 | 18:00
| Rajshahi | 232 | 17:00 | 220 | 22:00 | Bhola 225 MW | 246 | 21:00 | 237 | 18:30
| Khulna South | 233 | 9:00 | 220 | 20:00 | AKSML | 235 | 13:00 | 226 | 9:00
| Rampura | 231 | 2:00 | 224 | 16:00 | BSRM | 236 | 13:00 | 227 | 9:00
| Haripur | 230 | 4:00 | 225 | 11:00 | Bibiyana | 242 | 13:00 | 238 | 2:00
| Hasnabad | 229 | 3:00 | 225 | 1:00 | Bhulta | 234 | 3:00 | 226 | 11:00
| Shyampur | 229 | 1:00 | 222 | 11:00 | Ashuganj (S) | 238 | 1:00 | 233 | 24:00
| Aminbazar | 231 | 1:00 | 224 | 2:00 | Kaliakoir | 228 | 1:00 | 220 | 17:00
| Tongi | 230 | 1:00 | 218 | 10:00 | GPH | 236 | 13:00 | 223 | 21:00
| Comilla (N) | 233 | 8:00 | 229 | 10:00 | Jhenaidah | 229 | 10:00 | 213 | 22:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 131 | 10:00 | Madanhat | 139 | 0.75 | 134 | 0.33333
| Munsiganj | 135 | 1:00 | 131 | 10:00 | Hathazari | 139 | 0.79167 | 134 | 0.20833
| Sonargaon | 134 | 2:00 | 131 | 10:00 | Khulshi | 136 | 0.54167 | 131 | 0.375
| Shyampur | 137 | 1:00 | 132 | 11:00 | Halishahar | 138 | 0.79167 | 130 | 0.375
| Bhulta | 130 | 1:00 | 126 | 10:00 | Baraulia | 138 | 0.54167 | 131 | 0.375
| Madanganj | 135 | 2:00 | 130 | 10:00 | Sikalbaha | 140 | 0.79167 | 133 | 0.16667
| Shitalakhya | 137 | 1:00 | 130 | 11:00 | Dohazari | 134 | 0.79167 | 126 | 0.041667
| Rahim steal | 134 | 1:00 | 131 | 9:00 | Cox'sbazar | 123 | 0.54167 | 111 | 0.75
| Matuail | 135 | 1:00 | 131 | 10:00 | Chandraghona | 139 | 0.79167 | 133 | 0.375
| Ghorasal | 138 | 1:00 | 136 | 15:00 | Kaptai | 137 | 0.75 | 132 | 0.33333
| Narsinghdi | 133 | 9:00 | 123 | 19:30 | A. Khaer Stl. | 135 | 0.54167 | 131 | 0.29167
| Haripur (SBU) | 135 | 5:00 | 131 | 10:00 | Bakulia | 138 | 0.875 | 131 | 0.29167
| Sreenagar | 134 | 3:00 | 129 | 10:00 | Julda | 137 | 0.45833 | 133 | 0.125
| Ullon | 134 | 1:00 | 129 | 10:00 | TK Chemical | 139 | 0.79167 | 132 | 0.29167
| Hasnabad | 135 | 1:00 | 130 | 10:00 | Modern Steel | 137 | 0.75 | 131 | 0.20833
| Magbazar | 135 | 5:00 | 130 | 10:00 | Shahmirpur | 139 | 0.79167 | 131 | 0.41667
| Maniknagar | 135 | 1:00 | 130 | 11:00 | Khagrachhari | 137 | 0.54167 | 132 | 0.375
| Bangabhaban | 135 | 1:00 | 130 | 11:00 | Matarbari | 130 | 0.54167 | 115 | 0.29167
| Motijheel | 135 | 1:00 | 130 | 11:00 | Baroiar Hat | 136 | 0.54167 | 132 | 0.20833
| Narinda | 135 | 1:00 | 130 | 11:00 | Rangamati | 139 | 19:00 | 133 | 7:00
| Kazla | 135 | 1:00 | 130 | 11:00 | Agrabad | 137 | 18:00 | 133 | 16:00
| Dhanmondi | 135 | 4:00 | 130 | 10:00 | Goalpara S/S | 138 | 8:00 | 132 | 0.875
| Lalbag | 135 | 1:00 | 130 | 10:00 | Khulna Central S/S | 137 | 7:00 | 131 | 0.875
| Madartek | 135 | 3:00 | 129 | 10:00 | Noapara | 137 | 18:00 | 128 | 0.875
| Dhaka University | 135 | 2:00 | 129 | 10:00 | Jessore | 135 | 9:00 | 124 | 0.875
| Aftabnagar | 135 | 2:00 | 129 | 11:00 | Benapol | 134 | 0.375 | 125 | 0.83333
| Fatullah | 137 | 4:00 | 132 | 11:00 | Jhenida(Old) | 137 | 9:00 | 125 | 0.91667
| Nawabganj | 134 | 6:00 | 130 | 11:00 | Bottail | 135 | 0.375 | 128 | 0.875
| Keraniganj | 135 | 1:00 | 129 | 11:00 | G.K Project | 139 | 0.70833 | 134 | 0.8125
| Mirpur | 134 | 4:00 | 127 | 10:00 | Faridpur | 136 | 0.33333 | 128 | 0.91667
| Kalyanpur | 134 | 2:00 | 128 | 16:00 | Rajbari | 137 | 0.41667 | 127 | 0.91667
| Gulshan | 134 | 1:00 | 129 | 10:00 | Madaripur | 139 | 0.29167 | 132 | 0.83333
| Uttara | 132 | 2:00 | 125 | 10:00 | Shariyatpur S/S | 139 | 9:00 | 130 | 0.91667
| Uttara New | 132 | 1:00 | 127 | 10:00 | Gopalganj | 140 | 0.375 | 131 | 0.91667
| Kamrangirchar | 136 | 1:00 | 129 | 10:00 | Bagerhat | 137 | 9:00 | 128 | 0.91667
| Savar | 135 | 3:00 | 128 | 16:00 | Mongla | 135 | 5:00 | 128 | 0.79167
| Bhasantec | 137 | 3:00 | 130 | 11:00 | Satkhira | 137 | 9:00 | 126 | 22:00
| Agargaon | 137 | 1:00 | 132 | 10:00 | Gallamari | 137 | 0.25 | 126 | 21:00
| Satmosjid | 137 | 3:00 | 131 | 11:00 | Magura | 139 | 9:00 | 125 | 0.91667
| Tongi | 139 | 1:00 | 132 | 9:00 | Narail | 135 | 0.375 | 122 | 0.83333
| Kabirpur | 136 | 7:00 | 128 | 21:00 | Chuadanga | 132 | 8:00 | 117 | 0.83333
| Basundhara | 140 | 1:00 | 129 | 10:00 | Barisal(N) | 139 | 7:00 | 132 | 0.875
| Manikganj | 140 | 13:00 | 131 | 19:30 | Barisal (S) | 138 | 7:00 | 130 | 22:00
| Joydevpur | 140 | 18:00 | 133 | 10:00 | Patuakhali(S) | 137 | 0.41667 | 128 | 0.125
| New Tongi | 138 | 21:00 | 130 | 10:00 | Bhandaria | 137 | 0.375 | 125 | 0.79167
| Kodda | 137 | 21:00 | 124 | 11:00 | Borguna | 138 | 0.29167 | 129 | 0.79167
| Dhamrai | 137 | 1:00 | 132 | 11:00 | Jhenaidah(230kV S/S) | 136 | 8:00 | 126 | 21:00
| Rajendrapur | 136 | 21:00 | 122 | 11:00 | Ishurdi | 136 | 17:00 | 131 | 20:00
| Valuka | 124 | 11:00 | 108 | 1:00 | Ruppur Paromanobik | 137 | 17:00 | 131 | 21:00
| Tangail | 132 | 5:00 | 121 | 19:30 | Natore | 136 | 18:30 | 129 | 20:00
| Mymensing | 128 | 7:00 | 113 | 19:30 | Bogra | 135 | 18:00 | 125 | 20:00
| Kishorganj | 130 | 7:00 | 117 | 22:00 | Noagaon | 131 | 17:00 | 118 | 21:00
| Netrokona | 126 | 12:00 | 109 | 19:30 | Rajshahi | 135 | 18:00 | 128 | 1:00
| Jamalpur | 137 | 12:00 | 121 | 1:00 | Rajshahi New | 138 | 18:00 | 129 | 2:00
| Sherpur | 136 | 8:00 | 118 | 0:00 | C.Nawabganj | 135 | 18:00 | 128 | 4:00
| Srimongal | 137 | 6:00 | 131 | 1:00 | Amnura | 136 | 18:00 | 123 | 2:00
| Shahjibazar | 137 | 8:00 | 129 | 19:00 | Pabna | 135 | 17:00 | 129 | 19:00
| Fenchuganj | 135 | 8:00 | 129 | 1:00 | Shahjadpur | 139 | 5:00 | 133 | 19:00
| Khulawara | 135 | 9:00 | 129 | 1:00 | Serajganj | 132 | 12:00 | 125 | 19:30
| Sylhet | 131 | 7:00 | 125 | 1:00 | Niyamatpur | 128 | 17:00 | 114 | 21:00
| Chatak | 131 | 23:00 | 120 | 12:00 | Joypurhat | 130 | 17:00 | 117 | 21:00
| Sunamganj | 130 | 21:00 | 118 | 1:00 | Sherpur(Bogura) | 134 | 17:00 | 125 | 19:30
| Biani Bazar | 130 | 7:00 | 120 | 1:00 | Mohastangor | 133 | 13:00 | 122 | 21:00
| Comilla(s) | 130 | 11:00 | 125 | 18:00 | Bangura | 136 | 17:00 | 132 | 19:00
| Comilla(n) | 138 | 13:00 | 134 | 10:00 | Rangpur | 132 | 17:00 | 116 | 19:30
| Chandpur | 142 | 7:00 | 137 | 23:00 | Lalmonirhat | 132 | 17:00 | 115 | 21:00
| Feni | 138 | 13:00 | 130 | 2:00 | Saidpur | 132 | 17:00 | 112 | 19:30
| Chowmuhani | 134 | 17:00 | 130 | 24:00 | Purbasadipur | 131 | 17:00 | 113 | 21:00
| Ashuganj | 139 | 7:00 | 133 | 20:00 | Thakurgaon | 133 | 17:00 | 112 | 19:30
| Daudkandi | 136 | 18:30 | 128 | 23:00 | Palashbari | 133 | 14:00 | 120 | 19:30
| B.Baria | 135 | 7:00 | 126 | 23:00 | Barapukuria | 136 | 17:00 | 123 | 19:30
| Ramganj | 136 | 17:00 | 131 | 23:00 | Panchagar | 135 | 0.70833 | 114 | 0.8125
| Chaddagram | 138 | 12:00 | 132 | 11:00 | Joldhaka | 129 | 0.70833 | 111 | 0.83333
| PHP | 137 | 18:30 | 130 | 4:00 | Kurigram | 133 | 0.70833 | 113 | 0.8125
| Kochua | 137 | 18:00 | 134 | 24:00 | Mithapukur | 134 | 0.70833 | 119 | 0.8125
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-10-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 248 | 8849 | 3781 | 12630 |  |  |  | QF-LDC-11
0:30 | 182 | 8571 | 3740 | 12311 | Date: | 2021-10-02
1:00 | 116 | 8293 | 3699 | 11992
1:30 | 128 | 8159.5 | 3577.5 | 11737
2:00 | 140 | 8026 | 3456 | 11482
2:30 | 135 | 7978 | 3404.5 | 11382.5 | [5 empty] | Gen. at Eve. Peak | 13178 | 13178 MW (20:00 )
3:00 | 130 | 7930 | 3353 | 11283 | [6 empty] | 20:00
3:30 | 130 | 7780.5 | 3294 | 11074.5 | [5 empty] | Gen. at Day Peak | 10805 | 10805 MW (12:00 )
4:00 | 130 | 7631 | 3235 | 10866 | [6 empty] | 12:00
4:30 | 111 | 7466.5 | 3184.5 | 10651 | [5 empty] | Highest Generation | 13178
5:00 | 92 | 7302 | 3134 | 10436 | [6 empty] | 20:00
5:30 | 56 | 7127 | 3057.5 | 10184.5
6:00 | 20 | 6952 | 2981 | 9933
6:30 | 23 | 6913.5 | 2925 | 9838.5
7:00 | 26 | 6875 | 2869 | 9744
7:30 | 32 | 6842 | 2846.5 | 9688.5
8:00 | 38 | 6809 | 2824 | 9633
8:30 | 180 | 6850.5 | 2831 | 9681.5
9:00 | 322 | 6892 | 2838 | 9730
9:30 | 341 | 7005 | 2880.5 | 9885.5
10:00 | 360 | 7118 | 2923 | 10041
10:30 | 364 | 7160.5 | 2980 | 10140.5
11:00 | 368 | 7203 | 3037 | 10240
11:30 | 264 | 7440 | 3082.5 | 10522.5
12:00 | 160 | 7677 | 3128 | 10805
12:30 | 94 | 7807 | 3158.5 | 10965.5
13:00 | 28 | 7937 | 3189 | 11126
13:30 | 26 | 7765.5 | 3140 | 10905.5
14:00 | 24 | 7594 | 3091 | 10685
14:30 | 70 | 7824 | 3170.5 | 10994.5
15:00 | 116 | 8054 | 3250 | 11304
15:30 | 139 | 8020.5 | 3238.5 | 11259
16:00 | 162 | 7987 | 3227 | 11214
16:30 | 179 | 7838 | 3135.5 | 10973.5
17:00 | 196 | 7689 | 3044 | 10733
17:30 | 142 | 8018 | 3247.5 | 11265.5
18:00 | 88 | 8347 | 3451 | 11798
18:30 | 147 | 8737 | 3670.5 | 12407.5
19:00 | 206 | 9127 | 3890 | 13017
19:30 | 160 | 9098 | 4022 | 13120
20:00 | 144 | 9130 | 4048 | 13178 |  |  |  | Executive Engineer
20:30 | 187 | 9106 | 4031 | 13137 |  |  |  | Network Operation Division
21:00 | 230 | 9082 | 4014 | 13096
21:30 | 273 | 9070 | 3932 | 13002
22:00 | 316 | 9058 | 3850 | 12908 |  |  |  |  | Page 6 of 7
22:30 | 309 | 8997.5 | 3836.5 | 12834
23:00 | 302 | 8937 | 3823 | 12760
23:30 | 275 | 8893 | 3802 | 12695
24:00 | 248 | 8849 | 3781 | 12630
13178 MW (20:00 )
10805 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-02 |  | Energy |  | 276079497
[13 empty] | 2021-10-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4456 | 701 | 2257 | 0 | 3646 | 670 | 159 | 130 | 481 | 130 | 0 | 0
0:30 | 4300 | 704.5 | 2212 | 0 | 3578 | 637.5 | 159 | 176 | 417 | 127 | 0 | 0 | Date: | 2021-10-02
1:00 | 4144 | 708 | 2167 | 0 | 3510 | 605 | 159 | 222 | 353 | 124 | 0 | 0
1:30 | 4149.5 | 708 | 2212 | 0 | 3328.5 | 590 | 159 | 221.5 | 244.5 | 124 | 0 | 0 | [8 empty] | Total Energy | 276.0795 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 4155 | 708 | 2257 | 0 | 3147 | 575 | 159 | 221 | 136 | 124 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4163.5 | 708.5 | 2236.5 | 0 | 3098.5 | 570 | 159 | 205.5 | 119 | 122 | 0 | 0 | [8 empty] | Energy Requirement | 276.0795
3:00 | 4172 | 709 | 2216 | 0 | 3050 | 565 | 159 | 190 | 102 | 120 | 0 | 0
3:30 | 4162.5 | 708.5 | 2225 | 0 | 2922.5 | 545 | 159 | 155 | 77 | 120 | 0 | 0 | [6 empty] | Shortage
4:00 | 4153 | 708 | 2234 | 0 | 2795 | 525 | 159 | 120 | 52 | 120 | 0 | 0
4:30 | 4141.5 | 708 | 2243.5 | 0 | 2613 | 515 | 159 | 120 | 36 | 115 | 0 | 0
5:00 | 4130 | 708 | 2253 | 0 | 2431 | 505 | 159 | 120 | 20 | 110 | 0 | 0
5:30 | 4128 | 708 | 2212 | 0 | 2230.5 | 500 | 159 | 120 | 20 | 107 | 0 | 0
6:00 | 4126 | 708 | 2171 | 0 | 2030 | 495 | 159 | 120 | 20 | 104 | 0 | 0
6:30 | 4105 | 708.5 | 2178 | 0 | 1974 | 485 | 142 | 120 | 20 | 100 | 6 | 0 |  |  |  |  | Coal
7:00 | 4084 | 709 | 2185 | 0 | 1918 | 475 | 125 | 120 | 20 | 96 | 12 | 0
7:30 | 4047 | 708.5 | 2155 | 0 | 1925 | 465 | 125.5 | 120 | 12 | 98 | 32.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4010 | 708 | 2125 | 0 | 1932 | 455 | 126 | 120 | 4 | 100 | 53 | 0
8:30 | 4004.5 | 708.5 | 2126 | 0 | 1996 | 440 | 127 | 120 | 4 | 95 | 60.5 | 0
9:00 | 3999 | 709 | 2127 | 0 | 2060 | 425 | 128 | 120 | 4 | 90 | 68 | 0
9:30 | 4043 | 709 | 2142.5 | 0 | 2147.5 | 420 | 127 | 120 | 4 | 91 | 81.5 | 0
10:00 | 4087 | 709 | 2158 | 0 | 2235 | 415 | 126 | 120 | 4 | 92 | 95 | 0
10:30 | 4082 | 708.5 | 2154.5 | 0 | 2343.5 | 417 | 126 | 120 | 5 | 86 | 98 | 0
11:00 | 4077 | 708 | 2151 | 0 | 2452 | 419 | 126 | 120 | 6 | 80 | 101 | 0
11:30 | 4064.5 | 708 | 2136.5 | 0 | 2751.5 | 424 | 125 | 120 | 5 | 86 | 102 | 0
12:00 | 4052 | 708 | 2122 | 0 | 3051 | 429 | 124 | 120 | 4 | 92 | 103 | 0
12:30 | 4063 | 708.5 | 2126 | 0 | 3179.5 | 444.5 | 124 | 120 | 12 | 89 | 99 | 0
13:00 | 4074 | 709 | 2130 | 0 | 3308 | 460 | 124 | 120 | 20 | 86 | 95 | 0
13:30 | 4074 | 709 | 2130 | 0 | 3308 | 460 | 124 | 120 | 20 | 86 | 95 | 0
14:00 | 4074 | 709 | 2130 | 0 | 3308 | 460 | 124 | 120 | 20 | 86 | 95 | 0
14:30 | 4133 | 709 | 2164 | 0 | 3321 | 455.5 | 124 | 120 | 24.5 | 94 | 70 | 0
15:00 | 4192 | 709 | 2198 | 0 | 3334 | 451 | 124 | 120 | 29 | 102 | 45 | 0
15:30 | 4189 | 709 | 2179 | 0 | 3296 | 465.5 | 124 | 120 | 32.5 | 102 | 42 | 0
16:00 | 4186 | 709 | 2160 | 0 | 3258 | 480 | 124 | 120 | 36 | 102 | 39 | 0
16:30 | 4189.5 | 708.5 | 2091 | 0 | 3089 | 479.5 | 124.5 | 120 | 38 | 106 | 27.5 | 0
17:00 | 4193 | 708 | 2022 | 0 | 2920 | 479 | 125 | 120 | 40 | 110 | 16 | 0
17:30 | 4190.5 | 704 | 2067.5 | 78.5 | 3115 | 475 | 125.5 | 140 | 240.5 | 121 | 8 | 0
18:00 | 4188 | 700 | 2113 | 157 | 3310 | 471 | 126 | 160 | 441 | 132 | 0 | 0
18:30 | 4273.5 | 700.5 | 2187 | 162 | 3586.5 | 520.5 | 143.5 | 191.5 | 506.5 | 136 | 0 | 0
19:00 | 4359 | 701 | 2261 | 167 | 3863 | 570 | 161 | 223 | 572 | 140 | 0 | 0
19:30 | 4424 | 701 | 2306 | 50 | 3881 | 659 | 161 | 222 | 574 | 142 | 0 | 0
20:00 | 4516 | 700 | 2302 | 50 | 3867 | 661 | 161 | 224 | 555 | 142 | 0 | 0
20:30 | 4507.5 | 700.5 | 2286.5 | 25 | 3871.5 | 665.5 | 161 | 217 | 561.5 | 141 | 0 | 0
21:00 | 4499 | 701 | 2271 | 0 | 3876 | 670 | 161 | 210 | 568 | 140 | 0 | 0
21:30 | 4489.5 | 700.5 | 2248 | 0 | 3845.5 | 670.5 | 161 | 180 | 568 | 139 | 0 | 0
22:00 | 4480 | 700 | 2225 | 0 | 3815 | 671 | 161 | 150 | 568 | 138 | 0 | 0
22:30 | 4470.5 | 700.5 | 2242 | 0 | 3772.5 | 670.5 | 160.5 | 150 | 531.5 | 136 | 0 | 0
23:00 | 4461 | 701 | 2259 | 0 | 3730 | 670 | 160 | 150 | 495 | 134 | 0 | 0
23:30 | 4458.5 | 701 | 2258 | 0 | 3688 | 670 | 159.5 | 140 | 488 | 132 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.2° C
24:00 | 4456 | 701 | 2257 | 0 | 3646 | 670 | 159 | 130 | 481 | 130 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 84 | 84 | 84 | 84 | 84 | 84 | 85 | 86 | 88 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 85 | 86 |  | 86 | 86 | 86 | 86 | 86 | 85 | 84 | 2014407
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1396000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 2 |  | 22 | 17 | 19 | 23 | 25 | 25 | 8 | 136285
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 |  | 2 | 1 | 4 | 1 | 1 |  | 5 | 5 | 5 | 1 | [9 empty] | 19305
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 34 | [15 empty] | 102 |  | 102 | 100 | 87 | 102 | 102 | 102 | 102 | 738696
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 51 | 51 | 51 | 51 | 51 | 67 | 105 | 105 | 85 | 90 | 105 | 85 | 73 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2204654
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 30 |  | 30 | [6 empty] | 102720
14 | Titas 50 MW Peaking PP | [17 empty] | 33 |  | 42 | 42 | 42 | 42 | 42 |  | 0 | 185272
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 147 | 150 | 153 | 153 | 153 | 148 | 129 | 129 | 70 | 128 | 150 | 145 | 127 | 127 | 184 | 149 | 182 | 127 |  | 185 | 185 | 185 | 181 | 182 | 182 | 185 | 5184000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 240 | 278 | 278 | 180 | 30 | 30 | 30 | 30 | 62 | 95 | 100 | 208 | 250 | 245 | 260 | 210 | 210 | 235 |  | 260 | 280 | 281 | 285 | 281 | 288 | 288 | 4907780
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 518545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 300 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 300 | 300 | 300 | 300 | 300 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 300 | 300 | 300 | 300 | 7229600
26
28 | Ashuganj TPP Unit- 3 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2293552
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 17 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 497232
33 | Ashuganj 225 MW CCPP | 208 | 209 | 209 | 208 | 208 | 209 | 183 | 167 | 164 | 158 | 190 | 198 | 180 | 205 | 183 | 206 | 209 | 206 |  | 208 | 206 | 206 | 208 | 209 | 210 | 210 | 4797000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 340 | 310 | 350 | 345 | 310 | 310 | 310 | 295 | 310 | 280 | 280 | 280 |  | 305 | 305 | 320 | 300 | 295 | 295 | 295 | 7455000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 305 | 340 | 310 | 320 | 340 | 310 | 310 | 310 | 280 | 300 | 280 | 280 | 280 |  | 285 | 295 | 330 | 335 | 330 | 310 | 310 | 7806800
35 | Ashuganj 55 MW PP (Precision) | 55 | 56 | 56 | 54 | 55 | 56 | 55 | 55 | 56 | 54 | 51 | 55 | 54 | 55 | 56 | 56 | 55 | 56 |  | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 1321440
36 | Chandpur 150 MW CCPP | 137 | 140 | 137 | 140 | 140 | 138 | 140 | 141 | 140 | 141 | 140 | 138 | 137 | 141 | 138 | 141 | 139 | 139 |  | 138 | 138 | 139 | 140 | 140 | 140 | 140 | 3304150
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 395 | 395 | 395 | 395 | 396 | 363 | 361 | 361 | 362 | 397 | 401 | 377 | 325 | 376 | 401 | 401 | 335 |  | 395 | 399 | 399 | 395 | 396 | 396 | 396 | 9337000
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6159750
41 | Haripur 360MW CCPP(HPL) | 327 | 329 | 329 | 330 | 331 | 332 | 332 | 333 | 320 | 320 | 320 | 320 | 320 | 317 | 317 | 317 | 287 | 270 |  | 320 | 320 | 320 | 322 | 321 | 322 | 321 | 7690000
42 | RPCL 210MW CCPP | 210 | 207 | 208 | 208 | 207 | 211 | 206 | 206 | 202 | 201 | 202 | 182 | 166 | 164 | 165 | 168 | 183 | 180 |  | 186 | 182 | 200 | 198 | 198 | 198 | 198 | 4549280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 27 | 41 | 54 | 54 | 57 | 50 | 12 | 9 | 11 | 8 | [9 empty] | 366650
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1025000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 262080
46 | Shajibazar 330 MW CCPP | [7 empty] | 0 | 6 | 7 | 6 | 7 | 107 | 107 | 158 | 158 | 160 | 159 |  | 161 | 160 | 160 | 159 | 161 | 161 | 162 | 1715000
47 | Shahjibazar GTPP Unit- 8 & 9 | 52 | 51 | 52 | 52 | 51 | 52 | 51 | 52 | 52 | 51 | 51 | 51 | 50 | 29 | 31 | 30 | 31 | 31 |  | 31 | 31 | 31 | 32 | 32 | 52 | 52 | 1050720
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 20 | 72 | 72 | 81 | 75 | 75 | 78 | 81 | 81 | 81 | 80 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1736640
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [16 empty] | 20 | 140 |  | 150 | 145 | 145 | 145 | 145 | 145 | 145 | 911010
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 382000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 206820
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 2 |  | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 185808
55 | Fenchugonj 51 MW PP (Barakatullah) | 45 | 45 | 45 | 45 | 26 | 39 | 36 | 39 | 39 | 39 | 42 | 42 | 44 | 44 | 44 | 42 | 42 | 42 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1004400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 561576
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 290 | 280 | 290 | 290 | 295 | 290 | 295 | 300 | 290 | 295 | 290 | 295 | 300 | 270 | 300 | 280 |  | 280 | 310 | 290 | 280 | 285 | 290 | 295 | 7118960
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7662000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1030273
59 | Tangail Palli Power Gen 22 MW | 18 | [10 empty] | 3 | 18 | 18 | 19 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 312000
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 21 |  | 15 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 457200
61 | Narshingdi 22 MW PP (Doreen) |  | 16 | 20 | 20 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 385812
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 485496
63 | Impoprt (Tripura) | 124 | 124 | 120 | 120 | 110 | 104 | 96 | 100 | 90 | 92 | 80 | 92 | 86 | 82 | 102 | 102 | 110 | 132 |  | 140 | 142 | 142 | 140 | 138 | 134 | 130 | 2784960
64 | Malancha, Ctg. EPZ (United) | 40 | 42 | 42 | 42 | 42 | 42 | 38 | 10 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  | 6 | 7 | 17 | 22 | 28 | 34 | 40 | 487200
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 464508
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 188280
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 29 |  | 10 | 33 | 33 | 33 | 33 | 33 | 33 | 758400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 8 | 21 | 21 | 21 | 21 | 21 | 21 | 498650
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 25 | 29 | 29 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 14 |  | 26 | 26 | 26 | 26 | 28 | 29 | 29 | 611100
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 767400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 70 | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 82 | 100 | 52 | 98 | 114 | 104 | 100 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1662120
| Chowmuhani 113 MW | 48 | 47 | 47 | 48 | 47 | 48 | 47 | 47 | 48 | 48 | 41 | 48 | 42 | 47 | 47 | 42 | 47 | 85 |  | 96 | 96 | 87 | 85 | 92 | 96 | 62 | 1405320
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3941280
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 35 | 42 | 51 | 42 |  | 51 | 51 | 51 | 51 | 51 | 25 |  | 515040
79 | Kodda 150MW PP | 133 | 98 | 98 | 48 | 16 | 16 | 16 | [5 empty] | 16 | 16 | 25 | 32 | 32 | 130 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1566720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 43 | 52 | 34 | 34 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 52 | 52 | 52 | 25 | 25 | 31 |  | 52 | 52 | 52 | 52 | 44 | 44 | 52 | 943186
| Gazipur 100 MW PP | 70 | 17 | [5 empty] | 17 | 17 | 17 | 17 | 58 | 90 | 70 | 75 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 52 | 52 | 1338000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | [9 empty] | 8760
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299265
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 85 | 51 | 51 | 51 | 51 | 51 | 51 | 71 | 97 | 51 | 77 | 110 | 68 | 85 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2243961
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 40 | [10 empty] | 8 | 32 | 10 | 23 | 42 | 42 | 53 |  | 53 | 52 | 45 | 48 | 40 | 40 | 38 | 531332
86 | Meghnaghat CCPP ( Summit) | 255 | 260 | 255 | 280 | 280 | 280 | 290 | 280 | 295 | 300 | 280 | 260 | 265 | 295 | 255 | 275 | 245 | 300 |  | 305 | 310 | 310 | 305 | 285 | 290 | 280 | 6683549
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 93 | 93 | 93 | 93 | 93 | 60 | 55 | 55 | 53 | 53 | 67 | 92 | 92 | 92 | 92 | 92 | 60 | 70 |  | 91 | 91 | 93 | 93 | 93 | 94 | 104 | 2023680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 50 | 50 | [8 empty] | 70 | 70 | 20 | 100 | 100 | 60 | 92 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 1265880
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 993526
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 50 | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 40 | 85 | 93 | 102 | 58 | 58 | 72 |  | 93 | 93 | 93 | 93 | 93 | 93 | 102 | 1402272
95 | Patenga 50MW PP (Baraka) | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 36 | 50 | 25 | 31 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 805920
96 | Chattogram 108 MW PP (ECPV) | 20 | 24 | [9 empty] | 8 | 30 | 12 | 14 | 20 | 24 | 58 |  | 86 | 87 | 86 | 86 | 86 | 86 | 53 | 711360
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 48 | 42 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1234800
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1082343
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 163 | 130 | 130 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3453136
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 12650
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1274760
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 40 |  | 12 | [5 empty] | 0 | 67118
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 30 |  | 25 | [5 empty] | 0 | 70532
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 168 | 184 | 160 | 175 | 183 | 170 | 183 |  | 198 | 199 | 199 | 199 | 200 | 200 | 190 | 4320000
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 31 |  | 100 | 50 | 50 |  |  |  | 0 | 182300
114 | Kodda 149 MW PP Unit-1 (Summit) | 107 | 99 | 80 | 64 | 50 | 50 | 50 | 66 | 105 | 140 | 149 | 149 | 149 | 149 | 149 | 120 | 100 | 111 |  | 149 | 149 | 149 | 149 | 149 | 140 | 149 | 2808720
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2354880
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 155 | 164 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4699200
117 | Ashuganj 150MW PP (Midland) | 133 | 123 | 123 | 127 | 130 | 128 | 130 | 110 | 125 | 130 | 128 | 123 | 117 | 122 | 120 | 120 | 123 | 122 |  | 125 | 125 | 123 | 123 | 123 | 122 | 123 | 2984132
118 | Bibiyana-III 400 MW CCPP | 318 | 317 | 318 | 317 | 317 | 317 | 317 | 317 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 317 | 316 | 316 |  | 316 | 316 | 316 | 316 | 317 | 316 | 316 | 7610000
| Jamalpur 115 MW PP (United) | 106 | 106 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2703600
| Anwara 300 MW PP (United) | 305 | 305 | 305 | 305 | 305 | 250 | 178 | 179 | 179 | 250 | 285 | 304 | 304 | 304 | 304 | 303 | 270 | 290 |  | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 6762000
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 92 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2375040
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 53 | 53 | 53 | 53 | 53 | 66 | 96 | 105 | 108 | 108 | 108 | 72 | 74 |  | 106 | 108 | 108 | 108 | 108 | 108 | 108 | 2258182
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 6 | 19 | 20 | 32 | 36 | 35 | 34 | 29 | 19 | 15 | 4 | [9 empty] | 238237
120 | Eastern Zone Total | 8293 | 8026 | 7930 | 7631 | 7302 | 6952 | 6875 | 6809 | 6892 | 7118 | 7203 | 7677 | 7937 | 7594 | 8054 | 7987 | 7689 | 8347 |  | 9127 | 9098 | 9130 | 9082 | 9058 | 8937 | 8849 | 193662532
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 32 | 32 | 27 | 29 | 29 | 29 | 29 | 216480
| Khulna 225 MW CCPP | 222 | 221 | 190 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 |  | 223 | 222 | 224 | 210 | 150 | 150 | 130 | 3716160
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 70 | 73 | 103 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2341920
130
131
132 | United Payra Power Ltd. | 54 | 17 | [15 empty] | 4 |  | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 372000
133 | Bhola Nutan Biddut BD LTD (GAS) | 202 | 222 | 211 | 211 | 211 | 220 | 180 | 184 | 183 | 181 | 181 | 181 | 181 | 181 | 218 | 218 | 218 | 217 |  | 223 | 223 | 224 | 224 | 224 | 224 | 225 | 4949809
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 424162
| Bhola 225 MW CCPP | 86 | 87 | 81 | 81 | 81 | 81 | 81 | 82 | 82 | 82 | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 81 | 1991435
140 | Bhola 33 MW PP (Venture) | 32 | 31 | 31 | 30 | 29 | 26 | 21 | 16 | 17 | 18 | 18 | 19 | 21 | 23 | 23 | 23 | 22 | 29 |  | 33 | 33 | 33 | 34 | 34 | 34 | 34 | 628054
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 4 | [7 empty] | 0 | 28800
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 32 | [24 empty] | 0 | 53424
146 | Bheramara HVDC | 708 | 708 | 709 | 708 | 708 | 708 | 709 | 708 | 709 | 709 | 708 | 708 | 709 | 708 | 709 | 709 | 708 | 700 |  | 701 | 701 | 700 | 701 | 700 | 701 | 701 | 17067636
147 | Bheramara 410 MW CCPP | 355 | 355 | 355 | 335 | 335 | 340 | 350 | 355 | 360 | 385 | 350 | 355 | 355 | 385 | 395 | 400 | 340 | 375 |  | 360 | 380 | 395 | 400 | 405 | 405 | 405 | 9051264
148 | Payra 1320 MW | 530 | 500 | 490 | 450 | 430 | 420 | 400 | 380 | 350 | 340 | 340 | 350 | 380 | 350 | 370 | 400 | 400 | 400 |  | 500 | 580 | 580 | 590 | 590 | 590 | 590 | 11760300
149
150 | Barapukuria TPP Unit-1 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 79 | 79 | 80 | 82 | 81 | 80 | 79 | 71 |  | 70 | 79 | 81 | 80 | 81 | 80 | 80 | 1846690
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | [16 empty] | 23 |  | 50 | 50 | 50 | 50 | 50 | 50 | 43 | 346832
| Sirajgonj 6.55 MW Solar | [6 empty] | 1 | 2 | 4 | 1 | 5 | 5 | 5 | 5 | 4 | 2 | 0 | [9 empty] | 33240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 178 | 181 | 188 | 188 | 191 | 188 | 175 | 174 | 175 | 181 | 200 | 192 | 196 | 177 | 190 | 185 | 186 | 172 |  | 182 | 188 | 193 | 187 | 179 | 175 | 172 | 4626064
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 185 | 184 | 184 | 185 | 189 | 181 | 172 | 171 | 178 | 190 | 191 | 192 | 181 | 188 | 196 | 191 | 176 |  | 188 | 193 | 196 | 192 | 178 | 170 | 168 | 4662773
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 345 | 396 | 361 | 374 | 392 | 350 | 350 | 330 | 361 | 391 | 414 | 392 | 395 | 349 | 392 | 400 | 292 | 377 |  | 400 | 412 | 414 | 390 | 354 | 370 | 366 | 9039400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 8 |  | 34 | 33 | 33 | 33 | 32 |  |  | 137662
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 21 | 21 |  | 21 | 18 | 21 | 21 | 21 | 21 | 22 | 483840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250938
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 27 | 27 | 27 | 27 |  |  | 0 | 105220
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 24 |  | 43 | 43 | 43 | 43 |  |  | 0 | 168154
167 | Katakhali 50 MW Peaking PP | [17 empty] | 29 |  | 37 | 40 | 40 | 36 | 36 | 36 | 30 | 232487
168 | Santahar 50 MW Peaking PP | 27 | [16 empty] | 18 |  | 31 | 33 | 33 | 33 | 34 | 35 | 34 | 238360
169 | Natore 52 MW PP (Rajlanka) | 52 | [10 empty] | 2 | 8 | 8 | 8 | 25 | 25 | 30 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 490560
170 | Chapainawabganj 100 MW Peaking PP | 88 | [16 empty] | 94 |  | 94 | 94 | 93 | 93 | 93 | 93 | 93 | 688616
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 22 | [7 empty] | 0 | 15891
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 70 | 35 | 35 | 35 | 35 | 35 | 55 | 92 | 92 | 92 | 94 | 70 | 70 | 80 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2063232
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 35 | 35 | 100 | 113 | 113 | 113 | 113 | 50 | 50 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2160096
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 70 | 34 | 34 | 34 | 35 | 35 | 87 | 100 | 71 | 99 | 105 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2195337
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 7 | 7 | 5 | 3 | [9 empty] | 30129
178
178