## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-04 | Monday
|  |  | Date (day): | 2021-10-04 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13554.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14830 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-03 | 2021-10-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 381 | 340 | 330 | 350 | 62 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 326 | 326 | 320 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 305 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 51 | 68 | 68 |  | 32 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 128 | 185 | 150 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 40 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 90 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 28 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 16 | 0 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 282 | 250 | 282 |  | 18 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 141 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 34 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2604 | 2983 | 3442 | 3764 | 1094 | 810
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 25 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 121 | 162 | 161 | 161 | 69 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 72 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 34 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 20 | 40 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 20 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 306 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 51 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 96 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 72 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1039 | 1378 | 1486 | 1564 | 134 | 671
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 100 | 100 |  |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 0 | 0 | 140 |  | 75 | ST Under maint.
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 285 | 300 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 305 | 300 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 36 | 45 | 45 | 150 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 108 | 60 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 138 | 140 | 140 |  | 23 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 157 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 136 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 100 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 51 | 96 | 95 | 96 |  | 17 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1788 | 1742 | 1979 | 2321 | 413 | 197
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 163 | 172 | 170 | 170 | 32 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 120 | 100 | 170 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 109 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 11 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 414 | 403 | 550.6 | 529 | 32 | 95
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 30 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 163 | 160 | 160 | 170 |  | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 47 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 57 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 145 | 145 | 145 | 200
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 315 | 316 | 316 | 316 | 84 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1669 | 1709 | 1764 | 1819 | 317 | 196
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 701 | 701 | 713 | 713
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 0 | 5 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 365 | 350 | 350 | 410 |  |  | FGMO
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 70 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1207 | 1241 | 1548 | 1718 | 0 | 98
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 34 | 30 | 32
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 87 | 84 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 17 | 17 | 17 | 17 | 78 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 390 | 450 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 181 | 224 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 695 | 829 | 1083 | 1239 | 78 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 34 | 35 |  | 36 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 28 | 28 |  | 22 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 187 | 185 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 183 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 361 | 423 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 39 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 94 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 898 | 1089 | 1500 | 1681 | 380 | 95
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 82 | 81 | 82
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 116 | 195 | 202 | 195 | 0 | 399
|  | Total |  |  |  |  | 22031 | 21180 | 10430 | 11569 | 13554.6 | 14830 | 2448 | 2667
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10035.1223 | 11131 | 13041.4256 | 14268.5392
| A. |  | 2021-10-03 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12173 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9621 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11569 | MW
| 3 | Day peak Generation : |  |  | 10430 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11131 | MW
| 4 | Evening peak Generation : |  |  | 11569 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 263.2069 | MKWHr | By Solar | 0.3794 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 156.727 | MKWHr |  | By Oil: | 69.1857 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.7741 | MKWHr |  | By Hydro: | 3.5155 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2448 | MW | Dhaka | 4196 | 4196 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2667 | MW | Chittagong | 1166 | 1166 |  | 0 |  | 18:00 |  | 128
|  |  |  | Total = |  |  | 5115 | MW | Khulna | 1343 | 1343 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1192.07 | MMCFD |  |  | Rajshahi | 1091 | 1091 |  | 0 |  | 19:00 |  | 136
| 8 | Fuel Cost : | i) Gas : | Taka | 163725980.868 | ii) Oil : | Taka | 521121551.86 | Comilla | 1219 | 1219 |  | 0 |  | 19:30 |  | 138
|  |  | iii) Coal : |  | 63579046.16 | Total | Taka | 748426578.888 | Mymensingh | 753 | 753 |  | 0 |  | 20:00 |  | 138
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.166 | MKWHr. | Sylhet | 413 | 413 |  | 0 |  | 21:00 |  | 136
|  | ii) During Peak Demand : |  |  | -154 | MW (E to W) at | 21:00 | hrs | Barisal | 365 | 365 |  | 0 |  | 22:00 |  | 134
|  | iii) Maximum : |  |  | -452 | MW at | 2:00 | hrs | Rangpur | 585 | 585 |  | 0 |  | 23:00 |  | 132
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.1° C |  |  | Total | 11131 | 11131 |  | 0
| B. |  | 2021-10-04 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14830 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 1830 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 281.0884 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8660 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.9295 | MKWHr. | ii) HVDC Flow at Peak Time |  | 701 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6957 | MKWHr. | iii) Maximum HVDC Flow : |  | 701 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.38 |  | (b) Today: | 106.35 |  | (c) Rule Curve: |  | 106.27
.

## YesterdayGen
2021-10-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 321 |  | 0 | 250 | 275 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 98 | 37 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 29 | 33 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 35 | 50 | 21 | 33 | 80 | 0 | 0 | 310 | 295 | 210 | 8 | 141 | 20 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 124 | 210 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 161 | 52 | 81 | 0 | 145 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 283 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 200 | 125 | 316 | 97 | 52 | 105 | 0 | 305 | 54 | 110 | 114 | 58 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 701 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 15 | 0 | 0 | 81 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 17 | 0 | 162 | 0 | 364 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 590 | 224 | 0 | 0 | 0 |  | 8700 | 3473 | 12173 | 4472 | 701 | 2227 | 0 | 3487 | 669 | 158 | 120 | 215 | 124 | 0 | 0 | 106.38
2:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 327 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 92 | 0 | 50 | 21 | 33 | 80 | 0 | 0 | 305 | 295 | 211 | 8 | 140 | 20 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 122 | 210 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 161 | 52 | 81 | 0 | 115 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 293 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 200 | 118 | 316 | 97 | 0 | 105 | 0 | 305 | 54 | 110 | 114 | 57 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 700 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 81 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 17 | 0 | 160 | 0 | 340 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 580 | 225 | 0 | 0 | 0 |  | 8498 | 3375 | 11873 | 4424 | 700 | 2235 | 0 | 3315 | 660 | 161 | 120 | 136 | 122 | 0 | 0 | 106.38
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 327 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 186 | 0 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 23 | 0 | 50 | 21 | 35 | 80 | 0 | 0 | 310 | 295 | 210 | 8 | 137 | 20 | 56 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 120 | 209 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 161 | 52 | 81 | 0 | 115 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 286 | 0 | 0 | 191 | 0 | 85 | 0 | 100 | 200 | 120 | 316 | 97 | 0 | 105 | 0 | 305 | 54 | 110 | 17 | 51 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 700 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 81 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 17 | 0 | 163 | 0 | 349 | 105 | 0 | 113 | 0 | 100 | 0 | 0 | 95 | 560 | 225 | 0 | 0 | 0 |  | 8087 | 3355 | 11442 | 4440 | 700 | 2230 | 0 | 2995 | 640 | 161 | 120 | 36 | 120 | 0 | 0 | 106.38
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 327 |  | 0 | 250 | 285 | 0 | 0 | 30 | 0 | 0 | 190 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 30 | 80 | 0 | 0 | 310 | 300 | 209 | 8 | 141 | 20 | 56 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 116 | 207 | 0 | 22 | 0 | 43 | 20 | 47 | 0 | 163 | 161 | 52 | 81 | 0 | 140 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 190 | 0 | 75 | 0 | 100 | 200 | 117 | 316 | 97 | 0 | 105 | 0 | 305 | 54 | 110 | 0 | 52 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 700 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 17 | 0 | 168 | 0 | 393 | 53 | 0 | 113 | 0 | 49 | 0 | 0 | 95 | 540 | 225 | 0 | 0 | 0 |  | 7868 | 3286 | 11154 | 4487 | 700 | 2287 | 0 | 2645 | 620 | 159 | 120 | 20 | 116 | 0 | 0 | 106.38
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 326 |  | 0 | 250 | 290 | 0 | 0 | 30 | 0 | 0 | 190 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 38 | 80 | 0 | 0 | 335 | 320 | 209 | 45 | 141 | 20 | 56 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 112 | 207 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 163 | 163 | 51 | 81 | 0 | 142 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 95 | 0 | 0 | 160 | 0 | 70 | 0 | 100 | 200 | 118 | 316 | 97 | 0 | 51 | 0 | 305 | 54 | 51 | 0 | 57 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 701 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 17 | 0 | 166 | 0 | 416 | 17 | 0 | 113 | 0 | 49 | 0 | 0 | 50 | 520 | 225 | 0 | 0 | 0 |  | 7706 | 3203 | 10909 | 4530 | 701 | 2351 | 0 | 2316 | 600 | 159 | 120 | 20 | 112 | 0 | 0 | 106.38
6:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 382 | 301 |  | 0 | 250 | 260 | 0 | 0 | 30 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 40 | 80 | 0 | 0 | 305 | 295 | 211 | 45 | 138 | 20 | 56 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 106 | 208 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 130 | 163 | 52 | 81 | 0 | 141 | 18 | 0 | 9 | 290 | 16 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 70 | 1 | 100 | 136 | 120 | 316 | 97 | 0 | 51 | 0 | 305 | 54 | 51 | 0 | 57 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 701 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 17 | 0 | 165 | 0 | 388 | 17 | 0 | 50 | 0 | 35 | 0 | 0 | 35 | 490 | 218 | 0 | 0 | 0 |  | 7339 | 2978 | 10317 | 4329 | 701 | 2221 | 0 | 2105 | 570 | 160 | 120 | 4 | 106 | 1 | 0 | 106.38
7:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 312 | 302 |  | 0 | 250 | 275 | 0 | 0 | 30 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 37 | 80 | 0 | 0 | 260 | 270 | 178 | 45 | 141 | 20 | 56 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 98 | 208 | 0 | 22 | 0 | 43 | 20 | 45 | 0 | 130 | 162 | 52 | 81 | 0 | 141 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 70 | 6 | 100 | 100 | 115 | 316 | 97 | 0 | 51 | 1 | 305 | 54 | 51 | 0 | 57 | 100 | 320 | 104 | 2 | 162 | 53 | 0 | 17 | 4 |  | 701 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 17 | 0 | 161 | 0 | 322 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 440 | 180 | 0 | 0 | 0 |  | 7065 | 2761 | 9826 | 4105 | 701 | 2115 | 0 | 1993 | 517 | 160 | 120 | 4 | 98 | 13 | 0 | 106.38
8:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 306 | 303 |  | 0 | 250 | 265 | 0 | 0 | 30 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 2 | 0 | 85 | 35 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 7 | 80 | 0 | 0 | 260 | 270 | 179 | 45 | 139 | 20 | 54 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 90 | 208 | 0 | 22 | 0 | 43 | 20 | 39 | 0 | 130 | 161 | 52 | 78 | 0 | 0 | 18 | 0 | 9 | 275 | 16 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 117 | 0 | 90 | 100 | 103 | 317 | 98 | 0 | 51 | 2 | 304 | 54 | 51 | 0 | 57 | 100 | 320 | 104 | 12 | 162 | 53 | 0 | 17 | 8 |  | 701 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 17 | 0 | 167 | 0 | 321 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 440 | 181 | 0 | 0 | 1 |  | 6850 | 2771 | 9621 | 3962 | 701 | 2059 | 0 | 2020 | 522 | 120 | 120 | 4 | 90 | 23 | 0 | 106.38
9:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 306 | 300 |  | 0 | 250 | 283 | 0 | 0 | 30 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 88 | 35 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 2 | 80 | 0 | 0 | 310 | 270 | 183 | 45 | 140 | 20 | 55 | 0 | 43 | 0 | 0 | 8 | 19 | 0 | 33 | 18 | 90 | 205 | 0 | 22 | 1 | 43 | 20 | 39 | 0 | 130 | 162 | 51 | 78 | 0 | 120 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 143 | 18 | 90 | 100 | 112 | 316 | 98 | 1 | 51 | 4 | 304 | 54 | 51 | 0 | 57 | 96 | 320 | 104 | 26 | 162 | 53 | 0 | 17 | 13 |  | 701 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 17 | 0 | 177 | 0 | 357 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 420 | 180 | 0 | 0 | 1 |  | 7106 | 2798 | 9904 | 4131 | 701 | 2109 | 0 | 2058 | 505 | 123 | 120 | 4 | 90 | 63 | 0 | 106.38
10:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 306 | 300 |  | 0 | 250 | 285 | 0 | 0 | 30 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 11 | 0 | 88 | 35 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 18 | 2 | 80 | 0 | 0 | 320 | 350 | 180 | 63 | 140 | 23 | 54 | 0 | 35 | 0 | 0 | 8 | 19 | 2 | 33 | 19 | 92 | 191 | 0 | 22 | 2 | 43 | 20 | 39 | 0 | 130 | 162 | 50 | 75 | 0 | 145 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 142 | 4 | 90 | 104 | 112 | 317 | 98 | 52 | 51 | 5 | 305 | 54 | 51 | 17 | 57 | 96 | 320 | 104 | 30 | 162 | 53 | 0 | 17 | 31 |  | 700 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 17 | 0 | 180 | 0 | 362 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 390 | 181 | 0 | 0 | 2 |  | 7332 | 2776 | 10108 | 4240 | 700 | 2142 | 0 | 2143 | 470 | 123 | 120 | 4 | 92 | 74 | 0 | 106.38
11:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 320 | 317 |  | 0 | 250 | 290 | 0 | 0 | 30 | 0 | 0 | 128 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 25 | 16 | 0 | 86 | 35 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 18 | 2 | 80 | 0 | 0 | 335 | 330 | 205 | 63 | 141 | 23 | 50 | 0 | 35 | 0 | 0 | 24 | 19 | 2 | 25 | 19 | 100 | 189 | 0 | 22 | 1 | 43 | 20 | 45 | 0 | 130 | 160 | 50 | 78 | 0 | 145 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 120 | 0 | 138 | 5 | 90 | 149 | 115 | 242 | 96 | 52 | 51 | 6 | 305 | 54 | 51 | 17 | 57 | 96 | 365 | 104 | 8 | 162 | 53 | 0 | 17 | 7 |  | 700 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 7 | 0 | 0 | 85 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 17 | 0 | 202 | 0 | 361 | 17 | 0 | 38 | 0 | 34 | 0 | 0 | 35 | 390 | 181 | 0 | 0 | 4 |  | 7385 | 2864 | 10249 | 4307 | 700 | 2168 | 0 | 2225 | 470 | 121 | 120 | 7 | 100 | 31 | 0 | 106.38
12:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 381 | 326 |  | 0 | 250 | 270 | 0 | 0 | 30 | 0 | 0 | 128 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 16 | 0 | 86 | 35 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19 | 18 | 3 | 80 | 0 | 0 | 325 | 320 | 203 | 63 | 140 | 23 | 49 | 0 | 35 | 0 | 0 | 24 | 19 | 2 | 33 | 20 | 102 | 163 | 0 | 22 | 2 | 43 | 20 | 45 | 0 | 130 | 158 | 51 | 78 | 0 | 145 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 120 | 0 | 141 | 0 | 90 | 157 | 108 | 315 | 96 | 52 | 72 | 2 | 306 | 54 | 51 | 17 | 51 | 96 | 320 | 104 | 11 | 162 | 72 | 0 | 17 | 35 |  | 701 | 0 | 365 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 85 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 17 | 0 | 196 | 0 | 361 | 17 | 0 | 70 | 0 | 34 | 0 | 1 | 50 | 390 | 181 | 0 | 0 | 3 |  | 7514 | 2916 | 10430 | 4367 | 701 | 2169 | 0 | 2321 | 471 | 121 | 120 | 4 | 102 | 54 | 0 | 106.37
13:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 404 | 342 |  | 0 | 250 | 275 | 0 | 0 | 30 | 0 | 0 | 180 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 16 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19 | 18 | 2 | 80 | 0 | 0 | 310 | 305 | 205 | 63 | 138 | 23 | 47 | 0 | 43 | 0 | 0 | 24 | 19 | 2 | 33 | 20 | 104 | 156 | 0 | 22 | 1 | 43 | 20 | 44 | 0 | 163 | 160 | 51 | 78 | 0 | 145 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 130 | 0 | 0 | 100 | 0 | 148 | 0 | 90 | 180 | 103 | 315 | 96 | 52 | 105 | 0 | 305 | 54 | 51 | 17 | 57 | 96 | 320 | 104 | 3 | 162 | 108 | 0 | 17 | 26 |  | 701 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 85 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 18 | 0 | 198 | 0 | 336 | 17 | 0 | 70 | 0 | 34 | 0 | 2 | 70 | 390 | 111 | 0 | 0 | 2 |  | 7716 | 2846 | 10562 | 4390 | 701 | 2115 | 0 | 2463 | 471 | 160 | 120 | 4 | 104 | 34 | 0 | 106.37
14:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 399 | 343 |  | 0 | 250 | 285 | 0 | 0 | 55 | 0 | 0 | 148 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 14 | 25 | 25 | 33 | 25 | 16 | 0 | 82 | 75 | 115 | 0 | 2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19 | 18 | 4 | 80 | 0 | 0 | 310 | 305 | 200 | 36 | 140 | 23 | 50 | 0 | 43 | 0 | 0 | 24 | 19 | 2 | 33 | 20 | 112 | 144 | 0 | 22 | 0 | 43 | 20 | 44 | 0 | 163 | 158 | 51 | 81 | 0 | 145 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 190 | 0 | 0 | 40 | 0 | 149 | 0 | 90 | 200 | 103 | 316 | 65 | 52 | 105 | 1 | 305 | 54 | 51 | 17 | 57 | 96 | 320 | 104 | 10 | 162 | 108 | 0 | 17 | 14 |  | 700 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 13 | 0 | 178 | 0 | 332 | 17 | 0 | 70 | 0 | 34 | 0 | 2 | 70 | 390 | 112 | 0 | 0 | 0 |  | 7695 | 2792 | 10487 | 4301 | 700 | 2089 | 0 | 2506 | 471 | 157 | 120 | 4 | 112 | 27 | 0 | 106.37
15:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 341 | 344 |  | 0 | 250 | 285 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 25 | 0 | 25 | 16 | 0 | 82 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19 | 18 | 2 | 80 | 0 | 0 | 325 | 320 | 193 | 8 | 139 | 23 | 51 | 0 | 35 | 0 | 0 | 24 | 19 | 2 | 33 | 21 | 112 | 145 | 0 | 22 | 0 | 43 | 20 | 42 | 0 | 163 | 158 | 51 | 81 | 0 | 145 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 190 | 0 | 0 | 35 | 0 | 99 | 8 | 90 | 200 | 103 | 316 | 35 | 52 | 105 | 0 | 305 | 54 | 51 | 17 | 57 | 100 | 320 | 104 | 3 | 162 | 108 | 0 | 17 | 11 |  | 700 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 18 | 0 | 190 | 0 | 404 | 17 | 0 | 80 | 0 | 34 | 0 | 2 | 90 | 390 | 123 | 0 | 0 | 0 |  | 7554 | 2956 | 10510 | 4290 | 700 | 2160 | 0 | 2475 | 468 | 157 | 120 | 4 | 112 | 24 | 0 | 106.37
16:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 340 | 260 |  | 0 | 250 | 278 | 0 | 0 | 55 | 0 | 0 | 129 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 20 | 25 | 25 | 33 | 33 | 22 | 0 | 82 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19 | 18 | 2 | 80 | 0 | 0 | 320 | 320 | 197 | 8 | 137 | 23 | 51 | 0 | 43 | 0 | 0 | 24 | 19 | 2 | 33 | 21 | 100 | 163 | 0 | 0 | 0 | 43 | 30 | 44 | 0 | 110 | 160 | 51 | 81 | 0 | 145 | 18 | 0 | 9 | 265 | 16 | 11 | 0 | 190 | 0 | 0 | 35 | 0 | 59 | 9 | 60 | 200 | 107 | 316 | 35 | 55 | 68 | 2 | 255 | 54 | 17 | 17 | 57 | 70 | 320 | 104 | 0 | 162 | 90 | 0 | 17 | 9 |  | 700 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 88 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 17 | 0 | 188 | 0 | 399 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 390 | 170 | 0 | 0 | 0 |  | 7107 | 2893 | 10000 | 4313 | 700 | 2028 | 0 | 2087 | 469 | 157 | 120 | 4 | 100 | 22 | 0 | 106.37
17:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 340 | 270 |  | 0 | 250 | 275 | 0 | 0 | 55 | 0 | 0 | 128 | 0 | 40 | 5 | 8 | 0 | 0 | 0 | 54 | 17 | 17 | 21 | 25 | 26 | 0 | 33 | 34 | 0 | 85 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 19 | 18 | 5 | 80 | 0 | 0 | 310 | 305 | 198 | 8 | 135 | 23 | 56 | 0 | 43 | 0 | 0 | 24 | 19 | 2 | 33 | 20 | 94 | 160 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 110 | 162 | 57 | 81 | 0 | 145 | 18 | 0 | 9 | 290 | 16 | 2 | 0 | 190 | 0 | 0 | 35 | 0 | 62 | 2 | 60 | 200 | 112 | 316 | 35 | 70 | 68 | 0 | 232 | 54 | 17 | 17 | 57 | 70 | 320 | 60 | 0 | 126 | 72 | 0 | 17 | 1 |  | 701 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 17 | 0 | 188 | 0 | 353 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 390 | 200 | 0 | 0 | 0 |  | 6985 | 2860 | 9845 | 4252 | 701 | 2058 | 0 | 1961 | 470 | 160 | 120 | 26 | 94 | 3 | 0 | 106.37
18:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 340 | 330 |  | 0 | 250 | 297 | 0 | 0 | 55 | 0 | 0 | 128 | 0 | 48 | 112 | 34 | 0 | 0 | 0 | 54 | 35 | 45 | 0 | 25 | 16 | 0 | 33 | 34 | 0 | 85 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 2 | 0 | 102 | 50 | 18 | 21 | 18 | 9 | 80 | 0 | 0 | 260 | 270 | 209 | 8 | 139 | 23 | 53 | 0 | 43 | 0 | 42 | 26 | 19 | 2 | 33 | 20 | 128 | 160 | 0 | 0 | 0 | 43 | 30 | 47 | 0 | 110 | 160 | 52 | 70 | 0 | 145 | 18 | 0 | 9 | 270 | 16 | 5 | 0 | 193 | 0 | 0 | 48 | 0 | 143 | 0 | 75 | 200 | 113 | 316 | 46 | 77 | 73 | 0 | 273 | 54 | 29 | 44 | 90 | 70 | 320 | 66 | 0 | 126 | 77 | 0 | 17 | 0 |  | 700 | 0 | 350 | 0 | 0 | 140 | 0 | 0 | 27 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 50 | 5 | 93 | 27 | 43 | 24 | 7 | 18 | 22 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 17 | 0 | 152 | 0 | 391 | 30 | 0 | 35 | 0 | 70 | 0 | 0 | 70 | 380 | 223 | 0 | 3 | 0 |  | 7579 | 3240 | 10819 | 4050 | 700 | 2178 | 0 | 2529 | 461 | 160 | 140 | 473 | 128 | 0 | 0 | 106.37
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 339 | 305 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 128 | 0 | 40 | 100 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 26 | 0 | 33 | 11 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 40 | 49 | 44 | 18 | 10 | 80 | 0 | 0 | 260 | 270 | 211 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 42 | 48 | 19 | 11 | 33 | 20 | 136 | 161 | 0 | 0 | 0 | 43 | 30 | 47 | 0 | 110 | 160 | 57 | 81 | 0 | 145 | 18 | 0 | 9 | 260 | 16 | 2 | 0 | 267 | 0 | 0 | 110 | 0 | 149 | 0 | 90 | 200 | 120 | 316 | 115 | 72 | 105 | 0 | 305 | 54 | 108 | 114 | 95 | 100 | 320 | 104 | 0 | 158 | 116 | 0 | 17 | 0 |  | 700 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 32 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 17 | 0 | 168 | 0 | 350 | 75 | 0 | 100 | 0 | 107 | 0 | 0 | 95 | 440 | 224 | 0 | 35 | 0 |  | 8290 | 3245 | 11535 | 4072 | 700 | 2113 | 0 | 3368 | 521 | 160 | 120 | 345 | 136 | 0 | 0 | 106.37
19:30 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 340 | 333 |  | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 160 | 0 | 40 | 82 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 0 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 40 | 0 | 50 | 18 | 14 | 80 | 0 | 0 | 310 | 335 | 0 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 138 | 162 | 0 | 0 | 0 | 43 | 30 | 47 | 0 | 110 | 162 | 57 | 81 | 0 | 145 | 18 | 0 | 9 | 325 | 16 | 2 | 0 | 278 | 0 | 0 | 110 | 0 | 149 | 0 | 90 | 200 | 122 | 315 | 115 | 35 | 105 | 0 | 305 | 54 | 110 | 114 | 95 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 0 |  | 700 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 17 | 0 | 181 | 0 | 380 | 75 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 460 | 224 | 0 | 35 | 0 |  | 8160 | 3318 | 11478 | 4089 | 700 | 2251 | 0 | 3272 | 542 | 160 | 120 | 206 | 138 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 340 | 333 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 40 | 82 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 0 | 33 | 0 | 0 | 87 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 40 | 0 | 50 | 18 | 20 | 80 | 0 | 0 | 285 | 305 | 0 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 138 | 173 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 161 | 57 | 81 | 0 | 145 | 18 | 0 | 9 | 300 | 16 | 2 | 0 | 282 | 0 | 0 | 110 | 0 | 149 | 0 | 90 | 200 | 123 | 316 | 115 | 34 | 105 | 0 | 305 | 54 | 110 | 114 | 95 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 0 |  | 701 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 17 | 0 | 189 | 0 | 402 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 460 | 224 | 0 | 35 | 0 |  | 8192 | 3351 | 11543 | 4117 | 701 | 2287 | 0 | 3270 | 542 | 162 | 120 | 206 | 138 | 0 | 0 | 106.37
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 340 | 326 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 40 | 90 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 28 | 33 | 0 | 0 | 87 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 40 | 0 | 50 | 18 | 20 | 100 | 0 | 0 | 285 | 305 | 0 | 36 | 138 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 136 | 172 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 163 | 57 | 81 | 0 | 145 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 282 | 0 | 0 | 100 | 0 | 149 | 0 | 90 | 200 | 60 | 316 | 109 | 34 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 0 |  | 701 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 17 | 0 | 183 | 0 | 423 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 224 | 0 | 17 | 0 |  | 8215 | 3354 | 11569 | 4165 | 701 | 2346 | 0 | 3193 | 532 | 162 | 120 | 214 | 136 | 0 | 0 | 106.37
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 340 | 325 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 40 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 28 | 33 | 0 | 0 | 87 | 75 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 10 | 0 | 50 | 18 | 35 | 120 | 0 | 0 | 330 | 345 | 0 | 63 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 134 | 181 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 162 | 57 | 81 | 0 | 145 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 281 | 0 | 0 | 100 | 0 | 144 | 0 | 90 | 200 | 10 | 316 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 76 | 94 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 0 |  | 701 | 0 | 335 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 17 | 0 | 186 | 0 | 404 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 224 | 0 | 0 | 0 |  | 8186 | 3242 | 11428 | 4260 | 701 | 2356 | 0 | 2980 | 532 | 162 | 120 | 183 | 134 | 0 | 0 | 106.37
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 340 | 327 |  | 0 | 250 | 315 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 24 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 28 | 33 | 0 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 24 | 18 | 38 | 135 | 0 | 0 | 315 | 305 | 0 | 63 | 142 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 132 | 173 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 160 | 63 | 81 | 0 | 145 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 230 | 0 | 0 | 70 | 0 | 85 | 0 | 90 | 200 | 10 | 322 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 50 | 97 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 0 |  | 700 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 17 | 0 | 182 | 0 | 409 | 17 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 490 | 224 | 0 | 0 | 0 |  | 7951 | 3153 | 11104 | 4213 | 700 | 2389 | 0 | 2633 | 572 | 162 | 120 | 183 | 132 | 0 | 0 | 106.37
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 340 | 327 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 7 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 12 | 21 | 25 | 29 | 28 | 33 | 0 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 12 | 18 | 37 | 135 | 0 | 0 | 310 | 305 | 0 | 63 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 120 | 189 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 162 | 63 | 81 | 0 | 145 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 195 | 0 | 0 | 40 | 0 | 72 | 0 | 90 | 200 | 10 | 322 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 70 | 63 | 100 | 320 | 96 | 0 | 162 | 116 | 0 | 17 | 0 |  | 700 | 0 | 315 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 17 | 0 | 178 | 0 | 406 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 113 | 520 | 224 | 0 | 0 | 0 |  | 7739 | 3107 | 10846 | 4203 | 700 | 2364 | 0 | 2410 | 602 | 161 | 120 | 166 | 120 | 0 | 0 | 106.37
KWH | 0 | 0 | 0 | 0 | 7218164 | 0 | 0 | 8657176 | 7588000 |  | 0 | 6157000 | 6769193 | 0 | 0 | 1110451 | 0 | 0 | 4033000 | 0 | 872064 | 942720 | 279965 | 0 | 0 | 0 | 1302840 | 1247139 | 1228092 | 401652 | 600000 | 628200 | 644600 | 797700 | 206880 | 0 | 1983535 | 1532000 | 2700000 | 0 | 90747 | 0 | 0 | 0 | 0 |  | 58080 | 0 | 766674 | 583440 | 109440 | 716160 | 454320 | 390240 | 2125490 | 0 | 0 | 7628500 | 7342000 | 3902000 | 819636 | 3338400 | 485280 | 1295040 | 0 | 982942 | 0 | 65792 | 795854 | 450432 | 156780 | 791200 | 508770 | 2695680 | 4284960 | 0 | 431064 | 7400 | 1021000 | 554400 | 1083000 | 0 | 3633790 | 3688000 | 1268160 | 1911360 | 0 | 3169700 | 401000 | 0 | 207360 | 7166000 | 379536 | 206 | 0 | 4636798 | 0 | 0 | 2757600 | 0 | 2789280 | 59265 | 2116800 | 4332960 | 2473952 | 7549000 | 2198400 | 818400 | 2116836 | 26041 | 7186036 | 1300215 | 1864246 | 995220 | 1599360 | 2304000 | 7766100 | 2477760 | 94080 | 3857760 | 2299582 | 0 | 442440 | 163375 |  | 16929454 | 0 | 8986752 | 0 | 0 | 3016320 | 0 | 0 | 132750 | 0 | 0 | 2040180 | 649734 | 0 | 0 | 0 | 0 | 75000 | 8067 | 290256 | 34450 | 40820 | 44063 | 90240 | 68331 | 492480 | 0 | 218034 | 1896872 | 0 | 0 | 0 | 0 | 0 | 0 | 4358964 | 0 | 416969 | 0 | 4524882 | 0 | 8989236 | 1109280 | 0 | 2003904 | 0 | 1409884 | 0 | 13215 | 1788768 | 11877200 | 4669418 | 0 | 129600 | 16020 |  | 186885710 | 76321143 | 263206853 | 103505602 | 16929454 | 53221398 | 0 | 63775743 | 13774072 | 3515535 | 3016320 | 2393653 | 2695680 | 379396 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8012162.04 | 0 | 0 | 8743747.76 | 7815640 |  | 0 | 6711130 | 7513804.23 | 0 | 0 | 9394415.46 | 0 | 0 | 6977090 | 0 | 7953223.68 | 9276364.8 | 2581277.3 | 0 | 0 | 0 | 9510732 | 9640384.47 | 12108987.12 | 301239 | 450000 | 0 | 0 | 0 | 2000529.6 | 0 | 535554.45 | 413640 | 4887000 | 0 | 843039.63 | 0 | 0 | 0 | 0 |  | 0 | 0 | 7436737.8 | 5571852 | 952128 | 5671987.2 | 572443.2 | 1159012.8 | 3145725.2 | 0 | 0 | 5645090 | 7342000 | 3589840 | 1057330.44 | 3839160 | 548366.4 | 1813056 | 0 | 1680830.82 | 0 | 664499.2 | 7600405.7 | 572048.64 | 117585 | 1384600 | 381577.5 | 20217600 | 4542057.6 | 0 | 547451.28 | 117956 | 1674440 | 887040 | 1927740 | 0 | 4142520.6 | 3835520 | 2498275.2 | 3650697.6 | 0 | 5483581 | 878190 | 0 | 423014.4 | 7237660 | 284652 | 156.56 | 0 | 35054192.88 | 0 | 0 | 14339520 | 0 | 27446515.2 | 692807.85 | 17251920 | 47012616 | 17441361.6 | 7020570 | 20049408 | 7733880 | 18437641.56 | 0 | 54326432.16 | 11324872.65 | 16386722.34 | 9932295.6 | 13706515.2 | 15344640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97513655.04 | 0 | 9436089.6 | 0 | 0 | 41806195.2 | 0 | 0 | 1392547.5 | 0 | 0 | 2305403.4 | 1007087.7 | 0 | 0 | 0 | 0 | 738000 | 81960.72 | 2568765.6 | 265265 | 551886.4 | 426970.47 | 874425.6 | 662810.7 | 945561.6 | 0 | 165051.738 | 11438138.16 | 0 | 0 | 0 | 0 | 0 | 0 | 5753832.48 | 0 | 625453.5 | 0 | 5294111.94 | 0 | 8899343.64 | 11580883.2 | 0 | 19017048.96 | 0 | 10940699.84 | 0 | 146025.75 | 13218995.52 | 52140908 | 0 | 0 | 0 | 0 |  | 568266700.72 | 299797117.258 | 868063817.978 | 107116097.538 | 97513655.04 | 56609883.33 | 0 | 456066699.87 | 63579046.16 | 949194.45 | 41806195.2 | 23248656.79 | 20217600 | 956789.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 381 | 326 |  | 0 | 250 | 270 | 0 | 0 | 30 | 0 | 0 | 128 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 16 | 0 | 86 | 35 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19 | 18 | 3 | 80 | 0 | 0 | 325 | 320 | 203 | 63 | 140 | 23 | 49 | 0 | 35 | 0 | 0 | 24 | 19 | 2 | 33 | 20 | 102 | 163 | 0 | 22 | 2 | 43 | 20 | 45 | 0 | 130 | 158 | 51 | 78 | 0 | 145 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 120 | 0 | 141 | 0 | 90 | 157 | 108 | 315 | 96 | 52 | 72 | 2 | 306 | 54 | 51 | 17 | 51 | 96 | 320 | 104 | 11 | 162 | 72 | 0 | 17 | 35 |  | 701 | 0 | 365 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 85 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 17 | 0 | 196 | 0 | 361 | 17 | 0 | 70 | 0 | 34 | 0 | 1 | 50 | 390 | 181 | 0 | 0 | 3 |  | 10430 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 340 | 326 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 40 | 90 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 28 | 33 | 0 | 0 | 87 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 0 | 50 | 18 | 20 | 100 | 0 | 0 | 285 | 305 | 0 | 36 | 138 | 23 | 56 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 136 | 172 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 163 | 57 | 81 | 0 | 145 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 282 | 0 | 0 | 100 | 0 | 149 | 0 | 90 | 200 | 60 | 316 | 109 | 34 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 0 |  | 701 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 17 | 0 | 183 | 0 | 423 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 224 | 0 | 17 | 0 |  | 11569 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 350 | 320 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 21 | 15 | 100 | 0 | 0 | 330 | 330 | 140 | 45 | 140 | 23 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 170 | 0 | 22 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 60 | 81 | 0 | 200 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 282 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 96 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 713 | 0 | 410 | 0 | 0 | 225 | 0 | 0 | 25 | 40 | 0 | 88 | 32 | 110 | 0 | 0 | 0 | 50 | 35 | 94 | 28 | 50 | 40 | 52 | 33 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 17 | 100 | 220 | 0 | 400 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 330 | 320 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 102 | 149 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 34 | 100 | 90 | 25 | 21 | 5 | 100 | 0 | 0 | 300 | 300 | 0 | 45 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 170 | 0 | 22 | 1.6 | 43 | 30 | 50 | 0 | 163 | 160 | 60 | 81 | 0 | 145 | 18 | 0 | 10 | 341 | 16 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 100 | 95 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 713 | 0 | 350 | 0 | 0 | 225 | 0 | 0 | 5 | 0 | 0 | 84 | 30 | 110 | 0 | 0 | 0 | 50 | 34 | 90 | 28 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 17 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 339 | 292 | 0 | 0 | 250 | 265 | 0 | 0 | 30 | 0 | 0 | 130 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 21 | 25 | 26 | 28 |  | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 365 | 305 | 0 | 160 | 139 | 20 | 52 | 0 | 43 | 0 | 0 | 25 | 19 | 5 | 33 | 18 | 100 | 193 | 0 | 22 | 1 | 43 | 30 | 47 | 0 | 110 | 160 | 61 | 78 | 0 | 110 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 2 | 0 | 0 | 8 | 0 | 50 | 12 | 70 | 155 | 0 | 323 | 60 | 18 | 17 | 2 | 233 | 35 | 17 | 0 | 48 | 70 | 320 | 0 | 15 | 0 | 17 | 0 | 17 | 10 | 0 | 707 | 0 | 295 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 17 | 0 | 176 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 172 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9621 | 8:00
| Highest Generation |  | 12173 | 1:00
| Day Peak Generation |  | 10430 | 12:00
| Evening Peak Generation |  | 11569 | 21:00
| HVDC Max Flow |  | 701 | 1:00
| HVDC EvPeak Flow |  | 701 | 21:00
| Load factor L.F |  | 90.09%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-04
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10430 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8660 | MW
Evening Peak Generation : |  | 11569 | MW Hour : | 21:00 | Available Max Generation : |  | 14830 | MW
E.P. Demand (at gen end) : |  | 11569 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12173 | MW Hour : | 1:00 | Reserve(Generation end) |  | 1830 | MW
Total Gen. (MKWH) : |  | 263.2069 | System Load Factor : | 90.09% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -452 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-04
Actual : | 106.35 | Ft.(MSL) , | Rule curve : | 106.27 | Ft.( MSL )
Gas Consumed : | Total = | 1192.07 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163725980.868
: |  | Coal : | 63579046.16 | Oil : | 521121551.86 | Total : | 748426578.888
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4647.0015 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1585.3059 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1421.2846 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1284.5712 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1160.6716 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 936.6337 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 517.1975 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 240.9854 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 722.4096 |  |  | 0 | 0%
Total | 0 |  | 12516.0609 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Fenchuganj 3,4
7) Raozan #02
8) Shajibazar 330 Mw GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar 230/132 kV T-01 transformer was under shut down from 10:02 to 17:20 for C/M.
b) Aminbazar-Bosila 132 kV Ckt tripped at 10:44 showing dist.Z1 and was switched on at 11:18.
c) Bogura 230/132 kV T-1 transformer was under shut down from 08:16 to 17:21 for A/M.
d) Chatak-Sunamganj 132 kV Ckt tripped at 10:07 showing dist.Z2,B-phase at Chatak end & main |  |  |  |  | About 19 MW power interruption occurred under Sunamganj S/S area
protection trip at Sunamganj end and was switched on at 10:18. |  |  |  |  | from 10:07 to 10:18.
e) Ghorasal-Narshingdi 132 kV Ckt-1 & 2 were shut down at 11:36 for ROW and were switched on at 17:11.
f) Lalmonirhat 132/33 kV T-2 transformer was under shut down from 08:25 to 14:30 for A/M.
g) Mirpur-Uttara 3rd phase 132 kV Ckt was under shut down from 08:52 to 17:58 for A/M.
h) Natore-Bogura 132 kV Ckt-1 was under shut down from 09:56 to 12:34 for oil leakage maintenance
at 132 kV CT at Natore end.
i) Rangamati-Khagrachari 132 kV Ckt-1 was under shut down from 08:57 to 15:37 for A/M.
j) Bogura(O)-Bogura(N) 132 kV Ckt-1 was under shut down from 11:27 to 15:18 for C/M.
k) Sylhet-Chatak 132 kV Ckt-1 tripped at 10:34 showing no signal and was switched on at 12:39. |  |  |  |  | About 10 MW power interruption occurred under Chatak S/S area
from 10:34 to 12:39.
l) Tongi-Kodda-300 MW 230 kV Ckt was under shut down from 09:08 to 16:17 for A/M.
m) Tongi-Bashundhara 132 kV Ckt-1 was under shut down at 08:34 for D/W.
n) GPH Ispat 230/132 kV t-1 transformer was shut down at 12:44 for oil leakage maintenance.
o) RPCL-Tangail 132 kV Ckt-2 tripped at 12:32 showing dist.Z1,R-phase and was switched on at 13:05.
p) Siddirganj 132/33 kV T-1 & T-2 transformers tripped at 12:02 showing O/C relay,R-phase and were |  |  |  |  | About 60 MW power interruption occurred under Siddirganj S/S area
switched on at 12:24. |  |  |  |  | from 12:02 to 12:24.
q) Barishal-Bhola 230 kV Ckt-2 tripped at 13:55 showing dist.Z1 and was switched on at 14:26.
r) Jhenaidah 230/132 kV T-1 transformer tripped at 14:12 showing differential relay and was switched on at 15:25.
s) Natore-Bogura 132 kV Ckt-1 tripped at 15:33 showing dist.Z1,B-phase and was switched on at 15:43.
t) Mymensing-Jamalpur 132 kV Ckt-2 tripped at 14:36 showing dist.Z1,A-phase at Mymensing end &
E/F relay at Jamalpur end and was switched on at 14:48.
u) Haripur S/S-Haripur-360 MW 230 kv Ckt-1 tripped at 15:02 showing dist.relay and was switched on at 16:51.
v) Agargaon-Aminbazar 132 kV Ckt-2 was under shut down from 14:53 to 16:22 for C/M.
w) Barisal-Patuakhali 132 kV Ckt tripped at 17:33 showing dist.Z1 at Patuakhali end and was switched |  |  |  |  | About 45 MW power interruption occurred under Patuakhali S/S area
on at 17:39. |  |  |  |  | from 17:33 to 17:39.
x) Bogura(O)-Bogura(N) 132 kV Ckt-2 was under shut down from 15:23 to 18:37 for C/M.
y) Nutun bidyut-220 MW CCPP ST was synchronized at 15:26.
z) Ashuganj-225 MW CCPP ST & GT tripped at 19:15 & 19:24 respectively due to problem with damper.
aa) Noapara 33 kV full Bus is shut down since 07:28(4/10/21) due to 33 kV C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7218164 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8657176
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 326 | 7588000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6157000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 305 | 6769193 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1110451
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 51 | 279965 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 401652
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 4033000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 872064 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1302840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 90 | 942720 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1247139
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1228092
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1228200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 644600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 797700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 206880 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 282 | 4636798 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2789280
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 34 | 818400 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2477760
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3857760
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 163375
| Dhaka area Total |  |  |  | 5719 | 2983 | 65428209
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 90747 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 59265
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 716160
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 162 | 3515535 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2116836
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 766674 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 583440 | Low demand
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2116800 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 454320
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 390240
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 109440 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26041
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 7186036
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1300215
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1864246
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2304000
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2299582
| Chattogram area Total |  |  |  | 2382 | 1378 | 28599577
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2125490 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 3902000 | Tripped
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7628500 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7342000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 485280 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1295040
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 819636 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 982942 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 60 | 2473952 | Low demand
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 65792 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3338400 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 4332960
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 450432
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 156780
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 2695680
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 791200
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 795854
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 508770
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 995220
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1599360 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 442440 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1742 | 43227728
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 172 | 4284960 | Engine problem
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 431064
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7400
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 2757600 | High voltage
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 109 | 2198400
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 94080
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 58080 | Reserve.
| Mymensingh Area Total |  |  |  | 709 | 403 | 9831584
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1021000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 554400 | Engine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3633790
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 163 | 3688000 | Machine problem
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1083000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 206
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1268160 | Machine problem
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1911360
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 3169700 | ST under maint
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 401000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 379536
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7166000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 7549000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 207360
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7766100 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1709 | 39798612
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 701 | 16929454
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 132750 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3016320 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8986752 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1109280 | Low demand
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1241 | 30174556
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 649734
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2040180 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 416969 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 450 | 11877200 | Low demand
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 4669418
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 129600 | Low demand
| Barisal Area Total |  |  |  | 2046 | 829 | 19783101
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 75000 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 8067 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 34450 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 40820 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 44063 | Reserve.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4358964 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 4524882 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 423 | 8989236 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 68331 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 492480
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 218034
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 90240 | Reserve.
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 39 | 290256 | Low demand
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2003904
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1788768
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 16020
| Rajshahi Area Total |  |  |  | 2179 | 1089 | 23043515
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 82 | 1896872
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1409884
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 13215
| Rangpur Area Total |  |  |  | 605 | 195 | 3319971
| Total |  |  |  | 21180 | 11569 | 263206853
| Eastern Grid Total |  |  |  | 14221 | 8215 | 186885710
| Western Grid Total |  |  |  | 6959 | 3354 | 76321143
| National Grid Total |  |  |  | 21180 | 11569 | 263206853
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-03
(a) ENTIRE EASTERN GRID : |  | 7747 | MW | (b) ENTIRE WESTERN GRID : |  | 3384 | MW
i) Dhaka area |  | 4196 | MW | i) Khulna area |  | 1343 | MW
ii) Chittagong area |  | 1166 | MW | ii) Rajshahi area |  | 1091 | MW
iii) Comilla area |  | 1219 | MW | iii) Barisal area |  | 365 | MW
iv) Mymensingh area |  | 753 | MW | iv) Rangpur area |  | 585 | MW
v) Sylhet area |  | 413 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11131 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 126 | 18:00 | Kishoreganj | 144 | 1:00 | Jessore | 98 | 1:00
Munsiganj | 96 | 1:00 | Netrokona | 114 | 2:00 | Benapol | 52 | 1:00
Sonargaon | 78 | 6:00 | Jamalpur | 150 | 2:00 | Jhenida(Old) | 100 | 1:00
Shyampur | 196 | 10:00 | Sherpur | 126 | 1:00 | Bottail | 126 | 18:30
Bhulta | 192 | 1:00 | Srimongal | 47 | 1:00 | G.K Project | 58 | 18:30
Madanganj | 53 | 10:00 | Shahjibazar | 111 | 1:00 | Faridpur | 142 | 1:00
Shitalakhya | 101 | 11:00 | Fenchuganj | 33 | 1:00 | Rajbari | 50 | 18:30
Rahim steel | 19 | 10:00 | Kulawara | 36 | 19:00 | Madaripur | 96 | 19:30
Matuail | 57 | 9:00 | Sylhet | 123 | 19:00 | Sariatpur | 64 | 1:00
Ghorasal | 75 | 1:00 | Chatak | 25 | 22:00 | Gopalganj | 94 | 18:30
Narsingdi | 183 | 1:00 | Sunamganj | 43 | 22:00 | Bagerhat | 94 | 18:30
Haripur (SBU) | 122 | 1:00 | Biani Bazar | 62 | 19:30 | Mongla | 46 | 10:00
Sreenagar | 40 | 1:00 | Comilla (S) | 138 | 19:30 | Satkhira | 110 | 21:00
Ullon | 65 | 18:00 | Comilla(N) | 151 | 18:30 | Gallamari | 33 | 13:00
Hasnabad | 83 | 1:00 | Chandpur | 76 | 1:00 | Magura | 48 | 1:00
Magbazar | 108 | 12:00 | Feni | 127 | 19:00 | Norail | 42 | 1:00
Maniknagar | 74 | 11:00 | Chowmuhani | 214 | 21:00 | Chuadanga | 96 | 20:00
Bangabhaban | 15 | 11:00 | Ashuganj | 44 | 1:00 | Barisal(N) | 42 | 19:00
Motijheel | 34 | 13:00 | Daudkandi | 146 | 21:00 | Barisal (S) | 108 | 20:00
Narinda | 68 | 13:00 | B.Baria | 161 | 21:00 | Patuakhali | 113 | 21:00
Kazla | 78 | 19:30 | Ramganj | 90 | 22:00 | Bhandaria | 50 | 19:00
Dhanmondi | 228 | 13:00 | Chaddagram | 45 | 18:30 | Borguna | 18 | 19:00
Lalbag | 78 | 13:00 | PHP | 8 | 1:00 | Borhan Uddin | 44 | 1:00
Madartek | 73 | 1:00 | Kochua | 56 | 18:00 | Ishurdi | 67 | 20:00
Dhaka University | 42 | 13:00 | Madunaghat | 61 | 14:00 | Ruppur Paromanobik | 4 | 17:00
Aftabnagar | 16 | 14:00 | Hathazari | 96 | 18:00 | Natore | 119 | 20:00
Fatullah | 61 | 10:00 | Khulshi | 207 | 11:00 | Bogra | 166 | 2:00
Nawabganj | 51 | 21:00 | Halishahar | 133 | 14:00 | Noagaon | 104 | 1:00
Keraniganj | 74 | 18:30 | Baraulia | 150 | 10:00 | Rajshahi | 146 | 1:00
Mirpur | 136 | 12:00 | Sikalbaha | 42 | 13:00 | Rajshahi New | 17 | 1:00
Kalyanpur | 96 | 18:30 | Dohazari | 114 | 19:30 | C.Nawabganj | 51 | 1:00
Gulshan | 128 | 12:00 | Cox'sbazar | 85 | 18:30 | Amnura | 43 | 1:00
Uttara | 90 | 18:00 | Chandraghona | 28 | 18:00 | Pabna | 95 | 20:00
Uttara New | 31 | 18:30 | Kaptai | 4.4 | 19:00 | Shahjadpur | 86 | 21:00
Kamrangirchar | 102 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 82 | 1:00
Savar | 181 | 12:00 | Bakulia | 95 | 9:00 | Niyamatpur | 67 | 1:00
Bhasantec | 142 | 18:00 | Julda | 18 | 1:00 | Joypurhat | 55 | 1:00
Agargaon | 92 | 12:00 | TK chemical | 19 | 18:00 | Sherpur(Bogura) | 56 | 1:00
Satmosjid | 111 | 14:00 | Modern Steel | 9 | 12:00 | Mohastangor | 64 | 1:00
Tongi | 137 | 15:00 | Shahmirpur | 31 | 18:00 | Bhangura | 28 | 21:00
Kabirpur | 220 | 18:00 | Khagrachhari | 28 | 1:00 | Rangpur | 125 | 1:00
Basundhara | 208 | 14:00 | Matarbari | 31 | 1:00 | Lalmonirhat | 38 | 1:00
Manikganj | 72 | 19:30 | Baroiar Hat | 46 | 18:30 | Saidpur | 86 | 1:00
Joydevpur | 182 | 12:00 | Rangamati | 14 | 18:00 | Purbasadipur | 93 | 1:00
New Tongi | 93 | 12:00 | Abul Khair 230 | 145 | 6:00 | Thakurgaon | 73 | 1:00
Kodda | 260 | 13:00 | BSRM | 150 | 5:00 | Palashbari | 114 | 1:00
Dhamrai | 102 | 18:30 | GPH Ispat | 32 | 6:00 | Barapukuria | 44 | 2:00
Rajendrapur | 94 | 1:00 | Agrabad | 88 | 18:00 | Panchagar | 45 | 18:30
Valuka | 118 | 11:00 | Goalpara | 26 | 1:00 | Joldhaka | 57 | 18:30
Tangail | 201 | 1:00 | Central S/S | 96 | 21:00 | Kurigram | 56 | 1:00
Mymensing | 196 | 2:00 | Noapara | 47 | 19:30 | Mithapukur | 28 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 6:00 | 402 | 13:00 | Kaliakoir | 395 | 0.25 | 388 | 0.45833
| Bheramara | 402 | 6:00 | 398 | 19:00 | Bhulta | 385 | 0.25 | 374 | 0.625
| Ashuganj(N) | 394 | 19:00 | 382 | 16:00 | Gopalganj | 405 | 0.625 | 386 | 0.041667
| Payra | 408 | 6:00 | 399 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 16:00 | Hathazari | 237 | 18:30 | 225 | 16:00
| Ishurdi | 235 | 6:00 | 224 | 1:00 | Megnaghat | 236 | 7:00 | 228 | 12:00
| Ashuganj | 242 | 6:00 | 236 | 15:00 | Fenchuganj | 244 | 6:00 | 241 | 1:00
| Serajganj | 230 | 8:00 | 225 | 1:00 | Siddhirganj | 232 | 7:00 | 223 | 16:00
| Baghabari | 233 | 14:00 | 227 | 1:00 | Maniknagar | 230 | 7:00 | 220 | 6:00
| Barapukuria | 237 | 9:00 | 228 | 1:00 | Agargaon | 228 | 8:00 | 219 | 15:00
| Bogra | 228 | 12:00 | 216 | 1:00 | Barisal | 239 | 21:00 | 226 | 6:00
| Rajshahi | 230 | 18:00 | 218 | 21:00 | Bhola 225 MW | 244 | 8:00 | 237 | 22:00
| Khulna South | 231 | 8:00 | 219 | 1:00 | AKSML | 235 | 21:00 | 224 | 16:00
| Rampura | 229 | 5:00 | 221 | 16:00 | BSRM | 236 | 8:00 | 225 | 16:00
| Haripur | 230 | 6:00 | 223 | 12:00 | Bibiyana | 244 | 6:00 | 238 | 11:00
| Hasnabad | 227 | 4:00 | 219 | 7:00 | Bhulta | 232 | 6:00 | 224 | 11:00
| Shyampur | 228 | 6:00 | 219 | 12:00 | Ashuganj (S) | 238 | 6:00 | 231 | 16:00
| Aminbazar | 230 | 1:00 | 221 | 2:00 | Kaliakoir | 226 | 1:00 | 216 | 17:00
| Tongi | 229 | 21:00 | 215 | 15:00 | GPH | 237 | 19:00 | 224 | 16:00
| Comilla (N) | 234 | 8:00 | 227 | 15:00 | Jhenaidah | 227 | 14:00 | 214 | 2:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 5:00 | 129 | 15:00 | Madanhat | 139 | 0.77083 | 132 | 0.29167
| Munsiganj | 135 | 1:00 | 129 | 11:00 | Hathazari | 139 | 0.79167 | 134 | 0.70833
| Sonargaon | 135 | 8:00 | 129 | 16:00 | Khulshi | 136 | 0.77083 | 128 | 0.66667
| Shyampur | 136 | 2:00 | 130 | 12:00 | Halishahar | 137 | 0.875 | 127 | 0.66667
| Bhulta | 127 | 1:00 | 125 | 11:00 | Baraulia | 137 | 0.79167 | 131 | 0.29167
| Madanganj | 134 | 1:00 | 128 | 11:00 | Sikalbaha | 138 | 0.77083 | 130 | 0.66667
| Shitalakhya | 135 | 1:00 | 130 | 10:00 | Dohazari | 134 | 0.77083 | 125 | 0.625
| Rahim steal | 134 | 5:00 | 130 | 10:00 | Cox'sbazar | 116 | 0.33333 | 106 | 0.75
| Matuail | 134 | 5:00 | 129 | 15:00 | Chandraghona | 138 | 0.77083 | 133 | 0.41667
| Ghorasal | 138 | 7:00 | 134 | 16:00 | Kaptai | 137 | 0.75 | 132 | 0.66667
| Narsinghdi | 134 | 7:00 | 123 | 1:00 | A. Khaer Stl. | 135 | 0.041667 | 128 | 0.625
| Haripur (SBU) | 134 | 5:00 | 130 | 11:00 | Bakulia | 137 | 0.77083 | 129 | 0.70833
| Sreenagar | 134 | 6:00 | 127 | 15:00 | Julda | 137 | 0.041667 | 132 | 0.45833
| Ullon | 134 | 2:00 | 126 | 16:00 | TK Chemical | 138 | 0.875 | 132 | 0.25
| Hasnabad | 134 | 1:00 | 129 | 11:00 | Modern Steel | 137 | 0.875 | 130 | 0.66667
| Magbazar | 135 | 3:00 | 126 | 11:00 | Shahmirpur | 138 | 0.77083 | 132 | 0.375
| Maniknagar | 135 | 3:00 | 128 | 11:00 | Khagrachhari | 137 | 0.041667 | 131 | 0.625
| Bangabhaban | 135 | 3:00 | 128 | 11:00 | Matarbari | 130 | 0.45833 | 110 | 0.66667
| Motijheel | 135 | 3:00 | 128 | 11:00 | Baroiar Hat | 135 | 0.77083 | 130 | 0.625
| Narinda | 135 | 3:00 | 128 | 11:00 | Rangamati | 137 | 18:30 | 131 | 16:00
| Kazla | 135 | 3:00 | 128 | 11:00 | Agrabad | 137 | 21:00 | 128 | 16:00
| Dhanmondi | 134 | 2:00 | 128 | 16:00 | Goalpara S/S | 137 | 6:00 | 133 | 0.041667
| Lalbag | 135 | 7:00 | 128 | 11:00 | Khulna Central S/S | 137 | 8:00 | 132 | 0.041667
| Madartek | 135 | 6:00 | 127 | 11:00 | Noapara | 137 | 18:00 | 130 | 0.041667
| Dhaka University | 135 | 6:00 | 127 | 11:00 | Jessore | 134 | 17:00 | 126 | 0.041667
| Aftabnagar | 135 | 7:00 | 126 | 12:00 | Benapol | 134 | 0.33333 | 125 | 0.041667
| Fatullah | 138 | 6:00 | 130 | 12:00 | Jhenida(Old) | 136 | 17:00 | 127 | 0.041667
| Nawabganj | 135 | 8:00 | 128 | 12:00 | Bottail | 135 | 0.33333 | 129 | 0.041667
| Keraniganj | 135 | 8:00 | 128 | 11:00 | G.K Project | 139 | 0.70833 | 134 | 0.041667
| Mirpur | 132 | 5:00 | 124 | 12:00 | Faridpur | 135 | 0.25 | 128 | 0.041667
| Kalyanpur | 132 | 5:00 | 126 | 12:00 | Rajbari | 135 | 0.75 | 127 | 0.041667
| Gulshan | 134 | 5:00 | 126 | 15:00 | Madaripur | 140 | 0.33333 | 132 | 0.875
| Uttara | 132 | 7:00 | 123 | 12:00 | Shariyatpur S/S | 140 | 6:00 | 130 | 0.91667
| Uttara New | 133 | 17:00 | 125 | 15:00 | Gopalganj | 142 | 0.25 | 133 | 0.91667
| Kamrangirchar | 134 | 6:00 | 128 | 11:00 | Bagerhat | 134 | 7:00 | 128 | 0.041667
| Savar | 133 | 4:00 | 127 | 12:00 | Mongla | 133 | 9:00 | 128 | 0.95833
| Bhasantec | 136 | 7:00 | 128 | 12:00 | Satkhira | 135 | 9:00 | 128 | 1:00
| Agargaon | 136 | 5:00 | 129 | 12:00 | Gallamari | 136 | 0.25 | 128 | 1:00
| Satmosjid | 136 | 6:00 | 129 | 11:00 | Magura | 136 | 17:00 | 124 | 0.041667
| Tongi | 139 | 18:00 | 128 | 15:00 | Narail | 134 | 0.70833 | 124 | 0.041667
| Kabirpur | 137 | 6:00 | 130 | 1:00 | Chuadanga | 130 | 6:00 | 119 | 0.041667
| Basundhara | 136 | 19:00 | 124 | 15:00 | Barisal(N) | 139 | 6:00 | 132 | 0.875
| Manikganj | 140 | 18:00 | 133 | 1:00 | Barisal (S) | 137 | 8:00 | 129 | 22:00
| Joydevpur | 138 | 18:30 | 129 | 11:00 | Patuakhali(S) | 136 | 0.33333 | 125 | 0.95833
| New Tongi | 137 | 21:00 | 126 | 15:00 | Bhandaria | 135 | 0.29167 | 123 | 0.875
| Kodda | 137 | 20:00 | 120 | 15:00 | Borguna | 137 | 0.29167 | 126 | 0.91667
| Dhamrai | 137 | 8:00 | 132 | 15:00 | Jhenaidah(230kV S/S) | 136 | 17:00 | 127 | 1:00
| Rajendrapur | 137 | 21:00 | 119 | 16:00 | Ishurdi | 136 | 14:00 | 131 | 1:00
| Valuka | 134 | 17:00 | 109 | 1:00 | Ruppur Paromanobik | 136 | 6:00 | 131 | 1:00
| Tangail | 137 | 18:00 | 126 | 1:00 | Natore | 135 | 18:30 | 128 | 1:00
| Mymensing | 134 | 13:00 | 114 | 1:00 | Bogra | 136 | 12:00 | 126 | 1:00
| Kishorganj | 133 | 17:00 | 118 | 1:00 | Noagaon | 132 | 17:00 | 120 | 1:00
| Netrokona | 133 | 17:00 | 110 | 1:00 | Rajshahi | 134 | 18:00 | 129 | 21:00
| Jamalpur | 141 | 13:00 | 121 | 1:00 | Rajshahi New | 136 | 18:00 | 128 | 20:00
| Sherpur | 140 | 13:00 | 118 | 1:00 | C.Nawabganj | 136 | 18:00 | 127 | 21:00
| Srimongal | 140 | 8:00 | 133 | 1:00 | Amnura | 138 | 18:00 | 126 | 4:00
| Shahjibazar | 137 | 7:00 | 130 | 1:00 | Pabna | 135 | 17:00 | 128 | 1:00
| Fenchuganj | 138 | 8:00 | 133 | 1:00 | Shahjadpur | 140 | 17:00 | 134 | 1:00
| Khulawara | 137 | 9:00 | 132 | 1:00 | Serajganj | 135 | 18:00 | 127 | 1:00
| Sylhet | 134 | 9:00 | 130 | 1:00 | Niyamatpur | 131 | 17:00 | 116 | 2:00
| Chatak | 133 | 6:00 | 130 | 21:00 | Joypurhat | 134 | 17:00 | 120 | 1:00
| Sunamganj | 133 | 9:00 | 126 | 1:00 | Sherpur(Bogura) | 135 | 12:00 | 125 | 1:00
| Biani Bazar | 134 | 7:00 | 127 | 1:00 | Mohastangor | 135 | 12:00 | 124 | 1:00
| Comilla(s) | 130 | 8:00 | 125 | 19:00 | Bangura | 135 | 5:00 | 132 | 1:00
| Comilla(n) | 138 | 8:00 | 132 | 15:00 | Rangpur | 134 | 11:00 | 117 | 1:00
| Chandpur | 139 | 5:00 | 137 | 1:00 | Lalmonirhat | 135 | 10:00 | 118 | 1:00
| Feni | 135 | 18:30 | 130 | 18:00 | Saidpur | 132 | 7:00 | 118 | 1:00
| Chowmuhani | 132 | 6:00 | 129 | 2:00 | Purbasadipur | 136 | 8:00 | 115 | 1:00
| Ashuganj | 140 | 7:00 | 134 | 1:00 | Thakurgaon | 133 | 7:00 | 116 | 1:00
| Daudkandi | 133 | 6:00 | 127 | 15:00 | Palashbari | 133 | 12:00 | 118 | 1:00
| B.Baria | 135 | 7:00 | 127 | 1:00 | Barapukuria | 137 | 9:00 | 128 | 1:00
| Ramganj | 135 | 9:00 | 131 | 3:00 | Panchagar | 136 | 0.29167 | 115 | 0.041667
| Chaddagram | 136 | 19:00 | 130 | 15:00 | Joldhaka | 132 | 0.375 | 113 | 0.041667
| PHP | 135 | 18:30 | 129 | 3:00 | Kurigram | 134 | 0.41667 | 118 | 0.041667
| Kochua | 137 | 18:30 | 134 | 2:00 | Mithapukur | 135 | 0.5 | 120 | 0.041667
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-10-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 40 | 7739 | 3107 | 10846 |  |  |  | QF-LDC-11
0:30 | 187 | 8219.5 | 3290 | 11509.5 | Date: | 2021-10-03
1:00 | 334 | 8700 | 3473 | 12173
1:30 | 393 | 8599 | 3424 | 12023
2:00 | 452 | 8498 | 3375 | 11873
2:30 | 389 | 8292.5 | 3365 | 11657.5 | [5 empty] | Gen. at Eve. Peak | 11569 | 11569 MW (21:00 )
3:00 | 326 | 8087 | 3355 | 11442 | [6 empty] | 21:00
3:30 | 289 | 7977.5 | 3320.5 | 11298 | [5 empty] | Gen. at Day Peak | 10430 | 10430 MW (12:00 )
4:00 | 252 | 7868 | 3286 | 11154 | [6 empty] | 12:00
4:30 | 226 | 7787 | 3244.5 | 11031.5 | [5 empty] | Highest Generation | 12173
5:00 | 200 | 7706 | 3203 | 10909 | [6 empty] | 1:00
5:30 | 158 | 7522.5 | 3090.5 | 10613
6:00 | 116 | 7339 | 2978 | 10317
6:30 | 123 | 7202 | 2869.5 | 10071.5
7:00 | 130 | 7065 | 2761 | 9826
7:30 | 76 | 6957.5 | 2766 | 9723.5
8:00 | 22 | 6850 | 2771 | 9621
8:30 | 108 | 6978 | 2784.5 | 9762.5
9:00 | 194 | 7106 | 2798 | 9904
9:30 | 207 | 7219 | 2787 | 10006
10:00 | 220 | 7332 | 2776 | 10108
10:30 | 238 | 7358.5 | 2820 | 10178.5
11:00 | 256 | 7385 | 2864 | 10249
11:30 | 248 | 7449.5 | 2890 | 10339.5
12:00 | 240 | 7514 | 2916 | 10430
12:30 | 134 | 7615 | 2881 | 10496
13:00 | 28 | 7716 | 2846 | 10562
13:30 | 19 | 7705.5 | 2819 | 10524.5
14:00 | 10 | 7695 | 2792 | 10487
14:30 | 159 | 7624.5 | 2874 | 10498.5
15:00 | 308 | 7554 | 2956 | 10510
15:30 | 356 | 7330.5 | 2924.5 | 10255
16:00 | 404 | 7107 | 2893 | 10000
16:30 | 390 | 7046 | 2876.5 | 9922.5
17:00 | 376 | 6985 | 2860 | 9845
17:30 | 268 | 7282 | 3050 | 10332
18:00 | 160 | 7579 | 3240 | 10819
18:30 | 174 | 7934.5 | 3242.5 | 11177
19:00 | 188 | 8290 | 3245 | 11535
19:30 | 120 | 8160 | 3318 | 11478
20:00 | 120 | 8192 | 3351 | 11543 |  |  |  | Executive Engineer
20:30 | 137 | 8203.5 | 3352.5 | 11556 |  |  |  | Network Operation Division
21:00 | 154 | 8215 | 3354 | 11569
21:30 | 170 | 8200.5 | 3298 | 11498.5
22:00 | 186 | 8186 | 3242 | 11428 |  |  |  |  | Page 6 of 7
22:30 | 105 | 8068.5 | 3197.5 | 11266
23:00 | 24 | 7951 | 3153 | 11104
23:30 | 32 | 7845 | 3130 | 10975
24:00 | 40 | 7739 | 3107 | 10846
11569 MW (21:00 )
10430 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-03 |  | Energy |  | 263206853
[13 empty] | 2021-10-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4203 | 700 | 2364 | 0 | 2410 | 602 | 161 | 120 | 166 | 120 | 0 | 0
0:30 | 4337.5 | 700.5 | 2295.5 | 0 | 2948.5 | 635.5 | 159.5 | 120 | 190.5 | 122 | 0 | 0 | Date: | 2021-10-03
1:00 | 4472 | 701 | 2227 | 0 | 3487 | 669 | 158 | 120 | 215 | 124 | 0 | 0
1:30 | 4448 | 700.5 | 2231 | 0 | 3401 | 664.5 | 159.5 | 120 | 175.5 | 123 | 0 | 0 | [8 empty] | Total Energy | 263.2069 | Total Energy Gen 263.207 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 263.207 MKWHr
2:00 | 4424 | 700 | 2235 | 0 | 3315 | 660 | 161 | 120 | 136 | 122 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4432 | 700 | 2232.5 | 0 | 3155 | 650 | 161 | 120 | 86 | 121 | 0 | 0 | [8 empty] | Energy Requirement | 263.2069
3:00 | 4440 | 700 | 2230 | 0 | 2995 | 640 | 161 | 120 | 36 | 120 | 0 | 0
3:30 | 4463.5 | 700 | 2258.5 | 0 | 2820 | 630 | 160 | 120 | 28 | 118 | 0 | 0 | [6 empty] | Shortage
4:00 | 4487 | 700 | 2287 | 0 | 2645 | 620 | 159 | 120 | 20 | 116 | 0 | 0
4:30 | 4508.5 | 700.5 | 2319 | 0 | 2480.5 | 610 | 159 | 120 | 20 | 114 | 0 | 0
5:00 | 4530 | 701 | 2351 | 0 | 2316 | 600 | 159 | 120 | 20 | 112 | 0 | 0
5:30 | 4429.5 | 701 | 2286 | 0 | 2210.5 | 585 | 159.5 | 120 | 12 | 109 | 0.5 | 0
6:00 | 4329 | 701 | 2221 | 0 | 2105 | 570 | 160 | 120 | 4 | 106 | 1 | 0
6:30 | 4217 | 701 | 2168 | 0 | 2049 | 543.5 | 160 | 120 | 4 | 102 | 7 | 0 |  |  |  |  | Coal
7:00 | 4105 | 701 | 2115 | 0 | 1993 | 517 | 160 | 120 | 4 | 98 | 13 | 0
7:30 | 4033.5 | 701 | 2087 | 0 | 2006.5 | 519.5 | 140 | 120 | 4 | 94 | 18 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3962 | 701 | 2059 | 0 | 2020 | 522 | 120 | 120 | 4 | 90 | 23 | 0
8:30 | 4046.5 | 701 | 2084 | 0 | 2039 | 513.5 | 121.5 | 120 | 4 | 90 | 43 | 0
9:00 | 4131 | 701 | 2109 | 0 | 2058 | 505 | 123 | 120 | 4 | 90 | 63 | 0
9:30 | 4185.5 | 700.5 | 2125.5 | 0 | 2100.5 | 487.5 | 123 | 120 | 4 | 91 | 68.5 | 0
10:00 | 4240 | 700 | 2142 | 0 | 2143 | 470 | 123 | 120 | 4 | 92 | 74 | 0
10:30 | 4273.5 | 700 | 2155 | 0 | 2184 | 470 | 122 | 120 | 5.5 | 96 | 52.5 | 0
11:00 | 4307 | 700 | 2168 | 0 | 2225 | 470 | 121 | 120 | 7 | 100 | 31 | 0
11:30 | 4337 | 700.5 | 2168.5 | 0 | 2273 | 470.5 | 121 | 120 | 5.5 | 101 | 42.5 | 0
12:00 | 4367 | 701 | 2169 | 0 | 2321 | 471 | 121 | 120 | 4 | 102 | 54 | 0
12:30 | 4378.5 | 701 | 2142 | 0 | 2392 | 471 | 140.5 | 120 | 4 | 103 | 44 | 0
13:00 | 4390 | 701 | 2115 | 0 | 2463 | 471 | 160 | 120 | 4 | 104 | 34 | 0
13:30 | 4390 | 701 | 2115 | 0 | 2463 | 471 | 160 | 120 | 4 | 104 | 34 | 0
14:00 | 4390 | 701 | 2115 | 0 | 2463 | 471 | 160 | 120 | 4 | 104 | 34 | 0
14:30 | 4340 | 700.5 | 2137.5 | 0 | 2469 | 469.5 | 158.5 | 120 | 4 | 108 | 29 | 0
15:00 | 4290 | 700 | 2160 | 0 | 2475 | 468 | 157 | 120 | 4 | 112 | 24 | 0
15:30 | 4301.5 | 700 | 2094 | 0 | 2281 | 468.5 | 157 | 120 | 4 | 106 | 23 | 0
16:00 | 4313 | 700 | 2028 | 0 | 2087 | 469 | 157 | 120 | 4 | 100 | 22 | 0
16:30 | 4282.5 | 700.5 | 2043 | 0 | 2024 | 469.5 | 158.5 | 120 | 15 | 97 | 12.5 | 0
17:00 | 4252 | 701 | 2058 | 0 | 1961 | 470 | 160 | 120 | 26 | 94 | 3 | 0
17:30 | 4151 | 700.5 | 2118 | 0 | 2245 | 465.5 | 160 | 130 | 249.5 | 111 | 1.5 | 0
18:00 | 4050 | 700 | 2178 | 0 | 2529 | 461 | 160 | 140 | 473 | 128 | 0 | 0
18:30 | 4061 | 700 | 2145.5 | 0 | 2948.5 | 491 | 160 | 130 | 409 | 132 | 0 | 0
19:00 | 4072 | 700 | 2113 | 0 | 3368 | 521 | 160 | 120 | 345 | 136 | 0 | 0
19:30 | 4089 | 700 | 2251 | 0 | 3272 | 542 | 160 | 120 | 206 | 138 | 0 | 0
20:00 | 4117 | 701 | 2287 | 0 | 3270 | 542 | 162 | 120 | 206 | 138 | 0 | 0
20:30 | 4141 | 701 | 2316.5 | 0 | 3231.5 | 537 | 162 | 120 | 210 | 137 | 0 | 0
21:00 | 4165 | 701 | 2346 | 0 | 3193 | 532 | 162 | 120 | 214 | 136 | 0 | 0
21:30 | 4212.5 | 701 | 2351 | 0 | 3086.5 | 532 | 162 | 120 | 198.5 | 135 | 0 | 0
22:00 | 4260 | 701 | 2356 | 0 | 2980 | 532 | 162 | 120 | 183 | 134 | 0 | 0
22:30 | 4236.5 | 700.5 | 2372.5 | 0 | 2806.5 | 552 | 162 | 120 | 183 | 133 | 0 | 0
23:00 | 4213 | 700 | 2389 | 0 | 2633 | 572 | 162 | 120 | 183 | 132 | 0 | 0
23:30 | 4208 | 700 | 2376.5 | 0 | 2521.5 | 587 | 161.5 | 120 | 174.5 | 126 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 33.1° C
24:00 | 4203 | 700 | 2364 | 0 | 2410 | 602 | 161 | 120 | 166 | 120 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 263.207 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 263.207 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 83 | 86 | 86 | 84 | 84 | 85 | 85 | 85 | 88 | 88 | 86 | 86 | 85 | 82 | 82 | 82 | 85 | 85 |  | 85 | 85 | 87 | 87 | 87 | 87 | 86 | 1983535
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 35 | 35 | 35 | 35 | 35 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1532000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 110 | 120 | 120 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [13 empty] | 2 | 8 | 8 | 8 | 8 |  | 25 | 8 | 8 | 8 |  |  | 0 | 90747
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 |  | 18 | 4 | 5 |  |  |  | 8 | 9 | 2 | [9 empty] | 59265
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | [14 empty] | 17 | 102 |  | 102 | 85 | 85 | 85 | 85 | 85 | 68 | 766674
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 72 | 105 | 105 | 105 | 68 | 68 | 73 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2116836
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 42 |  | 42 | [5 empty] | 0 | 65792
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 185 | 185 | 186 | 190 | 190 | 125 | 127 | 127 | 128 | 128 | 128 | 128 | 180 | 148 | 150 | 129 | 128 | 128 |  | 128 | 160 | 185 | 185 | 185 | 185 | 185 | 4033000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 283 | 293 | 286 | 195 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 130 | 190 | 190 | 190 | 190 | 193 |  | 267 | 278 | 282 | 282 | 281 | 230 | 195 | 4636798
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 45 | 45 | 45 | 45 | 45 | 63 | 63 | 63 | 63 | 36 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 36 | 63 | 63 | 63 | 819636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 300 | 310 | 310 | 310 | 310 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 310 | 310 | 310 | 310 | 310 | 7218164
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 100 | 120 | 135 | 135 | 2125490
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 485280
33 | Ashuganj 225 MW CCPP | 210 | 211 | 210 | 209 | 209 | 211 | 178 | 179 | 183 | 180 | 205 | 203 | 205 | 200 | 193 | 197 | 198 | 209 |  | 211 | [6 empty] | 3902000
34 | Ashuganj 450 MW CCPP(South) | 295 | 295 | 295 | 300 | 320 | 295 | 270 | 270 | 270 | 350 | 330 | 320 | 305 | 305 | 320 | 320 | 305 | 270 |  | 270 | 335 | 305 | 305 | 345 | 305 | 305 | 7342000
| Ashuganj 450 MW CCPP(North) | 310 | 305 | 310 | 310 | 335 | 305 | 260 | 260 | 310 | 320 | 335 | 325 | 310 | 310 | 325 | 320 | 310 | 260 |  | 260 | 310 | 285 | 285 | 330 | 315 | 310 | 7628500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 54 | 55 | 54 | 50 | 49 | 47 | 50 | 51 | 51 | 56 | 53 |  | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 1295040
36 | Chandpur 150 MW CCPP | 141 | 140 | 137 | 141 | 141 | 138 | 141 | 139 | 140 | 140 | 141 | 140 | 138 | 140 | 139 | 137 | 135 | 139 |  | 139 | 139 | 140 | 138 | 140 | 142 | 140 | 3338400
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 396 | 396 | 396 | 396 | 382 | 312 | 306 | 306 | 306 | 320 | 381 | 404 | 399 | 341 | 340 | 340 | 340 |  | 339 | 340 | 340 | 340 | 340 | 340 | 340 | 8657176
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6157000
41 | Haripur 360MW CCPP(HPL) | 321 | 327 | 327 | 327 | 326 | 301 | 302 | 303 | 300 | 300 | 317 | 326 | 342 | 343 | 344 | 260 | 270 | 330 |  | 305 | 333 | 333 | 326 | 325 | 327 | 327 | 7588000
42 | RPCL 210MW CCPP | 210 | 210 | 209 | 207 | 207 | 208 | 208 | 208 | 205 | 191 | 189 | 163 | 156 | 144 | 145 | 163 | 160 | 160 |  | 161 | 162 | 173 | 172 | 181 | 173 | 189 | 4284960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 2 | 12 | 26 | 30 | 8 | 11 | 3 | 10 | 3 | 0 | [10 empty] | 94080
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1021000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 554400
46 | Shajibazar 330 MW CCPP | 161 | 161 | 161 | 161 | 163 | 163 | 162 | 161 | 162 | 162 | 160 | 158 | 160 | 158 | 158 | 160 | 162 | 160 |  | 160 | 162 | 161 | 163 | 162 | 160 | 162 | 3688000
47 | Shahjibazar GTPP Unit- 8 & 9 | 52 | 52 | 52 | 52 | 51 | 52 | 52 | 52 | 51 | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 57 | 52 |  | 57 | 57 | 57 | 57 | 57 | 63 | 63 | 1268160
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 75 | 78 | 78 | 78 | 81 | 81 | 81 | 81 | 70 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1911360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 115 | 115 | 140 | 142 | 141 | 141 |  | 120 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 3169700
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 401000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 207360
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 5 |  | 2 | 2 | 2 | 11 | 11 | 11 | 11 | 206
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 45 | 45 | 45 | 39 | 39 | 39 | 45 | 45 | 44 | 44 | 42 | 44 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1083000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 379536
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 295 | 300 | 295 | 290 | 280 | 275 | 280 | 300 | 300 | 310 | 290 | 280 | 300 | 265 | 290 | 270 |  | 260 | 325 | 300 | 290 | 300 | 290 | 295 | 7166000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 365 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7766100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 45 |  | 55 | 55 | 55 | 55 | 55 | 55 | 12 | 1228092
59 | Tangail Palli Power Gen 22 MW | 24 | [16 empty] | 2 |  | 22 | [6 empty] | 58080
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 454320
61 | Narshingdi 22 MW PP (Doreen) | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 |  | 14 | 20 | 20 | 21 |  |  | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 401652
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 431064
63 | Impoprt (Tripura) | 124 | 122 | 120 | 116 | 112 | 106 | 98 | 90 | 90 | 92 | 100 | 102 | 104 | 112 | 112 | 100 | 94 | 128 |  | 136 | 138 | 138 | 136 | 134 | 132 | 120 | 2695680
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 35 | 30 | 38 | 40 | 37 | 7 | 2 | 2 | 2 | 3 | 2 | 4 | 2 | 2 | 5 | 9 |  | 10 | 14 | 20 | 20 | 35 | 38 | 37 | 390240
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 450432
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 156780
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 791200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 508770
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 16 |  | 26 | 26 | 28 | 29 | 29 | 29 | 29 | 628200
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | [5 empty] | 0 | 28 | 28 | 28 | 28 | 644600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 797700
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 17 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 44 |  | 114 | 114 | 114 | 114 | 76 | 50 | 70 | 995220
| Chowmuhani 113 MW | 58 | 57 | 51 | 52 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 51 | 57 | 57 | 57 | 57 | 57 | 90 |  | 95 | 95 | 95 | 96 | 94 | 97 | 63 | 1599360
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 126 | 126 |  | 158 | 162 | 162 | 162 | 162 | 162 | 162 | 3857760
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 2 | 8 | 11 | 16 | 16 | 16 | 16 | 16 | 22 | 34 | 34 |  | 11 | [6 empty] | 206880
79 | Kodda 150MW PP | 98 | 64 | 32 | 16 | 16 | [11 empty] | 5 | 112 |  | 100 | 82 | 82 | 90 | 98 | 98 | 98 | 942720
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26 |  | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 795854
| Gazipur 100 MW PP | 52 | [7 empty] | 1 | 52 | 52 | 52 | 52 | 52 | 52 | 55 | 70 | 77 |  | 72 | 35 | 34 | 34 | 17 | 17 | 17 | 818400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 5 | 6 | 2 | 0 | 1 | 0 | 2 | 0 | [9 empty] | 26041
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1300215
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 29 |  | 108 | 110 | 110 | 110 | 110 | 110 | 110 | 1864246
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 37 | [15 empty] | 8 | 34 |  | 51 | 51 | 50 | 51 |  |  | 0 | 279965
86 | Meghnaghat CCPP ( Summit) | 275 | 290 | 270 | 285 | 290 | 260 | 275 | 265 | 283 | 285 | 290 | 270 | 275 | 285 | 285 | 278 | 275 | 297 |  | 290 | 300 | 280 | 305 | 305 | 315 | 290 | 6769193
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 94 | 93 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 60 | 66 |  | 104 | 104 | 104 | 104 | 104 | 104 | 96 | 2477760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 23 | [6 empty] | 10 | 10 | 20 | 20 | 20 | 20 | 20 | 10 | 50 |  | 40 | 40 | 40 | 40 | 10 |  | 0 | 583440
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 43 | 43 | 35 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 982942
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 64 | [7 empty] | 16 | 16 | 24 | 50 | 64 | 40 | 40 | 48 |  | 40 | 40 | 40 | 40 | 40 | 24 | 7 | 872064
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 25 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 |  | 44 | 50 | 50 | 50 | 50 | 24 | 12 | 716160
96 | Chattogram 108 MW PP (ECPV) | 35 | [15 empty] | 0 | 18 |  | 49 |  | 0 |  |  |  | 0 | 109440
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1110451
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1247139
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 110 | 110 | 110 |  | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 3633790
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | [9 empty] | 7400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1302840
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 191 | 191 | 191 | 190 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 40 | 35 | 35 | 35 | 48 |  | 110 | 110 | 110 | 100 | 100 | 70 | 40 | 2757600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 85 | 75 | 70 | 70 | 70 | 117 | 143 | 142 | 138 | 141 | 148 | 149 | 99 | 59 | 62 | 143 |  | 149 | 149 | 149 | 149 | 144 | 85 | 72 | 2789280
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 60 | 60 | 75 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2116800
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 136 | 100 | 100 | 100 | 104 | 149 | 157 | 180 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4332960
117 | Ashuganj 150MW PP (Midland) | 125 | 118 | 120 | 117 | 118 | 120 | 115 | 103 | 112 | 112 | 115 | 108 | 103 | 103 | 103 | 107 | 112 | 113 |  | 120 | 122 | 123 | 60 | 10 | 10 | 10 | 2473952
118 | Bibiyana-III 400 MW CCPP | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 317 | 316 | 317 | 242 | 315 | 315 | 316 | 316 | 316 | 316 | 316 |  | 316 | 315 | 316 | 316 | 316 | 322 | 322 | 7549000
| Jamalpur 115 MW PP (United) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 98 | 98 | 98 | 96 | 96 | 96 | 65 | 35 | 35 | 35 | 46 |  | 115 | 115 | 115 | 109 | 115 | 115 | 115 | 2198400
| Anwara 300 MW PP (United) | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 304 | 304 | 305 | 305 | 306 | 305 | 305 | 305 | 255 | 232 | 273 |  | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 7186036
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 96 | 96 | 96 | 96 | 96 | 100 | 70 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2304000
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 53 | 53 | 53 | 53 | 53 | 72 | 108 | 108 | 108 | 90 | 72 | 77 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2299582
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 442440
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 8 | 13 | 31 | 7 | 35 | 26 | 14 | 11 | 9 | 1 | [9 empty] | 163375
120 | Eastern Zone Total | 8700 | 8498 | 8087 | 7868 | 7706 | 7339 | 7065 | 6850 | 7106 | 7332 | 7385 | 7514 | 7716 | 7695 | 7554 | 7107 | 6985 | 7579 |  | 8290 | 8160 | 8192 | 8215 | 8186 | 7951 | 7739 | 186885710
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 15 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7 | 4 | 4 | 4 | 4 | 4 | 4 | 27 |  | 32 | [6 empty] | 132750
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3016320
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 |  | 75 | 75 | 70 | 70 | 70 | 17 | 0 | 1109280
130
131
132 | United Payra Power Ltd. | [17 empty] | 3 |  | 35 | 35 | 35 | 17 |  |  | 0 | 129600
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 225 | 225 | 225 | 225 | 218 | 180 | 181 | 180 | 181 | 181 | 181 | 111 | 112 | 123 | 170 | 200 | 223 |  | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 4669418
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 13 | 18 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 416969
| Bhola 225 MW CCPP | 81 | 81 | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 85 | 85 | 85 | 87 | 88 | 88 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 2040180
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 33 | 31 | 30 | 26 | 21 | 20 | 20 | 19 | 20 | 22 | 23 | 23 | 24 | 20 | 22 | 29 |  | 32 | 33 | 33 | 34 | 34 | 35 | 34 | 649734
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 701 | 700 | 700 | 700 | 701 | 701 | 701 | 701 | 701 | 700 | 700 | 701 | 701 | 700 | 700 | 700 | 701 | 700 |  | 700 | 700 | 701 | 701 | 701 | 700 | 700 | 16929454
147 | Bheramara 410 MW CCPP | 410 | 410 | 410 | 410 | 410 | 350 | 320 | 320 | 320 | 320 | 370 | 365 | 355 | 355 | 390 | 385 | 385 | 350 |  | 300 | 360 | 360 | 350 | 335 | 330 | 315 | 8986752
148 | Payra 1320 MW | 590 | 580 | 560 | 540 | 520 | 490 | 440 | 440 | 420 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 380 |  | 440 | 460 | 460 | 450 | 450 | 490 | 520 | 11877200
149
150 | Barapukuria TPP Unit-1 | 79 | 80 | 80 | 80 | 80 | 80 | 77 | 82 | 85 | 80 | 80 | 81 | 81 | 81 | 78 | 79 | 80 | 81 |  | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 1896872
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 | [7 empty] | 0 | 75000
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 2 | 4 | 3 | 2 | 0 | 0 | 0 | 0 | [9 empty] | 16020
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 167 | 165 | 167 | 173 | 170 | 170 | 165 | 164 | 164 | 166 | 172 | 187 | 197 | 172 | 175 | 181 | 170 | 161 |  | 172 | 171 | 178 | 185 | 182 | 167 | 165 | 4358964
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 160 | 163 | 168 | 166 | 165 | 161 | 167 | 177 | 180 | 202 | 196 | 198 | 178 | 190 | 188 | 188 | 152 |  | 168 | 181 | 189 | 183 | 186 | 182 | 178 | 4524882
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 364 | 340 | 349 | 393 | 416 | 388 | 322 | 321 | 357 | 362 | 361 | 361 | 336 | 332 | 404 | 399 | 353 | 391 |  | 350 | 380 | 402 | 423 | 404 | 409 | 406 | 8989236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 | [8 empty] | 8067
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 20 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 492480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 0 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 218034
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  |  | 0 |  |  |  |  | 0 | 34450
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 43 | [7 empty] | 0 | 40820
167 | Katakhali 50 MW Peaking PP | [17 empty] | 24 | [8 empty] | 44063
168 | Santahar 50 MW Peaking PP | 34 | [16 empty] | 18 | [8 empty] | 68331
169 | Natore 52 MW PP (Rajlanka) | 16 | [16 empty] | 7 |  | 8 | [5 empty] | 0 | 90240
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 93 |  | 69 | 39 | 39 | 39 |  |  |  | 290256
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 50 | 35 | 35 | 35 | 35 | 38 | 70 | 70 | 70 | 80 | 35 | 35 | 35 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2003904
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 70 | 70 | 90 | 35 | 35 | 70 |  | 95 | 95 | 95 | 113 | 113 | 113 | 113 | 1788768
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 100 | 49 | 49 | 35 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 70 |  | 107 | 113 | 113 | 113 | 113 | 34 | 0 | 1409884
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 0 | [9 empty] | 13215
178
178