## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-06 | Wednesday
|  |  | Date (day): | 2021-10-06 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13489.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14505 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-05 | 2021-10-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 373 | 346 | 350 | 350 | 62 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 188 | 192 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 240 | 255 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 42 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 18 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 300 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 16 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 32 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 230 | 298 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 30 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 25 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 25 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 35 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 94 | 94 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2724 | 3213 | 3595 | 3867 | 989 | 820
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 50 | 25 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 163 | 157 | 155 | 157 | 73 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 90 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 102 | 50 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 5 | 70 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 2 | 5 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 88 | 85 | 88 |  | 20 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 303 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 75 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 79 | 110 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1150 | 1503 | 1481 | 1543 | 133 | 689
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 |  |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 148 | 144 | 140 | 145 |  | 75 | ST Under maint.
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 300 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 265 | 300 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 30 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 108 | 125 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 92 | 90 | 92 |  | 71 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 138 | 172 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 128 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 9 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 25 | 105 | 100 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 48 | 88 | 95 | 96 |  | 17 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 16 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1523 | 1774 | 2012 | 2221 | 450 | 245
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 142 | 144 | 150 | 150 | 52 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 95 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 42 | 200 | 170 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 31 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 353 | 503 | 530.6 | 509 | 52 | 95
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 164 | 160 | 160 |  | 170 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 62 | 60 | 62
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 75 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 192 | 225 | 0 | 0 |  | 231 | Under maint.
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 322 | 321 | 320 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1750 | 1796 | 1630 | 1633 | 142 | 588
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 711 | 710 | 724 | 728
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 5 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 170 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 260 | 225 | 250 | 300 |  |  | FGMO
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 80 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1171 | 1214 | 1459 | 1623 | 0 | 98
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 32 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 87 | 84 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 17 | 17 | 17 | 17 | 78 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 510 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 223 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 713 | 886 | 1086 | 1240 | 78 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 19 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 131 | 124 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 189 | 177 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 391 | 421 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34 |  | 16 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 101 | 94 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 969 | 1324 | 1495 | 1676 | 380 | 100
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 79 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 152 | 193 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 21093 | 10505 | 12406 | 13489.6 | 14505 | 2224 | 3140
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10112.9466 | 11943 | 12986.1593 | 13963.664
| A. |  | 2021-10-05 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12406 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9235 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12406 | MW
| 3 | Day peak Generation : |  |  | 10505 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11943 | MW
| 4 | Evening peak Generation : |  |  | 12406 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 260.349 | MKWHr | By Solar | 0.51631 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 151.7139 | MKWHr |  | By Oil: | 70.5858 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.7899 | MKWHr |  | By Hydro: | 3.7683 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2224 | MW | Dhaka | 4309 | 4309 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3140 | MW | Chittagong | 1286 | 1286 |  | 0 |  | 18:00 |  | 134
|  |  |  | Total = |  |  | 5364 | MW | Khulna | 1490 | 1490 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1121.74 | MMCFD |  |  | Rajshahi | 1257 | 1257 |  | 0 |  | 19:00 |  | 128
| 8 | Fuel Cost : | i) Gas : | Taka | 156371021.258 | ii) Oil : | Taka | 554755039.5 | Comilla | 1125 | 1125 |  | 0 |  | 19:30 |  | 128
|  |  | iii) Coal : |  | 63665037.3 | Total | Taka | 774791098.058 | Mymensingh | 955 | 955 |  | 0 |  | 20:00 |  | 130
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 3.2515 | MKWHr. | Sylhet | 459 | 459 |  | 0 |  | 21:00 |  | 128
|  | ii) During Peak Demand : |  |  | -348 | MW (E to W) at | 19:00 | hrs | Barisal | 348 | 348 |  | 0 |  | 22:00 |  | 128
|  | iii) Maximum : |  |  | -488 | MW at | 23:00 | hrs | Rangpur | 714 | 714 |  | 0 |  | 23:00 |  | 124
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.6° C |  |  | Total | 11943 | 11943 |  | 0
| B. |  | 2021-10-06 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 31.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14505 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
| 4 | Reserve(Generation end) |  |  |  | 2005 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 262.3216 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9024 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1745 | MKWHr. | ii) HVDC Flow at Peak Time |  | 710 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8003 | MKWHr. | iii) Maximum HVDC Flow : |  | 713 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.3 |  | (b) Today: | 106.16 |  | (c) Rule Curve: |  | 106.45
.

## YesterdayGen
2021-10-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 394 | 303 |  | 0 | 250 | 285 | 0 | 0 | 55 | 337 | 0 | 0 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 40 | 0 | 33 | 19 | 37 | 100 | 0 | 0 | 280 | 285 | 114 | 26 | 90 | 23 | 30 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 0 | 21 | 124 | 135 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 130 | 164 | 61 | 78 | 0 | 191 | 18 | 0 | 9 | 265 | 24 | 11 | 0 | 95 | 0 | 0 | 40 | 0 | 84 | 0 | 100 | 200 | 80 | 322 | 115 | 17 | 105 | 0 | 304 | 39 | 110 | 114 | 48 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 35 | 0 |  | 710 | 0 | 265 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 17 | 0 | 194 | 0 | 375 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 50 | 520 | 223 | 0 | 17 | 0 |  | 7669 | 2968 | 10637 | 4274 | 710 | 2174 | 0 | 2392 | 601 | 159 | 120 | 83 | 124 | 0 | 0 | 106.31
2:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 395 | 311 |  | 0 | 250 | 305 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 40 | 0 | 33 | 19 | 37 | 100 | 0 | 0 | 305 | 315 | 107 | 8 | 91 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 122 | 149 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 130 | 161 | 62 | 78 | 0 | 191 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 40 | 0 | 100 | 0 | 100 | 200 | 80 | 322 | 97 | 0 | 105 | 0 | 304 | 54 | 110 | 100 | 47 | 100 | 320 | 55 | 0 | 108 | 116 | 0 | 35 | 0 |  | 710 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 17 | 0 | 194 | 0 | 392 | 17 | 0 | 35 | 0 | 25 | 0 | 0 | 35 | 520 | 224 | 0 | 0 | 0 |  | 7598 | 2931 | 10529 | 4364 | 710 | 2235 | 0 | 2138 | 599 | 158 | 120 | 83 | 122 | 0 | 0 | 106.31
3:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 395 | 319 |  | 0 | 250 | 275 | 0 | 0 | 40 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 82 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 40 | 0 | 29 | 0 | 37 | 100 | 0 | 0 | 280 | 285 | 103 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 120 | 156 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 162 | 62 | 78 | 0 | 191 | 18 | 0 | 9 | 285 | 24 | 11 | 0 | 15 | 0 | 0 | 40 | 0 | 99 | 0 | 100 | 200 | 80 | 322 | 98 | 0 | 105 | 0 | 304 | 54 | 110 | 88 | 48 | 100 | 320 | 17 | 0 | 108 | 116 | 0 | 35 | 0 |  | 711 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 17 | 0 | 194 | 0 | 391 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 500 | 225 | 0 | 0 | 0 |  | 7433 | 2887 | 10320 | 4298 | 711 | 2231 | 0 | 2053 | 579 | 157 | 120 | 51 | 120 | 0 | 0 | 106.31
4:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 394 | 327 |  | 0 | 250 | 280 | 0 | 0 | 30 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 82 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 37 | 100 | 0 | 0 | 280 | 285 | 101 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 120 | 160 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 163 | 162 | 62 | 78 | 0 | 191 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 100 | 0 | 100 | 200 | 80 | 322 | 98 | 0 | 105 | 0 | 304 | 54 | 68 | 88 | 42 | 100 | 320 | 17 | 0 | 54 | 116 | 0 | 32 | 0 |  | 710 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 17 | 0 | 194 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 225 | 0 | 0 | 0 |  | 7243 | 2763 | 10006 | 4304 | 710 | 2243 | 0 | 1768 | 550 | 157 | 120 | 34 | 120 | 0 | 0 | 106.3
5:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 394 | 328 |  | 0 | 250 | 280 | 0 | 0 | 30 | 336 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 19 | 37 | 100 | 0 | 0 | 280 | 285 | 108 | 8 | 90 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 116 | 160 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 110 | 161 | 62 | 75 | 0 | 192 | 18 | 0 | 9 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 100 | 0 | 100 | 200 | 80 | 319 | 98 | 0 | 85 | 0 | 250 | 54 | 68 | 88 | 42 | 100 | 320 | 17 | 0 | 54 | 116 | 0 | 0 | 0 |  | 711 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 17 | 0 | 179 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 225 | 0 | 0 | 0 |  | 7097 | 2738 | 9835 | 4308 | 711 | 2180 | 0 | 1662 | 530 | 158 | 120 | 50 | 116 | 0 | 0 | 106.3
6:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 394 | 328 |  | 0 | 250 | 275 | 0 | 0 | 30 | 340 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 28 | 100 | 0 | 0 | 280 | 285 | 110 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 108 | 160 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 110 | 163 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 99 | 1 | 60 | 200 | 40 | 322 | 98 | 0 | 51 | 0 | 178 | 54 | 51 | 34 | 41 | 70 | 321 | 17 | 0 | 54 | 72 | 0 | 0 | 0 |  | 710 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 17 | 0 | 160 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 225 | 0 | 0 | 0 |  | 6741 | 2681 | 9422 | 4306 | 710 | 2156 | 0 | 1329 | 500 | 159 | 120 | 33 | 108 | 1 | 0 | 106.3
7:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 362 | 304 |  | 0 | 250 | 295 | 0 | 0 | 30 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 8 | 19 | 2 | 100 | 0 | 0 | 285 | 295 | 105 | 8 | 91 | 23 | 30 | 0 | 43 | 0 | 0 | 25 | 19 | 8 | 25 | 17 | 100 | 160 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 110 | 161 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 305 | 24 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 107 | 4 | 30 | 200 | 40 | 322 | 96 | 0 | 51 | 1 | 178 | 54 | 51 | 34 | 48 | 40 | 320 | 17 | 3 | 54 | 53 | 0 | 0 | 3 |  | 711 | 0 | 285 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 18 | 0 | 162 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 225 | 0 | 0 | 0 |  | 6590 | 2654 | 9244 | 4283 | 711 | 2119 | 0 | 1244 | 480 | 159 | 120 | 17 | 100 | 11 | 0 | 106.3
8:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 372 | 261 |  | 0 | 250 | 280 | 0 | 0 | 30 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 30 | 28 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 19 | 15 | 7 | 100 | 0 | 0 | 285 | 290 | 105 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 0 | 34 | 19 | 8 | 25 | 21 | 104 | 160 | 0 | 22 | 1 | 43 | 30 | 44 | 0 | 110 | 162 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 290 | 22 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 123 | 13 | 76 | 0 | 55 | 322 | 98 | 0 | 51 | 2 | 177 | 54 | 51 | 82 | 47 | 100 | 320 | 32 | 9 | 59 | 53 | 0 | 10 | 5 |  | 711 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 18 | 0 | 177 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 224 | 0 | 0 | 0 |  | 6588 | 2647 | 9235 | 4297 | 711 | 2037 | 0 | 1279 | 479 | 160 | 120 | 17 | 104 | 31 | 0 | 106.29
9:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 396 | 222 |  | 0 | 250 | 275 | 0 | 0 | 30 | 336 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 30 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 19 | 15 | 4 | 100 | 0 | 0 | 280 | 285 | 95 | 8 | 93 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 104 | 158 | 0 | 22 | 1 | 43 | 30 | 44 | 0 | 110 | 162 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 300 | 22 | 2 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 13 | 90 | 40 | 105 | 322 | 98 | 20 | 51 | 3 | 267 | 54 | 51 | 98 | 48 | 100 | 320 | 54 | 11 | 112 | 53 | 0 | 0 | 20 |  | 710 | 0 | 275 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 18 | 0 | 195 | 0 | 363 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 10 | 380 | 224 | 0 | 0 | 0 |  | 6904 | 2660 | 9564 | 4299 | 710 | 2020 | 0 | 1627 | 457 | 160 | 120 | 17 | 104 | 50 | 0 | 106.29
10:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 405 | 200 |  | 0 | 250 | 260 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 13 | 25 | 30 | 28 | 33 | 8 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 19 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 137 | 8 | 90 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 7 | 33 | 21 | 104 | 156 | 0 | 22 | 2 | 43 | 30 | 45 | 0 | 110 | 162 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 290 | 22 | 2 | 0 | 32 | 0 | 0 | 40 | 0 | 149 | 2 | 90 | 85 | 105 | 322 | 115 | 35 | 70 | 2 | 287 | 54 | 73 | 114 | 47 | 75 | 320 | 88 | 18 | 162 | 75 | 0 | 0 | 7 |  | 710 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 17 | 0 | 177 | 0 | 338 | 17 | 0 | 50 | 0 | 34 | 0 | 2 | 30 | 360 | 190 | 0 | 0 | 0 |  | 7195 | 2673 | 9868 | 4265 | 710 | 1911 | 0 | 2107 | 439 | 162 | 120 | 17 | 104 | 33 | 0 | 106.28
11:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 404 | 188 |  | 0 | 250 | 260 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 18 | 25 | 30 | 28 | 33 | 24 | 0 | 88 | 75 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 19 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 144 | 8 | 90 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 13 | 114 | 150 | 0 | 22 | 1 | 43 | 30 | 45 | 0 | 110 | 161 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 290 | 22 | 2 | 0 | 100 | 0 | 0 | 40 | 0 | 149 | 10 | 90 | 94 | 105 | 323 | 115 | 35 | 79 | 3 | 303 | 36 | 108 | 114 | 47 | 75 | 320 | 94 | 17 | 162 | 79 | 0 | 1 | 9 |  | 711 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 17 | 0 | 169 | 0 | 357 | 35 | 0 | 105 | 0 | 37 | 0 | 3 | 90 | 380 | 220 | 0 | 0 | 0 |  | 7344 | 2858 | 10202 | 4214 | 711 | 1948 | 0 | 2413 | 459 | 163 | 120 | 17 | 114 | 43 | 0 | 106.27
12:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 373 | 188 |  | 0 | 250 | 240 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 0 | 28 | 0 | 32 | 0 | 88 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 5 | 0 | 20 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 148 | 8 | 90 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 7 | 33 | 14 | 116 | 142 | 0 | 22 | 1 | 43 | 30 | 47 | 0 | 163 | 162 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 280 | 22 | 2 | 0 | 230 | 0 | 0 | 42 | 0 | 149 | 20 | 90 | 138 | 108 | 322 | 115 | 35 | 90 | 5 | 303 | 36 | 110 | 25 | 48 | 75 | 320 | 94 | 31 | 162 | 79 | 0 | 16 | 31 |  | 711 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 17 | 0 | 189 | 0 | 391 | 80 | 0 | 113 | 0 | 70 | 0 | 3 | 113 | 370 | 220 | 0 | 0 | 0 |  | 7500 | 3005 | 10505 | 4168 | 711 | 2007 | 0 | 2663 | 449 | 163 | 120 | 17 | 116 | 91 | 0 | 106.27
13:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 338 | 184 |  | 0 | 250 | 230 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 72 | 28 | 8 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 27 | 28 | 0 | 43 | 0 | 84 | 75 | 120 | 0 | 3 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 42 | 15 | 6 | 80 | 0 | 0 | 260 | 265 | 148 | 8 | 90 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 7 | 33 | 18 | 116 | 142 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 110 | 162 | 63 | 78 | 0 | 192 | 18 | 0 | 9 | 260 | 22 | 2 | 0 | 286 | 0 | 0 | 70 | 0 | 149 | 20 | 90 | 155 | 108 | 322 | 115 | 35 | 105 | 1 | 305 | 49 | 110 | 17 | 47 | 70 | 320 | 94 | 30 | 162 | 95 | 0 | 17 | 13 |  | 710 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 85 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 183 | 0 | 294 | 105 | 0 | 113 | 0 | 72 | 0 | 3 | 113 | 370 | 160 | 0 | 0 | 0 |  | 7567 | 2849 | 10416 | 4087 | 710 | 1766 | 0 | 2897 | 449 | 159 | 120 | 45 | 116 | 67 | 0 | 106.26
14:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 310 | 184 |  | 0 | 250 | 270 | 0 | 0 | 40 | 255 | 0 | 0 | 0 | 72 | 48 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 28 | 16 | 51 | 0 | 84 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 25 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 132 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 15 | 116 | 130 | 0 | 22 | 1 | 43 | 30 | 47 | 0 | 110 | 162 | 62 | 75 | 0 | 152 | 18 | 0 | 9 | 280 | 24 | 2 | 0 | 286 | 0 | 0 | 40 | 0 | 149 | 10 | 90 | 136 | 117 | 323 | 95 | 17 | 105 | 4 | 305 | 54 | 110 | 17 | 48 | 70 | 320 | 93 | 28 | 162 | 116 | 0 | 17 | 10 |  | 710 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 0 | 181 | 0 | 345 | 70 | 0 | 113 | 0 | 70 | 0 | 4 | 113 | 370 | 124 | 0 | 0 | 0 |  | 7475 | 2813 | 10288 | 3956 | 710 | 1830 | 0 | 2825 | 450 | 159 | 120 | 65 | 116 | 57 | 0 | 106.26
15:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 322 | 187 |  | 0 | 250 | 270 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 72 | 48 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 33 | 16 | 51 | 0 | 80 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 25 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 133 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 15 | 116 | 130 | 0 | 22 | 1 | 43 | 30 | 47 | 0 | 163 | 159 | 61 | 75 | 0 | 216 | 18 | 0 | 9 | 300 | 24 | 2 | 0 | 285 | 0 | 0 | 55 | 0 | 149 | 9 | 90 | 136 | 120 | 322 | 104 | 17 | 92 | 3 | 305 | 54 | 110 | 17 | 48 | 70 | 320 | 94 | 19 | 162 | 116 | 0 | 9 | 7 |  | 709 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 17 | 0 | 171 | 0 | 366 | 105 | 0 | 113 | 0 | 70 | 0 | 4 | 113 | 400 | 172 | 0 | 0 | 0 |  | 7631 | 2939 | 10570 | 4067 | 709 | 1981 | 0 | 2839 | 475 | 155 | 120 | 65 | 116 | 43 | 0 | 106.25
16:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 335 | 190 |  | 0 | 250 | 270 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 72 | 48 | 10 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 30 | 33 | 16 | 51 | 0 | 82 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 25 | 15 | 5 | 80 | 0 | 0 | 270 | 275 | 133 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 8 | 114 | 141 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 163 | 61 | 75 | 0 | 219 | 18 | 0 | 9 | 295 | 24 | 2 | 0 | 282 | 0 | 0 | 40 | 0 | 122 | 9 | 90 | 100 | 117 | 322 | 115 | 17 | 95 | 1 | 305 | 54 | 110 | 17 | 48 | 70 | 320 | 94 | 12 | 162 | 116 | 0 | 17 | 6 |  | 709 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 168 | 0 | 360 | 105 | 0 | 70 | 0 | 34 | 0 | 3 | 70 | 420 | 171 | 0 | 0 | 0 |  | 7564 | 2817 | 10381 | 4099 | 709 | 1974 | 0 | 2616 | 496 | 157 | 120 | 65 | 114 | 31 | 0 | 106.25
17:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 316 | 190 |  | 0 | 250 | 240 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 72 | 64 | 10 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 27 | 33 | 16 | 51 | 0 | 82 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 2 | 0 | 17 | 10 | 4 | 25 | 15 | 6 | 80 | 0 | 0 | 260 | 270 | 133 | 8 | 92 | 13 | 30 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 8 | 104 | 146 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 130 | 162 | 62 | 75 | 0 | 191 | 18 | 0 | 7 | 290 | 24 | 2 | 0 | 282 | 0 | 0 | 40 | 0 | 115 | 3 | 100 | 100 | 123 | 321 | 115 | 17 | 105 | 0 | 305 | 54 | 68 | 17 | 49 | 70 | 320 | 94 | 3 | 162 | 116 | 0 | 17 | 3 |  | 709 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 0 | 167 | 0 | 366 | 105 | 0 | 70 | 0 | 34 | 0 | 2 | 70 | 420 | 161 | 0 | 0 | 0 |  | 7392 | 2811 | 10203 | 4003 | 709 | 1899 | 0 | 2621 | 498 | 157 | 120 | 81 | 104 | 11 | 0 | 106.24
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 306 | 192 |  | 0 | 250 | 290 | 0 | 0 | 36 | 300 | 0 | 0 | 0 | 85 | 100 | 29 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 22 | 33 | 16 | 51 | 0 | 82 | 75 | 115 | 0 | 9 | 0 | 0 | 0 | 0 |  | 22 | 0 | 92 | 70 | 37 | 30 | 15 | 3 | 80 | 0 | 0 | 290 | 300 | 143 | 8 | 90 | 13 | 30 | 0 | 43 | 0 | 50 | 35 | 19 | 11 | 33 | 8 | 134 | 144 | 0 | 22 | 0 | 43 | 30 | 45 | 0 | 110 | 162 | 61 | 40 | 0 | 205 | 18 | 0 | 9 | 280 | 24 | 2 | 20 | 291 | 154 | 40 | 76 | 0 | 115 | 0 | 100 | 127 | 128 | 321 | 95 | 52 | 76 | 0 | 253 | 54 | 85 | 70 | 88 | 100 | 320 | 94 | 0 | 162 | 72 | 0 | 17 | 0 |  | 709 | 0 | 225 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 50 | 5 | 93 | 27 | 16 | 25 | 14 | 11 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 1 | 162 | 0 | 357 | 105 | 0 | 81 | 0 | 93 | 0 | 0 | 90 | 460 | 211 | 0 | 4 | 0 |  | 8169 | 3268 | 11437 | 4105 | 709 | 1937 | 215 | 3053 | 541 | 157 | 160 | 426 | 134 | 0 | 0 | 106.24
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 346 | 192 |  | 0 | 250 | 255 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 102 | 150 | 42 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 16 | 51 | 0 | 82 | 75 | 120 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 70 | 88 | 50 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 144 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 50 | 52 | 19 | 11 | 33 | 9 | 128 | 144 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 164 | 62 | 75 | 0 | 225 | 18 | 0 | 9 | 290 | 24 | 5 | 20 | 298 | 30 | 25 | 200 | 25 | 149 | 0 | 100 | 172 | 125 | 321 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 105 | 88 | 100 | 320 | 94 | 0 | 162 | 110 | 0 | 17 | 0 |  | 710 | 0 | 225 | 0 | 0 | 170 | 0 | 0 | 4 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 50 | 19 | 93 | 27 | 43 | 37 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 177 | 0 | 421 | 105 | 0 | 101 | 0 | 113 | 0 | 0 | 113 | 510 | 223 | 0 | 17 | 0 |  | 8789 | 3617 | 12406 | 4152 | 710 | 2079 | 100 | 3781 | 590 | 157 | 170 | 539 | 128 | 0 | 0 | 106.22
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 351 | 192 |  | 0 | 250 | 271 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 16 | 51 | 0 | 84 | 75 | 120 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 70 | 88 | 50 | 15 | 5 | 80 | 0 | 0 | 260 | 265 | 144 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 50 | 52 | 19 | 11 | 33 | 9 | 128 | 147 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 160 | 62 | 75 | 0 | 225 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 122 | 321 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 0 | 0 |  | 713 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 4 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 50 | 30 | 93 | 27 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 175 | 0 | 390 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 223 | 0 | 17 | 0 |  | 8760 | 3629 | 12389 | 4154 | 713 | 2067 | 0 | 3834 | 610 | 159 | 170 | 554 | 128 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 352 | 192 |  | 0 | 250 | 245 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 70 | 88 | 50 | 15 | 8 | 80 | 0 | 0 | 260 | 265 | 146 | 8 | 90 | 23 | 30 | 0 | 51 | 0 | 50 | 52 | 19 | 11 | 33 | 9 | 130 | 149 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 162 | 62 | 75 | 0 | 225 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 122 | 321 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 95 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 6 | 0 |  | 713 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 4 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 50 | 30 | 93 | 27 | 43 | 40 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 175 | 0 | 388 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 223 | 0 | 17 | 0 |  | 8766 | 3637 | 12403 | 4176 | 713 | 2041 | 0 | 3841 | 620 | 159 | 170 | 553 | 130 | 0 | 0 | 106.23
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 351 | 193 |  | 0 | 250 | 250 | 0 | 0 | 44 | 300 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 25 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 96 | 70 | 88 | 50 | 15 | 18 | 80 | 0 | 0 | 260 | 265 | 144 | 8 | 90 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 9 | 128 | 149 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 159 | 62 | 75 | 0 | 225 | 18 | 0 | 9 | 280 | 18 | 11 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 128 | 321 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 98 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 | 0 |  | 713 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 10 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 0 | 25 | 0 | 93 | 12 | 16 | 0 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 16 | 0 | 172 | 0 | 390 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 224 | 0 | 17 | 0 |  | 8701 | 3524 | 12225 | 4158 | 713 | 2061 | 0 | 3787 | 640 | 160 | 170 | 408 | 128 | 0 | 0 | 106.22
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 352 | 192 |  | 0 | 250 | 255 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 25 | 0 | 85 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 70 | 63 | 50 | 15 | 28 | 80 | 0 | 0 | 260 | 265 | 144 | 8 | 90 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 9 | 128 | 149 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 160 | 62 | 75 | 0 | 226 | 18 | 0 | 9 | 285 | 18 | 11 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 135 | 321 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 94 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 | 0 |  | 712 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 16 | 0 | 172 | 0 | 390 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 223 | 0 | 17 | 0 |  | 8718 | 3416 | 12134 | 4167 | 712 | 2079 | 0 | 3748 | 640 | 160 | 120 | 380 | 128 | 0 | 0 | 106.22
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 352 | 195 |  | 0 | 250 | 280 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 115 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 23 | 33 | 33 | 8 | 0 | 87 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 70 | 0 | 40 | 15 | 30 | 80 | 0 | 0 | 270 | 305 | 30 | 8 | 93 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 9 | 124 | 148 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 160 | 62 | 75 | 0 | 226 | 18 | 0 | 9 | 280 | 18 | 11 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 137 | 321 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 | 0 |  | 712 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 16 | 0 | 169 | 0 | 389 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 224 | 0 | 17 | 0 |  | 8549 | 3278 | 11827 | 4088 | 712 | 2102 | 0 | 3662 | 640 | 162 | 120 | 217 | 124 | 0 | 0 | 106.21
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 352 | 229 |  | 0 | 250 | 260 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 115 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 8 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 80 | 0 | 40 | 15 | 31 | 80 | 0 | 0 | 280 | 310 | 39 | 8 | 92 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 9 | 120 | 155 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 162 | 62 | 75 | 0 | 0 | 18 | 0 | 9 | 300 | 18 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 140 | 321 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 114 | 73 | 100 | 320 | 94 | 0 | 162 | 110 | 0 | 17 | 0 |  | 707 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 17 | 0 | 165 | 0 | 389 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 224 | 0 | 17 | 0 |  | 8333 | 3270 | 11603 | 3897 | 707 | 2139 | 0 | 3617 | 621 | 162 | 140 | 200 | 120 | 0 | 0 | 106.21
KWH | 0 | 0 | 0 | 0 | 7205600 | 0 | 0 | 8835070 | 5618000 |  | 0 | 6158000 | 6529658 | 0 | 0 | 1005020 | 7694131 | 0 | 0 | 0 | 1210032 | 1287840 | 390736 | 0 | 0 | 0 | 1172880 | 1010122 | 982251 | 295920 | 600000 | 660060 | 790700 | 646500 | 575040 | 0 | 1960271 | 1808000 | 2800000 | 0 | 117570 | 0 | 0 | 0 | 0 |  | 147600 | 0 | 1069655 | 671520 | 381120 | 672000 | 351840 | 398880 | 2214464 | 0 | 0 | 6943700 | 6915000 | 2897000 | 217454 | 2192950 | 498096 | 748800 | 0 | 1055788 | 0 | 126824 | 1142256 | 444348 | 234180 | 712100 | 391800 | 2800320 | 3462240 | 0 | 480276 | 10800 | 1021000 | 704160 | 1107600 | 0 | 3417381 | 3755000 | 1465536 | 1805760 | 0 | 4671150 | 403000 | 0 | 207180 | 7154000 | 553512 | 161664 | 30336 | 4137489 | 123969 | 48757 | 2184000 | 53584 | 3131712 | 114750 | 2157120 | 3828000 | 2552581 | 7730000 | 2578800 | 985200 | 2214690 | 26039 | 6794618 | 1247900 | 2320907 | 1865040 | 1438920 | 2096640 | 7647300 | 1740480 | 201540 | 3254400 | 2402455 | 0 | 377280 | 133381 |  | 17174545 | 0 | 6227424 | 0 | 0 | 3252480 | 0 | 0 | 11520 | 0 | 0 | 2101347 | 620304 | 0 | 0 | 0 | 0 | 153447 | 45981 | 479304 | 94170 | 114507 | 88808 | 327840 | 148076 | 497280 | 0 | 240804 | 1906910 | 0 | 0 | 0 | 0 | 0 | 0 | 3453809 | 0 | 416425 | 37440 | 4501555 | 0 | 8936545 | 1461600 | 0 | 1793280 | 0 | 1241856 | 0 | 29795 | 1670112 | 11883000 | 4921582 | 0 | 138000 | 0 |  | 186379243 | 73969746 | 260348989 | 101903236 | 17174545 | 49810637 | 294086 | 63627744 | 13789910 | 3768271 | 3252480 | 3411455 | 2800320 | 516305 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7998216 | 0 | 0 | 8923420.7 | 5786540 |  | 0 | 6712220 | 7247920.38 | 0 | 0 | 8502469.2 | 8001896.24 | 0 | 0 | 0 | 11035491.84 | 12672345.6 | 3602585.92 | 0 | 0 | 0 | 8562024 | 7808243.06 | 9684994.86 | 221940 | 450000 | 0 | 0 | 0 | 5560636.8 | 0 | 529273.17 | 488160 | 5068000 | 0 | 1092225.3 | 0 | 0 | 0 | 0 |  | 0 | 0 | 10375653.5 | 6413016 | 3315744 | 5322240 | 443318.4 | 1184673.6 | 3277406.72 | 0 | 0 | 5138338 | 6915000 | 2665240 | 280515.66 | 2521892.5 | 562848.48 | 1048320 | 0 | 1805397.48 | 0 | 1280922.4 | 10908544.8 | 564321.96 | 175635 | 1246175 | 293850 | 21002400 | 3669974.4 | 0 | 609950.52 | 172152 | 1674440 | 1126656 | 1971528 | 0 | 3895814.34 | 3905200 | 2887105.92 | 3449001.6 | 0 | 8081089.5 | 882570 | 0 | 422647.2 | 7225540 | 415134 | 122864.64 | 516015.36 | 31279416.84 | 2104993.62 | 815217.04 | 11356800 | 895924.48 | 30816046.08 | 1341427.5 | 17580528 | 41533800 | 17995696.05 | 7188900 | 23518656 | 9310140 | 19289949.9 | 0 | 51367312.08 | 10869209 | 20400772.53 | 18613099.2 | 12331544.4 | 13963622.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98925379.2 | 0 | 6538795.2 | 0 | 0 | 45079372.8 | 0 | 0 | 120844.8 | 0 | 0 | 2374522.11 | 961471.2 | 0 | 0 | 0 | 0 | 1509918.48 | 467166.96 | 4241840.4 | 725109 | 1548134.64 | 860549.52 | 3176769.6 | 1436337.2 | 954777.6 | 0 | 182288.628 | 11498667.3 | 0 | 0 | 0 | 0 | 0 | 0 | 4559027.88 | 0 | 624637.5 | 636854.4 | 5266819.35 | 0 | 8847179.55 | 15259104 | 0 | 17018227.2 | 0 | 9636802.56 | 0 | 329234.75 | 12342127.68 | 52166370 | 0 | 0 | 0 | 0 |  | 590290795.17 | 307288329.508 | 897579124.678 | 103952837.148 | 98925379.2 | 52418184.11 | 4969004.9 | 471741082.94 | 63665037.3 | 1017433.17 | 45079372.8 | 32965578.86 | 21002400 | 1842814.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 373 | 188 |  | 0 | 250 | 240 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 0 | 28 | 0 | 32 | 0 | 88 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 5 | 0 | 20 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 148 | 8 | 90 | 23 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 7 | 33 | 14 | 116 | 142 | 0 | 22 | 1 | 43 | 30 | 47 | 0 | 163 | 162 | 62 | 78 | 0 | 192 | 18 | 0 | 9 | 280 | 22 | 2 | 0 | 230 | 0 | 0 | 42 | 0 | 149 | 20 | 90 | 138 | 108 | 322 | 115 | 35 | 90 | 5 | 303 | 36 | 110 | 25 | 48 | 75 | 320 | 94 | 31 | 162 | 79 | 0 | 16 | 31 |  | 711 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 17 | 0 | 189 | 0 | 391 | 80 | 0 | 113 | 0 | 70 | 0 | 3 | 113 | 370 | 220 | 0 | 0 | 0 |  | 10505 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 346 | 192 | 0 | 0 | 250 | 255 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 102 | 150 | 42 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 16 | 51 | 0 | 82 | 75 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 102 | 70 | 88 | 50 | 15 | 2 | 80 | 0 | 0 | 260 | 265 | 144 | 8 | 92 | 23 | 30 | 0 | 43 | 0 | 50 | 52 | 19 | 11 | 33 | 9 | 128 | 144 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 164 | 62 | 75 | 0 | 225 | 18 | 0 | 9 | 290 | 24 | 5 | 20 | 298 | 30 | 25 | 200 | 25 | 149 | 0 | 100 | 172 | 125 | 321 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 105 | 88 | 100 | 320 | 94 | 0 | 162 | 110 | 0 | 17 | 0 |  | 710 | 0 | 225 | 0 | 0 | 170 | 0 | 0 | 4 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 50 | 19 | 93 | 27 | 43 | 37 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 177 | 0 | 421 | 105 | 0 | 101 | 0 | 113 | 0 | 0 | 113 | 510 | 223 | 0 | 17 | 0 |  | 12406 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 350 | 300 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 51 | 0 | 82 | 75 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 88 | 50 | 15 | 10 | 80 | 0 | 0 | 330 | 330 | 145 | 8 | 92 | 23 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 150 | 0 | 22 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 62 | 80 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 135 | 321 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 728 | 0 | 300 | 0 | 0 | 225 | 0 | 0 | 25 | 40 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 94 | 27 | 50 | 40 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 17 | 100 | 220 | 0 | 400 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 350 | 300 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 80 | 75 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 |  | 50 | 100 | 85 | 25 | 15 | 5 | 80 | 0 | 0 | 300 | 300 | 140 | 8 | 90 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 150 | 0 | 22 | 1.6 | 43 | 30 | 50 | 0 | 163 | 160 | 60 | 80 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 320 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 100 | 95 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 724 | 0 | 250 | 0 | 0 | 225 | 0 | 0 | 5 | 0 | 0 | 84 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 27 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 17 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 362 | 294 | 0 | 0 | 250 | 250 | 0 | 0 | 30 | 218 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 18 | 25 | 8 | 30 |  | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 80 | 0 | 0 | 260 | 270 | 142 | 8 | 93 | 23 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 5 | 21 | 94 | 161 | 0 | 22 | 1 | 43 | 30 | 44 | 0 | 110 | 161 | 25 | 75 | 0 | 0 | 0 | 0 | 9 | 270 | 18 | 5 | 0 | 95 | 0 | 0 | 70 | 0 | 92 | 0 | 90 | 85 | 140 | 321 | 85 | 3 | 34 | 2 | 230 | 22 | 51 | 0 | 48 | 90 | 300 | 68 | 23 | 108 | 72 | 0 | 17 | 7 | 0 | 709 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 17 | 0 | 163 | 0 | 429 | 17 | 0 | 40 | 0 | 34 | 0 | 1 | 50 | 400 | 150 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9235 | 8:00
| Highest Generation |  | 12406 | 19:00
| Day Peak Generation |  | 10505 | 12:00
| Evening Peak Generation |  | 12406 | 19:00
| HVDC Max Flow |  | 713 | 19:30
| HVDC EvPeak Flow |  | 710 | 19:00
| Load factor L.F |  | 87.44%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-06
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10505 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9024 | MW
Evening Peak Generation : |  | 12406 | MW Hour : | 19:00 | Available Max Generation : |  | 14505 | MW
E.P. Demand (at gen end) : |  | 12406 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12500 | MW
Maximum Generation : |  | 12406 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2005 | MW
Total Gen. (MKWH) : |  | 260.349 | System Load Factor : | 87.44% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -488 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-06
Actual : | 106.16 | Ft.(MSL) , | Rule curve : | 106.45 | Ft.( MSL )
Gas Consumed : | Total = | 1121.74 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 156371021.258
: |  | Coal : | 63665037.3 | Oil : | 554755039.5 | Total : | 774791098.058
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4472.6828 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1524.7641 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1366.816 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1235.2742 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1116.1667 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 900.7166 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 498.7408 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 231.7807 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 694.7008 |  |  | 0 | 0%
Total | 0 |  | 12041.6427 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Sylhet-225 MW
7) Raozan #02
8) Shajibazar 330 Mw GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Kaliakoir 230 kV Ckt-1 was under shut down from 10:28 to 15:19 for A/M.
b) Cumilla(N)-Megnaghat 230 kV Ckt-1 tripped at 12:24 showing dist.Z1,A-phase at Cumilla(N) end &
dist.Z1,R-phase at Megnaghat end and was switched on at 12:50.
c) Hathazari-Abul Khair 230 kV Ckt-1 tripped at 12:25 showing dist.Z1,R-hase from both end and was
switched on at 13:59.
d) HVDC 400 kV 10CF24 filter was shut down at 08:15 for A/M.
e) Joydevpur-Ghorasal 132 kV Ckt-2 was shut down at 13:04 for PT maintenance at Ghorasal end.
f) Khagrachari 132/33 kV T-1 transformer was under shut down from 10:01 to 13:41 for C/M.
g) Mirpur-Uttara 132 kV Ckt was under shut down from 08:53 to 21:03 for A/M.
h) Rangamati-Khagrachari 132 kV Ckt-1 was under shut down from 08:53 to 16:07 for A/M.
i) Palashbari-Mithapukur 132 kV Ckt was under shut down from 11:45 to 15:07 for bus maintenance.
j) Lalmonirhat 132/33 kV T-3 transformer was under shut down from 08:20 to 15:45 for A/M.
k) Bogura 230/132 kV T-2 transformer was under shut down from 08:19 to 16:35 for A/M.
l) Jhenaidah(N) 230/132 kV T-1 transformer was under shut down from 14:42 to 16:14 for protection test.
m) Jhenaidah(N) 230/132 kV T-2 transformer was under shut down from 16:22 to 16:54 for protection test.
n) Rampal 230/11 kV startup transformer was charged at 18:39 at 11 kV end.
o) Sylhet-225 MW CCPP tripped at 23:37 showing E/F relay.
p) Siddirganj-335 MW CCPP ST was forced shut down at 05:21 for maintenance work.
q) Kishorganj 132/33 kV T-3 transformer is under shut down since 07:34(6/10/21) for C/M.
r) Bhulta 132/33 kV T-2 transformer was under shut down from 06:45 to 07:50(6/10/21) due to red hot
maintenance at 132 kV CB.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7205600 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8835070
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 192 | 5618000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6158000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 255 | 6529658 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 1005020 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 42 | 390736 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 295920
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7694131 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1210032
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1172880
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1287840
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1010122
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 982251
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1260060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 790700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 646500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 575040
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 4137489
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 30 | 123969 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 25 | 48757 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 53584 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3131712
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 985200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 1740480 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3254400
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 133381
| Dhaka area Total |  |  |  | 5719 | 3213 | 66276532
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 117570 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 114750
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 672000
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 157 | 3768271 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2214690
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1069655
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 70 | 671520 | Low demand
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2157120
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 351840
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 398880
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 88 | 381120 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26039
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 6794618
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1247900
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2320907
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2096640
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 110 | 2402455
| Chattogram area Total |  |  |  | 2382 | 1503 | 29605975
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2214464 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 144 | 2897000 | ST under maint
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6943700 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6915000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 498096 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 748800 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1055788 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 2552581 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 126824
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2192950 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 172 | 3828000 | High voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 444348
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 234180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2800320
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 712100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1142256
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 391800 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 30336 | Low demand
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1865040 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 88 | 1438920 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 377280 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1774 | 39627237
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 144 | 3462240 | Engine problem
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 480276
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10800
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 2184000
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2578800
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 201540
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 147600
| Mymensingh Area Total |  |  |  | 622 | 503 | 9065256
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1021000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 704160 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3417381
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 164 | 3755000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1107600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 161664
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1465536 | Machine problem
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1805760
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 225 | 4671150
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 403000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 553512
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7154000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 321 | 7730000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 207180
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7647300 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1796 | 41804243
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 710 | 17174545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 11520 | Low demand
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 170 | 3252480 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 6227424 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 37440 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1461600
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1214 | 28165009
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 620304
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2101347 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 416425 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 510 | 11883000
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 223 | 4921582
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 138000 | Low demand
| Barisal Area Total |  |  |  | 2046 | 886 | 20080658
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 153447
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 19 | 45981 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 94170 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 114507 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 88808 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 124 | 3453809 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 177 | 4501555 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 421 | 8936545 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 148076 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 497280
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240804
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 327840
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 479304 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 101 | 1793280 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1670112
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 0
| Rajshahi Area Total |  |  |  | 2179 | 1324 | 22545518
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1906910
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1241856
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29795
| Rangpur Area Total |  |  |  | 605 | 193 | 3178561
| Total |  |  |  | 21093 | 12406 | 260348989
| Eastern Grid Total |  |  |  | 14134 | 8789 | 186379243
| Western Grid Total |  |  |  | 6959 | 3617 | 73969746
| National Grid Total |  |  |  | 21093 | 12406 | 260348989
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-05
(a) ENTIRE EASTERN GRID : |  | 8134 | MW | (b) ENTIRE WESTERN GRID : |  | 3809 | MW
i) Dhaka area |  | 4309 | MW | i) Khulna area |  | 1490 | MW
ii) Chittagong area |  | 1286 | MW | ii) Rajshahi area |  | 1257 | MW
iii) Comilla area |  | 1125 | MW | iii) Barisal area |  | 348 | MW
iv) Mymensingh area |  | 955 | MW | iv) Rangpur area |  | 714 | MW
v) Sylhet area |  | 459 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11943 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 10:00 | Kishoreganj | 134 | 21:00 | Jessore | 120 | 18:30
Munsiganj | 94 | 0:00 | Netrokona | 101 | 20:00 | Benapol | 60 | 21:00
Sonargaon | 72 | 0:00 | Jamalpur | 143 | 20:00 | Jhenida(Old) | 118 | 18:30
Shyampur | 198 | 10:00 | Sherpur | 114 | 19:00 | Bottail | 124 | 18:30
Bhulta | 190 | 1:00 | Srimongal | 46 | 19:00 | G.K Project | 58 | 19:30
Madanganj | 52 | 18:00 | Shahjibazar | 98 | 1:00 | Faridpur | 144 | 21:00
Shitalakhya | 102 | 13:00 | Fenchuganj | 42 | 24:00 | Rajbari | 52 | 20:00
Rahim steel | 26 | 15:00 | Kulawara | 42 | 18:00 | Madaripur | 95 | 22:00
Matuail | 62 | 12:00 | Sylhet | 116 | 18:00 | Sariatpur | 62 | 21:00
Ghorasal | 76 | 22:00 | Chatak | 27 | 21:00 | Gopalganj | 92 | 20:00
Narsingdi | 175 | 1:00 | Sunamganj | 47 | 20:00 | Bagerhat | 93 | 19:30
Haripur (SBU) | 117 | 16:00 | Biani Bazar | 60 | 18:30 | Mongla | 47 | 12:00
Sreenagar | 39 | 21:00 | Comilla (S) | 134 | 18:00 | Satkhira | 103 | 23:00
Ullon | 61 | 1:00 | Comilla(N) | 137 | 22:00 | Gallamari | 33 | 13:00
Hasnabad | 78 | 1:00 | Chandpur | 74 | 22:00 | Magura | 54 | 19:30
Magbazar | 100 | 11:00 | Feni | 129 | 18:30 | Norail | 46 | 18:30
Maniknagar | 72 | 11:00 | Chowmuhani | 198 | 0:00 | Chuadanga | 100 | 21:00
Bangabhaban | 14 | 10:00 | Ashuganj | 34 | 7:00 | Barisal(N) | 43 | 21:00
Motijheel | 31 | 11:00 | Daudkandi | 142 | 1:00 | Barisal (S) | 104 | 19:30
Narinda | 64 | 13:00 | B.Baria | 14 | 1:00 | Patuakhali | 112 | 22:00
Kazla | 84 | 13:00 | Ramganj | 88 | 22:00 | Bhandaria | 50 | 19:30
Dhanmondi | 187 | 11:00 | Chaddagram | 44 | 20:00 | Borguna | 18 | 20:00
Lalbag | 75 | 13:00 | PHP | 9 | 20:00 | Borhan Uddin | 45 | 21:00
Madartek | 68 | 1:00 | Kochua | 62 | 21:00 | Ishurdi | 66 | 19:00
Dhaka University | 39 | 11:00 | Madunaghat | 61 | 18:30 | Ruppur Paromanobik | 3 | 1:00
Aftabnagar | 15 | 10:00 | Hathazari | 100 | 19:00 | Natore | 125 | 20:00
Fatullah | 63 | 10:00 | Khulshi | 204 | 15:00 | Bogra | 158 | 20:00
Nawabganj | 49 | 21:00 | Halishahar | 90 | 16:00 | Noagaon | 104 | 21:00
Keraniganj | 68 | 20:00 | Baraulia | 141 | 11:00 | Rajshahi | 155 | 21:00
Mirpur | 124 | 11:00 | Sikalbaha | 42 | 18:00 | Rajshahi New | 18 | 21:00
Kalyanpur | 90 | 18:00 | Dohazari | 106 | 20:00 | C.Nawabganj | 65 | 19:30
Gulshan | 128 | 11:00 | Cox'sbazar | 82.5 | 19:00 | Amnura | 41 | 20:00
Uttara | 84 | 11:00 | Chandraghona | 28 | 18:00 | Pabna | 101 | 18:30
Uttara New | 31 | 12:00 | Kaptai | 4.2 | 18:30 | Shahjadpur | 99 | 21:00
Kamrangirchar | 100 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 106 | 20:00
Savar | 165 | 12:00 | Bakulia | 119 | 18:00 | Niyamatpur | 70 | 21:00
Bhasantec | 137 | 12:00 | Julda | 23 | 12:00 | Joypurhat | 53 | 20:00
Agargaon | 89 | 12:00 | TK chemical | 28.9 | 20:00 | Sherpur(Bogura) | 54 | 18:30
Satmosjid | 102 | 12:00 | Modern Steel | 10 | 9:00 | Mohastangor | 62 | 19:30
Tongi | 119 | 18:00 | Shahmirpur | 22 | 16:00 | Bhangura | 32 | 19:00
Kabirpur | 234 | 12:00 | Khagrachhari | 26 | 19:00 | Rangpur | 118 | 18:30
Basundhara | 196 | 12:00 | Matarbari | 31 | 1:00 | Lalmonirhat | 37 | 19:00
Manikganj | 68 | 21:00 | Baroiar Hat | 48 | 18:00 | Saidpur | 85 | 18:30
Joydevpur | 183 | 18:00 | Rangamati | 14 | 10:00 | Purbasadipur | 86 | 18:30
New Tongi | 90 | 12:00 | Abul Khair 230 | 156 | 2:00 | Thakurgaon | 77 | 18:30
Kodda | 282 | 12:00 | BSRM | 152 | 2:00 | Palashbari | 110 | 19:30
Dhamrai | 108 | 18:00 | GPH Ispat | 22 | 12:00 | Barapukuria | 45 | 19:00
Rajendrapur | 100 | 19:00 | Agrabad | 71 | 18:00 | Panchagar | 48 | 18:30
Valuka | 120 | 15:00 | Goalpara | 29 | 13:00 | Joldhaka | 54 | 19:30
Tangail | 196 | 19:00 | Central S/S | 102 | 18:30 | Kurigram | 53 | 18:30
Mymensing | 192 | 18:00 | Noapara | 43 | 22:00 | Mithapukur | 28 | 18:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 24:00 | 402 | 10:00 | Kaliakoir | 396 | 0.41667 | 387 | 0.375
| Bheramara | 401 | 14:00 | 396 | 22:00 | Bhulta | 385 | 24:00 | 377 | 0.45833
| Ashuganj(N) | 392 | 17:00 | 383 | 11:00 | Gopalganj | 404 | 0.625 | 387 | 0.041667
| Payra | 410 | 22:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 236 | 19:00 | 226 | 6:00
| Ishurdi | 234 | 17:00 | 224 | 1:00 | Megnaghat | 231 | 17:00 | 228 | 11:00
| Ashuganj | 240 | 6:00 | 236 | 4:00 | Fenchuganj | 245 | 24:00 | 241 | 1:00
| Serajganj | 230 | 10:00 | 225 | 1:00 | Siddhirganj | 232 | 24:00 | 225 | 11:00
| Baghabari | 233 | 17:00 | 225 | 18:30 | Maniknagar | 230 | 24:00 | 223 | 11:00
| Barapukuria | 237 | 1:00 | 227 | 18:30 | Agargaon | 229 | 8:00 | 220 | 11:00
| Bogra | 226 | 15:00 | 216 | 18:30 | Barisal | 239 | 20:00 | 231 | 1:00
| Rajshahi | 230 | 17:00 | 217 | 1:00 | Bhola 225 MW | 242 | 8:00 | 236 | 1:00
| Khulna South | 232 | 17:00 | 219 | 1:00 | AKSML | 237 | 20:00 | 227 | 7:00
| Rampura | 229 | 4:00 | 226 | 9:00 | BSRM | 234 | 19:00 | 229 | 2:00
| Haripur | 230 | 23:00 | 225 | 11:00 | Bibiyana | 244 | 13:00 | 239 | 11:00
| Hasnabad | 228 | 23:00 | 220 | 11:00 | Bhulta | 233 | 24:00 | 224 | 11:00
| Shyampur | 228 | 22:00 | 221 | 11:00 | Ashuganj (S) | 237 | 14:00 | 233 | 11:00
| Aminbazar | 231 | 1:00 | 222 | 2:00 | Kaliakoir | 231 | 13:00 | 222 | 9:00
| Tongi | 232 | 23:00 | 220 | 9:00 | GPH | 236 | 19:00 | 229 | 6:00
| Comilla (N) | 232 | 19:00 | 228 | 11:00 | Jhenaidah | 228 | 17:00 | 214 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 0:00 | 130 | 11:00 | Madanhat | 140 | 0.77083 | 134 | 0.58333
| Munsiganj | 136 | 21:00 | 130 | 10:00 | Hathazari | 139 | 0.79167 | 133 | 0.20833
| Sonargaon | 131 | 1:00 | 130 | 7:00 | Khulshi | 136 | 0.83333 | 130 | 0.29167
| Shyampur | 136 | 21:00 | 131 | 11:00 | Halishahar | 138 | 0.79167 | 130 | 0.29167
| Bhulta | 130 | 13:00 | 126 | 1:00 | Baraulia | 139 | 0.875 | 130 | 0.58333
| Madanganj | 135 | 22:00 | 130 | 10:00 | Sikalbaha | 140 | 0.8125 | 130 | 0.25
| Shitalakhya | 136 | 18:30 | 130 | 10:00 | Dohazari | 133 | 0.79167 | 127 | 0.16667
| Rahim steal | 134 | 18:00 | 131 | 9:00 | Cox'sbazar | 116 | 0.375 | 105 | 0.25
| Matuail | 134 | 0:00 | 130 | 11:00 | Chandraghona | 138 | 0.83333 | 134 | 0.29167
| Ghorasal | 138 | 7:00 | 137 | 1:00 | Kaptai | 136 | 0.91667 | 135 | 0.041667
| Narsinghdi | 133 | 10:00 | 125 | 22:00 | A. Khaer Stl. | 137 | 0.875 | 133 | 0.33333
| Haripur (SBU) | 134 | 14:00 | 131 | 9:00 | Bakulia | 138 | 0.79167 | 131 | 0.29167
| Sreenagar | 135 | 0:00 | 129 | 11:00 | Julda | 139 | 0.79167 | 132 | 0.16667
| Ullon | 134 | 23:00 | 128 | 11:00 | TK Chemical | 137 | 0.8125 | 133 | 0.375
| Hasnabad | 138 | 10:00 | 130 | 9:00 | Modern Steel | 138 | 0.875 | 130 | 0.20833
| Magbazar | 135 | 0:00 | 127 | 11:00 | Shahmirpur | 138 | 0.83333 | 130 | 0.083333
| Maniknagar | 134 | 22:00 | 129 | 11:00 | Khagrachhari | 136 | 0.79167 | 131 | 0.66667
| Bangabhaban | 134 | 22:00 | 129 | 11:00 | Matarbari | 120 | 0.29167 | 110 | 0.041667
| Motijheel | 134 | 22:00 | 129 | 11:00 | Baroiar Hat | 136 | 0.375 | 130 | 0.625
| Narinda | 134 | 22:00 | 129 | 11:00 | Rangamati | 137 | 19:00 | 133 | 6:00
| Kazla | 134 | 22:00 | 129 | 11:00 | Agrabad | 136 | 19:00 | 130 | 16:00
| Dhanmondi | 134 | 22:00 | 128 | 11:00 | Goalpara S/S | 138 | 13:00 | 131 | 0.041667
| Lalbag | 134 | 18:30 | 128 | 11:00 | Khulna Central S/S | 137 | 12:00 | 132 | 0.041667
| Madartek | 134 | 6:00 | 128 | 11:00 | Noapara | 136 | 17:00 | 128 | 0.041667
| Dhaka University | 134 | 6:00 | 129 | 10:00 | Jessore | 133 | 10:00 | 124 | 0.8125
| Aftabnagar | 134 | 4:00 | 129 | 10:00 | Benapol | 134 | 0.41667 | 124 | 0.8125
| Fatullah | 136 | 18:30 | 130 | 13:00 | Jhenida(Old) | 136 | 17:00 | 126 | 0.91667
| Nawabganj | 134 | 18:30 | 129 | 11:00 | Bottail | 135 | 0.41667 | 129 | 0.083333
| Keraniganj | 134 | 18:30 | 128 | 11:00 | G.K Project | 138 | 0.41667 | 134 | 0.041667
| Mirpur | 132 | 0:00 | 126 | 11:00 | Faridpur | 133 | 0.25 | 129 | 0.875
| Kalyanpur | 132 | 22:00 | 127 | 11:00 | Rajbari | 134 | 0.41667 | 128 | 0.041667
| Gulshan | 134 | 0:00 | 128 | 11:00 | Madaripur | 139 | 0.25 | 131 | 0.75
| Uttara | 132 | 22:00 | 125 | 10:00 | Shariyatpur S/S | 138 | 17:00 | 130 | 0.041667
| Uttara New | 137 | 13:00 | 128 | 3:00 | Gopalganj | 141 | 0.41667 | 132 | 0.041667
| Kamrangirchar | 134 | 18:30 | 128 | 11:00 | Bagerhat | 135 | 12:00 | 125 | 0.041667
| Savar | 134 | 22:00 | 128 | 8:00 | Mongla | 135 | 16:00 | 126 | 0.95833
| Bhasantec | 135 | 22:00 | 128 | 11:00 | Satkhira | 137 | 17:00 | 126 | 20:00
| Agargaon | 136 | 23:00 | 129 | 11:00 | Gallamari | 135 | 0.41667 | 126 | 23:00
| Satmosjid | 136 | 0:00 | 129 | 11:00 | Magura | 135 | 9:00 | 125 | 0.77083
| Tongi | 141 | 23:00 | 131 | 9:00 | Narail | 133 | 0.41667 | 123 | 0.77083
| Kabirpur | 135 | 13:00 | 130 | 15:00 | Chuadanga | 131 | 10:00 | 118 | 0.83333
| Basundhara | 138 | 0:00 | 129 | 9:00 | Barisal(N) | 139 | 7:00 | 131 | 0.91667
| Manikganj | 140 | 13:00 | 135 | 21:00 | Barisal (S) | 137 | 10:00 | 129 | 21:00
| Joydevpur | 138 | 0:00 | 131 | 9:00 | Patuakhali(S) | 134 | 0.70833 | 125 | 0.91667
| New Tongi | 140 | 23:00 | 129 | 9:00 | Bhandaria | 135 | 0.29167 | 124 | 0.875
| Kodda | 139 | 0:00 | 125 | 2:00 | Borguna | 137 | 0.29167 | 126 | 0.875
| Dhamrai | 137 | 22:00 | 131 | 9:00 | Jhenaidah(230kV S/S) | 134 | 9:00 | 127 | 18:30
| Rajendrapur | 137 | 23:00 | 124 | 10:00 | Ishurdi | 136 | 17:00 | 131 | 1:00
| Valuka | 127 | 6:00 | 116 | 21:00 | Ruppur Paromanobik | 135 | 16:00 | 132 | 18:00
| Tangail | 135 | 1:00 | 126 | 10:00 | Natore | 136 | 18:00 | 129 | 1:00
| Mymensing | 130 | 5:00 | 121 | 21:00 | Bogra | 136 | 17:00 | 128 | 18:30
| Kishorganj | 132 | 9:00 | 120 | 21:00 | Noagaon | 132 | 17:00 | 123 | 18:30
| Netrokona | 129 | 6:00 | 118 | 21:00 | Rajshahi | 134 | 17:00 | 128 | 1:00
| Jamalpur | 134 | 9:00 | 126 | 2:00 | Rajshahi New | 136 | 17:00 | 127 | 1:00
| Sherpur | 134 | 10:00 | 123 | 3:00 | C.Nawabganj | 134 | 18:00 | 126 | 1:00
| Srimongal | 139 | 11:00 | 133 | 24:00 | Amnura | 133 | 18:00 | 125 | 2:00
| Shahjibazar | 136 | 9:00 | 132 | 1:00 | Pabna | 134 | 17:00 | 128 | 1:00
| Fenchuganj | 141 | 24:00 | 134 | 17:00 | Shahjadpur | 135 | 4:00 | 133 | 1:00
| Khulawara | 136 | 8:00 | 134 | 1:00 | Serajganj | 132 | 13:00 | 126 | 20:00
| Sylhet | 134 | 4:00 | 131 | 18:00 | Niyamatpur | 130 | 17:00 | 120 | 18:00
| Chatak | 133 | 2:00 | 125 | 23:00 | Joypurhat | 132 | 11:00 | 124 | 18:30
| Sunamganj | 133 | 5:00 | 122 | 24:00 | Sherpur(Bogura) | 135 | 17:00 | 128 | 18:30
| Biani Bazar | 134 | 8:00 | 129 | 18:00 | Mohastangor | 134 | 10:00 | 127 | 18:30
| Comilla(s) | 128 | 5:00 | 124 | 18:00 | Bangura | 136 | 16:00 | 130 | 18:30
| Comilla(n) | 138 | 19:30 | 134 | 1:00 | Rangpur | 130 | 1:00 | 118 | 18:00
| Chandpur | 140 | 22:00 | 135 | 18:30 | Lalmonirhat | 131 | 15:00 | 121 | 18:30
| Feni | 138 | 9:00 | 130 | 15:00 | Saidpur | 134 | 4:00 | 120 | 18:30
| Chowmuhani | 134 | 21:00 | 130 | 0:00 | Purbasadipur | 131 | 13:00 | 116 | 18:00
| Ashuganj | 139 | 13:00 | 135 | 20:00 | Thakurgaon | 133 | 14:00 | 114 | 18:00
| Daudkandi | 134 | 18:00 | 128 | 1:00 | Palashbari | 132 | 11:00 | 123 | 19:30
| B.Baria | 134 | 17:00 | 128 | 23:00 | Barapukuria | 137 | 1:00 | 127 | 18:30
| Ramganj | 138 | 10:00 | 129 | 8:00 | Panchagar | 134 | 0.58333 | 120 | 0.77083
| Chaddagram | 138 | 9:00 | 132 | 15:00 | Joldhaka | 129 | 0.45833 | 114 | 0.77083
| PHP | 137 | 9:00 | 130 | 15:00 | Kurigram | 130 | 0.041667 | 120 | 0.77083
| Kochua | 137 | 21:00 | 133 | 20:00 | Mithapukur | 134 | 0.58333 | 120 | 0.77083
Page 7 of 7

## L-Curve
Date | 2021-10-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 400 | 8333 | 3270 | 11603 |  |  |  | QF-LDC-11
0:30 | 344 | 8001 | 3119 | 11120 | Date: | 2021-10-05
1:00 | 288 | 7669 | 2968 | 10637
1:30 | 247 | 7633.5 | 2949.5 | 10583
2:00 | 206 | 7598 | 2931 | 10529
2:30 | 202 | 7515.5 | 2909 | 10424.5 | [5 empty] | Gen. at Eve. Peak | 12406 | 12406 MW (19:00 )
3:00 | 198 | 7433 | 2887 | 10320 | [6 empty] | 19:00
3:30 | 202 | 7338 | 2825 | 10163 | [5 empty] | Gen. at Day Peak | 10505 | 10505 MW (12:00 )
4:00 | 206 | 7243 | 2763 | 10006 | [6 empty] | 12:00
4:30 | 193 | 7170 | 2750.5 | 9920.5 | [5 empty] | Highest Generation | 12406
5:00 | 180 | 7097 | 2738 | 9835 | [6 empty] | 19:00
5:30 | 101 | 6919 | 2709.5 | 9628.5
6:00 | 22 | 6741 | 2681 | 9422
6:30 | 41 | 6665.5 | 2667.5 | 9333
7:00 | 60 | 6590 | 2654 | 9244
7:30 | 44 | 6589 | 2650.5 | 9239.5
8:00 | 28 | 6588 | 2647 | 9235
8:30 | 52 | 6746 | 2653.5 | 9399.5
9:00 | 76 | 6904 | 2660 | 9564
9:30 | 71 | 7049.5 | 2666.5 | 9716
10:00 | 66 | 7195 | 2673 | 9868
10:30 | 132 | 7269.5 | 2765.5 | 10035
11:00 | 198 | 7344 | 2858 | 10202
11:30 | 139 | 7422 | 2931.5 | 10353.5
12:00 | 80 | 7500 | 3005 | 10505
12:30 | 137 | 7533.5 | 2927 | 10460.5
13:00 | 194 | 7567 | 2849 | 10416
13:30 | 197 | 7521 | 2831 | 10352
14:00 | 200 | 7475 | 2813 | 10288
14:30 | 145 | 7553 | 2876 | 10429
15:00 | 90 | 7631 | 2939 | 10570
15:30 | 58 | 7597.5 | 2878 | 10475.5
16:00 | 26 | 7564 | 2817 | 10381
16:30 | 58 | 7478 | 2814 | 10292
17:00 | 90 | 7392 | 2811 | 10203
17:30 | 124 | 7780.5 | 3039.5 | 10820
18:00 | 158 | 8169 | 3268 | 11437
18:30 | 253 | 8479 | 3442.5 | 11921.5
19:00 | 348 | 8789 | 3617 | 12406
19:30 | 396 | 8760 | 3629 | 12389
20:00 | 404 | 8766 | 3637 | 12403 |  |  |  | Executive Engineer
20:30 | 442 | 8733.5 | 3580.5 | 12314 |  |  |  | Network Operation Division
21:00 | 480 | 8701 | 3524 | 12225
21:30 | 476 | 8709.5 | 3470 | 12179.5
22:00 | 472 | 8718 | 3416 | 12134 |  |  |  |  | Page 6 of 7
22:30 | 480 | 8633.5 | 3347 | 11980.5
23:00 | 488 | 8549 | 3278 | 11827
23:30 | 444 | 8441 | 3274 | 11715
24:00 | 400 | 8333 | 3270 | 11603
12406 MW (19:00 )
10505 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-05 |  | Energy |  | 260348989
[13 empty] | 2021-10-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3897 | 707 | 2139 | 0 | 3617 | 621 | 162 | 140 | 200 | 120 | 0 | 0
0:30 | 4085.5 | 708.5 | 2156.5 | 0 | 3004.5 | 611 | 160.5 | 130 | 141.5 | 122 | 0 | 0 | Date: | 2021-10-05
1:00 | 4274 | 710 | 2174 | 0 | 2392 | 601 | 159 | 120 | 83 | 124 | 0 | 0
1:30 | 4319 | 710 | 2204.5 | 0 | 2265 | 600 | 158.5 | 120 | 83 | 123 | 0 | 0 | [8 empty] | Total Energy | 260.349 | Total Energy Gen 260.349 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.349 MKWHr
2:00 | 4364 | 710 | 2235 | 0 | 2138 | 599 | 158 | 120 | 83 | 122 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4331 | 710.5 | 2233 | 0 | 2095.5 | 589 | 157.5 | 120 | 67 | 121 | 0 | 0 | [8 empty] | Energy Requirement | 260.349
3:00 | 4298 | 711 | 2231 | 0 | 2053 | 579 | 157 | 120 | 51 | 120 | 0 | 0
3:30 | 4301 | 710.5 | 2237 | 0 | 1910.5 | 564.5 | 157 | 120 | 42.5 | 120 | 0 | 0 | [6 empty] | Shortage
4:00 | 4304 | 710 | 2243 | 0 | 1768 | 550 | 157 | 120 | 34 | 120 | 0 | 0
4:30 | 4306 | 710.5 | 2211.5 | 0 | 1715 | 540 | 157.5 | 120 | 42 | 118 | 0 | 0
5:00 | 4308 | 711 | 2180 | 0 | 1662 | 530 | 158 | 120 | 50 | 116 | 0 | 0
5:30 | 4307 | 710.5 | 2168 | 0 | 1495.5 | 515 | 158.5 | 120 | 41.5 | 112 | 0.5 | 0
6:00 | 4306 | 710 | 2156 | 0 | 1329 | 500 | 159 | 120 | 33 | 108 | 1 | 0
6:30 | 4294.5 | 710.5 | 2137.5 | 0 | 1286.5 | 490 | 159 | 120 | 25 | 104 | 6 | 0 |  |  |  |  | Coal
7:00 | 4283 | 711 | 2119 | 0 | 1244 | 480 | 159 | 120 | 17 | 100 | 11 | 0
7:30 | 4290 | 711 | 2078 | 0 | 1261.5 | 479.5 | 159.5 | 120 | 17 | 102 | 21 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4297 | 711 | 2037 | 0 | 1279 | 479 | 160 | 120 | 17 | 104 | 31 | 0
8:30 | 4298 | 710.5 | 2028.5 | 0 | 1453 | 468 | 160 | 120 | 17 | 104 | 40.5 | 0
9:00 | 4299 | 710 | 2020 | 0 | 1627 | 457 | 160 | 120 | 17 | 104 | 50 | 0
9:30 | 4282 | 710 | 1965.5 | 0 | 1867 | 448 | 161 | 120 | 17 | 104 | 41.5 | 0
10:00 | 4265 | 710 | 1911 | 0 | 2107 | 439 | 162 | 120 | 17 | 104 | 33 | 0
10:30 | 4239.5 | 710.5 | 1929.5 | 0 | 2260 | 449 | 162.5 | 120 | 17 | 109 | 38 | 0
11:00 | 4214 | 711 | 1948 | 0 | 2413 | 459 | 163 | 120 | 17 | 114 | 43 | 0
11:30 | 4191 | 711 | 1977.5 | 0 | 2538 | 454 | 163 | 120 | 17 | 115 | 67 | 0
12:00 | 4168 | 711 | 2007 | 0 | 2663 | 449 | 163 | 120 | 17 | 116 | 91 | 0
12:30 | 4127.5 | 710.5 | 1886.5 | 0 | 2780 | 449 | 161 | 120 | 31 | 116 | 79 | 0
13:00 | 4087 | 710 | 1766 | 0 | 2897 | 449 | 159 | 120 | 45 | 116 | 67 | 0
13:30 | 4087 | 710 | 1766 | 0 | 2897 | 449 | 159 | 120 | 45 | 116 | 67 | 0
14:00 | 4087 | 710 | 1766 | 0 | 2897 | 449 | 159 | 120 | 45 | 116 | 67 | 0
14:30 | 4077 | 709.5 | 1873.5 | 0 | 2868 | 462 | 157 | 120 | 55 | 116 | 55 | 0
15:00 | 4067 | 709 | 1981 | 0 | 2839 | 475 | 155 | 120 | 65 | 116 | 43 | 0
15:30 | 4083 | 709 | 1977.5 | 0 | 2727.5 | 485.5 | 156 | 120 | 65 | 115 | 37 | 0
16:00 | 4099 | 709 | 1974 | 0 | 2616 | 496 | 157 | 120 | 65 | 114 | 31 | 0
16:30 | 4051 | 709 | 1936.5 | 0 | 2618.5 | 497 | 157 | 120 | 73 | 109 | 21 | 0
17:00 | 4003 | 709 | 1899 | 0 | 2621 | 498 | 157 | 120 | 81 | 104 | 11 | 0
17:30 | 4054 | 709 | 1918 | 107.5 | 2837 | 519.5 | 157 | 140 | 253.5 | 119 | 5.5 | 0
18:00 | 4105 | 709 | 1937 | 215 | 3053 | 541 | 157 | 160 | 426 | 134 | 0 | 0
18:30 | 4128.5 | 709.5 | 2008 | 157.5 | 3417 | 565.5 | 157 | 165 | 482.5 | 131 | 0 | 0
19:00 | 4152 | 710 | 2079 | 100 | 3781 | 590 | 157 | 170 | 539 | 128 | 0 | 0
19:30 | 4154 | 713 | 2067 | 0 | 3834 | 610 | 159 | 170 | 554 | 128 | 0 | 0
20:00 | 4176 | 713 | 2041 | 0 | 3841 | 620 | 159 | 170 | 553 | 130 | 0 | 0
20:30 | 4167 | 713 | 2051 | 0 | 3814 | 630 | 159.5 | 170 | 480.5 | 129 | 0 | 0
21:00 | 4158 | 713 | 2061 | 0 | 3787 | 640 | 160 | 170 | 408 | 128 | 0 | 0
21:30 | 4162.5 | 712.5 | 2070 | 0 | 3767.5 | 640 | 160 | 145 | 394 | 128 | 0 | 0
22:00 | 4167 | 712 | 2079 | 0 | 3748 | 640 | 160 | 120 | 380 | 128 | 0 | 0
22:30 | 4127.5 | 712 | 2090.5 | 0 | 3705 | 640 | 161 | 120 | 298.5 | 126 | 0 | 0
23:00 | 4088 | 712 | 2102 | 0 | 3662 | 640 | 162 | 120 | 217 | 124 | 0 | 0
23:30 | 3992.5 | 709.5 | 2120.5 | 0 | 3639.5 | 630.5 | 162 | 130 | 208.5 | 122 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 32.6° C
24:00 | 3897 | 707 | 2139 | 0 | 3617 | 621 | 162 | 140 | 200 | 120 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 260.349 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.349 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 84 | 83 | 82 | 82 | 83 | 84 | 84 | 85 | 85 | 87 | 88 | 88 | 84 | 84 | 80 | 82 | 82 | 82 |  | 82 | 84 | 84 | 85 | 85 | 87 | 87 | 1960271
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1808000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 90 | 120 | 120 | 120 | 115 | 115 | 115 | 115 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 3 | 8 | 8 | 8 | 8 | 9 |  | 16 | 16 | 16 | 8 | 8 | 8 | 0 | 117570
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 13 | 13 | 2 | 10 | 20 | 20 | 10 | 9 | 9 | 3 | [9 empty] | 114750
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 92 |  | 102 | 102 | 102 | 96 | 102 | 102 | 85 | 1069655
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 85 | 51 | 51 | 51 | 51 | 70 | 79 | 90 | 105 | 105 | 92 | 95 | 105 | 76 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2214690
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 20 |  | 20 | [6 empty] | 30336
14 | Titas 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 |  |  |  | 0 | 126824
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 337 | 335 | 338 | 337 | 336 | 340 | 336 | 338 | 336 | 335 | 335 | 335 | 300 | 255 | 300 | 300 | 280 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7694131
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 15 | 15 | [6 empty] | 32 | 100 | 230 | 286 | 286 | 285 | 282 | 282 | 291 |  | 298 | 298 | 300 | 298 | 298 | 298 | 300 | 4137489
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7205600
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2214464
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 13 | 13 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 498096
33 | Ashuganj 225 MW CCPP | 114 | 107 | 103 | 101 | 108 | 110 | 105 | 105 | 95 | 137 | 144 | 148 | 148 | 132 | 133 | 133 | 133 | 143 |  | 144 | 144 | 146 | 144 | 144 | 30 | 39 | 2897000
34 | Ashuganj 450 MW CCPP(South) | 285 | 315 | 285 | 285 | 285 | 285 | 295 | 290 | 285 | 265 | 265 | 265 | 265 | 265 | 265 | 275 | 270 | 300 |  | 265 | 265 | 265 | 265 | 265 | 305 | 310 | 6915000
| Ashuganj 450 MW CCPP(North) | 280 | 305 | 280 | 280 | 280 | 280 | 285 | 285 | 280 | 260 | 260 | 260 | 260 | 260 | 260 | 270 | 260 | 290 |  | 260 | 260 | 260 | 260 | 260 | 270 | 280 | 6943700
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 748800
36 | Chandpur 150 MW CCPP | 90 | 91 | 92 | 92 | 90 | 92 | 91 | 92 | 93 | 90 | 90 | 90 | 90 | 92 | 92 | 92 | 92 | 90 |  | 92 | 92 | 90 | 90 | 90 | 93 | 92 | 2192950
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 394 | 395 | 395 | 394 | 394 | 394 | 362 | 372 | 396 | 405 | 404 | 373 | 338 | 310 | 322 | 335 | 316 | 306 |  | 346 | 351 | 352 | 351 | 352 | 352 | 352 | 8835070
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6158000
41 | Haripur 360MW CCPP(HPL) | 303 | 311 | 319 | 327 | 328 | 328 | 304 | 261 | 222 | 200 | 188 | 188 | 184 | 184 | 187 | 190 | 190 | 192 |  | 192 | 192 | 192 | 193 | 192 | 195 | 229 | 5618000
42 | RPCL 210MW CCPP | 135 | 149 | 156 | 160 | 160 | 160 | 160 | 160 | 158 | 156 | 150 | 142 | 142 | 130 | 130 | 141 | 146 | 144 |  | 144 | 147 | 149 | 149 | 149 | 148 | 155 | 3462240
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 9 | 11 | 18 | 17 | 31 | 30 | 28 | 19 | 12 | 3 | [9 empty] | 201540
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1021000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 704160
46 | Shajibazar 330 MW CCPP | 164 | 161 | 162 | 162 | 161 | 163 | 161 | 162 | 162 | 162 | 161 | 162 | 162 | 162 | 159 | 163 | 162 | 162 |  | 164 | 160 | 162 | 159 | 160 | 160 | 162 | 3755000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 63 | 62 | 61 | 61 | 62 | 61 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1465536
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 75 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 40 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1805760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 191 | 191 | 191 | 191 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 152 | 216 | 219 | 191 | 205 |  | 225 | 225 | 225 | 225 | 226 | 226 | 0 | 4671150
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 403000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 207180
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 8 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 161664
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 44 | 45 | 45 | 47 | 47 | 47 | 47 | 47 | 44 | 45 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1107600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 22 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 18 | 18 | 18 | 18 | 553512
57 | Bibiana-II 341 MW CCPP (Summit) | 265 | 300 | 285 | 300 | 285 | 290 | 305 | 290 | 300 | 290 | 290 | 280 | 260 | 280 | 300 | 295 | 290 | 280 |  | 290 | 290 | 280 | 280 | 285 | 280 | 300 | 7154000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7647300
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 982251
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 2 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 147600
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 |  |  | 19 | 19 | 19 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 351840
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 13 | 18 | 19 | [5 empty] | 18 |  | 19 | 18 | 18 | 18 | 18 | 16 | 18 | 295920
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 480276
63 | Impoprt (Tripura) | 124 | 122 | 120 | 120 | 116 | 108 | 100 | 104 | 104 | 104 | 114 | 116 | 116 | 116 | 116 | 114 | 104 | 134 |  | 128 | 128 | 130 | 128 | 128 | 124 | 120 | 2800320
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 37 | 37 | 28 | 2 | 7 | 4 | 2 | 2 | 2 | 6 | 2 | 2 | 5 | 6 | 3 |  | 2 | 5 | 8 | 18 | 28 | 30 | 31 | 398880
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 444348
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 7 | 11 | 7 | 7 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 234180
67 | Jangalia 33MW PP (Summit) |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 712100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 21 | 21 | 21 | 13 | 14 | 18 | 15 | 15 | 8 | 8 | 8 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 391800
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 27 | 28 | 30 | 30 | 27 | 22 |  | 30 | 30 | 30 | 30 | 30 | 23 | 30 | 660060
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 646500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 100 | 88 | 88 | 88 | 34 | 34 | 82 | 98 | 114 | 114 | 25 | 17 | 17 | 17 | 17 | 17 | 70 |  | 105 | 114 | 114 | 114 | 114 | 114 | 114 | 1865040
| Chowmuhani 113 MW | 48 | 47 | 48 | 42 | 42 | 41 | 48 | 47 | 48 | 47 | 47 | 48 | 47 | 48 | 48 | 48 | 49 | 88 |  | 88 | 96 | 95 | 98 | 94 | 96 | 73 | 1438920
| Manikgonj 162MW PP(MPGL) | 162 | 108 | 108 | 54 | 54 | 54 | 54 | 59 | 112 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3254400
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [9 empty] | 8 | 24 | 32 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 25 | 25 | 8 | 8 | 575040
79 | Kodda 150MW PP | 32 | 32 |  |  | 16 | 16 | [6 empty] | 28 | 48 | 48 | 48 | 64 | 100 |  | 150 | 150 | 150 | 150 | 150 | 115 | 115 | 1287840
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 52 | 52 | 52 | 52 | 52 | 25 | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 25 | 35 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1142256
| Gazipur 100 MW PP | 17 | [7 empty] | 20 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 52 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 985200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 2 | 3 | 5 | 1 | 4 | 3 | 1 | 0 | [9 empty] | 26039
| Jodiac Power | 39 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 36 | 49 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1247900
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 68 | 68 | 51 | 51 | 51 | 51 | 73 | 108 | 110 | 110 | 110 | 110 | 110 | 68 | 85 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2320907
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 8 | 10 | 10 | 10 | 10 | 29 |  | 42 | 51 | 51 | 51 | 51 | 51 | 51 | 390736
86 | Meghnaghat CCPP ( Summit) | 285 | 305 | 275 | 280 | 280 | 275 | 295 | 280 | 275 | 260 | 260 | 240 | 230 | 270 | 270 | 270 | 240 | 290 |  | 255 | 271 | 245 | 250 | 255 | 280 | 260 | 6529658
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 94 | 55 | 17 | 17 | 17 | 17 | 17 | 32 | 54 | 88 | 94 | 94 | 94 | 93 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1740480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 40 | 40 | 40 | [8 empty] | 5 | 10 | 10 | 10 | 10 | 10 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 671520
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 1055788
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | [6 empty] | 3 | 16 | 40 | 48 | 72 | 72 | 72 | 72 | 72 | 85 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1210032
95 | Patenga 50MW PP (Baraka) | 33 | 33 | 29 |  |  |  | 8 | 19 | 19 | 19 | 19 | 20 | 42 | 25 | 25 | 25 | 25 | 30 |  | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 672000
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 4 | 37 |  | 88 | 88 | 88 | 88 | 63 |  | 0 | 381120
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 40 | 40 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 36 |  | 40 | 40 | 40 | 44 | 55 | 55 | 55 | 1005020
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1010122
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 163 | 163 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 110 | 110 | 163 | 163 | 130 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3417381
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | [9 empty] | 10800
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1172880
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 154 |  | 30 | [6 empty] | 123969
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 40 |  | 25 | [5 empty] | 0 | 48757
106 | Mymensingh 200 MW PP (United) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 70 | 40 | 55 | 40 | 40 | 76 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2184000
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 25 | [5 empty] | 0 | 53584
114 | Kodda 149 MW PP Unit-1 (Summit) | 84 | 100 | 99 | 100 | 100 | 99 | 107 | 123 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 122 | 115 | 115 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3131712
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 60 | 30 | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2157120
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 40 | 85 | 94 | 138 | 155 | 136 | 136 | 100 | 100 | 127 |  | 172 | 200 | 200 | 200 | 200 | 200 | 200 | 3828000
117 | Ashuganj 150MW PP (Midland) | 80 | 80 | 80 | 80 | 80 | 40 | 40 | 55 | 105 | 105 | 105 | 108 | 108 | 117 | 120 | 117 | 123 | 128 |  | 125 | 122 | 122 | 128 | 135 | 137 | 140 | 2552581
118 | Bibiyana-III 400 MW CCPP | 322 | 322 | 322 | 322 | 319 | 322 | 322 | 322 | 322 | 322 | 323 | 322 | 322 | 323 | 322 | 322 | 321 | 321 |  | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 7730000
| Jamalpur 115 MW PP (United) | 115 | 97 | 98 | 98 | 98 | 98 | 96 | 98 | 98 | 115 | 115 | 115 | 115 | 95 | 104 | 115 | 115 | 95 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2578800
| Anwara 300 MW PP (United) | 304 | 304 | 304 | 304 | 250 | 178 | 178 | 177 | 267 | 287 | 303 | 303 | 305 | 305 | 305 | 305 | 305 | 253 |  | 304 | 305 | 305 | 305 | 305 | 305 | 304 | 6794618
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 70 | 40 | 100 | 100 | 75 | 75 | 75 | 70 | 70 | 70 | 70 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2096640
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 72 | 53 | 53 | 53 | 75 | 79 | 79 | 95 | 116 | 116 | 116 | 116 | 72 |  | 110 | 116 | 116 | 116 | 116 | 116 | 110 | 2402455
| Bhairob 54.5 MW | 35 | 35 | 35 | 32 |  |  |  | 10 |  |  | 1 | 16 | 17 | 17 | 9 | 17 | 17 | 17 |  | 17 |  | 6 | 17 | 17 | 17 | 17 | 377280
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 5 | 20 | 7 | 9 | 31 | 13 | 10 | 7 | 6 | 3 | [9 empty] | 133381
120 | Eastern Zone Total | 7669 | 7598 | 7433 | 7243 | 7097 | 6741 | 6590 | 6588 | 6904 | 7195 | 7344 | 7500 | 7567 | 7475 | 7631 | 7564 | 7392 | 8169 |  | 8789 | 8760 | 8766 | 8701 | 8718 | 8549 | 8333 | 186379243
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 4 | 4 | 4 | 10 |  |  |  | 11520
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 |  | 170 | 170 | 170 | 170 | 120 | 120 | 140 | 3252480
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | [6 empty] | 17 | 35 | 80 | 105 | 70 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1461600
130
131
132 | United Payra Power Ltd. | 17 | [16 empty] | 4 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 138000
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 224 | 225 | 225 | 225 | 225 | 225 | 224 | 224 | 190 | 220 | 220 | 160 | 124 | 172 | 171 | 161 | 211 |  | 223 | 223 | 223 | 224 | 223 | 224 | 224 | 4921582
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 16 | 16 | 16 | 17 | 416425
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 85 | 88 | 87 | 88 | 87 | 87 |  | 87 | 87 | 87 | 87 | 88 | 87 | 87 | 2101347
140 | Bhola 33 MW PP (Venture) | 34 | 32 | 32 | 31 | 29 | 26 | 13 | 15 | 20 | 19 | 20 | 20 | 20 | 17 | 22 | 21 | 21 | 31 |  | 32 | 32 | 33 | 35 | 35 | 34 | 34 | 620304
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 1 | [7 empty] | 0 | 37440
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 710 | 710 | 711 | 710 | 711 | 710 | 711 | 711 | 710 | 710 | 711 | 711 | 710 | 710 | 709 | 709 | 709 | 709 |  | 710 | 713 | 713 | 713 | 712 | 712 | 707 | 17174545
147 | Bheramara 410 MW CCPP | 265 | 270 | 270 | 270 | 270 | 280 | 285 | 280 | 275 | 270 | 260 | 260 | 250 | 240 | 235 | 230 | 230 | 225 |  | 225 | 220 | 220 | 220 | 225 | 220 | 220 | 6227424
148 | Payra 1320 MW | 520 | 520 | 500 | 470 | 450 | 420 | 400 | 400 | 380 | 360 | 380 | 370 | 370 | 370 | 400 | 420 | 420 | 460 |  | 510 | 530 | 540 | 560 | 560 | 560 | 540 | 11883000
149
150 | Barapukuria TPP Unit-1 | 81 | 79 | 79 | 80 | 80 | 80 | 80 | 79 | 77 | 79 | 79 | 79 | 79 | 80 | 75 | 76 | 78 | 81 |  | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 1906910
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 25 |  |  |  | 153447
Sirajgonj 6.55 MW Solar
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 144 | 144 | 144 | 150 | 152 | 153 | 160 | 157 | 148 | 141 | 137 | 131 | 124 | 121 | 129 | 124 | 121 | 121 |  | 124 | 124 | 124 | 121 | 121 | 122 | 120 | 3453809
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 194 | 194 | 194 | 194 | 179 | 160 | 162 | 177 | 195 | 177 | 169 | 189 | 183 | 181 | 171 | 168 | 167 | 162 |  | 177 | 175 | 175 | 172 | 172 | 169 | 165 | 4501555
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 375 | 392 | 391 | 379 | 388 | 373 | 363 | 348 | 363 | 338 | 357 | 391 | 294 | 345 | 366 | 360 | 366 | 357 |  | 421 | 390 | 388 | 390 | 390 | 389 | 389 | 8936545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 19 | 30 | 30 |  |  |  |  | 45981
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 19 | 20 | 20 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 497280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240804
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  | 27 | 27 | 27 | 12 |  |  |  | 94170
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 16 |  | 43 | 43 | 43 | 16 |  |  | 0 | 114507
167 | Katakhali 50 MW Peaking PP | [17 empty] | 25 |  | 37 | 40 | 40 |  |  |  |  | 88808
168 | Santahar 50 MW Peaking PP | [17 empty] | 11 |  | 34 | 35 | 34 | 34 | 34 |  |  | 148076
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 1 | 14 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 327840
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 93 |  | 93 | 93 | 93 | 93 | 94 |  | 0 | 479304
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 35 | 35 | [5 empty] | 1 | 50 | 105 | 113 | 113 | 113 | 113 | 70 | 70 | 81 |  | 101 | 113 | 113 | 113 | 113 | 113 | 113 | 1793280
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 35 | 35 | [5 empty] | 10 | 30 | 90 | 113 | 113 | 113 | 113 | 70 | 70 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1670112
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 25 | [7 empty] | 34 | 37 | 70 | 72 | 70 | 70 | 34 | 34 | 93 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1241856
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 3 | 2 | [9 empty] | 29795
178
178