## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-07 | Thursday
|  |  | Date (day): | 2021-10-07 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13414.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14551 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-06 | 2021-10-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 398 | 412 | 412 | 0
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 188 | 178 | 215 | 215 | 145 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 280 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 45 | 45 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 43 | 51 | 50 | 55 |  | 45 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 21 | 19 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 338 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 100 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 30 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 296 | 300 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 158 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 50 | 100 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 38 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 93 | 93 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2782 | 3626 | 3573 | 3849 | 853 | 815
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 115 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 4 | 25 | 25 | 25 |  | 0
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 50 | 25 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 161 | 157 | 155 | 157 | 73 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 0 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 13 | 8 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 9 | 87 | 85 | 88 |  | 20 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1319 | 1555 | 1445 | 1554 | 133 | 678
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 70 | 80 | 80 |  |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 139 | 124 | 140 | 145 |  | 75 | ST Under maint.
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 260 | 360 | 360 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 260 | 300 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51 |  | 0 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 128 | 140 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 90 | 90 | 92 |  | 71 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 180 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 0 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 140 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 10 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 50 | 150 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 100 | 100 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 48 | 97 | 95 | 96 |  | 17 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1728 | 1949 | 2080 | 2259 | 450 | 237
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 147 | 160 | 160 | 42 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 146 | 190 | 170 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 107 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 57 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 2 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 499 | 488 | 540.6 | 519 | 42 | 8
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 32 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 161 | 161 | 165 | 165 |  | 165 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 46 | 47 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 36 | 57 | 60 | 62
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 81 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 10 | 21 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 321 | 323 | 320 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1528 | 1502 | 1635 | 1638 | 142 | 583
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 709 | 712 | 724 | 728
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 5 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 135 | 215 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 215 | 215 | 250 | 300 |  |  | FGMO
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1164 | 1279 | 1359 | 1623 | 0 | 98
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 3 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 87 | 84 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 17 | 47 | 17 | 17 | 78 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 410 | 540 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 753 | 916 | 1086 | 1240 | 78 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 37 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 121 | 125 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 169 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 329 | 414 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 34 |  | 16 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 6 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 94 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 842 | 1321 | 1495 | 1676 | 380 | 100
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 85 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 169 | 193 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 10784 | 12829 | 13414.6 | 14551 | 2078 | 3024
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10363.7022 | 12329 | 12891.7767 | 13983.8864
| A. |  | 2021-10-06 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 12829 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9024 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12829 | MW
| 3 | Day peak Generation : |  |  | 10784 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12329 | MW
| 4 | Evening peak Generation : |  |  | 12829 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 267.4698 | MKWHr | By Solar | 0.71415 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 144.5409 | MKWHr |  | By Oil: | 84.6082 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.9901 | MKWHr |  | By Hydro: | 3.7576 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2078 | MW | Dhaka | 4358 | 4358 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3024 | MW | Chittagong | 1334 | 1334 |  | 0 |  | 18:00 |  | 148
|  |  |  | Total = |  |  | 5102 | MW | Khulna | 1541 | 1541 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1104.6 | MMCFD |  |  | Rajshahi | 1323 | 1323 |  | 0 |  | 19:00 |  | 142
| 8 | Fuel Cost : | i) Gas : | Taka | 145517971.11 | ii) Oil : | Taka | 674803550.69 | Comilla | 1203 | 1203 |  | 0 |  | 19:30 |  | 140
|  |  | iii) Coal : |  | 64511114.11 | Total | Taka | 884832635.91 | Mymensingh | 996 | 996 |  | 0 |  | 20:00 |  | 142
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.7855 | MKWHr. | Sylhet | 492 | 492 |  | 0 |  | 21:00 |  | 138
|  | ii) During Peak Demand : |  |  | -408 | MW (E to W) at | 19:30 | hrs | Barisal | 342 | 342 |  | 0 |  | 22:00 |  | 138
|  | iii) Maximum : |  |  | -444 | MW at | 21:00 | hrs | Rangpur | 740 | 740 |  | 0 |  | 23:00 |  | 138
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.5° C |  |  | Total | 12329 | 12329 |  | 0
| B. |  | 2021-10-07 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 31.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14551 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 1551 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 271.035 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9243 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1651 | MKWHr. | ii) HVDC Flow at Peak Time |  | 712 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6938 | MKWHr. | iii) Maximum HVDC Flow : |  | 715 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.16 |  | (b) Today: | 106 |  | (c) Rule Curve: |  | 106.54
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 352 | 323 |  | 0 | 250 | 225 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 98 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 50 | 0 | 40 | 15 | 31 | 80 | 0 | 0 | 280 | 305 | 37 | 8 | 92 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 21 | 114 | 161 | 0 | 22 | 0 | 43 | 30 | 47 | 0 | 163 | 163 | 62 | 75 | 0 | 0 | 18 | 0 | 9 | 265 | 18 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 133 | 321 | 115 | 35 | 105 | 0 | 304 | 54 | 102 | 34 | 53 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 220 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 0 | 161 | 0 | 389 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 200 | 0 | 17 | 0 |  | 8054 | 3258 | 11312 | 3906 | 710 | 2138 | 0 | 3361 | 619 | 160 | 155 | 149 | 114 | 0 | 0 | 106.2
2:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 352 | 326 |  | 0 | 250 | 255 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 7 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 32 | 15 | 31 | 80 | 0 | 0 | 280 | 305 | 37 | 8 | 92 | 23 | 52 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 112 | 161 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 130 | 162 | 62 | 75 | 0 | 0 | 18 | 0 | 9 | 280 | 18 | 11 | 0 | 300 | 0 | 0 | 130 | 0 | 73 | 0 | 100 | 200 | 138 | 321 | 115 | 0 | 105 | 0 | 304 | 54 | 110 | 0 | 48 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 709 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 17 | 0 | 161 | 0 | 398 | 70 | 0 | 113 | 0 | 100 | 0 | 0 | 113 | 510 | 225 | 0 | 0 | 0 |  | 7618 | 3111 | 10729 | 3909 | 709 | 2204 | 0 | 2812 | 589 | 158 | 120 | 116 | 112 | 0 | 0 | 106.2
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 359 | 327 |  | 0 | 250 | 265 | 0 | 0 | 30 | 271 | 0 | 0 | 0 | 7 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 25 | 15 | 31 | 80 | 0 | 0 | 280 | 305 | 37 | 8 | 91 | 23 | 47 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 110 | 160 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 130 | 161 | 62 | 75 | 0 | 0 | 18 | 0 | 9 | 285 | 18 | 11 | 0 | 195 | 0 | 0 | 130 | 0 | 50 | 0 | 100 | 200 | 135 | 321 | 115 | 0 | 105 | 0 | 304 | 54 | 102 | 0 | 48 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 17 | 0 | 161 | 0 | 414 | 70 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 470 | 225 | 0 | 0 | 0 |  | 7456 | 3066 | 10522 | 3892 | 710 | 2231 | 0 | 2636 | 549 | 158 | 120 | 116 | 110 | 0 | 0 | 106.19
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 372 | 326 |  | 0 | 250 | 257 | 0 | 0 | 30 | 240 | 0 | 0 | 0 | 7 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 31 | 80 | 0 | 0 | 280 | 305 | 33 | 8 | 91 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 106 | 161 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 130 | 161 | 62 | 75 | 0 | 0 | 18 | 0 | 9 | 280 | 18 | 11 | 0 | 145 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 155 | 137 | 321 | 115 | 0 | 105 | 0 | 304 | 54 | 110 | 0 | 48 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 709 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 17 | 0 | 161 | 0 | 414 | 53 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 460 | 225 | 0 | 0 | 0 |  | 7231 | 2885 | 10116 | 3876 | 709 | 2224 | 0 | 2322 | 539 | 156 | 120 | 64 | 106 | 0 | 0 | 106.18
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 341 | 332 |  | 0 | 250 | 280 | 0 | 0 | 30 | 233 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 80 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 80 | 0 | 0 | 295 | 320 | 32 | 8 | 93 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 160 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 130 | 158 | 62 | 75 | 0 | 0 | 18 | 0 | 9 | 295 | 18 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 120 | 137 | 321 | 115 | 0 | 105 | 0 | 304 | 54 | 68 | 0 | 47 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 17 | 0 | 163 | 0 | 414 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 470 | 225 | 0 | 0 | 0 |  | 7104 | 2828 | 9932 | 3870 | 710 | 2273 | 0 | 2091 | 549 | 155 | 120 | 64 | 100 | 0 | 0 | 106.17
6:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 356 | 332 |  | 0 | 250 | 262 | 0 | 0 | 30 | 219 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 80 | 0 | 0 | 270 | 295 | 50 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 96 | 163 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 130 | 163 | 63 | 75 | 0 | 0 | 18 | 0 | 9 | 265 | 18 | 11 | 0 | 95 | 0 | 0 | 70 | 0 | 50 | 1 | 100 | 85 | 145 | 322 | 115 | 0 | 34 | 0 | 251 | 54 | 51 | 0 | 48 | 100 | 320 | 94 | 0 | 162 | 90 | 0 | 17 | 0 |  | 709 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 17 | 0 | 162 | 0 | 423 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 420 | 210 | 0 | 0 | 0 |  | 6708 | 2775 | 9483 | 3853 | 709 | 2216 | 0 | 1800 | 499 | 157 | 120 | 32 | 96 | 1 | 0 | 106.16
7:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 300 |  | 0 | 250 | 277 | 0 | 0 | 30 | 222 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 0 | 30 | 0 | 0 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 80 | 0 | 0 | 260 | 265 | 142 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 90 | 162 | 0 | 22 | 0 | 43 | 30 | 44 | 0 | 110 | 160 | 52 | 75 | 0 | 0 | 18 | 0 | 9 | 285 | 18 | 11 | 0 | 95 | 0 | 0 | 70 | 0 | 53 | 3 | 60 | 85 | 137 | 320 | 85 | 0 | 34 | 0 | 196 | 17 | 51 | 0 | 48 | 60 | 315 | 55 | 8 | 108 | 22 | 0 | 17 | 1 |  | 709 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 17 | 0 | 155 | 0 | 418 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 400 | 160 | 0 | 0 | 0 |  | 6332 | 2692 | 9024 | 3855 | 709 | 2137 | 0 | 1432 | 479 | 158 | 120 | 32 | 90 | 12 | 0 | 106.15
8:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 362 | 294 |  | 0 | 250 | 250 | 0 | 0 | 30 | 218 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 18 | 25 | 8 | 30 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 80 | 0 | 0 | 260 | 270 | 142 | 8 | 93 | 23 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 5 | 21 | 94 | 161 | 0 | 22 | 1 | 43 | 30 | 44 | 0 | 110 | 161 | 25 | 75 | 0 | 0 | 0 | 0 | 9 | 270 | 18 | 5 | 0 | 95 | 0 | 0 | 70 | 0 | 92 | 0 | 90 | 85 | 140 | 321 | 85 | 3 | 34 | 2 | 230 | 22 | 51 | 0 | 48 | 90 | 300 | 68 | 23 | 108 | 72 | 0 | 17 | 7 |  | 709 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 17 | 0 | 163 | 0 | 429 | 17 | 0 | 40 | 0 | 34 | 0 | 1 | 50 | 400 | 150 | 0 | 0 | 0 |  | 6455 | 2705 | 9160 | 3751 | 709 | 2056 | 0 | 1725 | 479 | 160 | 120 | 32 | 94 | 34 | 0 | 106.14
9:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 369 | 236 |  | 0 | 250 | 275 | 0 | 0 | 30 | 218 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 10 | 33 | 33 | 2 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 80 | 0 | 0 | 340 | 265 | 140 | 8 | 92 | 23 | 54 | 0 | 51 | 0 | 0 | 0 | 14 | 11 | 25 | 21 | 58 | 156 | 0 | 22 | 1 | 44 | 30 | 44 | 0 | 130 | 162 | 36 | 75 | 0 | 0 | 0 | 0 | 9 | 270 | 18 | 0 | 0 | 142 | 0 | 0 | 70 | 0 | 149 | 7 | 90 | 85 | 133 | 323 | 85 | 17 | 34 | 3 | 245 | 54 | 51 | 0 | 48 | 100 | 320 | 93 | 38 | 158 | 72 | 0 | 17 | 11 |  | 709 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 174 | 0 | 422 | 17 | 0 | 80 | 0 | 34 | 0 | 2 | 70 | 400 | 180 | 0 | 0 | 0 |  | 6836 | 2787 | 9623 | 3891 | 709 | 2062 | 0 | 2040 | 480 | 161 | 120 | 40 | 58 | 62 | 0 | 106.13
10:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 202 |  | 0 | 250 | 300 | 0 | 0 | 40 | 214 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 10 | 30 | 25 | 25 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 4 | 80 | 0 | 0 | 305 | 315 | 140 | 8 | 92 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 25 | 21 | 94 | 153 | 0 | 22 | 2 | 44 | 30 | 44 | 0 | 130 | 160 | 35 | 75 | 0 | 0 | 0 | 0 | 9 | 300 | 18 | 0 | 0 | 165 | 0 | 0 | 70 | 0 | 149 | 5 | 100 | 85 | 132 | 321 | 96 | 17 | 83 | 4 | 298 | 54 | 83 | 0 | 48 | 100 | 320 | 93 | 48 | 162 | 102 | 0 | 17 | 19 |  | 710 | 0 | 215 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 17 | 0 | 165 | 0 | 390 | 17 | 0 | 94 | 0 | 34 | 0 | 3 | 90 | 400 | 180 | 0 | 0 | 0 |  | 7217 | 2771 | 9988 | 3895 | 710 | 2053 | 0 | 2330 | 480 | 161 | 120 | 64 | 94 | 81 | 0 | 106.12
11:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 202 |  | 0 | 250 | 300 | 0 | 0 | 45 | 219 | 0 | 0 | 0 | 58 | 64 | 5 | 0 | 0 | 0 | 35 | 55 | 55 | 18 | 25 | 6 | 33 | 25 | 25 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 24 | 15 | 3 | 80 | 0 | 0 | 265 | 275 | 138 | 8 | 92 | 23 | 52 | 0 | 51 | 0 | 0 | 2 | 19 | 11 | 25 | 17 | 96 | 154 | 0 | 22 | 2 | 44 | 30 | 47 | 0 | 163 | 160 | 35 | 75 | 0 | 0 | 0 | 0 | 7 | 300 | 18 | 8 | 0 | 285 | 0 | 0 | 93 | 0 | 149 | 20 | 100 | 142 | 130 | 321 | 115 | 17 | 105 | 5 | 303 | 54 | 110 | 0 | 47 | 90 | 320 | 93 | 43 | 162 | 108 | 0 | 0 | 24 |  | 709 | 0 | 210 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 0 | 151 | 0 | 384 | 70 | 0 | 94 | 0 | 70 | 0 | 3 | 113 | 400 | 200 | 0 | 0 | 0 |  | 7518 | 2878 | 10396 | 3805 | 709 | 2100 | 0 | 2764 | 480 | 161 | 120 | 64 | 96 | 97 | 0 | 106.11
12:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 188 |  | 0 | 250 | 260 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 84 | 100 | 43 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 6 | 33 | 25 | 30 | 0 | 86 | 75 | 120 | 0 | 4 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 70 | 9 | 39 | 16 | 5 | 80 | 0 | 0 | 310 | 295 | 139 | 8 | 93 | 23 | 50 | 0 | 51 | 0 | 0 | 10 | 19 | 11 | 25 | 17 | 94 | 154 | 0 | 22 | 3 | 44 | 30 | 46 | 0 | 163 | 161 | 36 | 75 | 0 | 0 | 0 | 0 | 9 | 305 | 10 | 8 | 50 | 296 | 0 | 0 | 146 | 50 | 149 | 19 | 100 | 180 | 128 | 321 | 115 | 38 | 105 | 4 | 305 | 54 | 110 | 80 | 48 | 90 | 320 | 93 | 57 | 162 | 108 | 0 | 17 | 33 |  | 709 | 0 | 215 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 0 | 150 | 0 | 329 | 105 | 0 | 94 | 0 | 85 | 0 | 4 | 113 | 410 | 220 | 0 | 0 | 0 |  | 7856 | 2928 | 10784 | 3650 | 709 | 2017 | 100 | 3208 | 490 | 161 | 135 | 100 | 94 | 120 | 0 | 106.1
13:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 180 |  | 0 | 250 | 240 | 0 | 0 | 45 | 0 | 0 | 90 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 6 | 33 | 25 | 51 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 80 | 70 | 40 | 16 | 6 | 110 | 0 | 0 | 280 | 290 | 117 | 8 | 93 | 23 | 54 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 25 | 17 | 100 | 142 | 0 | 22 | 2 | 44 | 30 | 23 | 0 | 163 | 158 | 31 | 75 | 0 | 0 | 0 | 0 | 9 | 280 | 10 | 8 | 0 | 296 | 0 | 0 | 170 | 0 | 149 | 16 | 100 | 180 | 127 | 322 | 97 | 105 | 105 | 4 | 305 | 42 | 110 | 98 | 49 | 90 | 320 | 93 | 51 | 162 | 108 | 0 | 17 | 32 |  | 709 | 0 | 215 | 0 | 0 | 170 | 0 | 0 | 4 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 0 | 146 | 0 | 326 | 105 | 0 | 94 | 0 | 107 | 0 | 4 | 113 | 420 | 222 | 0 | 0 | 0 |  | 8041 | 3010 | 11051 | 3686 | 709 | 1925 | 0 | 3538 | 500 | 160 | 170 | 154 | 100 | 109 | 0 | 106.09
14:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 358 | 180 |  | 0 | 250 | 278 | 0 | 0 | 45 | 0 | 0 | 62 | 0 | 102 | 150 | 52 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 6 | 33 | 25 | 51 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 75 | 50 | 16 | 7 | 80 | 0 | 0 | 265 | 275 | 115 | 8 | 93 | 23 | 55 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 15 | 104 | 141 | 0 | 22 | 2 | 44 | 30 | 44 | 0 | 110 | 157 | 30 | 72 | 0 | 0 | 0 | 0 | 9 | 270 | 10 | 8 | 0 | 296 | 0 | 0 | 150 | 0 | 149 | 17 | 100 | 180 | 127 | 322 | 97 | 105 | 105 | 4 | 305 | 54 | 110 | 98 | 47 | 100 | 320 | 93 | 44 | 162 | 108 | 0 | 17 | 28 |  | 710 | 0 | 215 | 0 | 0 | 130 | 0 | 0 | 4 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 40 | 0 | 145 | 0 | 236 | 105 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 420 | 220 | 0 | 0 | 0 |  | 7927 | 2966 | 10893 | 3550 | 710 | 1851 | 0 | 3582 | 500 | 157 | 130 | 209 | 104 | 100 | 0 | 106.08
15:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 380 | 180 |  | 0 | 250 | 240 | 0 | 0 | 45 | 40 | 0 | 94 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 6 | 25 | 25 | 51 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 75 | 50 | 16 | 4 | 80 | 0 | 0 | 260 | 265 | 139 | 8 | 92 | 23 | 20 | 0 | 43 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 106 | 142 | 0 | 22 | 1 | 44 | 30 | 36 | 0 | 163 | 159 | 31 | 72 | 0 | 0 | 0 | 0 | 9 | 290 | 10 | 8 | 20 | 298 | 0 | 0 | 150 | 50 | 149 | 13 | 100 | 186 | 127 | 322 | 95 | 105 | 105 | 3 | 304 | 54 | 110 | 98 | 49 | 100 | 320 | 93 | 17 | 162 | 108 | 0 | 17 | 20 |  | 710 | 0 | 215 | 0 | 0 | 130 | 0 | 0 | 5 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 46 | 0 | 147 | 0 | 316 | 105 | 0 | 94 | 0 | 105 | 0 | 5 | 113 | 420 | 219 | 0 | 0 | 0 |  | 8104 | 3049 | 11153 | 3647 | 710 | 1917 | 70 | 3599 | 499 | 157 | 130 | 259 | 106 | 59 | 0 | 106.07
16:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 180 |  | 0 | 250 | 275 | 0 | 0 | 45 | 42 | 0 | 33 | 0 | 102 | 150 | 33 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 9 | 33 | 25 | 25 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 93 | 36 | 28 | 50 | 16 | 5 | 80 | 0 | 0 | 270 | 355 | 124 | 8 | 90 | 23 | 20 | 0 | 51 | 0 | 50 | 43 | 22 | 8 | 33 | 20 | 102 | 142 | 0 | 22 | 1 | 44 | 30 | 36 | 0 | 163 | 159 | 30 | 73 | 0 | 0 | 17 | 0 | 9 | 280 | 10 | 8 | 0 | 296 | 0 | 0 | 100 | 0 | 149 | 7 | 100 | 200 | 125 | 322 | 95 | 35 | 105 | 2 | 304 | 54 | 110 | 34 | 48 | 90 | 325 | 93 | 15 | 162 | 108 | 0 | 17 | 9 |  | 709 | 0 | 225 | 0 | 0 | 130 | 0 | 0 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 48 | 0 | 170 | 0 | 414 | 105 | 0 | 94 | 0 | 105 | 0 | 3 | 113 | 410 | 218 | 0 | 0 | 0 |  | 7896 | 3157 | 11053 | 3775 | 709 | 2051 | 0 | 3223 | 490 | 157 | 130 | 379 | 102 | 37 | 0 | 106.06
17:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 180 |  | 0 | 250 | 240 | 0 | 0 | 45 | 81 | 0 | 36 | 0 | 48 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 9 | 33 | 33 | 25 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 10 | 21 | 50 | 16 | 7 | 80 | 0 | 0 | 270 | 285 | 135 | 8 | 90 | 20 | 20 | 0 | 51 | 0 | 50 | 16 | 0 | 8 | 33 | 20 | 98 | 148 | 0 | 22 | 0 | 44 | 20 | 36 | 0 | 110 | 159 | 31 | 79 | 0 | 0 | 17 | 0 | 9 | 300 | 10 | 8 | 0 | 300 | 0 | 0 | 80 | 0 | 106 | 2 | 100 | 136 | 127 | 322 | 106 | 35 | 105 | 1 | 304 | 54 | 110 | 34 | 53 | 100 | 380 | 93 | 3 | 162 | 109 | 0 | 17 | 4 |  | 709 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 22 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 50 | 26 | 0 | 0 | 0 | 32 | 8 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 47 | 0 | 174 | 0 | 358 | 53 | 0 | 94 | 0 | 50 | 0 | 2 | 113 | 420 | 177 | 0 | 0 | 0 |  | 7602 | 3012 | 10614 | 3796 | 709 | 1893 | 0 | 2885 | 502 | 157 | 130 | 432 | 98 | 12 | 0 | 106.05
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 313 | 180 |  | 0 | 250 | 280 | 0 | 0 | 45 | 332 | 0 | 36 | 0 | 102 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 18 | 33 | 33 | 38 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 70 | 49 | 50 | 16 | 12 | 80 | 0 | 0 | 270 | 270 | 132 | 8 | 92 | 20 | 30 | 0 | 51 | 0 | 50 | 22 | 22 | 8 | 33 | 21 | 148 | 147 | 0 | 22 | 0 | 44 | 20 | 36 | 0 | 110 | 161 | 50 | 76 | 0 | 0 | 17 | 0 | 9 | 300 | 10 | 8 | 140 | 300 | 156 | 85 | 106 | 99 | 118 | 0 | 90 | 143 | 128 | 322 | 107 | 48 | 105 | 0 | 304 | 54 | 110 | 95 | 96 | 90 | 320 | 93 | 0 | 162 | 114 | 0 | 17 | 0 |  | 710 | 0 | 215 | 0 | 0 | 155 | 0 | 0 | 32 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 50 | 38 | 81 | 27 | 34 | 37 | 8 | 16 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 47 | 0 | 172 | 0 | 400 | 105 | 0 | 64 | 0 | 80 | 0 | 0 | 95 | 430 | 220 | 0 | 3 | 0 |  | 8642 | 3346 | 11988 | 3932 | 710 | 2030 | 480 | 3308 | 512 | 157 | 155 | 556 | 148 | 0 | 0 | 106.05
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 390 | 180 |  | 0 | 250 | 280 | 0 | 0 | 45 | 339 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 87 | 50 | 17 | 10 | 70 | 0 | 0 | 260 | 260 | 124 | 8 | 92 | 23 | 52 | 0 | 51 | 0 | 50 | 52 | 0 | 8 | 33 | 21 | 142 | 147 | 0 | 22 | 0 | 44 | 22 | 47 | 0 | 100 | 161 | 56 | 81 | 0 | 0 | 17 | 0 | 9 | 305 | 21 | 11 | 150 | 300 | 154 | 100 | 190 | 100 | 149 | 0 | 100 | 165 | 133 | 322 | 107 | 102 | 105 | 0 | 304 | 54 | 110 | 100 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 712 | 0 | 220 | 0 | 0 | 214 | 0 | 0 | 32 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 50 | 37 | 93 | 27 | 43 | 37 | 43 | 35 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 47 | 0 | 170 | 0 | 414 | 105 | 0 | 94 | 0 | 108 | 0 | 0 | 113 | 520 | 222 | 0 | 17 | 0 |  | 9077 | 3673 | 12750 | 3957 | 712 | 2077 | 504 | 3802 | 599 | 157 | 214 | 586 | 142 | 0 | 0 | 106.04
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 178 |  | 0 | 250 | 280 | 0 | 0 | 45 | 338 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 87 | 50 | 17 | 13 | 70 | 0 | 0 | 260 | 260 | 124 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 50 | 52 | 0 | 8 | 33 | 21 | 140 | 147 | 0 | 22 | 0 | 43 | 32 | 47 | 0 | 100 | 161 | 57 | 81 | 0 | 0 | 17 | 0 | 9 | 280 | 21 | 11 | 150 | 300 | 158 | 100 | 190 | 100 | 149 | 0 | 100 | 200 | 140 | 323 | 107 | 105 | 105 | 0 | 304 | 54 | 110 | 100 | 97 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 712 | 0 | 215 | 0 | 0 | 215 | 0 | 0 | 32 | 0 | 0 | 87 | 3 | 0 | 0 | 0 | 0 | 50 | 37 | 93 | 27 | 43 | 37 | 52 | 35 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 47 | 0 | 169 | 0 | 414 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 222 | 0 | 17 | 0 |  | 9120 | 3709 | 12829 | 3970 | 712 | 2059 | 508 | 3862 | 620 | 157 | 215 | 586 | 140 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 178 |  | 0 | 250 | 270 | 0 | 0 | 45 | 338 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 88 | 50 | 17 | 15 | 70 | 0 | 0 | 260 | 260 | 125 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 50 | 52 | 0 | 8 | 33 | 21 | 142 | 147 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 100 | 162 | 57 | 81 | 0 | 0 | 17 | 0 | 9 | 280 | 21 | 11 | 150 | 300 | 80 | 100 | 190 | 100 | 149 | 0 | 100 | 200 | 140 | 322 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 100 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 712 | 0 | 215 | 0 | 0 | 215 | 0 | 0 | 32 | 0 | 0 | 87 | 3 | 0 | 0 | 0 | 0 | 50 | 37 | 93 | 27 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 32 | 0 | 169 | 0 | 414 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 550 | 222 | 0 | 17 | 0 |  | 9058 | 3707 | 12765 | 3981 | 712 | 2037 | 430 | 3870 | 629 | 160 | 215 | 589 | 142 | 0 | 0 | 106.04
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 178 |  | 0 | 250 | 275 | 0 | 0 | 45 | 338 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 88 | 50 | 17 | 25 | 70 | 0 | 0 | 260 | 260 | 127 | 8 | 91 | 23 | 55 | 0 | 51 | 0 | 50 | 52 | 0 | 8 | 33 | 21 | 138 | 147 | 0 | 22 | 0 | 43 | 42 | 48 | 0 | 110 | 161 | 56 | 81 | 0 | 0 | 17 | 0 | 9 | 290 | 21 | 11 | 100 | 300 | 33 | 70 | 190 | 100 | 149 | 0 | 100 | 200 | 142 | 323 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 114 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 712 | 0 | 210 | 0 | 0 | 214 | 0 | 0 | 30 | 0 | 0 | 87 | 12 | 0 | 0 | 0 | 0 | 50 | 35 | 93 | 27 | 43 | 32 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 32 | 0 | 169 | 0 | 414 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 560 | 222 | 0 | 17 | 0 |  | 8982 | 3709 | 12691 | 3979 | 712 | 2082 | 303 | 3886 | 640 | 160 | 214 | 577 | 138 | 0 | 0 | 106.04
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 179 |  | 0 | 250 | 290 | 0 | 0 | 45 | 336 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 88 | 50 | 17 | 27 | 70 | 0 | 0 | 260 | 265 | 139 | 8 | 90 | 23 | 56 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 138 | 147 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 56 | 81 | 0 | 0 | 17 | 0 | 9 | 300 | 21 | 11 | 50 | 300 | 0 | 40 | 190 | 50 | 149 | 0 | 100 | 200 | 138 | 323 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 114 | 95 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 | 0 |  | 713 | 0 | 210 | 0 | 0 | 215 | 0 | 0 | 30 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 31 | 93 | 27 | 43 | 32 | 52 | 32 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 32 | 0 | 166 | 0 | 414 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 560 | 224 | 0 | 17 | 0 |  | 8900 | 3724 | 12624 | 4012 | 713 | 2154 | 140 | 3882 | 640 | 160 | 215 | 570 | 138 | 0 | 0 | 106.04
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 178 |  | 0 | 250 | 270 | 0 | 0 | 45 | 336 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 87 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 92 | 88 | 48 | 17 | 36 | 70 | 0 | 0 | 260 | 265 | 141 | 8 | 91 | 23 | 56 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 138 | 146 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 162 | 51 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 21 | 11 | 0 | 300 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 200 | 137 | 323 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 114 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 713 | 0 | 210 | 0 | 0 | 215 | 0 | 0 | 22 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 43 | 31 | 93 | 27 | 43 | 24 | 52 | 32 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 32 | 0 | 166 | 0 | 414 | 105 | 0 | 100 | 0 | 113 | 0 | 0 | 113 | 560 | 225 | 0 | 17 | 0 |  | 8730 | 3708 | 12438 | 4012 | 713 | 2133 | 0 | 3878 | 640 | 162 | 215 | 547 | 138 | 0 | 0 | 106.03
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 190 |  | 0 | 250 | 255 | 0 | 0 | 45 | 339 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 30 | 33 | 51 | 0 | 87 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 92 | 88 | 47 | 17 | 32 | 70 | 0 | 0 | 285 | 275 | 142 | 8 | 91 | 23 | 56 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 134 | 145 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 270 | 21 | 11 | 0 | 300 | 0 | 0 | 182 | 0 | 149 | 0 | 100 | 200 | 137 | 323 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 100 | 59 | 100 | 320 | 94 | 0 | 162 | 110 | 0 | 17 | 0 |  | 715 | 0 | 215 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 43 | 0 | 93 | 27 | 0 | 24 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 155 | 0 | 370 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 224 | 0 | 17 | 0 |  | 8617 | 3564 | 12181 | 4040 | 715 | 2046 | 0 | 3781 | 640 | 162 | 217 | 446 | 134 | 0 | 0 | 106.03
KWH | 0 | 0 | 0 | 0 | 7389073 | 0 | 0 | 9230340 | 5584000 |  | 0 | 6160750 | 6556422 | 0 | 0 | 1024449 | 5254875 | 0 | 388000 | 0 | 1420560 | 2566080 | 624005 | 0 | 0 | 0 | 1225440 | 1259010 | 1253615 | 419364 | 600000 | 463680 | 801700 | 728000 | 647520 | 0 | 1945609 | 1812000 | 2900000 | 0 | 304923 | 0 | 0 | 0 | 0 |  | 270240 | 0 | 979196 | 1095720 | 858240 | 794400 | 384048 | 456000 | 1967314 | 0 | 0 | 7018900 | 6992000 | 2644000 | 217454 | 2155000 | 458280 | 1179840 | 0 | 1229142 | 0 | 462744 | 701482 | 354168 | 226800 | 712300 | 467310 | 2693760 | 3582560 | 0 | 486576 | 12500 | 1029000 | 738960 | 1032000 | 0 | 3274364 | 3734000 | 1128960 | 1834560 | 0 | 0 | 259000 | 0 | 206460 | 7175000 | 446016 | 220032 | 566784 | 5951561 | 364169 | 343755 | 3357600 | 510805 | 2906500 | 120825 | 2275200 | 3905280 | 3226690 | 7741000 | 2559600 | 1369200 | 2296654 | 31680 | 7000364 | 1220630 | 2447189 | 1243740 | 1475880 | 2242560 | 7701500 | 2196480 | 322750 | 3841920 | 2478982 | 0 | 431640 | 197264 |  | 17165090 | 0 | 5547168 | 0 | 0 | 3704640 | 0 | 0 | 205440 | 0 | 0 | 2093726 | 395960 | 0 | 0 | 0 | 0 | 501648 | 282467 | 588736 | 175400 | 227681 | 222817 | 533280 | 190294 | 502800 | 0 | 226260 | 1886837 | 0 | 0 | 0 | 0 | 0 | 0 | 3220400 | 0 | 649051 | 0 | 4124936 | 0 | 9181600 | 1793280 | 0 | 2094336 | 0 | 1938864 | 0 | 29126 | 2302080 | 12103300 | 5070245 | 0 | 146400 | 0 |  | 190365943 | 77103862 | 267469805 | 93835246 | 17165090 | 50705648 | 1785513 | 73118595 | 13990137 | 3757609 | 3704640 | 5999422 | 2693760 | 714145 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8201871.03 | 0 | 0 | 9322643.4 | 5751520 |  | 0 | 6715217.5 | 7277628.42 | 0 | 0 | 8666838.54 | 5465070 | 0 | 671240 | 0 | 12955507.2 | 25250227.2 | 5753326.1 | 0 | 0 | 0 | 8945712 | 9732147.3 | 12360643.9 | 314523 | 450000 | 0 | 0 | 0 | 6261518.4 | 0 | 525314.43 | 489240 | 5249000 | 0 | 2832734.67 | 0 | 0 | 0 | 0 |  | 0 | 0 | 9498201.2 | 10464126 | 7466688 | 6291648 | 483900.48 | 1354320 | 2911624.72 | 0 | 0 | 5193986 | 6992000 | 2432480 | 280515.66 | 2478250 | 517856.4 | 1651776 | 0 | 2101832.82 | 0 | 4673714.4 | 6699153.1 | 449793.36 | 170100 | 1246525 | 350482.5 | 20203200 | 3797513.6 | 0 | 617951.52 | 199250 | 1687560 | 1182336 | 1836960 | 0 | 3732774.96 | 3883360 | 2224051.2 | 3504009.6 | 0 | 0 | 567210 | 0 | 421178.4 | 7246750 | 334512 | 167224.32 | 9640995.84 | 44993801.16 | 6183589.62 | 5747583.6 | 17459520 | 8540659.6 | 28599960 | 1412444.25 | 18542880 | 42372288 | 22748164.5 | 7199130 | 23343552 | 12938940 | 20003856.34 | 0 | 52922751.84 | 10631687.3 | 21510791.31 | 12412525.2 | 12648291.6 | 14935449.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98870918.4 | 0 | 5824526.4 | 0 | 0 | 51346310.4 | 0 | 0 | 2155065.6 | 0 | 0 | 2365910.38 | 613738 | 0 | 0 | 0 | 0 | 4936216.32 | 2869864.72 | 5210313.6 | 1350580 | 3078247.12 | 2159096.73 | 5167483.2 | 1845851.8 | 965376 | 0 | 171278.82 | 11377627.11 | 0 | 0 | 0 | 0 | 0 | 0 | 4250928 | 0 | 973576.5 | 0 | 4826175.12 | 0 | 9089784 | 18721843.2 | 0 | 19875248.64 | 0 | 15045584.64 | 0 | 321842.3 | 17012371.2 | 53133487 | 0 | 0 | 0 | 0 |  | 663295600.09 | 343559245.2 | 1006854845.29 | 92001013.25 | 98870918.4 | 53516957.86 | 30112828.66 | 534745860.06 | 64511114.11 | 1014554.43 | 51346310.4 | 58598551.57 | 20203200 | 1933536.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 188 |  | 0 | 250 | 260 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 84 | 100 | 43 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 6 | 33 | 25 | 30 | 0 | 86 | 75 | 120 | 0 | 4 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 70 | 9 | 39 | 16 | 5 | 80 | 0 | 0 | 310 | 295 | 139 | 8 | 93 | 23 | 50 | 0 | 51 | 0 | 0 | 10 | 19 | 11 | 25 | 17 | 94 | 154 | 0 | 22 | 3 | 44 | 30 | 46 | 0 | 163 | 161 | 36 | 75 | 0 | 0 | 0 | 0 | 9 | 305 | 10 | 8 | 50 | 296 | 0 | 0 | 146 | 50 | 149 | 19 | 100 | 180 | 128 | 321 | 115 | 38 | 105 | 4 | 305 | 54 | 110 | 80 | 48 | 90 | 320 | 93 | 57 | 162 | 108 | 0 | 17 | 33 |  | 709 | 0 | 215 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 0 | 150 | 0 | 329 | 105 | 0 | 94 | 0 | 85 | 0 | 4 | 113 | 410 | 220 | 0 | 0 | 0 |  | 10784 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 178 | 0 | 0 | 250 | 280 | 0 | 0 | 45 | 338 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 82 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 102 | 100 | 87 | 50 | 17 | 13 | 70 | 0 | 0 | 260 | 260 | 124 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 50 | 52 | 0 | 8 | 33 | 21 | 140 | 147 | 0 | 22 | 0 | 43 | 32 | 47 | 0 | 100 | 161 | 57 | 81 | 0 | 0 | 17 | 0 | 9 | 280 | 21 | 11 | 150 | 300 | 158 | 100 | 190 | 100 | 149 | 0 | 100 | 200 | 140 | 323 | 107 | 105 | 105 | 0 | 304 | 54 | 110 | 100 | 97 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 712 | 0 | 215 | 0 | 0 | 215 | 0 | 0 | 32 | 0 | 0 | 87 | 3 | 0 | 0 | 0 | 0 | 50 | 37 | 93 | 27 | 43 | 37 | 52 | 35 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 47 | 0 | 169 | 0 | 414 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 222 | 0 | 17 | 0 |  | 12829 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 215 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 55 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 51 | 0 | 82 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 88 | 50 | 17 | 10 | 80 | 0 | 0 | 360 | 330 | 145 | 8 | 92 | 23 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 160 | 0 | 22 | 0 | 43 | 30 | 50 | 0 | 163 | 165 | 62 | 80 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 135 | 321 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 728 | 0 | 300 | 0 | 0 | 225 | 0 | 0 | 25 | 40 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 94 | 27 | 50 | 40 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 17 | 100 | 220 | 0 | 400 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 215 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 80 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 0 | 100 | 85 | 25 | 17 | 8 | 80 | 0 | 0 | 360 | 300 | 140 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 160 | 0 | 22 | 1.6 | 43 | 30 | 50 | 0 | 163 | 165 | 60 | 80 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 320 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 100 | 95 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 724 | 0 | 250 | 0 | 0 | 225 | 0 | 0 | 5 | 0 | 0 | 84 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 27 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 17 | 50 | 200 | 0 | 400 | 105 | 0 | 94 | 0 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 212 | 0 | 0 | 250 | 280 | 0 | 0 | 30 | 338 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 30 | 33 |  | 0 | 0 | 82 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 70 | 0 | 0 | 360 | 300 | 140 | 8 | 91 | 20 | 57 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 100 | 158 | 0 | 22 | 0 | 43 | 42 | 42 | 0 | 130 | 165 | 56 | 81 | 0 | 0 | 18 | 0 | 0 | 290 | 0 | 11 | 0 | 45 | 0 | 0 | 148 | 0 | 88 | 0 | 100 | 120 | 128 | 322 | 98 | 0 | 34 | 2 | 215 | 54 | 34 | 0 | 48 | 100 | 320 | 55 | 21 | 54 | 0 | 0 | 17 | 10 | 0 | 711 | 0 | 235 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 17 | 0 | 193 | 0 | 414 | 53 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 400 | 214 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9024 | 7:00
| Highest Generation |  | 12829 | 19:30
| Day Peak Generation |  | 10784 | 12:00
| Evening Peak Generation |  | 12829 | 19:30
| HVDC Max Flow |  | 715 | 24:00
| HVDC EvPeak Flow |  | 712 | 19:30
| Load factor L.F |  | 86.87%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-07
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10784 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9243 | MW
Evening Peak Generation : |  | 12829 | MW Hour : | 19:30 | Available Max Generation : |  | 14551 | MW
E.P. Demand (at gen end) : |  | 12829 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12829 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1551 | MW
Total Gen. (MKWH) : |  | 267.4698 | System Load Factor : | 86.87% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -444 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-07
Actual : | 106 | Ft.(MSL) , | Rule curve : | 106.54 | Ft.( MSL )
Gas Consumed : | Total = | 1104.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145517971.11
: |  | Coal : | 64511114.11 | Oil : | 674803550.69 | Total : | 884832635.91
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4641.7812 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1583.4929 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1419.6535 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1283.0949 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1159.3388 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 935.5581 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 516.6448 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 240.7097 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 721.5798 |  |  | 0 | 0%
Total | 0 |  | 12501.8537 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Sylhet-225 MW
7) Raozan #02
8) Shajibazar 330 Mw GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kulshi-Bakulia 132 kV Ckt was under shut down from 08:54 to 14:39 for C/M.
b) HVDC 400 kV 10CF15 filter was shut down at 08:32 for A/M.
c) Rangamati-Khagrachori 132 kV Ckt-1 was under shut down from 08:41 to 15:34 for A/M.
d) Sikalbaha old-Sikalbaha new 132 kV Ckt-1 was under shut down from 09:02 to 17:12 for D/W.
e) Cumilla(S) 132/33 kV T3 & T4 transformer tripped at 08:57 showing 50/51N,O/C,B phase relay |  |  |  |  | About 36 MW power interruption occurred under Cumilla(s) S/S area
due to 33 kV Y-phase PT burst and were switched on at 09:41,16:28 respectively. |  |  |  |  | from 08:57 to 09:41.
f) Haripur-Fatulla 132 kV Ckt was under shut down from 10:11 to 15:47 for C/M by Madanganj grid S/S.
g) Mithapukur 132/33 kV T2 transformer was under shut down from 13:07 to 13:25 due to 33 kV maint
by NESCO.
h) Siddhirganj 335 MW GT was shut down at 11:58 for ST synchronizing.
i) Siddhirganj peaking GT-1 was synchronized at 12:13 and shut down at 18:37 due to gas pressure low.
j) HVDC pole-2 cooling pump-2 was under shut down from 13:40 to 13:48 for C/M.
k) Polashbari 132/33 kV T1 transformer was under shut down from 08:22 to 15:26 for A/M.
l) Bogura 230/132 kV T2 transformer was under shut down from 08:27 to 15:33 for A/M.
m) Siddhirganj 335 MW GT & ST were synchronized at 14:04,16:45 respectively.
n) Mymensing 132/33 kV T1 & T2 transformer were under shut down from 17:59 to 18:08 due to loop
burst of 33 kV ishwarganj feeder.
o) Dohazari-Cox's Bazar 132 kV Ckt-1 was under shut down since 06:50(07-10-21) for A/M.
p) Hathazari-Baraulia 132 kV Ckt-2 tripped at 06:23 from Hathazari end showing dist R,Y phase and
was switched on at 07:18(07-10-21).
q) Purbasadipur 132/33 kV T2 & T3 transformer tripped at 02:14 due to fire occurred at capacitor bank |  |  |  |  | About 45 MW power interruption occurred under Purbasadipur S/S area
and were switched on at 03:20,03:55(07-10-2021) respectively. |  |  |  |  | from 02:14 to 03:20.
r) Mymensing S/S-RPCL 132 kV Ckt-2 was under shut down since 07:28 for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7389073 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 398 | 9230340
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 178 | 5584000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6160750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6556422 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 45 | 1024449 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 51 | 624005 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 419364
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 388000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 338 | 5254875
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1420560
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1225440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2566080
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1259010
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1253615
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1063680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 801700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 728000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 647520
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5951561
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 158 | 364169 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 343755
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 510805
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2906500
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1369200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 2196480 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3841920
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 197264
| Dhaka area Total |  |  |  | 5560 | 3626 | 71278537
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 304923
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120825
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 794400
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 157 | 3757609 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2296654
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 979196
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1095720
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2275200
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 384048 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 456000
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 87 | 858240 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31680
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 7000364
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1220630
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2447189
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2242560
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2478982
| Chattogram area Total |  |  |  | 2382 | 1555 | 31644220
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 70 | 1967314 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 124 | 2644000 | ST under maint
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7018900 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6992000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 458280 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1179840
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1229142
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 3226690 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 462744
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2155000 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3905280
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 354168
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 226800
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2693760
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 712300
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 701482
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 467310 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 566784 | Low demand
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1243740 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 97 | 1475880 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 431640 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1949 | 40330508
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 147 | 3582560 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 486576
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12500
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 3357600
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 107 | 2559600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 322750
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 270240
| Mymensingh Area Total |  |  |  | 622 | 488 | 10591826
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1029000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 738960 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3274364 | Transformer O/L
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 161 | 3734000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1032000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 220032
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1128960 | Machine problem
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1834560
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 259000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 21 | 446016
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7175000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 323 | 7741000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 206460
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7701500 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1502 | 36520852
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 712 | 17165090
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 205440 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 215 | 3704640
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 215 | 5547168 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1793280
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1279 | 28415618
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 3 | 395960
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2093726 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 47 | 649051 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 12103300
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5070245
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 146400 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 916 | 20458682
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 501648
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 37 | 282467 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 175400 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 227681 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 222817 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 125 | 3220400 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 169 | 4124936 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9181600 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 190294 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 502800
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226260
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 533280
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 588736 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2094336 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2302080
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 0
| Rajshahi Area Total |  |  |  | 2179 | 1321 | 24374735
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1886837
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1938864
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29126
| Rangpur Area Total |  |  |  | 605 | 193 | 3854827
| Total |  |  |  | 20934 | 12829 | 267469805
| Eastern Grid Total |  |  |  | 13975 | 9120 | 190365943
| Western Grid Total |  |  |  | 6959 | 3709 | 77103862
| National Grid Total |  |  |  | 20934 | 12829 | 267469805
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-06
(a) ENTIRE EASTERN GRID : |  | 8383 | MW | (b) ENTIRE WESTERN GRID : |  | 3946 | MW
i) Dhaka area |  | 4358 | MW | i) Khulna area |  | 1541 | MW
ii) Chittagong area |  | 1334 | MW | ii) Rajshahi area |  | 1323 | MW
iii) Comilla area |  | 1203 | MW | iii) Barisal area |  | 342 | MW
iv) Mymensingh area |  | 996 | MW | iv) Rangpur area |  | 740 | MW
v) Sylhet area |  | 492 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12329 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 10:00 | Kishoreganj | 134 | 18:30 | Jessore | 118 | 18:30
Munsiganj | 96 | 19:30 | Netrokona | 107 | 18:30 | Benapol | 56 | 19:00
Sonargaon | 74 | 11:00 | Jamalpur | 145 | 18:3 | Jhenida(Old) | 116 | 18:30
Shyampur | 200 | 10:00 | Sherpur | 128 | 20:00 | Bottail | 126 | 18:30
Bhulta | 195 | 22:00 | Srimongal | 53 | 18:00 | G.K Project | 58 | 19:30
Madanganj | 52 | 10:00 | Shahjibazar | 123 | 22:00 | Faridpur | 152 | 20:00
Shitalakhya | 113 | 12:00 | Fenchuganj | 41 | 18:00 | Rajbari | 58 | 18:30
Rahim steel | 15 | 17:00 | Kulawara | 46 | 18:30 | Madaripur | 102 | 21:00
Matuail | 60 | 9:00 | Sylhet | 134 | 18:00 | Sariatpur | 68 | 20:00
Ghorasal | 71 | 0:00 | Chatak | 30 | 19:30 | Gopalganj | 94 | 20:00
Narsingdi | 167 | 20:00 | Sunamganj | 47 | 24:00 | Bagerhat | 97 | 18:30
Haripur (SBU) | 120 | 10:00 | Biani Bazar | 60 | 18:00 | Mongla | 40 | 14:00
Sreenagar | 40 | 20:00 | Comilla (S) | 148 | 18:00 | Satkhira | 104 | 21:00
Ullon | 64 | 13:00 | Comilla(N) | 131 | 19:30 | Gallamari | 33 | 12:00
Hasnabad | 79 | 20:00 | Chandpur | 78 | 20:00 | Magura | 58 | 18:30
Magbazar | 105 | 12:00 | Feni | 132 | 18:00 | Norail | 47 | 18:30
Maniknagar | 66 | 13:00 | Chowmuhani | 212 | 22:00 | Chuadanga | 98 | 20:00
Bangabhaban | 12 | 10:00 | Ashuganj | 36 | 0:00 | Barisal(N) | 43 | 19:00
Motijheel | 30 | 11:00 | Daudkandi | 156 | 20:00 | Barisal (S) | 112 | 18:30
Narinda | 66 | 13:00 | B.Baria | 165 | 21:00 | Patuakhali | 112 | 22:00
Kazla | 78 | 18:00 | Ramganj | 90 | 22:00 | Bhandaria | 50 | 18:30
Dhanmondi | 208 | 13:00 | Chaddagram | 47 | 22:00 | Borguna | 18 | 21:00
Lalbag | 78 | 13:00 | PHP | 9 | 17:0 | Borhan Uddin | 48 | 18:00
Madartek | 69 | 23:00 | Kochua | 68 | 19:00 | Ishurdi | 69 | 19:30
Dhaka University | 38 | 12:00 | Madunaghat | 62 | 18:00 | Ruppur Paromanobik | 3 | 18:00
Aftabnagar | 14 | 11:00 | Hathazari | 96 | 18:00 | Natore | 128 | 20:00
Fatullah | 63 | 15:00 | Khulshi | 207 | 16:00 | Bogra | 159 | 20:00
Nawabganj | 52 | 22:00 | Halishahar | 97 | 17:00 | Noagaon | 108 | 20:00
Keraniganj | 70 | 18:30 | Baraulia | 155 | 18:00 | Rajshahi | 150 | 22:00
Mirpur | 119 | 12:00 | Sikalbaha | 46 | 13:00 | Rajshahi New | 19 | 20:00
Kalyanpur | 93 | 18:00 | Dohazari | 116 | 20:00 | C.Nawabganj | 67 | 20:00
Gulshan | 130 | 13:00 | Cox'sbazar | 98 | 21:00 | Amnura | 48 | 21:00
Uttara | 78 | 13:00 | Chandraghona | 30 | 18:00 | Pabna | 110 | 19:30
Uttara New | 28 | 12:00 | Kaptai | 4.5 | 18:00 | Shahjadpur | 104 | 19:00
Kamrangirchar | 100 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 107 | 19:00
Savar | 157 | 19:00 | Bakulia | 123 | 18:00 | Niyamatpur | 74 | 21:00
Bhasantec | 132 | 12:00 | Julda | 23 | 13:00 | Joypurhat | 56 | 19:00
Agargaon | 86 | 12:00 | TK chemical | 25.5 | 1:00 | Sherpur(Bogura) | 57 | 19:30
Satmosjid | 104 | 18:00 | Modern Steel | 10 | 15:00 | Mohastangor | 64 | 19:00
Tongi | 122 | 11:00 | Shahmirpur | 36 | 18:00 | Bhangura | 32 | 19:30
Kabirpur | 281 | 13:00 | Khagrachhari | 30 | 17:00 | Rangpur | 128 | 22:00
Basundhara | 172 | 11:00 | Matarbari | 38 | 20:00 | Lalmonirhat | 42 | 19:30
Manikganj | 68 | 20:00 | Baroiar Hat | 48 | 18:00 | Saidpur | 91 | 19:30
Joydevpur | 176 | 18:00 | Rangamati | 14 | 18:00 | Purbasadipur | 92 | 19:30
New Tongi | 92 | 12:00 | Abul Khair 230 | 154 | 1:00 | Thakurgaon | 76 | 19:00
Kodda | 256 | 18:00 | BSRM | 155 | 19:00 | Palashbari | 113 | 21:00
Dhamrai | 108 | 15:00 | GPH Ispat | 23 | 12:00 | Barapukuria | 51 | 21:00
Rajendrapur | 104 | 18:30 | Agrabad | 72 | 14:00 | Panchagar | 49 | 18:30
Valuka | 134 | 18:00 | Goalpara | 27 | 19:00 | Joldhaka | 52 | 21:00
Tangail | 213 | 21:00 | Central S/S | 102 | 21:00 | Kurigram | 56 | 18:00
Mymensing | 180 | 22:00 | Noapara | 45 | 19:00 | Mithapukur | 29 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 6:00 | 403 | 21:00 | Kaliakoir | 396 | 0.29167 | 390 | 0.625
| Bheramara | 401 | 7:00 | 394 | 16:00 | Bhulta | 391 | 0.041667 | 380 | 0.5
| Ashuganj(N) | 395 | 1:00 | 388 | 10:00 | Gopalganj | 407 | 0.625 | 388 | 0.91667
| Payra | 409 | 1:00 | 399 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 7:00 | 230 | 1:00 | Hathazari | 237 | 21:00 | 226 | 5:00
| Ishurdi | 235 | 8:00 | 224 | 18:30 | Megnaghat | 231 | 8:00 | 228 | 10:00
| Ashuganj | 243 | 6:00 | 238 | 19:00 | Fenchuganj | 243 | 1:00 | 237 | 18:30
| Serajganj | 231 | 17:00 | 225 | 18:30 | Siddhirganj | 232 | 1:00 | 228 | 11:00
| Baghabari | 233 | 17:00 | 224 | 18:30 | Maniknagar | 231 | 1:00 | 226 | 10:00
| Barapukuria | 236 | 6:00 | 223 | 18:30 | Agargaon | 231 | 6:00 | 224 | 10:00
| Bogra | 226 | 6:00 | 213 | 18:30 | Barisal | 239 | 13:00 | 230 | 22:00
| Rajshahi | 228 | 7:00 | 220 | 20:00 | Bhola 225 MW | 243 | 6:00 | 236 | 22:00
| Khulna South | 232 | 8:00 | 217 | 18:30 | AKSML | 237 | 13:00 | 229 | 7:00
| Rampura | 230 | 2:00 | 227 | 10:00 | BSRM | 234 | 12:00 | 230 | 7:00
| Haripur | 230 | 1:00 | 227 | 10:00 | Bibiyana | 243 | 4:00 | 239 | 15:00
| Hasnabad | 228 | 1:00 | 224 | 15:00 | Bhulta | 235 | 6:00 | 228 | 13:00
| Shyampur | 230 | 1:00 | 224 | 10:00 | Ashuganj (S) | 239 | 8:00 | 235 | 16:00
| Aminbazar | 231 | 1:00 | 226 | 2:00 | Kaliakoir | 231 | 1:00 | 226 | 16:00
| Tongi | 232 | 1:00 | 221 | 12:00 | GPH | 235 | 17:00 | 228 | 7:00
| Comilla (N) | 232 | 1:00 | 210 | 24:00 | Jhenaidah | 228 | 12:00 | 215 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 7:00 | 131 | 9:00 | Madanhat | 140 | 0.77083 | 133 | 0.33333
| Munsiganj | 136 | 1:00 | 131 | 10:00 | Hathazari | 137 | 0.77083 | 133 | 0.20833
| Sonargaon | 134 | 18:30 | 130 | 10:00 | Khulshi | 136 | 0.79167 | 129 | 0.41667
| Shyampur | 137 | 1:00 | 133 | 10:00 | Halishahar | 138 | 0.83333 | 130 | 0.25
| Bhulta | 130 | 4:00 | 126 | 10:00 | Baraulia | 138 | 0.83333 | 132 | 0.41667
| Madanganj | 136 | 1:00 | 130 | 10:00 | Sikalbaha | 139 | 0.77083 | 129 | 0.25
| Shitalakhya | 137 | 18:30 | 132 | 9:00 | Dohazari | 134 | 0.875 | 127 | 0.20833
| Rahim steal | 135 | 18:30 | 131 | 10:00 | Cox'sbazar | 120 | 0.875 | 104 | 0.20833
| Matuail | 135 | 7:00 | 131 | 9:00 | Chandraghona | 138 | 0.70833 | 134 | 0.29167
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 137 | 0.875 | 135 | 0.041667
| Narsinghdi | 134 | 6:00 | 123 | 22:00 | A. Khaer Stl. | 136 | 0.875 | 131 | 0.25
| Haripur (SBU) | 134 | 1:00 | 131 | 11:00 | Bakulia | 138 | 0.8125 | 131 | 0.29167
| Sreenagar | 135 | 1:00 | 130 | 10:00 | Julda | 138 | 0.75 | 132 | 0.29167
| Ullon | 136 | 6:00 | 130 | 12:00 | TK Chemical | 138 | 0.79167 | 132 | 0.20833
| Hasnabad | 135 | 1:00 | 131 | 10:00 | Modern Steel | 137 | 0.83333 | 131 | 0.375
| Magbazar | 135 | 2:00 | 129 | 16:00 | Shahmirpur | 139 | 0.83333 | 132 | 0.33333
| Maniknagar | 135 | 2:00 | 130 | 15:00 | Khagrachhari | 136 | 0.70833 | 132 | 0.29167
| Bangabhaban | 135 | 2:00 | 130 | 15:00 | Matarbari | 130 | 0.95833 | 115 | 0.29167
| Motijheel | 135 | 2:00 | 130 | 15:00 | Baroiar Hat | 136 | 0.58333 | 130 | 0.20833
| Narinda | 135 | 2:00 | 130 | 15:00 | Rangamati | 137 | 23:00 | 132 | 6:00
| Kazla | 135 | 2:00 | 130 | 15:00 | Agrabad | 138 | 22:00 | 130 | 5:00
| Dhanmondi | 135 | 5:00 | 130 | 11:00 | Goalpara S/S | 138 | 8:00 | 130 | 0.77083
| Lalbag | 135 | 1:00 | 131 | 10:00 | Khulna Central S/S | 137 | 8:00 | 129 | 0.875
| Madartek | 136 | 6:00 | 130 | 12:00 | Noapara | 135 | 11:00 | 126 | 0.47917
| Dhaka University | 135 | 1:00 | 131 | 9:00 | Jessore | 133 | 7:00 | 123 | 0.875
| Aftabnagar | 136 | 3:00 | 131 | 10:00 | Benapol | 133 | 0.29167 | 123 | 0.875
| Fatullah | 138 | 19:30 | 133 | 10:00 | Jhenida(Old) | 137 | 18:00 | 125 | 0.83333
| Nawabganj | 135 | 6:00 | 132 | 9:00 | Bottail | 136 | 0.33333 | 129 | 0.77083
| Keraniganj | 136 | 19:30 | 131 | 10:00 | G.K Project | 139 | 0.625 | 134 | 0.77083
| Mirpur | 132 | 1:00 | 129 | 11:00 | Faridpur | 136 | 0.29167 | 128 | 0.91667
| Kalyanpur | 132 | 1:00 | 130 | 10:00 | Rajbari | 135 | 0.29167 | 128 | 0.95833
| Gulshan | 136 | 6:00 | 124 | 17:00 | Madaripur | 138 | 0.20833 | 130 | 0.91667
| Uttara | 133 | 4:00 | 129 | 10:00 | Shariyatpur S/S | 139 | 7:00 | 130 | 0.875
| Uttara New | 133 | 1:00 | 128 | 10:00 | Gopalganj | 142 | 0.29167 | 131 | 0.91667
| Kamrangirchar | 136 | 19:30 | 130 | 16:00 | Bagerhat | 134 | 8:00 | 125 | 0.77083
| Savar | 135 | 8:00 | 131 | 6:00 | Mongla | 132 | 5:00 | 126 | 0.77083
| Bhasantec | 137 | 1:00 | 131 | 10:00 | Satkhira | 135 | 6:00 | 124 | 21:00
| Agargaon | 138 | 1:00 | 133 | 10:00 | Gallamari | 136 | 0.25 | 126 | 18:00
| Satmosjid | 137 | 1:00 | 133 | 10:00 | Magura | 135 | 6:00 | 125 | 0.77083
| Tongi | 141 | 19:30 | 134 | 15:00 | Narail | 134 | 0.33333 | 123 | 0.77083
| Kabirpur | 136 | 6:00 | 129 | 18:30 | Chuadanga | 130 | 6:00 | 117 | 0.875
| Basundhara | 137 | 23:00 | 132 | 9:00 | Barisal(N) | 139 | 6:00 | 130 | 0.91667
| Manikganj | 140 | 13:00 | 134 | 21:00 | Barisal (S) | 137 | 6:00 | 129 | 21:00
| Joydevpur | 139 | 24:00 | 133 | 8:00 | Patuakhali(S) | 134 | 0.29167 | 125 | 0.875
| New Tongi | 139 | 22:00 | 134 | 15:00 | Bhandaria | 135 | 0.29167 | 124 | 0.875
| Kodda | 139 | 19:30 | 127 | 7:00 | Borguna | 135 | 0.16667 | 126 | 0.875
| Dhamrai | 138 | 1:00 | 134 | 16:00 | Jhenaidah(230kV S/S) | 135 | 6:00 | 126 | 19:30
| Rajendrapur | 138 | 1:00 | 126 | 4:00 | Ishurdi | 137 | 7:00 | 131 | 21:00
| Valuka | 125 | 8:00 | 108 | 21:00 | Ruppur Paromanobik | 136 | 17:00 | 132 | 19:00
| Tangail | 133 | 8:00 | 123 | 18:30 | Natore | 135 | 7:00 | 130 | 18:30
| Mymensing | 134 | 8:00 | 113 | 18:30 | Bogra | 135 | 10:00 | 126 | 18:30
| Kishorganj | 134 | 8:00 | 118 | 22:00 | Noagaon | 132 | 17:00 | 119 | 18:30
| Netrokona | 129 | 12:00 | 111 | 20:0 | Rajshahi | 135 | 17:00 | 130 | 21:00
| Jamalpur | 139 | 12:00 | 124 | 20:00 | Rajshahi New | 134 | 7:00 | 130 | 18:30
| Sherpur | 137 | 12:00 | 122 | 20:00 | C.Nawabganj | 134 | 18:00 | 127 | 2:00
| Srimongal | 138 | 6:00 | 130 | 23:00 | Amnura | 135 | 18:00 | 127 | 3:00
| Shahjibazar | 138 | 8:00 | 128 | 22:00 | Pabna | 135 | 8:00 | 129 | 21:00
| Fenchuganj | 137 | 8:00 | 129 | 19:30 | Shahjadpur | 140 | 16:00 | 133 | 21:00
| Khulawara | 135 | 7:00 | 128 | 18:30 | Serajganj | 132 | 4:00 | 126 | 19:30
| Sylhet | 131 | 6:00 | 123 | 18:00 | Niyamatpur | 130 | 8:00 | 115 | 18:30
| Chatak | 129 | 5:00 | 120 | 18:00 | Joypurhat | 134 | 17:00 | 118 | 18:30
| Sunamganj | 129 | 7:00 | 116 | 18:00 | Sherpur(Bogura) | 135 | 15:00 | 126 | 18:30
| Biani Bazar | 131 | 7:00 | 120 | 18:00 | Mohastangor | 135 | 17:00 | 123 | 18:30
| Comilla(s) | 129 | 5:00 | 121 | 18:00 | Bangura | 137 | 8:00 | 130 | 18:30
| Comilla(n) | 139 | 15:00 | 135 | 10:00 | Rangpur | 131 | 15:00 | 117 | 21:00
| Chandpur | 140 | 1:00 | 136 | 23:00 | Lalmonirhat | 131 | 4:00 | 115 | 18:30
| Feni | 137 | 12:00 | 130 | 3:00 | Saidpur | 132 | 5:00 | 116 | 18:30
| Chowmuhani | 134 | 15:00 | 130 | 1:00 | Purbasadipur | 130 | 15:00 | 111 | 18:30
| Ashuganj | 141 | 8:00 | 133 | 23:00 | Thakurgaon | 135 | 6:00 | 108 | 18:30
| Daudkandi | 137 | 18:00 | 131 | 10:00 | Palashbari | 132 | 17:00 | 121 | 18:30
| B.Baria | 135 | 7:00 | 126 | 22:00 | Barapukuria | 136 | 15:00 | 123 | 18:30
| Ramganj | 137 | 13:00 | 132 | 1:00 | Panchagar | 139 | 0.25 | 113 | 0.77083
| Chaddagram | 137 | 13:00 | 131 | 4:00 | Joldhaka | 131 | 0.25 | 109 | 0.77083
| PHP | 135 | 13:00 | 129 | 5:00 | Kurigram | 129 | 0.25 | 118 | 0.75
| Kochua | 137 | 12:00 | 134 | 4:00 | Mithapukur | 133 | 0.25 | 120 | 0.77083
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-10-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 340 | 8617 | 3564 | 12181 |  |  |  | QF-LDC-11
0:30 | 352 | 8335.5 | 3411 | 11746.5 | Date: | 2021-10-06
1:00 | 364 | 8054 | 3258 | 11312
1:30 | 330 | 7836 | 3184.5 | 11020.5
2:00 | 296 | 7618 | 3111 | 10729
2:30 | 290 | 7537 | 3088.5 | 10625.5 | [5 empty] | Gen. at Eve. Peak | 12829 | 12829 MW (19:30 )
3:00 | 284 | 7456 | 3066 | 10522 | [6 empty] | 19:30
3:30 | 279 | 7343.5 | 2975.5 | 10319 | [5 empty] | Gen. at Day Peak | 10784 | 10784 MW (12:00 )
4:00 | 274 | 7231 | 2885 | 10116 | [6 empty] | 12:00
4:30 | 256 | 7167.5 | 2856.5 | 10024 | [5 empty] | Highest Generation | 12829
5:00 | 238 | 7104 | 2828 | 9932 | [6 empty] | 19:30
5:30 | 132 | 6906 | 2801.5 | 9707.5
6:00 | 26 | 6708 | 2775 | 9483
6:30 | 79 | 6520 | 2733.5 | 9253.5
7:00 | 132 | 6332 | 2692 | 9024
7:30 | 66 | 6393.5 | 2698.5 | 9092
8:00 | 0 | 6455 | 2705 | 9160
8:30 | 55 | 6645.5 | 2746 | 9391.5
9:00 | 110 | 6836 | 2787 | 9623
9:30 | 105 | 7026.5 | 2779 | 9805.5
10:00 | 100 | 7217 | 2771 | 9988
10:30 | 102 | 7367.5 | 2824.5 | 10192
11:00 | 104 | 7518 | 2878 | 10396
11:30 | 86 | 7687 | 2903 | 10590
12:00 | 68 | 7856 | 2928 | 10784
12:30 | 102 | 7948.5 | 2969 | 10917.5
13:00 | 136 | 8041 | 3010 | 11051
13:30 | 141 | 7984 | 2988 | 10972
14:00 | 146 | 7927 | 2966 | 10893
14:30 | 109 | 8015.5 | 3007.5 | 11023
15:00 | 72 | 8104 | 3049 | 11153
15:30 | 108 | 8000 | 3103 | 11103
16:00 | 144 | 7896 | 3157 | 11053
16:30 | 134 | 7749 | 3084.5 | 10833.5
17:00 | 124 | 7602 | 3012 | 10614
17:30 | 169 | 8122 | 3179 | 11301
18:00 | 214 | 8642 | 3346 | 11988
18:30 | 309 | 8859.5 | 3509.5 | 12369
19:00 | 404 | 9077 | 3673 | 12750
19:30 | 408 | 9120 | 3709 | 12829
20:00 | 440 | 9058 | 3707 | 12765 |  |  |  | Executive Engineer
20:30 | 442 | 9020 | 3708 | 12728 |  |  |  | Network Operation Division
21:00 | 444 | 8982 | 3709 | 12691
21:30 | 405 | 8941 | 3716.5 | 12657.5
22:00 | 366 | 8900 | 3724 | 12624 |  |  |  |  | Page 6 of 7
22:30 | 346 | 8815 | 3716 | 12531
23:00 | 326 | 8730 | 3708 | 12438
23:30 | 333 | 8673.5 | 3636 | 12309.5
24:00 | 340 | 8617 | 3564 | 12181
12829 MW (19:30 )
10784 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-06 |  | Energy |  | 267469805
[13 empty] | 2021-10-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4040 | 715 | 2046 | 0 | 3781 | 640 | 162 | 217 | 446 | 134 | 0 | 0
0:30 | 3973 | 712.5 | 2092 | 0 | 3571 | 629.5 | 161 | 186 | 297.5 | 124 | 0 | 0 | Date: | 2021-10-06
1:00 | 3906 | 710 | 2138 | 0 | 3361 | 619 | 160 | 155 | 149 | 114 | 0 | 0
1:30 | 3907.5 | 709.5 | 2171 | 0 | 3086.5 | 604 | 159 | 137.5 | 132.5 | 113 | 0 | 0 | [8 empty] | Total Energy | 267.4698 | Total Energy Gen 267.470 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 267.470 MKWHr
2:00 | 3909 | 709 | 2204 | 0 | 2812 | 589 | 158 | 120 | 116 | 112 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3900.5 | 709.5 | 2217.5 | 0 | 2724 | 569 | 158 | 120 | 116 | 111 | 0 | 0 | [8 empty] | Energy Requirement | 267.4698
3:00 | 3892 | 710 | 2231 | 0 | 2636 | 549 | 158 | 120 | 116 | 110 | 0 | 0
3:30 | 3884 | 709.5 | 2227.5 | 0 | 2479 | 544 | 157 | 120 | 90 | 108 | 0 | 0 | [6 empty] | Shortage
4:00 | 3876 | 709 | 2224 | 0 | 2322 | 539 | 156 | 120 | 64 | 106 | 0 | 0
4:30 | 3873 | 709.5 | 2248.5 | 0 | 2206.5 | 544 | 155.5 | 120 | 64 | 103 | 0 | 0
5:00 | 3870 | 710 | 2273 | 0 | 2091 | 549 | 155 | 120 | 64 | 100 | 0 | 0
5:30 | 3861.5 | 709.5 | 2244.5 | 0 | 1945.5 | 524 | 156 | 120 | 48 | 98 | 0.5 | 0
6:00 | 3853 | 709 | 2216 | 0 | 1800 | 499 | 157 | 120 | 32 | 96 | 1 | 0
6:30 | 3854 | 709 | 2176.5 | 0 | 1616 | 489 | 157.5 | 120 | 32 | 93 | 6.5 | 0 |  |  |  |  | Coal
7:00 | 3855 | 709 | 2137 | 0 | 1432 | 479 | 158 | 120 | 32 | 90 | 12 | 0
7:30 | 3803 | 709 | 2096.5 | 0 | 1578.5 | 479 | 159 | 120 | 32 | 92 | 23 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3751 | 709 | 2056 | 0 | 1725 | 479 | 160 | 120 | 32 | 94 | 34 | 0
8:30 | 3821 | 709 | 2059 | 0 | 1882.5 | 479.5 | 160.5 | 120 | 36 | 76 | 48 | 0
9:00 | 3891 | 709 | 2062 | 0 | 2040 | 480 | 161 | 120 | 40 | 58 | 62 | 0
9:30 | 3893 | 709.5 | 2057.5 | 0 | 2185 | 480 | 161 | 120 | 52 | 76 | 71.5 | 0
10:00 | 3895 | 710 | 2053 | 0 | 2330 | 480 | 161 | 120 | 64 | 94 | 81 | 0
10:30 | 3850 | 709.5 | 2076.5 | 0 | 2547 | 480 | 161 | 120 | 64 | 95 | 89 | 0
11:00 | 3805 | 709 | 2100 | 0 | 2764 | 480 | 161 | 120 | 64 | 96 | 97 | 0
11:30 | 3727.5 | 709 | 2058.5 | 50 | 2986 | 485 | 161 | 127.5 | 82 | 95 | 108.5 | 0
12:00 | 3650 | 709 | 2017 | 100 | 3208 | 490 | 161 | 135 | 100 | 94 | 120 | 0
12:30 | 3668 | 709 | 1971 | 50 | 3373 | 495 | 160.5 | 152.5 | 127 | 97 | 114.5 | 0
13:00 | 3686 | 709 | 1925 | 0 | 3538 | 500 | 160 | 170 | 154 | 100 | 109 | 0
13:30 | 3686 | 709 | 1925 | 0 | 3538 | 500 | 160 | 170 | 154 | 100 | 109 | 0
14:00 | 3686 | 709 | 1925 | 0 | 3538 | 500 | 160 | 170 | 154 | 100 | 109 | 0
14:30 | 3666.5 | 709.5 | 1921 | 35 | 3568.5 | 499.5 | 158.5 | 150 | 206.5 | 103 | 84 | 0
15:00 | 3647 | 710 | 1917 | 70 | 3599 | 499 | 157 | 130 | 259 | 106 | 59 | 0
15:30 | 3711 | 709.5 | 1984 | 35 | 3411 | 494.5 | 157 | 130 | 319 | 104 | 48 | 0
16:00 | 3775 | 709 | 2051 | 0 | 3223 | 490 | 157 | 130 | 379 | 102 | 37 | 0
16:30 | 3785.5 | 709 | 1972 | 0 | 3054 | 496 | 157 | 130 | 405.5 | 100 | 24.5 | 0
17:00 | 3796 | 709 | 1893 | 0 | 2885 | 502 | 157 | 130 | 432 | 98 | 12 | 0
17:30 | 3864 | 709.5 | 1961.5 | 240 | 3096.5 | 507 | 157 | 142.5 | 494 | 123 | 6 | 0
18:00 | 3932 | 710 | 2030 | 480 | 3308 | 512 | 157 | 155 | 556 | 148 | 0 | 0
18:30 | 3944.5 | 711 | 2053.5 | 492 | 3555 | 555.5 | 157 | 184.5 | 571 | 145 | 0 | 0
19:00 | 3957 | 712 | 2077 | 504 | 3802 | 599 | 157 | 214 | 586 | 142 | 0 | 0
19:30 | 3970 | 712 | 2059 | 508 | 3862 | 620 | 157 | 215 | 586 | 140 | 0 | 0
20:00 | 3981 | 712 | 2037 | 430 | 3870 | 629 | 160 | 215 | 589 | 142 | 0 | 0
20:30 | 3980 | 712 | 2059.5 | 366.5 | 3878 | 634.5 | 160 | 214.5 | 583 | 140 | 0 | 0
21:00 | 3979 | 712 | 2082 | 303 | 3886 | 640 | 160 | 214 | 577 | 138 | 0 | 0
21:30 | 3995.5 | 712.5 | 2118 | 221.5 | 3884 | 640 | 160 | 214.5 | 573.5 | 138 | 0 | 0
22:00 | 4012 | 713 | 2154 | 140 | 3882 | 640 | 160 | 215 | 570 | 138 | 0 | 0
22:30 | 4012 | 713 | 2143.5 | 70 | 3880 | 640 | 161 | 215 | 558.5 | 138 | 0 | 0
23:00 | 4012 | 713 | 2133 | 0 | 3878 | 640 | 162 | 215 | 547 | 138 | 0 | 0
23:30 | 4026 | 714 | 2089.5 | 0 | 3829.5 | 640 | 162 | 216 | 496.5 | 136 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 32.5° C
24:00 | 4040 | 715 | 2046 | 0 | 3781 | 640 | 162 | 217 | 446 | 134 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 267.470 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 267.470 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 85 | 83 | 83 | 81 | 80 | 82 | 83 | 85 | 86 | 86 | 86 | 86 | 85 | 82 | 82 | 82 | 82 | 82 |  | 82 | 82 | 85 | 85 | 85 | 87 | 87 | 1945609
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1812000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 4 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 304923
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 |  | 7 | 5 | 20 | 19 | 16 | 17 | 13 | 7 | 2 | [9 empty] | 120825
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 34 | 34 | 0 | [11 empty] | 93 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 979196
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 34 | 34 | 34 | 34 | 83 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2296654
| Daudkandi 200 MW PP (B.Trac) | [11 empty] | 50 |  |  | 20 |  |  | 140 |  | 150 | 150 | 150 | 100 | 50 |  |  | 566784
14 | Titas 50 MW Peaking PP | [14 empty] | 48 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 462744
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [12 empty] | 90 | 62 | 94 | 33 | 36 | 36 | [8 empty] | 388000
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 271 | 240 | 233 | 219 | 222 | 218 | 218 | 214 | 219 |  |  |  | 40 | 42 | 81 | 332 |  | 339 | 338 | 338 | 338 | 336 | 336 | 339 | 5254875
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 195 | 145 | 95 | 95 | 95 | 95 | 142 | 165 | 285 | 296 | 296 | 296 | 298 | 296 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5951561
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7389073
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 110 | 80 | 80 | 80 | 80 | 80 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1967314
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 458280
33 | Ashuganj 225 MW CCPP | 37 | 37 | 37 | 33 | 32 | 50 | 142 | 142 | 140 | 140 | 138 | 139 | 117 | 115 | 139 | 124 | 135 | 132 |  | 124 | 124 | 125 | 127 | 139 | 141 | 142 | 2644000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 320 | 295 | 265 | 270 | 265 | 315 | 275 | 295 | 290 | 275 | 265 | 355 | 285 | 270 |  | 260 | 260 | 260 | 260 | 265 | 265 | 275 | 6992000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 295 | 270 | 260 | 260 | 340 | 305 | 265 | 310 | 280 | 265 | 260 | 270 | 270 | 270 |  | 260 | 260 | 260 | 260 | 260 | 260 | 285 | 7018900
35 | Ashuganj 55 MW PP (Precision) | 30 | 52 | 47 | 55 | 55 | 55 | 55 | 54 | 54 | 55 | 52 | 50 | 54 | 55 | 20 | 20 | 20 | 30 |  | 52 | 55 | 55 | 55 | 56 | 56 | 56 | 1179840
36 | Chandpur 150 MW CCPP | 92 | 92 | 91 | 91 | 93 | 90 | 90 | 93 | 92 | 92 | 92 | 93 | 93 | 93 | 92 | 90 | 90 | 92 |  | 92 | 90 | 90 | 91 | 90 | 91 | 91 | 2155000
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 352 | 352 | 359 | 372 | 341 | 356 | 396 | 362 | 369 | 399 | 400 | 398 | 400 | 358 | 380 | 399 | 397 | 313 |  | 390 | 398 | 398 | 399 | 399 | 399 | 400 | 9230340
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6160750
41 | Haripur 360MW CCPP(HPL) | 323 | 326 | 327 | 326 | 332 | 332 | 300 | 294 | 236 | 202 | 202 | 188 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 178 | 178 | 178 | 179 | 178 | 190 | 5584000
42 | RPCL 210MW CCPP | 161 | 161 | 160 | 161 | 160 | 163 | 162 | 161 | 156 | 153 | 154 | 154 | 142 | 141 | 142 | 142 | 148 | 147 |  | 147 | 147 | 147 | 147 | 147 | 146 | 145 | 3582560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 8 | 23 | 38 | 48 | 43 | 57 | 51 | 44 | 17 | 15 | 3 | [9 empty] | 322750
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1029000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 |  | 22 | 32 | 42 | 42 | 42 | 42 | 42 | 738960
46 | Shajibazar 330 MW CCPP | 163 | 162 | 161 | 161 | 158 | 163 | 160 | 161 | 162 | 160 | 160 | 161 | 158 | 157 | 159 | 159 | 159 | 161 |  | 161 | 161 | 162 | 161 | 160 | 162 | 160 | 3734000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 63 | 52 | 25 | 36 | 35 | 35 | 36 | 31 | 30 | 31 | 30 | 31 | 50 |  | 56 | 57 | 57 | 56 | 56 | 51 | 52 | 1128960
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 72 | 72 | 73 | 79 | 76 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1834560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [8 empty] | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 259000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 206460
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220032
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 47 | 46 | 23 | 44 | 36 | 36 | 36 | 36 |  | 47 | 47 | 47 | 48 | 47 | 47 | 47 | 1032000
56 | Shahjahanulla 25 MW PP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 446016
57 | Bibiana-II 341 MW CCPP (Summit) | 265 | 280 | 285 | 280 | 295 | 265 | 285 | 270 | 270 | 300 | 300 | 305 | 280 | 270 | 290 | 280 | 300 | 300 |  | 305 | 280 | 280 | 290 | 300 | 290 | 270 | 7175000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 315 | 300 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 325 | 380 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7701500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1253615
59 | Tangail Palli Power Gen 22 MW | [11 empty] | 2 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 270240
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 384048
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 |  | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 419364
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 486576
63 | Impoprt (Tripura) | 114 | 112 | 110 | 106 | 100 | 96 | 90 | 94 | 58 | 94 | 96 | 94 | 100 | 104 | 106 | 102 | 98 | 148 |  | 142 | 140 | 142 | 138 | 138 | 138 | 134 | 2693760
64 | Malancha, Ctg. EPZ (United) | 31 | 31 | 31 | 31 | 38 | 38 | 34 | 7 | 3 | 4 | 3 | 5 | 6 | 7 | 4 | 5 | 7 | 12 |  | 10 | 13 | 15 | 25 | 27 | 36 | 32 | 456000
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 14 | 16 | 19 | 19 | 19 | 21 | 21 | 22 |  | 22 | [5 empty] | 19 | 19 | 19 | 354168
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 226800
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 712300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 17 | 15 | 20 | 20 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 467310
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 8 | 10 | 10 | 6 | 6 | 6 | 6 | 6 | 9 | 9 | 18 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 463680
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 33 | 30 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 801700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 728000
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 34 | 0 | [9 empty] | 80 | 98 | 98 | 98 | 34 | 34 | 95 |  | 100 | 100 | 100 | 114 | 114 | 114 | 100 | 1243740
| Chowmuhani 113 MW | 53 | 48 | 48 | 48 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 48 | 49 | 47 | 49 | 48 | 53 | 96 |  | 96 | 97 | 96 | 96 | 95 | 96 | 59 | 1475880
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 108 | 108 | 158 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3841920
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 2 | 25 | 25 | 30 | 51 | 51 | 51 | 25 | 25 | 38 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 647520
79 | Kodda 150MW PP | 98 | 82 | 82 | 64 | 64 | 32 | 32 | 32 | 40 | 64 | 64 | 100 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2566080
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 25 | 25 | 0 | [6 empty] | 2 | 10 | 43 | 52 | 52 | 43 | 16 | 22 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 701482
| Gazipur 100 MW PP | 35 | 0 | [5 empty] | 3 | 17 | 17 | 17 | 38 | 105 | 105 | 105 | 35 | 35 | 48 |  | 102 | 105 | 105 | 105 | 105 | 105 | 105 | 1369200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 4 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 31680
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 22 | 54 | 54 | 54 | 54 | 42 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1220630
| Karnaphuli Power Ltd. | 102 | 110 | 102 | 110 | 68 | 51 | 51 | 51 | 51 | 83 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2447189
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 20 | [9 empty] | 5 | 43 | 51 | 52 | 51 | 33 | 10 | 25 |  | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 624005
86 | Meghnaghat CCPP ( Summit) | 225 | 255 | 265 | 257 | 280 | 262 | 277 | 250 | 275 | 300 | 300 | 260 | 240 | 278 | 240 | 275 | 240 | 280 |  | 280 | 280 | 270 | 275 | 290 | 270 | 255 | 6556422
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 94 | 94 | 94 | 94 | 94 | 94 | 55 | 68 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 94 | 93 | 94 | 2196480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 50 | 0 | [8 empty] | 10 | 70 | 80 | 92 | 92 | 36 | 10 | 70 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 1095720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1229142
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 7 | 7 | 7 | 0 | [5 empty] | 58 | 84 | 102 | 102 | 102 | 102 | 48 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1420560
95 | Patenga 50MW PP (Baraka) | 40 | 32 | 25 | 25 | 0 |  |  |  |  | 12 | 24 | 39 | 40 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 48 | 47 | 794400
96 | Chattogram 108 MW PP (ECPV) | [11 empty] | 9 | 70 | 75 | 75 | 28 | 21 | 49 |  | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 858240
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1024449
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1259010
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 130 | 130 | 163 | 163 | 163 | 110 | 163 | 163 | 110 | 110 |  | 100 | 100 | 100 | 110 | 130 | 130 | 130 | 3274364
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 3 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 12500
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1225440
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 156 |  | 154 | 158 | 80 | 33 |  |  |  | 364169
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 85 |  | 100 | 100 | 100 | 70 | 40 |  |  | 343755
106 | Mymensingh 200 MW PP (United) | 200 | 130 | 130 | 100 | 100 | 70 | 70 | 70 | 70 | 70 | 93 | 146 | 170 | 150 | 150 | 100 | 80 | 106 |  | 190 | 190 | 190 | 190 | 190 | 191 | 182 | 3357600
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 50 |  |  | 50 |  |  | 99 |  | 100 | 100 | 100 | 100 | 50 |  |  | 510805
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 73 | 50 | 50 | 50 | 50 | 53 | 92 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 106 | 118 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2906500
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2275200
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 155 | 120 | 85 | 85 | 85 | 85 | 85 | 142 | 180 | 180 | 180 | 186 | 200 | 136 | 143 |  | 165 | 200 | 200 | 200 | 200 | 200 | 200 | 3905280
117 | Ashuganj 150MW PP (Midland) | 133 | 138 | 135 | 137 | 137 | 145 | 137 | 140 | 133 | 132 | 130 | 128 | 127 | 127 | 127 | 125 | 127 | 128 |  | 133 | 140 | 140 | 142 | 138 | 137 | 137 | 3226690
118 | Bibiyana-III 400 MW CCPP | 321 | 321 | 321 | 321 | 321 | 322 | 320 | 321 | 323 | 321 | 321 | 321 | 322 | 322 | 322 | 322 | 322 | 322 |  | 322 | 323 | 322 | 323 | 323 | 323 | 323 | 7741000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 85 | 85 | 85 | 96 | 115 | 115 | 97 | 97 | 95 | 95 | 106 | 107 |  | 107 | 107 | 115 | 115 | 115 | 115 | 115 | 2559600
| Anwara 300 MW PP (United) | 304 | 304 | 304 | 304 | 304 | 251 | 196 | 230 | 245 | 298 | 303 | 305 | 305 | 305 | 304 | 304 | 304 | 304 |  | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 7000364
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 90 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 90 | 100 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2242560
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 90 | 22 | 72 | 72 | 102 | 108 | 108 | 108 | 108 | 108 | 108 | 109 | 114 |  | 116 | 116 | 116 | 116 | 116 | 116 | 110 | 2478982
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 431640
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 1 | 7 | 11 | 19 | 24 | 33 | 32 | 28 | 20 | 9 | 4 | [9 empty] | 197264
120 | Eastern Zone Total | 8054 | 7618 | 7456 | 7231 | 7104 | 6708 | 6332 | 6455 | 6836 | 7217 | 7518 | 7856 | 8041 | 7927 | 8104 | 7896 | 7602 | 8642 |  | 9077 | 9120 | 9058 | 8982 | 8900 | 8730 | 8617 | 190365943
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [12 empty] | 4 | 4 | 5 | 10 | 22 | 32 |  | 32 | 32 | 32 | 30 | 30 | 22 |  | 205440
| Khulna 225 MW CCPP | 155 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 135 | 170 | 130 | 130 | 130 | 130 | 155 |  | 214 | 215 | 215 | 214 | 215 | 215 | 217 | 3704640
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 70 | 70 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 70 | 105 | 105 | 105 | 105 | 105 | 53 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1793280
130
131
132 | United Payra Power Ltd. | 17 | 0 | [15 empty] | 3 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 146400
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 225 | 225 | 225 | 225 | 210 | 160 | 150 | 180 | 180 | 200 | 220 | 222 | 220 | 219 | 218 | 177 | 220 |  | 222 | 222 | 222 | 222 | 224 | 225 | 224 | 5070245
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 46 | 48 | 47 | 47 |  | 47 | 47 | 32 | 32 | 32 | 32 | 17 | 649051
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 85 | 85 | 87 | 85 | 88 | 88 |  | 85 | 87 | 87 | 87 | 87 | 87 | 86 | 2093726
140 | Bhola 33 MW PP (Venture) | 33 | 31 | 31 | 30 | 28 | 25 | 22 | 16 | 17 | 17 | 20 | 20 | [8 empty] | 3 | 3 | 12 | 34 | 34 | 34 | 395960
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 710 | 709 | 710 | 709 | 710 | 709 | 709 | 709 | 709 | 710 | 709 | 709 | 709 | 710 | 710 | 709 | 709 | 710 |  | 712 | 712 | 712 | 712 | 713 | 713 | 715 | 17165090
147 | Bheramara 410 MW CCPP | 220 | 220 | 230 | 235 | 235 | 240 | 240 | 235 | 225 | 215 | 210 | 215 | 215 | 215 | 215 | 225 | 220 | 215 |  | 220 | 215 | 215 | 210 | 210 | 210 | 215 | 5547168
148 | Payra 1320 MW | 540 | 510 | 470 | 460 | 470 | 420 | 400 | 400 | 400 | 400 | 400 | 410 | 420 | 420 | 420 | 410 | 420 | 430 |  | 520 | 540 | 550 | 560 | 560 | 560 | 560 | 12103300
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 80 | 82 | 82 |  | 79 | 80 | 79 | 80 | 80 | 80 | 80 | 1886837
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 43 | 43 | 501648
Sirajgonj 6.55 MW Solar
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 121 | 125 | 126 | 126 | 129 | 132 | 134 | 128 | 124 | 123 | 121 | 121 | 121 | 124 | 125 | 125 | 125 | 125 |  | 124 | 125 | 125 | 125 | 124 | 124 | 124 | 3220400
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 161 | 161 | 161 | 161 | 163 | 162 | 155 | 163 | 174 | 165 | 151 | 150 | 146 | 145 | 147 | 170 | 174 | 172 |  | 170 | 169 | 169 | 169 | 166 | 166 | 155 | 4124936
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 389 | 398 | 414 | 414 | 414 | 423 | 418 | 429 | 422 | 390 | 384 | 329 | 326 | 236 | 316 | 414 | 358 | 400 |  | 414 | 414 | 414 | 414 | 414 | 414 | 370 | 9181600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 5 | 6 | 26 | 26 | 38 |  | 37 | 37 | 37 | 35 | 31 | 31 | 0 | 282467
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 502800
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 226260
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 175400
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 34 |  | 43 | 43 | 43 | 43 | 43 | 43 |  | 227681
167 | Katakhali 50 MW Peaking PP | [16 empty] | 32 | 37 |  | 37 | 37 | 40 | 32 | 32 | 24 | 24 | 222817
168 | Santahar 50 MW Peaking PP | [17 empty] | 16 |  | 35 | 35 | 35 | 35 | 32 | 32 | 34 | 190294
169 | Natore 52 MW PP (Rajlanka) | 52 | 0 | [9 empty] | 6 | 43 | 43 | 43 | 8 | 8 | 8 |  | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 533280
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 81 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 588736
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 70 | 35 | 35 | 35 | 40 | 80 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 64 |  | 94 | 94 | 94 | 94 | 94 | 100 | 113 | 2094336
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 50 | 70 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 95 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2302080
173 | Rangpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 100 | 70 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 70 | 85 | 107 | 113 | 105 | 105 | 50 | 80 |  | 108 | 113 | 113 | 113 | 113 | 113 | 113 | 1938864
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 3 | 2 | [9 empty] | 29126
178
178