## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-08 | Friday
|  |  | Date (day): | 2021-10-08 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13218.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14300 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-07 | 2021-10-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 334 | 354 | 305 | 360 | 52 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 172 | 161 | 200 | 200 | 160 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 295 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 45 | 45 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 51 | 51 | 51 | 51 |  | 49 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 18 | 20 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 336 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 300 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 110 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 21 | 100 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 93 | 93 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 3166 | 3527 | 3453 | 3778 | 920 | 819
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 9 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 42 | 46 | 25 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 163 | 159 | 160 | 160 | 70 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 97 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 0 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 80 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 8 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 88 | 88 | 85 | 88 |  | 20 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 98 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 102 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1387 | 1535 | 1450 | 1557 | 130 | 678
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 70 | 70 | 70 | 70 |  |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 138 | 141 | 140 | 145 |  | 75 | ST Under maint.
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 300 | 300 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 13 | 20 | 20 | 20 |  | 25 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 51 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 128 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 90 | 90 | 92 |  | 71 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 174 | 186 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 120 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 20 | 200 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 100 | 100 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 96 | 95 | 96 |  | 17 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1719 | 2041 | 2037 | 2216 | 450 | 240
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 132 | 143 | 160 | 160 | 42 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 180 | 199 | 170 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 85 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 485 | 501 | 540.6 | 519 | 42 | 8
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 43 | 43 |  | 47 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 162 | 165 | 165 |  | 165 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 46 | 44 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 56 | 60 | 62
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 78 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 322 | 322 | 320 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 321 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1531 | 1579 | 1648 | 1651 | 142 | 570
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 710 | 708 | 722 | 726
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 29 | 5 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 150 | 150 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 205 | 200 | 250 | 250 |  |  | FGMO
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 30 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1174 | 1322 | 1357 | 1571 | 0 | 98
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 0 | 33 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 85 | 85 | 85 |  | 109 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 17 | 17 | 17 | 17 | 78 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 530 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 214 | 215 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 716 | 915 | 1087 | 1237 | 78 | 109
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 0 | 43 |  |  | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 126 | 125 | 190 | 190 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 159 | 130 | 180 | 180 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 373 | 372 | 380 | 380 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 30 | 16 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 155 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 94 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 946 | 1369 | 1445 | 1578 | 380 | 101
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 82 | 76 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 78 | 107 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 167 | 183 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 11291 | 12972 | 13218.6 | 14300 | 2142 | 3022
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10789.642 | 12396 | 12631.6501 | 13665.0324
| A. |  | 2021-10-07 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 12972 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9243 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12972 | MW
| 3 | Day peak Generation : |  |  | 11291 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12396 | MW
| 4 | Evening peak Generation : |  |  | 12972 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 275.0987 | MKWHr | By Solar | 0.6383 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 147.2298 | MKWHr |  | By Oil: | 89.0907 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.392 | MKWHr |  | By Hydro: | 3.7414 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2142 | MW | Dhaka | 4567 | 4567 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3022 | MW | Chittagong | 1255 | 1255 |  | 0 |  | 18:00 |  | 140
|  |  |  | Total = |  |  | 5164 | MW | Khulna | 1565 | 1565 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1110.5 | MMCFD |  |  | Rajshahi | 1294 | 1294 |  | 0 |  | 19:00 |  | 120
| 8 | Fuel Cost : | i) Gas : | Taka | 147882979.734 | ii) Oil : | Taka | 736272656.31 | Comilla | 1217 | 1217 |  | 0 |  | 19:30 |  | 122
|  |  | iii) Coal : |  | 66258832 | Total | Taka | 950414468.044 | Mymensingh | 997 | 997 |  | 0 |  | 20:00 |  | 122
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 4.127 | MKWHr. | Sylhet | 510 | 510 |  | 0 |  | 21:00 |  | 124
|  | ii) During Peak Demand : |  |  | -320 | MW (E to W) at | 19:00 | hrs | Barisal | 323 | 323 |  | 0 |  | 22:00 |  | 124
|  | iii) Maximum : |  |  | -622 | MW at | 21:00 | hrs | Rangpur | 668 | 668 |  | 0 |  | 23:00 |  | 122
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.6° C |  |  | Total | 12396 | 12396 |  | 0
| B. |  | 2021-10-08 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14300 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2100 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 258.7268 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8955 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1535 | MKWHr. | ii) HVDC Flow at Peak Time |  | 708 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8531 | MKWHr. | iii) Maximum HVDC Flow : |  | 711 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106 |  | (b) Today: | 105.88 |  | (c) Rule Curve: |  | 106.63
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 210 |  | 0 | 250 | 265 | 0 | 0 | 45 | 337 | 0 | 0 | 0 | 102 | 115 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 30 | 33 | 25 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 26 | 92 | 59 | 30 | 17 | 38 | 70 | 0 | 0 | 280 | 285 | 141 | 8 | 90 | 23 | 56 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 128 | 145 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 164 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 270 | 21 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 200 | 137 | 323 | 97 | 105 | 105 | 0 | 305 | 54 | 110 | 100 | 50 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 220 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 152 | 0 | 363 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 208 | 0 | 17 | 0 |  | 8401 | 3348 | 11749 | 4043 | 711 | 2059 | 0 | 3617 | 639 | 161 | 217 | 174 | 128 | 0 | 0 | 106.02
2:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 241 |  | 0 | 250 | 265 | 0 | 0 | 45 | 337 | 0 | 0 | 0 | 64 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 30 | 33 | 0 | 0 | 81 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 25 | 17 | 38 | 70 | 0 | 0 | 280 | 270 | 138 | 8 | 91 | 23 | 56 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 120 | 154 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 162 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 280 | 21 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 200 | 127 | 323 | 97 | 0 | 105 | 0 | 304 | 54 | 110 | 0 | 51 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 225 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 149 | 0 | 363 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 227 | 0 | 17 | 0 |  | 7942 | 3255 | 11197 | 4036 | 711 | 2120 | 0 | 3130 | 609 | 156 | 217 | 98 | 120 | 0 | 0 | 106.02
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 262 |  | 0 | 250 | 265 | 0 | 0 | 45 | 337 | 0 | 0 | 0 | 32 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 30 | 33 | 0 | 0 | 81 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 38 | 70 | 0 | 0 | 280 | 270 | 139 | 8 | 92 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 122 | 157 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 161 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 21 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 120 | 0 | 100 | 200 | 127 | 322 | 97 | 0 | 105 | 0 | 305 | 54 | 110 | 0 | 48 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 230 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 0 | 145 | 0 | 360 | 105 | 0 | 113 | 0 | 0 | 0 | 0 | 113 | 510 | 220 | 0 | 17 | 0 |  | 7806 | 3114 | 10920 | 4033 | 711 | 2140 | 0 | 2852 | 591 | 156 | 217 | 98 | 122 | 0 | 0 | 106.01
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 292 |  | 0 | 250 | 255 | 0 | 0 | 45 | 337 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 30 | 33 | 0 | 0 | 81 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 70 | 0 | 0 | 280 | 270 | 139 | 8 | 91 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 120 | 160 | 0 | 22 | 0 | 43 | 42 | 44 | 0 | 130 | 160 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 270 | 18 | 11 | 0 | 245 | 0 | 0 | 192 | 0 | 88 | 0 | 100 | 120 | 128 | 322 | 97 | 0 | 105 | 0 | 305 | 54 | 110 | 0 | 48 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 17 | 0 | 145 | 0 | 362 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 70 | 510 | 220 | 0 | 0 | 0 |  | 7566 | 2934 | 10500 | 4041 | 711 | 2129 | 0 | 2534 | 591 | 156 | 120 | 98 | 120 | 0 | 0 | 106.01
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 312 |  | 0 | 250 | 265 | 0 | 0 | 30 | 337 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 30 | 33 | 0 | 0 | 80 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 39 | 70 | 0 | 0 | 280 | 270 | 139 | 8 | 92 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 116 | 160 | 0 | 22 | 0 | 43 | 42 | 42 | 0 | 130 | 160 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 280 | 18 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 86 | 0 | 100 | 120 | 138 | 322 | 98 | 0 | 105 | 0 | 303 | 54 | 51 | 0 | 49 | 100 | 320 | 66 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 245 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 17 | 0 | 155 | 0 | 364 | 70 | 0 | 70 | 0 | 38 | 0 | 0 | 35 | 490 | 225 | 0 | 0 | 0 |  | 7365 | 2821 | 10186 | 4065 | 710 | 2180 | 0 | 2251 | 571 | 155 | 40 | 98 | 116 | 0 | 0 | 106
6:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 318 |  | 0 | 250 | 275 | 0 | 0 | 30 | 338 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 21 | 25 | 30 | 30 | 33 | 0 | 0 | 80 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 70 | 0 | 0 | 280 | 270 | 139 | 8 | 93 | 23 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 104 | 160 | 0 | 22 | 0 | 43 | 42 | 42 | 0 | 130 | 162 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 270 | 18 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 88 | 1 | 100 | 120 | 137 | 322 | 98 | 0 | 34 | 0 | 268 | 54 | 34 | 0 | 47 | 100 | 320 | 55 | 0 | 141 | 53 | 0 | 17 | 0 |  | 710 | 0 | 245 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 17 | 0 | 194 | 0 | 390 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 460 | 225 | 0 | 0 | 0 |  | 6933 | 2871 | 9804 | 4095 | 710 | 2209 | 0 | 1887 | 539 | 155 | 40 | 64 | 104 | 1 | 0 | 106
7:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 266 |  | 0 | 250 | 270 | 0 | 0 | 30 | 338 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 21 | 25 | 30 | 30 | 8 | 0 | 0 | 81 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 70 | 0 | 0 | 280 | 275 | 140 | 8 | 94 | 20 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 28 | 21 | 102 | 160 | 0 | 22 | 0 | 43 | 42 | 42 | 0 | 130 | 164 | 52 | 81 | 0 | 0 | 18 | 0 | 9 | 270 | 18 | 11 | 0 | 45 | 0 | 0 | 98 | 0 | 86 | 3 | 60 | 120 | 138 | 322 | 98 | 0 | 34 | 1 | 215 | 54 | 34 | 0 | 48 | 100 | 320 | 55 | 4 | 14 | 0 | 0 | 17 | 3 |  | 711 | 0 | 245 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 17 | 0 | 195 | 0 | 390 | 53 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 420 | 214 | 0 | 0 | 0 |  | 6494 | 2749 | 9243 | 4080 | 711 | 2134 | 0 | 1491 | 501 | 156 | 40 | 16 | 102 | 12 | 0 | 105.99
8:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 212 |  | 0 | 250 | 280 | 0 | 0 | 30 | 338 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 70 | 0 | 0 | 360 | 300 | 140 | 8 | 91 | 20 | 57 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 100 | 158 | 0 | 22 | 0 | 43 | 42 | 42 | 0 | 130 | 165 | 56 | 81 | 0 | 0 | 18 | 0 | 0 | 290 | 0 | 11 | 0 | 45 | 0 | 0 | 148 | 0 | 88 | 0 | 100 | 120 | 128 | 322 | 98 | 0 | 34 | 2 | 215 | 54 | 34 | 0 | 48 | 100 | 320 | 55 | 21 | 54 | 0 | 0 | 17 | 10 |  | 711 | 0 | 235 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 17 | 0 | 193 | 0 | 414 | 53 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 400 | 214 | 0 | 0 | 0 |  | 6702 | 2742 | 9444 | 4195 | 711 | 2097 | 0 | 1613 | 480 | 157 | 40 | 16 | 100 | 35 | 0 | 105.99
9:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 184 |  | 0 | 250 | 265 | 0 | 0 | 32 | 338 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 40 | 55 | 19 | 25 | 27 | 33 | 33 | 10 | 0 | 84 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 1 | 16 | 2 | 70 | 0 | 0 | 260 | 295 | 131 | 8 | 91 | 20 | 52 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 21 | 104 | 152 | 0 | 22 | 1 | 44 | 42 | 39 | 0 | 130 | 159 | 56 | 81 | 0 | 0 | 18 | 0 | 0 | 310 | 0 | 0 | 0 | 50 | 0 | 0 | 190 | 0 | 135 | 0 | 100 | 123 | 137 | 323 | 98 | 0 | 73 | 4 | 285 | 54 | 47 | 0 | 47 | 100 | 320 | 72 | 21 | 98 | 0 | 0 | 17 | 16 |  | 711 | 0 | 225 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 17 | 0 | 182 | 0 | 417 | 58 | 0 | 50 | 0 | 40 | 0 | 3 | 90 | 380 | 214 | 0 | 0 | 0 |  | 6934 | 2778 | 9712 | 4032 | 711 | 2055 | 0 | 2090 | 460 | 159 | 40 | 16 | 104 | 45 | 0 | 105.98
10:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 389 | 167 |  | 0 | 250 | 285 | 0 | 0 | 45 | 336 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 16 | 33 | 33 | 41 | 0 | 86 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 20 | 18 | 5 | 70 | 0 | 0 | 290 | 330 | 139 | 8 | 92 | 20 | 30 | 0 | 43 | 0 | 0 | 16 | 19 | 8 | 25 | 21 | 108 | 148 | 0 | 22 | 2 | 44 | 42 | 39 | 0 | 130 | 158 | 55 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 182 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 169 | 128 | 322 | 97 | 0 | 105 | 5 | 305 | 41 | 90 | 17 | 48 | 100 | 320 | 92 | 45 | 162 | 0 | 0 | 11 | 22 |  | 710 | 0 | 220 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 17 | 0 | 175 | 0 | 390 | 105 | 0 | 113 | 0 | 70 | 0 | 5 | 95 | 380 | 214 | 0 | 0 | 0 |  | 7486 | 2880 | 10366 | 4091 | 710 | 1998 | 0 | 2703 | 460 | 161 | 40 | 16 | 108 | 79 | 0 | 105.98
11:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 339 | 153 |  | 0 | 250 | 260 | 0 | 0 | 45 | 340 | 0 | 0 | 0 | 94 | 82 | 36 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 29 | 33 | 33 | 50 | 0 | 86 | 75 | 115 | 0 | 6 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 92 | 26 | 37 | 18 | 5 | 70 | 0 | 0 | 260 | 300 | 140 | 8 | 90 | 13 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 25 | 21 | 110 | 148 | 0 | 22 | 1 | 44 | 42 | 46 | 0 | 130 | 160 | 56 | 81 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 275 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 174 | 127 | 322 | 97 | 44 | 105 | 5 | 305 | 36 | 93 | 98 | 48 | 90 | 320 | 93 | 41 | 162 | 21 | 0 | 17 | 31 |  | 710 | 0 | 210 | 0 | 0 | 80 | 0 | 0 | 3 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 17 | 0 | 166 | 0 | 373 | 105 | 0 | 113 | 0 | 77 | 0 | 6 | 113 | 390 | 214 | 0 | 0 | 0 |  | 7923 | 2925 | 10848 | 3969 | 710 | 1962 | 0 | 3218 | 469 | 161 | 80 | 85 | 110 | 84 | 0 | 105.97
12:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 334 | 172 |  | 0 | 250 | 280 | 0 | 0 | 45 | 333 | 0 | 0 | 0 | 102 | 115 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 29 | 33 | 33 | 51 | 0 | 88 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 92 | 88 | 42 | 18 | 2 | 70 | 0 | 0 | 280 | 320 | 138 | 8 | 93 | 13 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 25 | 21 | 118 | 132 | 0 | 22 | 2 | 44 | 42 | 46 | 0 | 110 | 159 | 55 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 20 | 275 | 0 | 0 | 180 | 21 | 149 | 9 | 100 | 174 | 125 | 322 | 85 | 90 | 105 | 5 | 305 | 36 | 98 | 98 | 47 | 90 | 320 | 93 | 43 | 162 | 102 | 0 | 17 | 31 |  | 710 | 0 | 205 | 0 | 0 | 150 | 0 | 0 | 4 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 17 | 0 | 159 | 0 | 373 | 105 | 0 | 113 | 0 | 78 | 0 | 7 | 113 | 400 | 214 | 0 | 0 | 0 |  | 8288 | 3003 | 11291 | 3970 | 710 | 1946 | 41 | 3495 | 482 | 163 | 150 | 119 | 118 | 97 | 0 | 105.97
13:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 324 | 168 |  | 0 | 250 | 270 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 115 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 26 | 33 | 33 | 50 | 0 | 88 | 75 | 120 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 82 | 46 | 18 | 2 | 70 | 0 | 0 | 260 | 300 | 139 | 8 | 93 | 13 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 25 | 21 | 120 | 119 | 0 | 22 | 2 | 44 | 42 | 47 | 0 | 130 | 160 | 56 | 81 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 11 | 124 | 293 | 0 | 0 | 180 | 90 | 149 | 19 | 100 | 177 | 130 | 322 | 86 | 90 | 105 | 4 | 305 | 36 | 110 | 98 | 48 | 90 | 320 | 93 | 26 | 162 | 108 | 0 | 17 | 30 |  | 711 | 0 | 205 | 0 | 0 | 150 | 0 | 0 | 4 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 17 | 0 | 146 | 0 | 371 | 105 | 0 | 113 | 0 | 85 | 0 | 7 | 113 | 450 | 214 | 0 | 0 | 0 |  | 8459 | 3046 | 11505 | 3898 | 711 | 1961 | 214 | 3549 | 532 | 163 | 150 | 119 | 120 | 88 | 0 | 105.96
14:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 324 | 165 |  | 0 | 250 | 275 | 0 | 0 | 45 | 333 | 0 | 0 | 0 | 102 | 98 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 120 | 0 | 22 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 89 | 46 | 18 | 6 | 70 | 0 | 0 | 260 | 305 | 137 | 8 | 92 | 13 | 30 | 0 | 43 | 0 | 36 | 52 | 19 | 8 | 33 | 21 | 112 | 106 | 0 | 22 | 1 | 44 | 43 | 47 | 0 | 110 | 156 | 55 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 100 | 300 | 0 | 40 | 188 | 70 | 149 | 17 | 100 | 192 | 125 | 322 | 86 | 70 | 105 | 2 | 305 | 36 | 92 | 62 | 47 | 90 | 320 | 93 | 23 | 162 | 108 | 0 | 17 | 26 |  | 708 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 6 | 0 | 0 | 85 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 17 | 0 | 134 | 0 | 355 | 105 | 0 | 113 | 0 | 85 | 0 | 7 | 113 | 450 | 214 | 0 | 0 | 0 |  | 8384 | 3048 | 11432 | 3875 | 708 | 1948 | 210 | 3522 | 531 | 160 | 150 | 140 | 112 | 76 | 0 | 105.96
15:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 323 | 165 |  | 0 | 250 | 250 | 0 | 0 | 45 | 334 | 0 | 0 | 0 | 102 | 98 | 51 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 33 | 33 | 51 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 88 | 46 | 18 | 5 | 70 | 0 | 0 | 305 | 305 | 141 | 8 | 92 | 13 | 30 | 0 | 43 | 0 | 50 | 43 | 19 | 8 | 33 | 21 | 128 | 106 | 0 | 22 | 1 | 44 | 42 | 47 | 0 | 163 | 159 | 56 | 81 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 11 | 190 | 295 | 110 | 100 | 188 | 98 | 149 | 14 | 90 | 200 | 123 | 322 | 86 | 70 | 105 | 3 | 305 | 36 | 94 | 80 | 48 | 100 | 320 | 93 | 10 | 162 | 108 | 0 | 17 | 19 |  | 709 | 0 | 190 | 0 | 0 | 150 | 0 | 0 | 10 | 0 | 0 | 84 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 17 | 10 | 128 | 0 | 355 | 105 | 0 | 113 | 0 | 85 | 0 | 0 | 113 | 470 | 203 | 0 | 0 | 0 |  | 8725 | 3053 | 11778 | 3910 | 709 | 1972 | 508 | 3489 | 549 | 158 | 150 | 158 | 128 | 47 | 0 | 105.96
16:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 323 | 165 |  | 0 | 250 | 290 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 98 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 29 | 33 | 33 | 51 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 88 | 46 | 18 | 6 | 70 | 0 | 0 | 330 | 325 | 137 | 8 | 92 | 13 | 30 | 0 | 43 | 0 | 50 | 48 | 19 | 8 | 33 | 20 | 122 | 105 | 0 | 22 | 0 | 43 | 43 | 47 | 0 | 163 | 158 | 55 | 80 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 13 | 298 | 0 | 0 | 186 | 50 | 149 | 8 | 90 | 200 | 127 | 322 | 86 | 70 | 105 | 1 | 305 | 48 | 110 | 63 | 48 | 90 | 320 | 92 | 14 | 162 | 108 | 0 | 17 | 10 |  | 708 | 0 | 190 | 0 | 0 | 150 | 0 | 0 | 22 | 0 | 0 | 85 | 25 | 0 | 0 | 0 | 0 | 27 | 5 | 0 | 0 | 0 | 0 | 47 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 17 | 0 | 128 | 0 | 347 | 105 | 0 | 113 | 0 | 85 | 0 | 3 | 113 | 470 | 217 | 0 | 0 | 0 |  | 8367 | 3092 | 11459 | 3949 | 708 | 2008 | 63 | 3513 | 550 | 158 | 150 | 202 | 122 | 36 | 0 | 105.95
17:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 323 | 165 |  | 0 | 250 | 260 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 64 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 29 | 33 | 33 | 51 | 0 | 83 | 75 | 120 | 0 | 2 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 40 | 89 | 30 | 18 | 8 | 70 | 0 | 0 | 285 | 265 | 140 | 8 | 90 | 13 | 30 | 0 | 43 | 0 | 50 | 52 | 19 | 8 | 30 | 20 | 118 | 105 | 0 | 22 | 0 | 43 | 43 | 47 | 0 | 163 | 160 | 56 | 40 | 0 | 0 | 18 | 0 | 9 | 285 | 24 | 11 | 0 | 298 | 0 | 0 | 194 | 0 | 123 | 2 | 100 | 155 | 125 | 322 | 115 | 70 | 68 | 0 | 305 | 54 | 110 | 80 | 56 | 100 | 320 | 93 | 3 | 162 | 72 | 0 | 17 | 2 |  | 709 | 0 | 195 | 0 | 0 | 150 | 0 | 0 | 27 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 17 | 0 | 129 | 0 | 300 | 70 | 0 | 70 | 0 | 92 | 0 | 1 | 70 | 450 | 138 | 0 | 0 | 0 |  | 7958 | 2843 | 10801 | 3852 | 709 | 1808 | 0 | 3263 | 527 | 158 | 150 | 208 | 118 | 8 | 0 | 105.94
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 323 | 165 |  | 0 | 250 | 300 | 0 | 0 | 45 | 328 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 50 | 18 | 25 | 17 | 33 | 33 | 51 | 0 | 83 | 75 | 120 | 0 | 12 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 80 | 88 | 28 | 18 | 10 | 70 | 0 | 0 | 330 | 340 | 135 | 8 | 92 | 13 | 30 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 12 | 140 | 143 | 0 | 22 | 0 | 44 | 43 | 47 | 0 | 163 | 159 | 55 | 60 | 0 | 0 | 18 | 0 | 9 | 305 | 24 | 11 | 180 | 300 | 300 | 100 | 185 | 97 | 114 | 0 | 100 | 164 | 125 | 322 | 115 | 90 | 80 | 0 | 305 | 54 | 94 | 100 | 92 | 100 | 320 | 93 | 0 | 162 | 86 | 0 | 12 | 0 |  | 709 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 23 | 0 | 0 | 82 | 32 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 27 | 24 | 24 | 16 | 14 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 17 | 15 | 129 | 0 | 370 | 105 | 0 | 85 | 0 | 95 | 0 | 0 | 90 | 460 | 218 | 0 | 1 | 0 |  | 9173 | 3295 | 12468 | 3983 | 709 | 2057 | 692 | 3503 | 539 | 158 | 150 | 537 | 140 | 0 | 0 | 105.94
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 354 | 161 |  | 0 | 250 | 295 | 0 | 0 | 45 | 336 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 80 | 88 | 46 | 18 | 15 | 70 | 0 | 0 | 280 | 300 | 141 | 8 | 90 | 20 | 51 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 120 | 143 | 0 | 22 | 0 | 43 | 43 | 44 | 0 | 163 | 162 | 56 | 78 | 0 | 0 | 18 | 0 | 9 | 285 | 24 | 11 | 200 | 300 | 110 | 100 | 199 | 100 | 149 | 0 | 100 | 186 | 128 | 322 | 115 | 105 | 97 | 0 | 305 | 54 | 110 | 100 | 96 | 100 | 321 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 29 | 0 | 0 | 85 | 33 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 27 | 43 | 35 | 16 | 33 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 17 | 100 | 130 | 0 | 372 | 105 | 155 | 113 | 30 | 107 | 0 | 0 | 113 | 530 | 215 | 0 | 35 | 0 |  | 9183 | 3789 | 12972 | 3975 | 708 | 2069 | 765 | 3847 | 606 | 159 | 150 | 573 | 120 | 0 | 0 | 105.92
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 161 |  | 0 | 280 | 300 | 0 | 0 | 45 | 333 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 88 | 46 | 18 | 15 | 70 | 0 | 0 | 280 | 295 | 140 | 8 | 92 | 20 | 55 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 122 | 137 | 0 | 22 | 0 | 43 | 43 | 44 | 0 | 163 | 160 | 56 | 78 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 11 | 200 | 300 | 103 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 131 | 322 | 115 | 105 | 105 | 0 | 303 | 54 | 110 | 100 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 205 | 0 | 0 | 150 | 0 | 0 | 30 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 50 | 31 | 94 | 27 | 43 | 40 | 18 | 33 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 17 | 50 | 132 | 0 | 373 | 105 | 10 | 113 | 32 | 113 | 0 | 0 | 113 | 520 | 220 | 0 | 35 | 0 |  | 9306 | 3619 | 12925 | 4013 | 708 | 2130 | 563 | 3901 | 599 | 159 | 150 | 580 | 122 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 161 |  | 0 | 280 | 285 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 89 | 47 | 18 | 20 | 70 | 0 | 0 | 280 | 295 | 139 | 8 | 92 | 23 | 56 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 122 | 137 | 0 | 22 | 0 | 43 | 43 | 44 | 0 | 163 | 159 | 56 | 78 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 200 | 300 | 100 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 130 | 322 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 68 | 94 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 205 | 0 | 0 | 150 | 0 | 0 | 29 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 50 | 41 | 94 | 27 | 43 | 40 | 31 | 33 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 17 | 50 | 132 | 0 | 375 | 105 | 0 | 113 | 32 | 113 | 0 | 0 | 113 | 540 | 221 | 0 | 35 | 0 |  | 9257 | 3653 | 12910 | 4015 | 708 | 2114 | 550 | 3883 | 619 | 160 | 150 | 589 | 122 | 0 | 0 | 105.93
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 162 |  | 0 | 280 | 290 | 0 | 0 | 45 | 331 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 89 | 46 | 18 | 20 | 70 | 0 | 0 | 305 | 330 | 121 | 8 | 92 | 23 | 56 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 124 | 130 | 0 | 22 | 0 | 44 | 43 | 44 | 0 | 163 | 160 | 61 | 78 | 0 | 0 | 18 | 0 | 9 | 305 | 24 | 11 | 200 | 300 | 160 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 130 | 322 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 80 | 96 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 210 | 0 | 0 | 150 | 0 | 0 | 26 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 0 | 43 | 36 | 52 | 33 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 17 | 15 | 142 | 0 | 375 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 222 | 0 | 35 | 0 |  | 9383 | 3577 | 12960 | 4064 | 708 | 2136 | 575 | 3856 | 617 | 159 | 150 | 571 | 124 | 0 | 0 | 105.92
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 172 |  | 0 | 280 | 260 | 0 | 0 | 45 | 336 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 89 | 33 | 18 | 27 | 70 | 0 | 0 | 260 | 265 | 130 | 8 | 92 | 22 | 55 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 124 | 135 | 0 | 22 | 0 | 43 | 43 | 44 | 0 | 163 | 161 | 61 | 78 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 11 | 200 | 300 | 157 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 130 | 322 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 100 | 95 | 100 | 320 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 210 | 0 | 0 | 100 | 0 | 0 | 26 | 0 | 0 | 86 | 35 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 0 | 43 | 30 | 52 | 33 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 17 | 40 | 159 | 0 | 380 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 222 | 0 | 54 | 0 |  | 9276 | 3601 | 12877 | 3991 | 708 | 2123 | 597 | 3882 | 628 | 159 | 100 | 565 | 124 | 0 | 0 | 105.92
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 189 |  | 0 | 280 | 280 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 100 | 89 | 33 | 18 | 31 | 70 | 0 | 0 | 260 | 270 | 129 | 8 | 92 | 22 | 55 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 122 | 132 | 0 | 22 | 0 | 43 | 43 | 44 | 0 | 163 | 160 | 61 | 78 | 0 | 0 | 18 | 0 | 9 | 305 | 24 | 11 | 200 | 293 | 85 | 50 | 200 | 100 | 149 | 0 | 100 | 200 | 137 | 322 | 115 | 105 | 105 | 0 | 303 | 54 | 110 | 80 | 96 | 100 | 320 | 102 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 0 | 43 | 30 | 52 | 33 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 11 | 40 | 167 | 0 | 380 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 222 | 0 | 54 | 0 |  | 9186 | 3541 | 12727 | 3999 | 708 | 2163 | 475 | 3871 | 668 | 160 | 0 | 561 | 122 | 0 | 0 | 105.91
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 198 |  | 0 | 280 | 280 | 0 | 0 | 45 | 334 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 102 | 92 | 89 | 33 | 19 | 32 | 70 | 0 | 0 | 275 | 285 | 132 | 8 | 92 | 22 | 56 | 0 | 51 | 0 | 42 | 52 | 19 | 8 | 33 | 21 | 120 | 132 | 0 | 22 | 0 | 43 | 43 | 44 | 0 | 163 | 162 | 61 | 78 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 11 | 200 | 298 | 0 | 50 | 192 | 100 | 149 | 0 | 100 | 200 | 132 | 323 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 80 | 67 | 100 | 320 | 104 | 0 | 162 | 110 | 0 | 17 | 0 |  | 709 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 0 | 50 | 25 | 94 | 0 | 43 | 26 | 52 | 33 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 11 | 40 | 163 | 0 | 380 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 223 | 0 | 54 | 0 |  | 9085 | 3531 | 12616 | 4032 | 709 | 2170 | 390 | 3822 | 669 | 160 | 0 | 544 | 120 | 0 | 0 | 105.91
KWH | 0 | 0 | 0 | 0 | 7474482 | 0 | 0 | 9009770 | 4842000 |  | 0 | 6250550 | 6609280 | 0 | 0 | 1054585 | 8092031 | 0 | 0 | 0 | 1692576 | 2318880 | 782995 | 0 | 0 | 0 | 1303200 | 1223489 | 1202348 | 432936 | 600000 | 665280 | 819800 | 807800 | 764640 | 0 | 1917382 | 1824000 | 2800000 | 0 | 267033 | 0 | 0 | 0 | 0 |  | 306720 | 0 | 706231 | 1384920 | 1236480 | 708480 | 396864 | 494880 | 1720164 | 0 | 0 | 7146900 | 7210000 | 3338000 | 217454 | 2183430 | 415152 | 1127040 | 0 | 1171912 | 0 | 492148 | 860270 | 450792 | 225900 | 701200 | 519840 | 2853120 | 3216400 | 0 | 484560 | 10300 | 1031000 | 1014600 | 1074600 | 0 | 3475718 | 3692000 | 1312224 | 1854720 | 0 | 0 | 389000 | 0 | 190260 | 7172500 | 485376 | 231936 | 1658880 | 5863743 | 897301 | 638145 | 4392000 | 974545 | 3201840 | 95175 | 2316480 | 4160640 | 3131345 | 7697000 | 2407200 | 1435200 | 2340135 | 32150 | 7083164 | 1197309 | 2310026 | 1341780 | 1477560 | 2355840 | 7675900 | 2107200 | 258050 | 3584160 | 2110145 | 0 | 431280 | 201632 |  | 17153454 | 0 | 5321664 | 0 | 0 | 2781120 | 0 | 0 | 228000 | 0 | 0 | 2072708 | 630917 | 0 | 0 | 0 | 0 | 411264 | 225047 | 606968 | 93800 | 270452 | 185817 | 561120 | 218463 | 501360 | 0 | 239652 | 1876800 | 0 | 0 | 0 | 0 | 0 | 0 | 3264945 | 0 | 407376 | 359040 | 3951464 | 0 | 8934036 | 2274240 | 184209 | 2454624 | 50400 | 1827609 | 0 | 40994 | 2316000 | 12515200 | 5184409 | 0 | 321600 | 0 |  | 197633973 | 77464752 | 275098725 | 97090770 | 17153454 | 50139012 | 4712120 | 76204628 | 14392000 | 3741382 | 2781120 | 5392818 | 2853120 | 638301 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8296675.02 | 0 | 0 | 9099867.7 | 4987260 |  | 0 | 6813099.5 | 7336300.8 | 0 | 0 | 8921789.1 | 8415712.24 | 0 | 0 | 0 | 15436293.12 | 22817779.2 | 7219213.9 | 0 | 0 | 0 | 9513360 | 9457569.97 | 11855151.28 | 324702 | 450000 | 0 | 0 | 0 | 7394068.8 | 0 | 517693.14 | 492480 | 5068000 | 0 | 2480736.57 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6850440.7 | 13225986 | 10757376 | 5611161.6 | 500048.64 | 1469793.6 | 2545842.72 | 0 | 0 | 5288706 | 7210000 | 3070960 | 280515.66 | 2510944.5 | 469121.76 | 1577856 | 0 | 2003969.52 | 0 | 4970694.8 | 8215578.5 | 572505.84 | 169425 | 1227100 | 389880 | 21398400 | 3409384 | 0 | 615391.2 | 164182 | 1690840 | 1623360 | 1912788 | 0 | 3962318.52 | 3839680 | 2585081.28 | 3542515.2 | 0 | 0 | 851910 | 0 | 388130.4 | 7244225 | 364032 | 176271.36 | 28217548.8 | 44329897.08 | 15236170.98 | 10669784.4 | 22838400 | 16294392.4 | 31506105.6 | 1112595.75 | 18879312 | 45142944 | 22075982.25 | 7158210 | 21953664 | 13562640 | 20382575.85 | 0 | 53548719.84 | 10428561.39 | 20305128.54 | 13390964.4 | 12662689.2 | 15689894.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98803895.04 | 0 | 5587747.2 | 0 | 0 | 38546323.2 | 0 | 0 | 2391720 | 0 | 0 | 2342160.04 | 977921.35 | 0 | 0 | 0 | 0 | 4046837.76 | 2286477.52 | 5371666.8 | 722260 | 3656511.04 | 1800566.73 | 5437252.8 | 2119091.1 | 962611.2 | 0 | 181416.564 | 11317104 | 0 | 0 | 0 | 0 | 0 | 0 | 4309727.4 | 0 | 611064 | 6107270.4 | 4623212.88 | 0 | 8844695.64 | 23743065.6 | 3133395.09 | 23294381.76 | 475776 | 14182245.84 | 0 | 452983.7 | 17115240 | 54941728 | 0 | 0 | 0 | 0 |  | 724970349.02 | 348386348.654 | 1073356697.674 | 94967915.344 | 98803895.04 | 52915064.39 | 79658562.07 | 565412496.43 | 66258832 | 1010173.14 | 38546323.2 | 52655274.61 | 21398400 | 1729761.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 334 | 172 |  | 0 | 250 | 280 | 0 | 0 | 45 | 333 | 0 | 0 | 0 | 102 | 115 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 29 | 33 | 33 | 51 | 0 | 88 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 92 | 88 | 42 | 18 | 2 | 70 | 0 | 0 | 280 | 320 | 138 | 8 | 93 | 13 | 30 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 25 | 21 | 118 | 132 | 0 | 22 | 2 | 44 | 42 | 46 | 0 | 110 | 159 | 55 | 81 | 0 | 0 | 18 | 0 | 9 | 290 | 24 | 11 | 20 | 275 | 0 | 0 | 180 | 21 | 149 | 9 | 100 | 174 | 125 | 322 | 85 | 90 | 105 | 5 | 305 | 36 | 98 | 98 | 47 | 90 | 320 | 93 | 43 | 162 | 102 | 0 | 17 | 31 |  | 710 | 0 | 205 | 0 | 0 | 150 | 0 | 0 | 4 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 17 | 0 | 159 | 0 | 373 | 105 | 0 | 113 | 0 | 78 | 0 | 7 | 113 | 400 | 214 | 0 | 0 | 0 |  | 11291 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 354 | 161 | 0 | 0 | 250 | 295 | 0 | 0 | 45 | 336 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 102 | 80 | 88 | 46 | 18 | 15 | 70 | 0 | 0 | 280 | 300 | 141 | 8 | 90 | 20 | 51 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 21 | 120 | 143 | 0 | 22 | 0 | 43 | 43 | 44 | 0 | 163 | 162 | 56 | 78 | 0 | 0 | 18 | 0 | 9 | 285 | 24 | 11 | 200 | 300 | 110 | 100 | 199 | 100 | 149 | 0 | 100 | 186 | 128 | 322 | 115 | 105 | 97 | 0 | 305 | 54 | 110 | 100 | 96 | 100 | 321 | 93 | 0 | 162 | 116 | 0 | 17 | 0 |  | 708 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 29 | 0 | 0 | 85 | 33 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 27 | 43 | 35 | 16 | 33 | 22 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 17 | 100 | 130 | 0 | 372 | 105 | 155 | 113 | 30 | 107 | 0 | 0 | 113 | 530 | 215 | 0 | 35 | 0 |  | 12972 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 360 | 200 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 88 | 50 | 17 | 10 | 70 | 0 | 0 | 330 | 330 | 145 | 8 | 92 | 20 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 160 | 0 | 22 | 0 | 43 | 43 | 50 | 0 | 163 | 165 | 62 | 80 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 135 | 321 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 726 | 0 | 250 | 0 | 0 | 225 | 0 | 0 | 25 | 40 | 0 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 94 | 27 | 43 | 40 | 52 | 33 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 17 | 100 | 180 | 0 | 380 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 305 | 200 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 51 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 0 | 100 | 85 | 25 | 17 | 8 | 70 | 0 | 0 | 330 | 300 | 140 | 8 | 90 | 20 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 160 | 0 | 22 | 1.6 | 43 | 43 | 50 | 0 | 163 | 165 | 60 | 80 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 320 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 100 | 95 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 722 | 0 | 250 | 0 | 0 | 225 | 0 | 0 | 5 | 0 | 0 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 27 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 17 | 50 | 180 | 0 | 380 | 105 | 0 | 94 | 0 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 304 | 222 | 0 | 0 | 280 | 260 | 0 | 0 | 15 | 336 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 15 | 25 | 30 | 33 |  | 0 | 0 | 83 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 14 | 70 | 0 | 0 | 260 | 290 | 142 | 8 | 30 | 15 | 53 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 46 | 150 | 0 | 22 | 1 | 43 | 43 | 44 | 0 | 110 | 161 | 61 | 78 | 0 | 0 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 15 | 0 | 0 | 35 | 0 | 90 | 9 | 100 | 17 | 112 | 322 | 97 | 0 | 51 | 2 | 51 | 54 | 51 | 0 | 47 | 100 | 320 | 57 | 0 | 162 | 108 | 0 | 17 | 12 | 0 | 708 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 11 | 0 | 126 | 0 | 338 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 450 | 224 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9243 | 7:00
| Highest Generation |  | 12972 | 19:00
| Day Peak Generation |  | 11291 | 12:00
| Evening Peak Generation |  | 12972 | 19:00
| HVDC Max Flow |  | 711 | 1:00
| HVDC EvPeak Flow |  | 708 | 19:00
| Load factor L.F |  | 88.36%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-08
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11291 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8955 | MW
Evening Peak Generation : |  | 12972 | MW Hour : | 19:00 | Available Max Generation : |  | 14300 | MW
E.P. Demand (at gen end) : |  | 12972 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12200 | MW
Maximum Generation : |  | 12972 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2100 | MW
Total Gen. (MKWH) : |  | 275.0987 | System Load Factor : | 88.36% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -622 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-08
Actual : | 105.88 | Ft.(MSL) , | Rule curve : | 106.63 | Ft.( MSL )
Gas Consumed : | Total = | 1110.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 147882979.734
: |  | Coal : | 66258832 | Oil : | 736272656.31 | Total : | 950414468.044
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4335.4803 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1477.1129 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1323.9448 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1196.4736 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1081.1379 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 872.4471 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 484.2139 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 224.536 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 672.8918 |  |  | 0 | 0%
Total | 0 |  | 11668.2383 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Sylhet-225 MW
7) Raozan #02
8) Shajibazar 330 Mw GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar 230/132 kV T01 transformer was under shut down from 09:28 to 15:30 for A/M.
b) Baghabari-Shahjadpur 132 kV Ckt-2 was under shut down from 09:35 to 12:37 for C/M.
c) Kulshi-Bakulia 132 kV Ckt was under shut down from 08:47 to 13:13 for C/M.
d) Sikalbaha old-Sikalbaha new 132 kV Ckt-2 was under shut down from 08:32 to 17:07 for D/W.
e) Bogura 230/132 kV T03 transformer was under shut down from 08:15 to 15:25 for A/M.
f) Dohazari-Matarbari 132 kV Ckt was switched on at 08:58.
g) Madunaghat-Sikalbaha 132 kV Ckt-1 was shut down at 09:03 for D/W.
h) Mirpur 132/33 kV T1 transformer was under shut down from 08:11 to 20:03 fro A/M.
i) Polashbari 132/33 kV T2 transformer was under shut down from 08:10 to 15:30 fro A/M.
j) Rangamati-Khagrachori 132 kV Ckt-1 was under shut down from 08:40 to 15:33 for A/M.
k) Satmosjid 132/33 kV T2 transformer was under shut down from 09:06 to 10:17 for A/M.
l) Tongi-Kaliakoir 230 kV Ckt was under shut down from 09:34 to 15:56 for A/M.
m) Lalmonirhat 132/33 kV T1 transformer was under shut down from 12:30 to 14:35 for D/W.
n) Bhola 230/11 kV unit transformer was under shut down from 15:07 to 16:38 for C/M.
o) Lalmonirhat 132/33 kV T2 transformer was under shut down from 15:15 to 17:15 for C/M.
p) Chowmuhoni 33 kV T2 Bus was under shut down from 19:52 to 20:26 for C/M. |  |  |  |  | About 50 MW power interruption occurred under Chowmuhoni S/S
area from 19:52 to 20:26.
q) Gallamari-Khulna(S) 132 kV Ckt-2 was under shut down from 19:09 to 20:40 for A/M.
r) Patuakhali 132/33 kV T1 & T2 transformers tripped at 18:10 showing O/C, E/F relays at 33 kV end |  |  |  |  | About 46 MW power interruption occurred under Patuakhali S/S
and were switched on at 18:22,20:36 respectively. |  |  |  |  | area from 18:10 to 18:22.
t) Ashuganj-Kishoreganj 132 kV Ckt-2 tripped at 00:35(08-10-2021) from Ashuganj end showing
Dist Z1,B-phase and was switched on at 00:50(08-10-21).
u) Hathazari-Baraulia 132 kV Ckt-2 tripped at 04:10(08-10-2021) from Hathazari end showing E/F
relays and was switched on at 04:49(08-10-21).
v) Rangamati-Khagrachori 132 kV Ckt-1 tripped at 05:43(08-10-2021) showing Dist. Z1 R,Y-phase
relay at Rangamati end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7474482 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 354 | 9009770
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 161 | 4842000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6250550 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 295 | 6609280 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 45 | 1054585 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 51 | 782995 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 432936
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 336 | 8092031
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1692576
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1303200
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2318880
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1223489
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1202348
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1265280 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 819800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 807800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 764640
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5863743
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 110 | 897301 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 638145
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 974545
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3201840
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1435200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 2107200 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3584160
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 201632
| Dhaka area Total |  |  |  | 5560 | 3527 | 74850408
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 267033
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 95175
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 708480
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 159 | 3741382 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 97 | 2340135 | Engine problem
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 706231
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1384920 | Engine problem
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2316480
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 396864 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 494880
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 88 | 1236480 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32150
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 7083164
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1197309
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2310026
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2355840
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2110145
| Chattogram area Total |  |  |  | 2382 | 1535 | 31576694
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 70 | 1720164 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 141 | 3338000 | ST under maint
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7146900 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7210000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 415152 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1127040
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1171912
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 3131345 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 492148
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2183430 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 186 | 4160640 | Engine problem
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 450792
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 225900
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2853120
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 701200
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 860270
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 519840 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1658880
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1341780 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1477560 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 431280 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2041 | 42834807
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 143 | 3216400 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 484560
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10300
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 199 | 4392000
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2407200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 258050
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 306720
| Mymensingh Area Total |  |  |  | 622 | 501 | 11075230
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1031000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1014600 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3475718
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 162 | 3692000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 44 | 1074600 | Machine problem
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 231936
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1312224 | Machine problem
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1854720
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 389000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 485376
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7172500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 322 | 7697000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 190260
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 321 | 7675900 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1579 | 37296834
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 708 | 17153454
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 228000 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 150 | 2781120 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 5321664 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 359040
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2274240
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 30 | 50400 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1322 | 28167918
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 630917
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2072708 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 407376 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 12515200
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 215 | 5184409
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 321600 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 915 | 21132210
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 411264
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 30 | 225047 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 93800 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 270452 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 185817 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 125 | 3264945 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 3951464 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 372 | 8934036 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 218463 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 501360
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239652
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 561120 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 606968 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 155 | 184209 | Low demand
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2454624
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2316000
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 0
| Rajshahi Area Total |  |  |  | 2179 | 1369 | 24419221
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1876800
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1827609
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40994
| Rangpur Area Total |  |  |  | 605 | 183 | 3745403
| Total |  |  |  | 20934 | 12972 | 275098725
| Eastern Grid Total |  |  |  | 13975 | 9183 | 197633973
| Western Grid Total |  |  |  | 6959 | 3789 | 77464752
| National Grid Total |  |  |  | 20934 | 12972 | 275098725
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-07
(a) ENTIRE EASTERN GRID : |  | 8546 | MW | (b) ENTIRE WESTERN GRID : |  | 3850 | MW
i) Dhaka area |  | 4567 | MW | i) Khulna area |  | 1565 | MW
ii) Chittagong area |  | 1255 | MW | ii) Rajshahi area |  | 1294 | MW
iii) Comilla area |  | 1217 | MW | iii) Barisal area |  | 323 | MW
iv) Mymensingh area |  | 997 | MW | iv) Rangpur area |  | 668 | MW
v) Sylhet area |  | 510 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12396 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 18:00 | Kishoreganj | 140 | 1:00 | Jessore | 116 | 19:00
Munsiganj | 100 | 22:00 | Netrokona | 120 | 19:00 | Benapol | 58 | 20:00
Sonargaon | 80 | 0:00 | Jamalpur | 144 | 23:00 | Jhenida(Old) | 115 | 21:00
Shyampur | 204 | 10:00 | Sherpur | 126 | 22:00 | Bottail | 124 | 18:30
Bhulta | 219 | 20:00 | Srimongal | 54 | 22:00 | G.K Project | 58 | 21:00
Madanganj | 45 | 13:00 | Shahjibazar | 110 | 1:00 | Faridpur | 157 | 20:00
Shitalakhya | 105 | 18:30 | Fenchuganj | 49 | 19:00 | Rajbari | 58 | 18:30
Rahim steel | 23 | 17:00 | Kulawara | 46 | 18:00 | Madaripur | 105 | 22:00
Matuail | 51 | 1:00 | Sylhet | 142 | 18:00 | Sariatpur | 72 | 21:00
Ghorasal | 95 | 4:00 | Chatak | 31 | 19:00 | Gopalganj | 99 | 18:30
Narsingdi | 182 | 21:00 | Sunamganj | 50 | 20:00 | Bagerhat | 101 | 21:00
Haripur (SBU) | 119 | 19:30 | Biani Bazar | 66 | 18:00 | Mongla | 48 | 12:00
Sreenagar | 42 | 21:00 | Comilla (S) | 140 | 18:00 | Satkhira | 104 | 21:00
Ullon | 64 | 21:00 | Comilla(N) | 153 | 23:00 | Gallamari | 42 | 20:00
Hasnabad | 85 | 18:30 | Chandpur | 79 | 21:00 | Magura | 56 | 19:00
Magbazar | 106 | 12:00 | Feni | 121 | 20:00 | Norail | 46 | 19:00
Maniknagar | 73 | 13:00 | Chowmuhani | 213 | 21:00 | Chuadanga | 100 | 21:00
Bangabhaban | 13 | 10:00 | Ashuganj | 48 | 24:00 | Barisal(N) | 45 | 21:00
Motijheel | 30 | 11:00 | Daudkandi | 164 | 22:00 | Barisal (S) | 114 | 18:30
Narinda | 66 | 13:00 | B.Baria | 168 | 19:30 | Patuakhali | 125 | 22:00
Kazla | 84 | 11:00 | Ramganj | 100 | 22:00 | Bhandaria | 52 | 19:00
Dhanmondi | 204 | 13:00 | Chaddagram | 49 | 22:00 | Borguna | 18 | 19:30
Lalbag | 78 | 13:00 | PHP | 8 | 6:00 | Borhan Uddin | 46 | 21:00
Madartek | 69 | 22:00 | Kochua | 62 | 20:00 | Ishurdi | 67 | 19:00
Dhaka University | 38 | 12:00 | Madunaghat | 62 | 18:30 | Ruppur Paromanobik | 4 | 18:00
Aftabnagar | 16 | 20:00 | Hathazari | 96 | 18:00 | Natore | 127 | 20:00
Fatullah | 65 | 15:00 | Khulshi | 208 | 17:00 | Bogra | 158 | 19:30
Nawabganj | 52 | 10:00 | Halishahar | 95 | 10:00 | Noagaon | 106 | 20:00
Keraniganj | 72 | 18:00 | Baraulia | 157 | 19:30 | Rajshahi | 149 | 20:00
Mirpur | 125 | 18:00 | Sikalbaha | 47 | 11:00 | Rajshahi New | 18 | 20:00
Kalyanpur | 96 | 18:00 | Dohazari | 102 | 1:00 | C.Nawabganj | 63 | 20:00
Gulshan | 126 | 12:00 | Cox'sbazar | 108 | 20:00 | Amnura | 54 | 20:00
Uttara | 89 | 18:00 | Chandraghona | 30 | 20:00 | Pabna | 108 | 19:00
Uttara New | 30 | 18:30 | Kaptai | 4.5 | 18:30 | Shahjadpur | 97 | 20:00
Kamrangirchar | 103 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 98 | 19:30
Savar | 178 | 19:00 | Bakulia | 121 | 18:00 | Niyamatpur | 74 | 20:00
Bhasantec | 141 | 18:00 | Julda | 25 | 12:00 | Joypurhat | 56 | 19:00
Agargaon | 88 | 14:00 | TK chemical | 30 | 18:30 | Sherpur(Bogura) | 56 | 18:30
Satmosjid | 111 | 18:00 | Modern Steel | 9.5 | 9:00 | Mohastangor | 64 | 20:00
Tongi | 125 | 15:00 | Shahmirpur | 26 | 21:00 | Bhangura | 32 | 19:00
Kabirpur | 237 | 15:00 | Khagrachhari | 28 | 19:00 | Rangpur | 115 | 18:00
Basundhara | 190 | 18:00 | Matarbari | 43 | 19:30 | Lalmonirhat | 44 | 21:00
Manikganj | 74 | 21:00 | Baroiar Hat | 48 | 18:30 | Saidpur | 93 | 18:30
Joydevpur | 191 | 18:30 | Rangamati | 14 | 18:00 | Purbasadipur | 92 | 22:00
New Tongi | 89 | 12:00 | Abul Khair 230 | 145 | 18:00 | Thakurgaon | 75 | 23:00
Kodda | 271 | 15:00 | BSRM | 157 | 20:00 | Palashbari | 111 | 24:00
Dhamrai | 100 | 20:00 | GPH Ispat | 15 | 6:00 | Barapukuria | 49 | 21:00
Rajendrapur | 104 | 18:30 | Agrabad | 86 | 19:00 | Panchagar | 49 | 20:00
Valuka | 128 | 15:00 | Goalpara | 28 | 14:00 | Joldhaka | 51 | 21:00
Tangail | 217 | 21:00 | Central S/S | 96 | 18:30 | Kurigram | 55 | 21:00
Mymensing | 208 | 19:30 | Noapara | 42 | 18:00 | Mithapukur | 27 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 15:00 | 402 | 19:00 | Kaliakoir | 397 | 0.25 | 389 | 0.77083
| Bheramara | 401 | 1:00 | 395 | 21:00 | Bhulta | 390 | 0.16667 | 383 | 0.41667
| Ashuganj(N) | 395 | 5:00 | 389 | 9:00 | Gopalganj | 406 | 0.625 | 387 | 0.75
| Payra | 408 | 22:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 13:00 | 230 | 1:00 | Hathazari | 237 | 19:00 | 229 | 1:00
| Ishurdi | 234 | 17:00 | 224 | 21:00 | Megnaghat | 234 | 6:00 | 228 | 13:00
| Ashuganj | 242 | 14:00 | 240 | 1:00 | Fenchuganj | 243 | 3:00 | 238 | 18:00
| Serajganj | 230 | 6:00 | 225 | 1:00 | Siddhirganj | 234 | 5:00 | 231 | 9:00
| Baghabari | 233 | 17:00 | 225 | 20:00 | Maniknagar | 232 | 5:00 | 228 | 12:00
| Barapukuria | 236 | 11:00 | 225 | 22:00 | Agargaon | 231 | 6:00 | 226 | 10:00
| Bogra | 226 | 17:00 | 214 | 21:00 | Barisal | 238 | 13:00 | 231 | 15:00
| Rajshahi | 227 | 17:00 | 220 | 21:00 | Bhola 225 MW | 242 | 6:00 | 237 | 1:00
| Khulna South | 227 | 17:00 | 214 | 23:00 | AKSML | 237 | 13:00 | 227 | 8:00
| Rampura | 231 | 23:00 | 229 | 8:00 | BSRM | 236 | 15:00 | 228 | 8:00
| Haripur | 232 | 22:00 | 229 | 9:00 | Bibiyana | 243 | 13:00 | 237 | 24:00
| Hasnabad | 232 | 7:00 | 224 | 1:00 | Bhulta | 235 | 15:00 | 230 | 10:00
| Shyampur | 230 | 22:00 | 225 | 9:00 | Ashuganj (S) | 239 | 14:00 | 236 | 9:00
| Aminbazar | 231 | 1:00 | 223 | 2:00 | Kaliakoir | 231 | 1:00 | 227 | 8:00
| Tongi | 232 | 23:00 | 222 | 7:00 | GPH | 237 | 19:00 | 228 | 8:00
| Comilla (N) | 234 | 15:00 | 230 | 3:00 | Jhenaidah | 227 | 17:00 | 216 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 22:00 | 133 | 3:00 | Madanhat | 139 | 0.75 | 134 | 0.25
| Munsiganj | 137 | 14:00 | 134 | 7:00 | Hathazari | 139 | 0.79167 | 135 | 0.20833
| Sonargaon | 134 | 15:00 | 132 | 9:00 | Khulshi | 136 | 0.91667 | 130 | 0.33333
| Shyampur | 138 | 15:00 | 135 | 9:00 | Halishahar | 138 | 0.91667 | 130 | 0.41667
| Bhulta | 131 | 4:00 | 130 | 1:00 | Baraulia | 137 | 0.79167 | 131 | 0.41667
| Madanganj | 136 | 1:00 | 134 | 5:00 | Sikalbaha | 139 | 0.75 | 132 | 0.33333
| Shitalakhya | 138 | 22:00 | 134 | 8:00 | Dohazari | 133 | 0.75 | 127 | 0.29167
| Rahim steal | 135 | 3:00 | 134 | 1:00 | Cox'sbazar | 118 | 0.041667 | 105 | 0.875
| Matuail | 135 | 22:00 | 133 | 3:00 | Chandraghona | 138 | 0.54167 | 133 | 0.41667
| Ghorasal | 140 | 13:00 | 138 | 1:00 | Kaptai | 137 | 0.041667 | 135 | 0.29167
| Narsinghdi | 133 | 6:00 | 125 | 1:00 | A. Khaer Stl. | 136 | 0.75 | 132 | 0.33333
| Haripur (SBU) | 135 | 1:00 | 135 | 1:00 | Bakulia | 137 | 0.8125 | 130 | 0.41667
| Sreenagar | 136 | 15:00 | 132 | 8:00 | Julda | 139 | 0.79167 | 133 | 0.29167
| Ullon | 135 | 1:00 | 131 | 9:00 | TK Chemical | 138 | 0.75 | 131 | 0.33333
| Hasnabad | 136 | 15:00 | 135 | 1:00 | Modern Steel | 137 | 0.77083 | 130 | 0.41667
| Magbazar | 135 | 23:00 | 130 | 9:00 | Shahmirpur | 138 | 0.83333 | 134 | 0.20833
| Maniknagar | 136 | 4:00 | 132 | 12:00 | Khagrachhari | 136 | 0.79167 | 131 | 0.41667
| Bangabhaban | 136 | 4:00 | 132 | 12:00 | Matarbari | 130 | 0.45833 | 120 | 0.041667
| Motijheel | 136 | 4:00 | 132 | 12:00 | Baroiar Hat | 136 | 0.54167 | 130 | 0.125
| Narinda | 136 | 4:00 | 132 | 12:00 | Rangamati | 136 | 11:00 | 132 | 10:00
| Kazla | 136 | 4:00 | 132 | 12:00 | Agrabad | 137 | 22:00 | 130 | 8:00
| Dhanmondi | 136 | 4:00 | 131 | 11:00 | Goalpara S/S | 136 | 17:00 | 128 | 0.95833
| Lalbag | 136 | 15:00 | 132 | 10:00 | Khulna Central S/S | 135 | 17:00 | 127 | 0.95833
| Madartek | 136 | 4:00 | 130 | 10:00 | Noapara | 133 | 9:00 | 126 | 0.83333
| Dhaka University | 135 | 1:00 | 130 | 11:00 | Jessore | 133 | 17:00 | 124 | 0.83333
| Aftabnagar | 136 | 3:00 | 131 | 9:00 | Benapol | 133 | 0.375 | 123 | 0.83333
| Fatullah | 139 | 22:00 | 134 | 10:00 | Jhenida(Old) | 135 | 17:00 | 126 | 0.83333
| Nawabganj | 136 | 15:00 | 132 | 12:00 | Bottail | 135 | 0.70833 | 129 | 0.83333
| Keraniganj | 137 | 15:00 | 132 | 10:00 | G.K Project | 139 | 0.70833 | 135 | 0.041667
| Mirpur | 133 | 1:00 | 128 | 11:00 | Faridpur | 134 | 0.70833 | 129 | 0.041667
| Kalyanpur | 133 | 0:00 | 130 | 8:00 | Rajbari | 133 | 0.5 | 129 | 0.041667
| Gulshan | 134 | 1:00 | 130 | 9:00 | Madaripur | 137 | 0.54167 | 132 | 0.125
| Uttara | 133 | 4:00 | 129 | 9:00 | Shariyatpur S/S | 137 | 17:00 | 131 | 0.875
| Uttara New | 134 | 4:00 | 129 | 8:00 | Gopalganj | 142 | 0.20833 | 133 | 0.75
| Kamrangirchar | 136 | 15:00 | 131 | 12:00 | Bagerhat | 133 | 17:00 | 123 | 0.95833
| Savar | 136 | 4:00 | 130 | 6:00 | Mongla | 132 | 17:00 | 122 | 0.95833
| Bhasantec | 137 | 4:00 | 132 | 12:00 | Satkhira | 133 | 11:00 | 122 | 23:00
| Agargaon | 138 | 3:00 | 135 | 8:00 | Gallamari | 136 | 0.25 | 126 | 18:00
| Satmosjid | 137 | 2:00 | 132 | 12:00 | Magura | 135 | 17:00 | 125 | 0.8125
| Tongi | 140 | 1:00 | 134 | 7:00 | Narail | 132 | 0.41667 | 122 | 0.83333
| Kabirpur | 136 | 5.00 | 129 | 19:30 | Chuadanga | 130 | 17:00 | 118 | 0.91667
| Basundhara | 137 | 18:30 | 133 | 8:00 | Barisal(N) | 138 | 19:00 | 131 | 0.041667
| Manikganj | 140 | 3:00 | 134 | 18:00 | Barisal (S) | 136 | 4:00 | 131 | 14:00
| Joydevpur | 137 | 19:00 | 135 | 8:00 | Patuakhali(S) | 136 | 0.79167 | 127 | 0.58333
| New Tongi | 139 | 1:00 | 134 | 8:00 | Bhandaria | 135 | 0.29167 | 125 | 0.875
| Kodda | 138 | 1:00 | 128 | 8:00 | Borguna | 136 | 0.75 | 129 | 0.041667
| Dhamrai | 139 | 16:00 | 135 | 18:30 | Jhenaidah(230kV S/S) | 135 | 17:00 | 128 | 19:00
| Rajendrapur | 137 | 1:00 | 128 | 13:00 | Ishurdi | 137 | 17:00 | 132 | 19:30
| Valuka | 124 | 6:00 | 110 | 19:30 | Ruppur Paromanobik | 135 | 12:00 | 132 | 1:00
| Tangail | 134 | 5:00 | 122 | 23:00 | Natore | 135 | 17:00 | 129 | 1:00
| Mymensing | 128 | 6:00 | 114 | 19:00 | Bogra | 136 | 17:00 | 128 | 1:00
| Kishorganj | 130 | 6:00 | 118 | 19:30 | Noagaon | 132 | 17:00 | 121 | 21:00
| Netrokona | 124 | 6:00 | 109 | 19:00 | Rajshahi | 134 | 17:00 | 129 | 2:00
| Jamalpur | 139 | 9:00 | 122 | 23:00 | Rajshahi New | 135 | 17:00 | 129 | 2:00
| Sherpur | 137 | 8:00 | 120 | 0:00 | C.Nawabganj | 132 | 17:00 | 127 | 13:00
| Srimongal | 138 | 8:00 | 130 | 18:30 | Amnura | 134 | 18:00 | 127 | 5:00
| Shahjibazar | 136 | 7:00 | 129 | 20:00 | Pabna | 135 | 17:00 | 129 | 19:30
| Fenchuganj | 136 | 8:00 | 129 | 24:00 | Shahjadpur | 140 | 5:00 | 135 | 18:00
| Khulawara | 135 | 7:00 | 128 | 18:00 | Serajganj | 134 | 17:00 | 127 | 19:30
| Sylhet | 129 | 8:00 | 122 | 18:00 | Niyamatpur | 130 | 17:00 | 118 | 19:30
| Chatak | 128 | 6:00 | 120 | 18:00 | Joypurhat | 131 | 17:00 | 120 | 20:00
| Sunamganj | 126 | 7:00 | 115 | 22:00 | Sherpur(Bogura) | 135 | 17:00 | 128 | 20:00
| Biani Bazar | 128 | 7:00 | 119 | 18:00 | Mohastangor | 134 | 17:00 | 125 | 19:30
| Comilla(s) | 128 | 5:00 | 124 | 18:00 | Bangura | 135 | 6:00 | 130 | 19:30
| Comilla(n) | 140 | 20:00 | 136 | 1:00 | Rangpur | 130 | 14:00 | 119 | 21:00
| Chandpur | 140 | 17:00 | 136 | 1:00 | Lalmonirhat | 131 | 15:00 | 120 | 18:00
| Feni | 137 | 17:00 | 130 | 6:00 | Saidpur | 132 | 5:00 | 120 | 21:00
| Chowmuhani | 135 | 19:00 | 128 | 3:00 | Purbasadipur | 129 | 17:00 | 114 | 20:00
| Ashuganj | 140 | 8:00 | 133 | 20:00 | Thakurgaon | 132 | 11:00 | 113 | 18:00
| Daudkandi | 139 | 20:00 | 132 | 10:00 | Palashbari | 132 | 17:00 | 122 | 18:30
| B.Baria | 135 | 7:00 | 126 | 19:30 | Barapukuria | 136 | 11:00 | 126 | 21:00
| Ramganj | 137 | 17:00 | 131 | 23:00 | Panchagar | 134 | 0.45833 | 111 | 0.75
| Chaddagram | 138 | 19:00 | 132 | 5:00 | Joldhaka | 129 | 0.25 | 113 | 0.8125
| PHP | 137 | 17:00 | 129 | 2:00 | Kurigram | 133 | 0.25 | 118 | 0.875
| Kochua | 137 | 19:00 | 134 | 3:00 | Mithapukur | 134 | 0.70833 | 123 | 0.875
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-10-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 490 | 9085 | 3531 | 12616 |  |  |  | QF-LDC-11
0:30 | 431 | 8743 | 3439.5 | 12182.5 | Date: | 2021-10-07
1:00 | 372 | 8401 | 3348 | 11749
1:30 | 352 | 8171.5 | 3301.5 | 11473
2:00 | 332 | 7942 | 3255 | 11197
2:30 | 322 | 7874 | 3184.5 | 11058.5 | [5 empty] | Gen. at Eve. Peak | 12972 | 12972 MW (19:00 )
3:00 | 312 | 7806 | 3114 | 10920 | [6 empty] | 19:00
3:30 | 324 | 7686 | 3024 | 10710 | [5 empty] | Gen. at Day Peak | 11291 | 11291 MW (12:00 )
4:00 | 336 | 7566 | 2934 | 10500 | [6 empty] | 12:00
4:30 | 348 | 7465.5 | 2877.5 | 10343 | [5 empty] | Highest Generation | 12972
5:00 | 360 | 7365 | 2821 | 10186 | [6 empty] | 19:00
5:30 | 227 | 7149 | 2846 | 9995
6:00 | 94 | 6933 | 2871 | 9804
6:30 | 105 | 6713.5 | 2810 | 9523.5
7:00 | 116 | 6494 | 2749 | 9243
7:30 | 114 | 6598 | 2745.5 | 9343.5
8:00 | 112 | 6702 | 2742 | 9444
8:30 | 68 | 6818 | 2760 | 9578
9:00 | 24 | 6934 | 2778 | 9712
9:30 | 37 | 7210 | 2829 | 10039
10:00 | 50 | 7486 | 2880 | 10366
10:30 | 51 | 7704.5 | 2902.5 | 10607
11:00 | 52 | 7923 | 2925 | 10848
11:30 | 61 | 8105.5 | 2964 | 11069.5
12:00 | 70 | 8288 | 3003 | 11291
12:30 | 145 | 8373.5 | 3024.5 | 11398
13:00 | 220 | 8459 | 3046 | 11505
13:30 | 200 | 8421.5 | 3047 | 11468.5
14:00 | 180 | 8384 | 3048 | 11432
14:30 | 220 | 8554.5 | 3050.5 | 11605
15:00 | 260 | 8725 | 3053 | 11778
15:30 | 150 | 8546 | 3072.5 | 11618.5
16:00 | 40 | 8367 | 3092 | 11459
16:30 | 28 | 8162.5 | 2967.5 | 11130
17:00 | 16 | 7958 | 2843 | 10801
17:30 | 93 | 8565.5 | 3069 | 11634.5
18:00 | 170 | 9173 | 3295 | 12468
18:30 | 245 | 9178 | 3542 | 12720
19:00 | 320 | 9183 | 3789 | 12972
19:30 | 434 | 9306 | 3619 | 12925
20:00 | 446 | 9257 | 3653 | 12910 |  |  |  | Executive Engineer
20:30 | 534 | 9320 | 3615 | 12935 |  |  |  | Network Operation Division
21:00 | 622 | 9383 | 3577 | 12960
21:30 | 567 | 9329.5 | 3589 | 12918.5
22:00 | 512 | 9276 | 3601 | 12877 |  |  |  |  | Page 6 of 7
22:30 | 535 | 9231 | 3571 | 12802
23:00 | 558 | 9186 | 3541 | 12727
23:30 | 524 | 9135.5 | 3536 | 12671.5
24:00 | 490 | 9085 | 3531 | 12616
12972 MW (19:00 )
11291 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-07 |  | Energy |  | 275098725
[13 empty] | 2021-10-07 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4032 | 709 | 2170 | 390 | 3822 | 669 | 160 | 0 | 544 | 120 | 0 | 0
0:30 | 4037.5 | 710 | 2114.5 | 195 | 3719.5 | 654 | 160.5 | 108.5 | 359 | 124 | 0 | 0 | Date: | 2021-10-07
1:00 | 4043 | 711 | 2059 | 0 | 3617 | 639 | 161 | 217 | 174 | 128 | 0 | 0
1:30 | 4039.5 | 711 | 2089.5 | 0 | 3373.5 | 624 | 158.5 | 217 | 136 | 124 | 0 | 0 | [8 empty] | Total Energy | 275.0987 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 4036 | 711 | 2120 | 0 | 3130 | 609 | 156 | 217 | 98 | 120 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4034.5 | 711 | 2130 | 0 | 2991 | 600 | 156 | 217 | 98 | 121 | 0 | 0 | [8 empty] | Energy Requirement | 275.0987
3:00 | 4033 | 711 | 2140 | 0 | 2852 | 591 | 156 | 217 | 98 | 122 | 0 | 0
3:30 | 4037 | 711 | 2134.5 | 0 | 2693 | 591 | 156 | 168.5 | 98 | 121 | 0 | 0 | [6 empty] | Shortage
4:00 | 4041 | 711 | 2129 | 0 | 2534 | 591 | 156 | 120 | 98 | 120 | 0 | 0
4:30 | 4053 | 710.5 | 2154.5 | 0 | 2392.5 | 581 | 155.5 | 80 | 98 | 118 | 0 | 0
5:00 | 4065 | 710 | 2180 | 0 | 2251 | 571 | 155 | 40 | 98 | 116 | 0 | 0
5:30 | 4080 | 710 | 2194.5 | 0 | 2069 | 555 | 155 | 40 | 81 | 110 | 0.5 | 0
6:00 | 4095 | 710 | 2209 | 0 | 1887 | 539 | 155 | 40 | 64 | 104 | 1 | 0
6:30 | 4087.5 | 710.5 | 2171.5 | 0 | 1689 | 520 | 155.5 | 40 | 40 | 103 | 6.5 | 0 |  |  |  |  | Coal
7:00 | 4080 | 711 | 2134 | 0 | 1491 | 501 | 156 | 40 | 16 | 102 | 12 | 0
7:30 | 4137.5 | 711 | 2115.5 | 0 | 1552 | 490.5 | 156.5 | 40 | 16 | 101 | 23.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4195 | 711 | 2097 | 0 | 1613 | 480 | 157 | 40 | 16 | 100 | 35 | 0
8:30 | 4113.5 | 711 | 2076 | 0 | 1851.5 | 470 | 158 | 40 | 16 | 102 | 40 | 0
9:00 | 4032 | 711 | 2055 | 0 | 2090 | 460 | 159 | 40 | 16 | 104 | 45 | 0
9:30 | 4061.5 | 710.5 | 2026.5 | 0 | 2396.5 | 460 | 160 | 40 | 16 | 106 | 62 | 0
10:00 | 4091 | 710 | 1998 | 0 | 2703 | 460 | 161 | 40 | 16 | 108 | 79 | 0
10:30 | 4030 | 710 | 1980 | 0 | 2960.5 | 464.5 | 161 | 60 | 50.5 | 109 | 81.5 | 0
11:00 | 3969 | 710 | 1962 | 0 | 3218 | 469 | 161 | 80 | 85 | 110 | 84 | 0
11:30 | 3969.5 | 710 | 1954 | 20.5 | 3356.5 | 475.5 | 162 | 115 | 102 | 114 | 90.5 | 0
12:00 | 3970 | 710 | 1946 | 41 | 3495 | 482 | 163 | 150 | 119 | 118 | 97 | 0
12:30 | 3934 | 710.5 | 1953.5 | 127.5 | 3522 | 507 | 163 | 150 | 119 | 119 | 92.5 | 0
13:00 | 3898 | 711 | 1961 | 214 | 3549 | 532 | 163 | 150 | 119 | 120 | 88 | 0
13:30 | 3898 | 711 | 1961 | 214 | 3549 | 532 | 163 | 150 | 119 | 120 | 88 | 0
14:00 | 3898 | 711 | 1961 | 214 | 3549 | 532 | 163 | 150 | 119 | 120 | 88 | 0
14:30 | 3904 | 710 | 1966.5 | 361 | 3519 | 540.5 | 160.5 | 150 | 138.5 | 124 | 67.5 | 0
15:00 | 3910 | 709 | 1972 | 508 | 3489 | 549 | 158 | 150 | 158 | 128 | 47 | 0
15:30 | 3929.5 | 708.5 | 1990 | 285.5 | 3501 | 549.5 | 158 | 150 | 180 | 125 | 41.5 | 0
16:00 | 3949 | 708 | 2008 | 63 | 3513 | 550 | 158 | 150 | 202 | 122 | 36 | 0
16:30 | 3900.5 | 708.5 | 1908 | 31.5 | 3388 | 538.5 | 158 | 150 | 205 | 120 | 22 | 0
17:00 | 3852 | 709 | 1808 | 0 | 3263 | 527 | 158 | 150 | 208 | 118 | 8 | 0
17:30 | 3917.5 | 709 | 1932.5 | 346 | 3383 | 533 | 158 | 150 | 372.5 | 129 | 4 | 0
18:00 | 3983 | 709 | 2057 | 692 | 3503 | 539 | 158 | 150 | 537 | 140 | 0 | 0
18:30 | 3979 | 708.5 | 2063 | 728.5 | 3675 | 572.5 | 158.5 | 150 | 555 | 130 | 0 | 0
19:00 | 3975 | 708 | 2069 | 765 | 3847 | 606 | 159 | 150 | 573 | 120 | 0 | 0
19:30 | 4013 | 708 | 2130 | 563 | 3901 | 599 | 159 | 150 | 580 | 122 | 0 | 0
20:00 | 4015 | 708 | 2114 | 550 | 3883 | 619 | 160 | 150 | 589 | 122 | 0 | 0
20:30 | 4039.5 | 708 | 2125 | 562.5 | 3869.5 | 618 | 159.5 | 150 | 580 | 123 | 0 | 0
21:00 | 4064 | 708 | 2136 | 575 | 3856 | 617 | 159 | 150 | 571 | 124 | 0 | 0
21:30 | 4027.5 | 708 | 2129.5 | 586 | 3869 | 622.5 | 159 | 125 | 568 | 124 | 0 | 0
22:00 | 3991 | 708 | 2123 | 597 | 3882 | 628 | 159 | 100 | 565 | 124 | 0 | 0
22:30 | 3995 | 708 | 2143 | 536 | 3876.5 | 648 | 159.5 | 50 | 563 | 123 | 0 | 0
23:00 | 3999 | 708 | 2163 | 475 | 3871 | 668 | 160 | 0 | 561 | 122 | 0 | 0
23:30 | 4015.5 | 708.5 | 2166.5 | 432.5 | 3846.5 | 668.5 | 160 | 0 | 552.5 | 121 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.6° C
24:00 | 4032 | 709 | 2170 | 390 | 3822 | 669 | 160 | 0 | 544 | 120 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 81 | 81 | 81 | 80 | 80 | 81 | 82 | 84 | 86 | 86 | 88 | 88 | 85 | 83 | 83 | 83 | 83 |  | 84 | 84 | 85 | 84 | 84 | 85 | 85 | 1917382
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1824000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 6 | 17 | 17 | 22 |  |  | 2 | 12 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 267033
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 |  |  |  |  | 9 | 19 | 17 | 14 | 8 | 2 | [9 empty] | 95175
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 26 | [16 empty] | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 706231
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 34 | 34 | 34 | 73 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 68 | 80 |  | 97 | 105 | 105 | 105 | 105 | 105 | 105 | 2340135
| Daudkandi 200 MW PP (B.Trac) | [11 empty] | 20 | 124 | 100 | 190 | 13 |  | 180 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 1658880
14 | Titas 50 MW Peaking PP | [13 empty] | 36 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 492148
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 337 | 337 | 337 | 337 | 337 | 338 | 338 | 338 | 338 | 336 | 340 | 333 | 335 | 333 | 334 | 335 | 335 | 328 |  | 336 | 333 | 335 | 331 | 336 | 335 | 334 | 8092031
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 245 | 95 | 45 | 45 | 45 | 50 | 182 | 275 | 275 | 293 | 300 | 295 | 298 | 298 | 300 |  | 300 | 300 | 300 | 300 | 300 | 293 | 298 | 5863743
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7474482
26
28 | Ashuganj TPP Unit- 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1720164
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 20 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 20 | 20 | 23 | 23 | 22 | 22 | 22 | 415152
33 | Ashuganj 225 MW CCPP | 141 | 138 | 139 | 139 | 139 | 139 | 140 | 140 | 131 | 139 | 140 | 138 | 139 | 137 | 141 | 137 | 140 | 135 |  | 141 | 140 | 139 | 121 | 130 | 129 | 132 | 3338000
34 | Ashuganj 450 MW CCPP(South) | 285 | 270 | 270 | 270 | 270 | 270 | 275 | 300 | 295 | 330 | 300 | 320 | 300 | 305 | 305 | 325 | 265 | 340 |  | 300 | 295 | 295 | 330 | 265 | 270 | 285 | 7210000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 360 | 260 | 290 | 260 | 280 | 260 | 260 | 305 | 330 | 285 | 330 |  | 280 | 280 | 280 | 305 | 260 | 260 | 275 | 7146900
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 57 | 52 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 51 | 55 | 56 | 56 | 55 | 55 | 56 | 1127040
36 | Chandpur 150 MW CCPP | 90 | 91 | 92 | 91 | 92 | 93 | 94 | 91 | 91 | 92 | 90 | 93 | 93 | 92 | 92 | 92 | 90 | 92 |  | 90 | 92 | 92 | 92 | 92 | 92 | 92 | 2183430
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 399 | 400 | 398 | 397 | 397 | 397 | 398 | 400 | 389 | 339 | 334 | 324 | 324 | 323 | 323 | 323 | 323 |  | 354 | 400 | 400 | 395 | 395 | 394 | 395 | 9009770
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 280 | 280 | 280 | 280 | 280 | 280 | 6250550
41 | Haripur 360MW CCPP(HPL) | 210 | 241 | 262 | 292 | 312 | 318 | 266 | 212 | 184 | 167 | 153 | 172 | 168 | 165 | 165 | 165 | 165 | 165 |  | 161 | 161 | 161 | 162 | 172 | 189 | 198 | 4842000
42 | RPCL 210MW CCPP | 145 | 154 | 157 | 160 | 160 | 160 | 160 | 158 | 152 | 148 | 148 | 132 | 119 | 106 | 106 | 105 | 105 | 143 |  | 143 | 137 | 137 | 130 | 135 | 132 | 132 | 3216400
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 21 | 21 | 45 | 41 | 43 | 26 | 23 | 10 | 14 | 3 | [9 empty] | 258050
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 44 |  | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 1031000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1014600
46 | Shajibazar 330 MW CCPP | 164 | 162 | 161 | 160 | 160 | 162 | 164 | 165 | 159 | 158 | 160 | 159 | 160 | 156 | 159 | 158 | 160 | 159 |  | 162 | 160 | 159 | 160 | 161 | 160 | 162 | 3692000
47 | Shahjibazar GTPP Unit- 8 & 9 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 56 | 56 | 55 | 56 | 55 | 56 | 55 | 56 | 55 | 56 | 55 |  | 56 | 56 | 56 | 61 | 61 | 61 | 61 | 1312224
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 40 | 60 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1854720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 389000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 190260
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 231936
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 44 | 42 | 42 | 42 | 42 | 39 | 39 | 46 | 46 | 47 | 47 | 47 | 47 | 47 | 47 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1074600
56 | Shahjahanulla 25 MW PP | 21 | 21 | 21 | 18 | 18 | 18 | 18 |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 485376
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 290 | 270 | 280 | 270 | 270 | 290 | 310 | 290 | 300 | 290 | 300 | 290 | 300 | 290 | 285 | 305 |  | 285 | 300 | 290 | 305 | 300 | 305 | 300 | 7172500
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 321 | 320 | 320 | 320 | 320 | 320 | 320 | 7675900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 50 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1202348
59 | Tangail Palli Power Gen 22 MW | [10 empty] | 1 | 21 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 306720
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 |  |  | 14 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 396864
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432936
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 484560
63 | Impoprt (Tripura) | 128 | 120 | 122 | 120 | 116 | 104 | 102 | 100 | 104 | 108 | 110 | 118 | 120 | 112 | 128 | 122 | 118 | 140 |  | 120 | 122 | 122 | 124 | 124 | 122 | 120 | 2853120
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 30 | 39 | 39 | 36 | 8 | 2 | 5 | 5 | 2 | 2 | 6 | 5 | 6 | 8 | 10 |  | 15 | 15 | 20 | 20 | 27 | 31 | 32 | 494880
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 450792
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 225900
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 25 | 25 | 25 | 25 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 30 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 701200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 12 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 519840
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 16 | 29 | 29 | 26 | 29 | 29 | 29 | 29 | 17 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 665280
71 | Maona 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 807800
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 100 | [8 empty] | 17 | 98 | 98 | 98 | 62 | 80 | 63 | 80 | 100 |  | 100 | 100 | 68 | 80 | 100 | 80 | 80 | 1341780
| Chowmuhani 113 MW | 50 | 51 | 48 | 48 | 49 | 47 | 48 | 48 | 47 | 48 | 48 | 47 | 48 | 47 | 48 | 48 | 56 | 92 |  | 96 | 96 | 94 | 96 | 95 | 96 | 67 | 1477560
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 141 | 14 | 54 | 98 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3584160
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 25 | [7 empty] | 10 | 41 | 50 | 51 | 50 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 764640
79 | Kodda 150MW PP | 115 | 98 | 98 | 98 | 98 | 64 | 16 | 16 | 16 | 16 | 82 | 115 | 115 | 98 | 98 | 98 | 64 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2318880
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | [7 empty] | 16 | 52 | 52 | 52 | 52 | 43 | 48 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 860270
| Gazipur 100 MW PP | 105 | [9 empty] | 44 | 90 | 90 | 70 | 70 | 70 | 70 | 90 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1435200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 4 | 2 | 3 | 1 | 0 | [9 empty] | 32150
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 41 | 36 | 36 | 36 | 36 | 36 | 48 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1197309
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 51 | 34 | 34 | 34 | 47 | 90 | 93 | 98 | 110 | 92 | 94 | 110 | 110 | 94 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2310026
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 51 | [9 empty] | 36 | 51 | 51 | 51 | 51 | 50 | 51 | 50 |  | 51 | 51 | 51 | 50 | 51 | 51 | 50 | 782995
86 | Meghnaghat CCPP ( Summit) | 265 | 265 | 265 | 255 | 265 | 275 | 270 | 280 | 265 | 285 | 260 | 280 | 270 | 275 | 250 | 290 | 260 | 300 |  | 295 | 300 | 285 | 290 | 260 | 280 | 280 | 6609280
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 93 | 93 | 93 | 93 | 66 | 55 | 55 | 55 | 72 | 92 | 93 | 93 | 93 | 93 | 93 | 92 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 102 | 104 | 2107200
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 50 | [6 empty] | 10 | 10 | 92 | 92 | 92 | 92 | 80 | 80 | 40 | 80 |  | 80 | 100 | 100 | 100 | 100 | 100 | 92 | 1384920
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1171912
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 64 | 32 | [5 empty] | 24 | 58 | 94 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1692576
95 | Patenga 50MW PP (Baraka) | 30 | 25 | 25 | [5 empty] | 1 | 20 | 37 | 42 | 46 | 46 | 46 | 46 | 30 | 28 |  | 46 | 46 | 47 | 46 | 33 | 33 | 33 | 708480
96 | Chattogram 108 MW PP (ECPV) | 59 | [9 empty] | 26 | 88 | 82 | 89 | 88 | 88 | 89 | 88 |  | 88 | 88 | 89 | 89 | 89 | 89 | 89 | 1236480
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 45 | 45 | 45 | 30 | 30 | 30 | 30 | 32 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1054585
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1223489
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 130 | 110 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3475718
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | [9 empty] | 10300
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1303200
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 110 |  |  | 300 |  | 110 | 103 | 100 | 160 | 157 | 85 | 0 | 897301
105 | Bramhangoan 100 MW PP (Aggreko) | [13 empty] | 40 | 100 |  |  | 100 |  | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 638145
106 | Mymensingh 200 MW PP (United) | 192 | 192 | 192 | 192 | 192 | 150 | 98 | 148 | 190 | 180 | 180 | 180 | 180 | 188 | 188 | 186 | 194 | 185 |  | 199 | 200 | 200 | 200 | 200 | 200 | 192 | 4392000
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 21 | 90 | 70 | 98 | 50 |  | 97 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 974545
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 120 | 88 | 86 | 88 | 86 | 88 | 135 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 123 | 114 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3201840
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2316480
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 120 | 120 | 120 | 120 | 120 | 123 | 169 | 174 | 174 | 177 | 192 | 200 | 200 | 155 | 164 |  | 186 | 200 | 200 | 200 | 200 | 200 | 200 | 4160640
117 | Ashuganj 150MW PP (Midland) | 137 | 127 | 127 | 128 | 138 | 137 | 138 | 128 | 137 | 128 | 127 | 125 | 130 | 125 | 123 | 127 | 125 | 125 |  | 128 | 131 | 130 | 130 | 130 | 137 | 132 | 3131345
118 | Bibiyana-III 400 MW CCPP | 323 | 323 | 322 | 322 | 322 | 322 | 322 | 322 | 323 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 |  | 322 | 322 | 322 | 322 | 322 | 322 | 323 | 7697000
| Jamalpur 115 MW PP (United) | 97 | 97 | 97 | 97 | 98 | 98 | 98 | 98 | 98 | 97 | 97 | 85 | 86 | 86 | 86 | 86 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2407200
| Anwara 300 MW PP (United) | 305 | 304 | 305 | 305 | 303 | 268 | 215 | 215 | 285 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 |  | 305 | 303 | 305 | 304 | 304 | 303 | 304 | 7083164
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 100 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2355840
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 53 |  |  |  |  | 21 | 102 | 108 | 108 | 108 | 108 | 72 | 86 |  | 116 | 116 | 116 | 116 | 116 | 116 | 110 | 2110145
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 12 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 431280
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 10 | 16 | 22 | 31 | 31 | 30 | 26 | 19 | 10 | 2 | [9 empty] | 201632
120 | Eastern Zone Total | 8401 | 7942 | 7806 | 7566 | 7365 | 6933 | 6494 | 6702 | 6934 | 7486 | 7923 | 8288 | 8459 | 8384 | 8725 | 8367 | 7958 | 9173 |  | 9183 | 9306 | 9257 | 9383 | 9276 | 9186 | 9085 | 197633973
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [10 empty] | 3 | 4 | 4 | 6 | 10 | 22 | 27 | 23 |  | 29 | 30 | 29 | 26 | 26 | 22 | 22 | 228000
| Khulna 225 MW CCPP | 217 | 217 | 217 | 120 | 40 | 40 | 40 | 40 | 40 | 40 | 80 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 100 |  | 0 | 2781120
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 70 | 70 | 53 | 53 | 53 | 58 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2274240
130
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | [14 empty] | 1 |  | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 321600
133 | Bhola Nutan Biddut BD LTD (GAS) | 208 | 227 | 220 | 220 | 225 | 225 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 203 | 217 | 138 | 218 |  | 215 | 220 | 221 | 222 | 222 | 222 | 223 | 5184409
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 11 | 11 | 407376
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 85 | 85 | 85 | 84 | 85 | 86 | 82 |  | 85 | 86 | 86 | 86 | 86 | 87 | 87 | 2072708
140 | Bhola 33 MW PP (Venture) | 34 | 35 | 34 | 32 | 29 | 27 | 22 | 21 | 21 | 19 | 22 |  |  | 27 | 26 | 25 | 23 | 32 |  | 33 | 34 | 34 | 34 | 35 | 35 | 35 | 630917
141 | Noapara 100 MW PP (Bangla Trac) | [14 empty] | 10 |  |  | 15 |  | 100 | 50 | 50 | 15 | 40 | 40 | 40 | 359040
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 30 | 32 | 32 |  |  |  | 0 | 50400
146 | Bheramara HVDC | 711 | 711 | 711 | 711 | 710 | 710 | 711 | 711 | 711 | 710 | 710 | 710 | 711 | 708 | 709 | 708 | 709 | 709 |  | 708 | 708 | 708 | 708 | 708 | 708 | 709 | 17153454
147 | Bheramara 410 MW CCPP | 220 | 225 | 230 | 240 | 245 | 245 | 245 | 235 | 225 | 220 | 210 | 205 | 205 | 200 | 190 | 190 | 195 | 200 |  | 200 | 205 | 205 | 210 | 210 | 210 | 210 | 5321664
148 | Payra 1320 MW | 560 | 530 | 510 | 510 | 490 | 460 | 420 | 400 | 380 | 380 | 390 | 400 | 450 | 450 | 470 | 470 | 450 | 460 |  | 530 | 520 | 540 | 540 | 550 | 590 | 590 | 12515200
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 81 | 81 | 81 | 79 | 81 | 80 | 80 | 80 | 79 | 82 | 82 | 81 | 79 | 80 | 77 | 79 |  | 76 | 79 | 79 | 77 | 78 | 78 | 79 | 1876800
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 27 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 411264
Sirajgonj 6.55 MW Solar
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 124 | 124 | 124 | 126 | 135 | 139 | 139 | 141 | 133 | 129 | 126 | 126 | 123 | 123 | 123 | 123 | 123 | 123 |  | 125 | 125 | 124 | 125 | 127 | 128 | 128 | 3264945
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 152 | 149 | 145 | 145 | 155 | 194 | 195 | 193 | 182 | 175 | 166 | 159 | 146 | 134 | 128 | 128 | 129 | 129 |  | 130 | 132 | 132 | 142 | 159 | 167 | 163 | 3951464
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 363 | 363 | 360 | 362 | 364 | 390 | 390 | 414 | 417 | 390 | 373 | 373 | 371 | 355 | 355 | 347 | 300 | 370 |  | 372 | 373 | 375 | 375 | 380 | 380 | 380 | 8934036
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 5 | 17 | 30 |  | 30 | 31 | 41 | 30 | 30 | 30 | 25 | 225047
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239652
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  | 27 | 27 | 27 |  |  |  |  | 93800
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 24 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 270452
167 | Katakhali 50 MW Peaking PP | [17 empty] | 24 |  | 35 | 40 | 40 | 36 | 30 | 30 | 26 | 185817
168 | Santahar 50 MW Peaking PP | 33 | [16 empty] | 14 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 218463
169 | Natore 52 MW PP (Rajlanka) | 52 | [9 empty] | 3 | 30 | 33 | 43 | 52 | 47 | 16 | 16 |  | 16 | 18 | 31 | 52 | 52 | 52 | 52 | 561120
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 606968
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 155 | 10 |  |  |  |  | 0 | 184209
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 70 | 70 | 35 | 35 | 50 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 85 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2454624
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 70 | 35 | 35 | 35 | 35 | 90 | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2316000
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 |  |  | 38 | 70 | 34 | 34 | 40 | 70 | 77 | 78 | 85 | 85 | 85 | 85 | 92 | 95 |  | 107 | 113 | 113 | 113 | 113 | 113 | 113 | 1827609
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 5 | 6 | 7 | 7 | 7 |  | 3 | 1 | [9 empty] | 40994
178
178