## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-17 | Sunday
|  |  | Date (day): | 2021-10-17 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13549.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14754 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-16 | 2021-10-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 255 | 250 | 250 |  | 115 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 383 | 380 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 322 | 280 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 255 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 6 | 50 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 0 | 200 | 200 | 210
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 240 | 0 | 0 | 335 |  | Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 53 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 280 | 298 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 20 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 25 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 131 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2564 | 3238 | 3428 | 3750 | 1103 | 870
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 150 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 157 | 161 | 160 | 160 | 70 |  | Low water level & #2 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 51 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 16 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 9 | 6 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 32 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 304 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 90 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 94 | 108 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1193 | 1509 | 1475 | 1545 | 135 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 110 | 110 | 110 | 25 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 208 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 280 | 320 | 350 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 300 | 335 | 350 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 50 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 112 | 125 | 135 | 137 |  | 13 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 48 | 50 | 50 |  | 113 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 160 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 136 | 154 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 40 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 18 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 30 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 80 | 80 | 80 |  | 34 | Engine problem
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 48 | 87 | 95 | 96 |  | 17 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1736 | 1963 | 2037 | 2311 | 457 | 233
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 191 | 170 | 200 | 202 | 0
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 3 | 8 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 163 | 190 | 190 | 190 |  | 10
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 38 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 56 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 476 | 525 | 607.6 | 558 | 0 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 40 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 159 | 160 | 160 |  | 170 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 44 | 47 | 47 |  | 4 | Engine problem
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 59 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 83 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 24 | 24 |  | 1
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 270 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 321 | 321 | 320 | 320 | 80 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1790 | 1777 | 1863 | 1868 | 143 | 350
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 704 | 705 | 718 | 718
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 11 | 0 | 33 |  | 21 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 215 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 360 | 400 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 25 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 15 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1219 | 1411 | 1498 | 1721 | 0 | 90
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 32 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 82 | 12 | 17 | 17 | 78 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 480 | 580 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 80 | 220 | 107 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 665 | 944 | 954 | 1217 | 78 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 30 | 35 |  | 36 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 28 | 28 | 50 |  | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 121 | 113 | 144 | 144
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 176 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | under maint
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 412 | 372 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 20 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 92 | 90 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 111 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 974 | 1273 | 1486 | 1591 | 220 | 68
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 76 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 198 | 189 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 10815 | 12829 | 13549.6 | 14754 | 2136 | 2824
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10363.9886 | 12294 | 12984.5493 | 14138.7229
| A. |  | 2021-10-16 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12829 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9068 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12829 | MW
| 3 | Day peak Generation : |  |  | 10815 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12294 | MW
| 4 | Evening peak Generation : |  |  | 12829 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 264.1314 | MKWHr | By Solar | 0.75732 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 150.8571 | MKWHr |  | By Oil: | 74.9972 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.0753 | MKWHr |  | By Hydro: | 2.1602 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2136 | MW | Dhaka | 4441 | 4441 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2824 | MW | Chittagong | 1315 | 1315 |  | 0 |  | 18:00 |  | 158
|  |  |  | Total = |  |  | 4960 | MW | Khulna | 1414 | 1414 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1192.6 | MMCFD |  |  | Rajshahi | 1319 | 1319 |  | 0 |  | 19:00 |  | 154
| 8 | Fuel Cost : | i) Gas : | Taka | 162234731.816 | ii) Oil : | Taka | 573598943.34 | Comilla | 1147 | 1147 |  | 0 |  | 19:30 |  | 156
|  |  | iii) Coal : |  | 69241895.89 | Total | Taka | 805075571.046 | Mymensingh | 1056 | 1056 |  | 0 |  | 20:00 |  | 156
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.794 | MKWHr. | Sylhet | 545 | 545 |  | 0 |  | 21:00 |  | 156
|  | ii) During Peak Demand : |  |  | -162 | MW (E to W) at | 19:00 | hrs | Barisal | 351 | 351 |  | 0 |  | 22:00 |  | 154
|  | iii) Maximum : |  |  | -162 | MW at | 19:00 | hrs | Rangpur | 706 | 706 |  | 0 |  | 23:00 |  | 150
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.5° C |  |  | Total | 12294 | 12294 |  | 0
| B. |  | 2021-10-17 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14754 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10900 | MW
| 4 | Reserve(Generation end) |  |  |  | 1154 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 280.0053 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9764 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0385 | MKWHr. | ii) HVDC Flow at Peak Time |  | 705 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2458 | MKWHr. | iii) Maximum HVDC Flow : |  | 714 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.97 |  | (b) Today: | 104.82 |  | (c) Rule Curve: |  | 107.5
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 340 | 331 |  | 0 | 250 | 250 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 24 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 20 | 0 | 36 | 18 | 42 | 100 | 0 | 0 | 260 | 280 | 213 | 26 | 48 | 26 | 53 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 25 | 21 | 130 | 203 | 8 | 21 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 56 | 81 | 0 | 219 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 191 | 0 | 88 | 0 | 90 | 120 | 125 | 321 | 78 | 50 | 68 | 0 | 305 | 54 | 68 | 17 | 47 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 25 | 33 | 21 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 144 | 0 | 168 | 0 | 82 | 0 | 160 | 0 | 375 | 17 | 0 | 113 | 0 | 56 | 0 | 0 | 113 | 470 | 0 | 0 | 54 | 0 |  | 7623 | 3220 | 10843 | 4351 | 706 | 2065 | 0 | 2621 | 549 | 160 | 120 | 141 | 130 | 0 | 0 | 104.99
2:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 340 | 332 |  | 0 | 250 | 280 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 19 | 18 | 42 | 100 | 0 | 0 | 265 | 290 | 214 | 26 | 50 | 26 | 53 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 21 | 128 | 206 | 8 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 56 | 81 | 0 | 219 | 18 | 0 | 9 | 275 | 24 | 11 | 0 | 95 | 0 | 0 | 190 | 0 | 86 | 0 | 90 | 120 | 125 | 321 | 78 | 35 | 68 | 0 | 305 | 54 | 51 | 17 | 49 | 100 | 320 | 104 | 0 | 162 | 90 | 0 | 17 | 0 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 25 | 32 | 21 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 144 | 0 | 177 | 0 | 82 | 0 | 142 | 0 | 410 | 17 | 0 | 113 | 0 | 56 | 0 | 0 | 113 | 470 | 38 | 0 | 54 | 0 |  | 7553 | 3235 | 10788 | 4372 | 706 | 2153 | 0 | 2523 | 549 | 160 | 120 | 77 | 128 | 0 | 0 | 104.99
3:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 340 | 333 |  | 0 | 250 | 300 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 42 | 100 | 0 | 0 | 260 | 280 | 214 | 26 | 50 | 26 | 53 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 21 | 126 | 207 | 8 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 161 | 56 | 81 | 0 | 219 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 190 | 0 | 67 | 0 | 90 | 120 | 130 | 321 | 78 | 35 | 51 | 0 | 305 | 54 | 51 | 6 | 49 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 703 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 170 | 0 | 82 | 0 | 156 | 0 | 407 | 17 | 0 | 113 | 0 | 56 | 0 | 0 | 113 | 470 | 32 | 0 | 54 | 0 |  | 7365 | 3128 | 10493 | 4366 | 703 | 2179 | 0 | 2289 | 550 | 160 | 120 | 0 | 126 | 0 | 0 | 104.98
4:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 340 | 331 |  | 0 | 250 | 270 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 42 | 100 | 0 | 0 | 260 | 280 | 213 | 26 | 51 | 26 | 53 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 21 | 124 | 209 | 8 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 56 | 81 | 0 | 219 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 52 | 0 | 90 | 120 | 135 | 321 | 78 | 35 | 51 | 0 | 251 | 40 | 51 | 0 | 48 | 100 | 320 | 69 | 0 | 144 | 53 | 0 | 17 | 0 |  | 703 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 78 | 0 | 0 | 0 | 0 | 144 | 0 | 170 | 0 | 82 | 0 | 160 | 0 | 408 | 17 | 0 | 113 | 0 | 56 | 0 | 0 | 113 | 470 | 109 | 0 | 0 | 0 |  | 7189 | 3154 | 10343 | 4371 | 703 | 2225 | 0 | 2092 | 548 | 160 | 120 | 0 | 124 | 0 | 0 | 104.98
5:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 191 | 332 |  | 0 | 250 | 250 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 42 | 100 | 0 | 0 | 260 | 280 | 215 | 26 | 52 | 26 | 53 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 21 | 122 | 212 | 8 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 56 | 81 | 0 | 219 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 76 | 0 | 0 | 192 | 0 | 50 | 0 | 90 | 120 | 130 | 321 | 78 | 35 | 51 | 0 | 250 | 54 | 51 | 0 | 49 | 100 | 320 | 54 | 0 | 144 | 53 | 0 | 17 | 0 |  | 703 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 160 | 0 | 82 | 0 | 161 | 0 | 365 | 17 | 0 | 113 | 0 | 56 | 0 | 0 | 113 | 490 | 106 | 0 | 35 | 0 |  | 7078 | 3121 | 10199 | 4189 | 703 | 2145 | 0 | 2190 | 570 | 160 | 120 | 0 | 122 | 0 | 0 | 104.97
6:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 315 |  | 0 | 250 | 250 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 42 | 100 | 0 | 0 | 260 | 280 | 215 | 26 | 49 | 26 | 54 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 21 | 114 | 212 | 8 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 162 | 57 | 81 | 0 | 205 | 18 | 0 | 9 | 260 | 24 | 11 | 0 | 90 | 0 | 0 | 193 | 0 | 50 | 1 | 70 | 100 | 135 | 321 | 38 | 35 | 34 | 0 | 196 | 35 | 51 | 0 | 48 | 70 | 320 | 53 | 0 | 108 | 53 | 0 | 17 | 0 |  | 704 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 159 | 0 | 82 | 0 | 130 | 0 | 340 | 17 | 0 | 35 | 0 | 63 | 0 | 0 | 35 | 480 | 108 | 0 | 17 | 0 |  | 6612 | 2894 | 9506 | 3955 | 704 | 2087 | 0 | 1805 | 560 | 160 | 120 | 0 | 114 | 1 | 0 | 104.97
7:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 272 |  | 0 | 250 | 270 | 0 | 0 | 48 | 240 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 36 | 100 | 0 | 0 | 270 | 275 | 181 | 26 | 51 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 18 | 106 | 207 | 8 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 162 | 57 | 81 | 0 | 178 | 18 | 0 | 9 | 270 | 24 | 11 | 0 | 90 | 0 | 0 | 150 | 0 | 50 | 6 | 40 | 68 | 100 | 321 | 38 | 17 | 34 | 1 | 140 | 35 | 51 | 0 | 49 | 40 | 320 | 53 | 12 | 108 | 35 | 0 | 17 | 3 |  | 704 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 158 | 0 | 84 | 0 | 70 | 0 | 310 | 0 | 0 | 35 | 0 | 100 | 0 | 1 | 35 | 450 | 108 | 0 | 0 | 0 |  | 6293 | 2775 | 9068 | 3856 | 704 | 2036 | 0 | 1532 | 530 | 161 | 120 | 0 | 106 | 23 | 0 | 104.96
8:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 272 |  | 0 | 250 | 285 | 0 | 0 | 55 | 240 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 29 | 33 | 25 | 0 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 6 | 100 | 0 | 0 | 300 | 295 | 181 | 26 | 50 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 14 | 110 | 205 | 8 | 22 | 1 | 43 | 42 | 47 | 0 | 130 | 161 | 62 | 81 | 0 | 179 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 90 | 0 | 0 | 150 | 0 | 50 | 0 | 40 | 68 | 100 | 321 | 38 | 17 | 34 | 2 | 139 | 35 | 51 | 0 | 49 | 40 | 320 | 53 | 26 | 108 | 35 | 0 | 17 | 8 |  | 703 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 144 | 0 | 166 | 0 | 83 | 0 | 0 | 0 | 343 | 0 | 0 | 35 | 0 | 75 | 0 | 0 | 35 | 440 | 107 | 0 | 0 | 0 |  | 6374 | 2708 | 9082 | 3844 | 703 | 2074 | 0 | 1513 | 519 | 162 | 120 | 0 | 110 | 37 | 0 | 104.96
9:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 327 |  | 0 | 250 | 290 | 0 | 0 | 55 | 240 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 25 | 25 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 4 | 100 | 0 | 0 | 270 | 310 | 183 | 26 | 50 | 23 | 53 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 0 | 118 | 205 | 8 | 22 | 2 | 44 | 42 | 47 | 0 | 163 | 159 | 60 | 81 | 0 | 179 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 90 | 0 | 0 | 150 | 0 | 85 | 0 | 90 | 68 | 110 | 321 | 38 | 17 | 34 | 4 | 175 | 35 | 51 | 0 | 48 | 100 | 320 | 53 | 39 | 108 | 35 | 0 | 17 | 23 |  | 704 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 130 | 0 | 196 | 0 | 81 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 0 | 70 | 0 | 4 | 35 | 440 | 106 | 0 | 0 | 0 |  | 6688 | 2777 | 9465 | 3830 | 704 | 2218 | 0 | 1723 | 518 | 162 | 120 | 0 | 118 | 72 | 0 | 104.95
10:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 331 |  | 0 | 250 | 295 | 0 | 0 | 55 | 240 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 25 | 25 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 7 | 100 | 0 | 0 | 345 | 285 | 188 | 26 | 50 | 23 | 53 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 0 | 122 | 202 | 8 | 22 | 2 | 44 | 42 | 44 | 0 | 163 | 157 | 60 | 84 | 0 | 220 | 18 | 0 | 9 | 320 | 16 | 11 | 0 | 90 | 0 | 0 | 150 | 0 | 113 | 5 | 90 | 68 | 115 | 321 | 38 | 17 | 38 | 4 | 295 | 35 | 51 | 0 | 47 | 100 | 320 | 57 | 50 | 131 | 45 | 0 | 17 | 27 |  | 703 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 123 | 0 | 200 | 0 | 82 | 0 | 0 | 0 | 414 | 0 | 0 | 42 | 0 | 70 | 0 | 6 | 55 | 440 | 106 | 0 | 0 | 0 |  | 7033 | 2822 | 9855 | 3916 | 703 | 2275 | 0 | 1943 | 520 | 162 | 120 | 0 | 122 | 94 | 0 | 104.95
11:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 322 |  | 0 | 250 | 260 | 0 | 0 | 55 | 240 | 0 | 94 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 21 | 25 | 29 | 33 | 25 | 25 | 0 | 84 | 75 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 5 | 135 | 0 | 0 | 310 | 295 | 209 | 26 | 50 | 13 | 50 | 0 | 51 | 0 | 0 | 10 | 20 | 5 | 33 | 0 | 130 | 202 | 8 | 22 | 2 | 44 | 42 | 44 | 0 | 163 | 157 | 60 | 81 | 0 | 220 | 18 | 0 | 9 | 305 | 24 | 11 | 0 | 135 | 0 | 0 | 149 | 0 | 131 | 7 | 90 | 84 | 112 | 321 | 38 | 17 | 78 | 4 | 305 | 43 | 76 | 0 | 43 | 100 | 320 | 99 | 53 | 162 | 86 | 0 | 17 | 31 |  | 703 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 126 | 0 | 195 | 0 | 83 | 0 | 0 | 0 | 403 | 1 | 0 | 76 | 0 | 90 | 0 | 6 | 100 | 440 | 105 | 0 | 0 | 0 |  | 7303 | 2982 | 10285 | 4065 | 703 | 2197 | 0 | 2290 | 518 | 159 | 120 | 0 | 130 | 103 | 0 | 104.94
12:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 322 |  | 0 | 250 | 275 | 0 | 0 | 55 | 240 | 0 | 95 | 0 | 32 | 0 | 6 | 0 | 0 | 0 | 35 | 55 | 35 | 21 | 25 | 28 | 33 | 25 | 25 | 0 | 82 | 75 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 18 | 4 | 135 | 0 | 0 | 315 | 305 | 207 | 26 | 50 | 23 | 50 | 0 | 51 | 0 | 0 | 25 | 21 | 5 | 33 | 0 | 136 | 191 | 3 | 22 | 3 | 44 | 42 | 44 | 0 | 163 | 154 | 60 | 77 | 0 | 220 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 163 | 0 | 131 | 10 | 90 | 160 | 112 | 321 | 38 | 17 | 105 | 2 | 304 | 54 | 110 | 17 | 48 | 100 | 320 | 104 | 56 | 162 | 94 | 0 | 17 | 33 |  | 704 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 121 | 0 | 185 | 0 | 82 | 0 | 0 | 0 | 412 | 25 | 0 | 113 | 0 | 113 | 0 | 7 | 113 | 480 | 80 | 0 | 0 | 0 |  | 7759 | 3056 | 10815 | 4075 | 704 | 2178 | 0 | 2776 | 558 | 157 | 120 | 0 | 136 | 111 | 0 | 104.94
13:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 322 |  | 0 | 250 | 278 | 0 | 0 | 55 | 240 | 0 | 95 | 0 | 102 | 0 | 30 | 0 | 0 | 0 | 35 | 35 | 35 | 21 | 25 | 28 | 33 | 25 | 25 | 0 | 82 | 75 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 70 | 8 | 25 | 18 | 9 | 110 | 0 | 0 | 325 | 310 | 209 | 26 | 50 | 26 | 52 | 0 | 51 | 0 | 0 | 34 | 21 | 5 | 33 | 18 | 140 | 165 | 8 | 22 | 2 | 44 | 42 | 44 | 0 | 110 | 155 | 59 | 79 | 0 | 220 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 296 | 0 | 0 | 175 | 0 | 133 | 8 | 90 | 200 | 113 | 321 | 38 | 50 | 105 | 3 | 304 | 54 | 110 | 51 | 48 | 100 | 320 | 104 | 53 | 162 | 97 | 0 | 17 | 30 |  | 703 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 118 | 0 | 187 | 0 | 54 | 0 | 0 | 0 | 408 | 60 | 0 | 113 | 0 | 113 | 0 | 7 | 113 | 540 | 102 | 0 | 0 | 0 |  | 8012 | 3157 | 11169 | 4071 | 703 | 2136 | 0 | 3120 | 619 | 157 | 120 | 0 | 140 | 103 | 0 | 104.93
14:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 322 |  | 0 | 250 | 250 | 0 | 0 | 55 | 240 | 0 | 95 | 0 | 102 | 48 | 26 | 0 | 0 | 0 | 35 | 35 | 35 | 21 | 25 | 28 | 33 | 25 | 42 | 0 | 82 | 75 | 110 | 0 | 11 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 20 | 25 | 18 | 2 | 110 | 0 | 0 | 305 | 300 | 207 | 26 | 50 | 26 | 52 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 18 | 146 | 163 | 8 | 22 | 2 | 44 | 42 | 47 | 0 | 110 | 155 | 60 | 79 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 298 | 0 | 0 | 186 | 0 | 132 | 15 | 90 | 200 | 123 | 321 | 38 | 88 | 105 | 2 | 305 | 54 | 110 | 80 | 48 | 100 | 320 | 104 | 46 | 162 | 97 | 0 | 17 | 25 |  | 704 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 124 | 0 | 190 | 0 | 52 | 0 | 0 | 0 | 410 | 0 | 0 | 113 | 0 | 113 | 0 | 7 | 113 | 540 | 130 | 0 | 10 | 0 |  | 8158 | 3159 | 11317 | 4042 | 704 | 2133 | 0 | 3253 | 617 | 157 | 120 | 48 | 146 | 97 | 0 | 104.93
15:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 10 | 322 |  | 0 | 250 | 260 | 0 | 0 | 55 | 240 | 0 | 94 | 0 | 102 | 150 | 26 | 0 | 0 | 0 | 54 | 30 | 35 | 21 | 25 | 28 | 33 | 25 | 49 | 0 | 82 | 75 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 80 | 70 | 26 | 18 | 3 | 110 | 0 | 0 | 325 | 295 | 206 | 26 | 50 | 23 | 51 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 18 | 150 | 165 | 8 | 22 | 1 | 43 | 42 | 47 | 0 | 110 | 155 | 60 | 78 | 0 | 214 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 298 | 0 | 0 | 185 | 0 | 132 | 7 | 90 | 200 | 118 | 321 | 38 | 72 | 105 | 1 | 305 | 54 | 110 | 80 | 49 | 100 | 320 | 104 | 35 | 162 | 97 | 0 | 17 | 18 |  | 704 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 118 | 0 | 177 | 0 | 12 | 0 | 0 | 0 | 407 | 75 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 500 | 205 | 0 | 54 | 0 |  | 8327 | 3324 | 11651 | 4089 | 704 | 2174 | 0 | 3462 | 578 | 157 | 120 | 150 | 150 | 67 | 0 | 104.92
16:00 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 30 | 317 |  | 0 | 250 | 240 | 0 | 0 | 55 | 240 | 0 | 33 | 0 | 48 | 150 | 10 | 0 | 0 | 0 | 54 | 35 | 17 | 21 | 25 | 28 | 33 | 25 | 50 | 0 | 83 | 75 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 34 | 20 | 58 | 30 | 18 | 6 | 110 | 0 | 0 | 325 | 300 | 210 | 26 | 48 | 26 | 47 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 0 | 18 | 144 | 168 | 8 | 22 | 1 | 44 | 42 | 47 | 0 | 110 | 154 | 61 | 82 | 0 | 214 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 298 | 0 | 0 | 185 | 0 | 132 | 6 | 78 | 200 | 120 | 321 | 38 | 90 | 105 | 1 | 305 | 54 | 110 | 58 | 48 | 100 | 298 | 93 | 19 | 162 | 97 | 0 | 17 | 9 |  | 705 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 114 | 0 | 175 | 0 | 11 | 0 | 0 | 0 | 379 | 35 | 0 | 50 | 0 | 113 | 0 | 3 | 113 | 500 | 182 | 0 | 17 | 1 |  | 8018 | 3125 | 11143 | 3989 | 705 | 2080 | 0 | 3146 | 577 | 158 | 120 | 184 | 144 | 40 | 0 | 104.92
17:00 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 67 | 280 |  | 0 | 250 | 265 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 48 | 98 | 10 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 25 | 50 | 0 | 84 | 75 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 34 | 20 | 32 | 44 | 18 | 10 | 110 | 0 | 0 | 300 | 300 | 208 | 26 | 48 | 26 | 49 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 10 | 6 | 134 | 174 | 8 | 19 | 0 | 44 | 42 | 47 | 0 | 110 | 157 | 60 | 83 | 0 | 215 | 18 | 0 | 10 | 275 | 16 | 11 | 0 | 298 | 0 | 0 | 188 | 0 | 131 | 0 | 90 | 136 | 122 | 321 | 38 | 90 | 51 | 0 | 232 | 54 | 51 | 52 | 48 | 90 | 320 | 84 | 3 | 162 | 72 | 0 | 17 | 1 |  | 704 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 4 | 54 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 118 | 0 | 178 | 0 | 11 | 0 | 0 | 0 | 303 | 35 | 0 | 50 | 0 | 54 | 0 | 1 | 50 | 500 | 151 | 0 | 17 | 0 |  | 7663 | 2966 | 10629 | 4002 | 704 | 1962 | 0 | 2722 | 577 | 159 | 120 | 244 | 134 | 5 | 0 | 104.91
18:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 216 | 322 |  | 0 | 250 | 290 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 150 | 30 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 20 | 33 | 25 | 50 | 0 | 85 | 75 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 70 | 32 | 50 | 18 | 3 | 110 | 0 | 0 | 295 | 315 | 207 | 26 | 50 | 26 | 50 | 0 | 51 | 0 | 47 | 35 | 22 | 11 | 33 | 18 | 158 | 170 | 8 | 19 | 0 | 44 | 42 | 44 | 0 | 163 | 155 | 58 | 83 | 0 | 220 | 18 | 0 | 10 | 280 | 16 | 11 | 150 | 298 | 154 | 50 | 179 | 98 | 132 | 0 | 90 | 150 | 123 | 321 | 115 | 90 | 56 | 0 | 290 | 54 | 63 | 80 | 57 | 100 | 320 | 92 | 0 | 162 | 81 | 0 | 17 | 0 |  | 704 | 0 | 380 | 0 | 0 | 155 | 0 | 0 | 4 | 0 | 0 | 65 | 31 | 0 | 0 | 0 | 0 | 50 | 5 | 92 | 0 | 32 | 27 | 16 | 20 | 19 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 104 | 0 | 176 | 0 | 11 | 10 | 0 | 0 | 401 | 73 | 0 | 65 | 15 | 80 | 0 | 0 | 70 | 520 | 201 | 0 | 35 | 0 |  | 8938 | 3449 | 12387 | 4180 | 704 | 2235 | 462 | 3239 | 597 | 160 | 155 | 497 | 158 | 0 | 0 | 104.91
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 383 | 322 |  | 0 | 250 | 255 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 33 | 25 | 50 | 0 | 86 | 75 | 150 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 100 | 32 | 50 | 18 | 9 | 110 | 0 | 0 | 280 | 300 | 208 | 26 | 48 | 26 | 50 | 0 | 51 | 0 | 50 | 40 | 22 | 8 | 33 | 18 | 154 | 170 | 8 | 19 | 0 | 43 | 40 | 44 | 0 | 163 | 159 | 59 | 83 | 0 | 220 | 18 | 0 | 10 | 270 | 16 | 11 | 30 | 298 | 20 | 0 | 190 | 25 | 131 | 0 | 90 | 200 | 125 | 321 | 115 | 90 | 105 | 0 | 305 | 54 | 110 | 80 | 87 | 90 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 705 | 0 | 360 | 0 | 0 | 215 | 0 | 0 | 11 | 0 | 0 | 65 | 32 | 0 | 0 | 0 | 0 | 50 | 28 | 92 | 27 | 43 | 31 | 52 | 34 | 20 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 113 | 0 | 176 | 0 | 12 | 0 | 0 | 0 | 372 | 105 | 0 | 111 | 15 | 113 | 0 | 0 | 113 | 580 | 220 | 0 | 35 | 0 |  | 9012 | 3817 | 12829 | 4352 | 705 | 2189 | 75 | 3774 | 656 | 161 | 215 | 548 | 154 | 0 | 0 | 104.89
19:30 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 370 | 327 |  | 0 | 250 | 270 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 33 | 25 | 25 | 0 | 86 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 100 | 31 | 50 | 18 | 9 | 110 | 0 | 0 | 280 | 305 | 210 | 26 | 50 | 26 | 50 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 18 | 156 | 171 | 8 | 19 | 0 | 43 | 42 | 47 | 0 | 163 | 161 | 59 | 83 | 0 | 220 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 298 | 0 | 0 | 189 | 0 | 131 | 0 | 90 | 200 | 126 | 321 | 115 | 90 | 105 | 0 | 305 | 54 | 110 | 86 | 96 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 704 | 0 | 360 | 0 | 0 | 215 | 0 | 0 | 15 | 0 | 0 | 65 | 33 | 0 | 0 | 0 | 0 | 50 | 28 | 93 | 27 | 43 | 31 | 52 | 34 | 20 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 113 | 0 | 178 | 0 | 12 | 0 | 0 | 0 | 364 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 580 | 220 | 0 | 35 | 0 |  | 8895 | 3820 | 12715 | 4320 | 704 | 2220 | 0 | 3778 | 658 | 161 | 215 | 503 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 378 | 331 |  | 0 | 250 | 270 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 150 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 33 | 33 | 25 | 0 | 86 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 100 | 20 | 50 | 18 | 18 | 110 | 0 | 0 | 280 | 305 | 213 | 26 | 50 | 26 | 49 | 0 | 51 | 0 | 0 | 43 | 22 | 0 | 33 | 18 | 156 | 174 | 8 | 19 | 0 | 43 | 42 | 47 | 0 | 163 | 160 | 59 | 84 | 0 | 220 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 298 | 0 | 0 | 190 | 0 | 131 | 0 | 90 | 200 | 122 | 321 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 52 | 94 | 100 | 320 | 97 | 0 | 162 | 108 | 0 | 17 | 0 |  | 704 | 0 | 360 | 0 | 0 | 215 | 0 | 0 | 26 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 50 | 28 | 93 | 27 | 43 | 32 | 52 | 34 | 20 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 114 | 0 | 178 | 0 | 12 | 0 | 0 | 0 | 380 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 580 | 221 | 0 | 35 | 0 |  | 8806 | 3851 | 12657 | 4334 | 704 | 2251 | 0 | 3663 | 658 | 161 | 215 | 515 | 156 | 0 | 0 | 104.9
21:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 371 | 337 |  | 0 | 250 | 290 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 115 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 88 | 50 | 12 | 47 | 18 | 30 | 110 | 0 | 0 | 315 | 310 | 211 | 26 | 51 | 23 | 48 | 0 | 51 | 0 | 0 | 43 | 22 | 0 | 33 | 18 | 156 | 180 | 8 | 17 | 0 | 43 | 41 | 47 | 0 | 163 | 161 | 59 | 84 | 0 | 220 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 298 | 0 | 0 | 190 | 0 | 126 | 0 | 90 | 200 | 132 | 320 | 115 | 90 | 105 | 0 | 305 | 54 | 110 | 35 | 96 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 705 | 0 | 370 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 50 | 41 | 93 | 27 | 43 | 32 | 52 | 34 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 115 | 0 | 179 | 0 | 12 | 0 | 0 | 0 | 407 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 600 | 221 | 0 | 35 | 0 |  | 8723 | 3899 | 12622 | 4379 | 705 | 2311 | 0 | 3564 | 678 | 161 | 215 | 453 | 156 | 0 | 0 | 104.89
22:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 337 |  | 0 | 250 | 275 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 115 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 50 | 12 | 47 | 18 | 30 | 110 | 0 | 0 | 290 | 305 | 213 | 26 | 48 | 26 | 51 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 18 | 154 | 181 | 8 | 19 | 0 | 43 | 41 | 47 | 0 | 163 | 160 | 59 | 84 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 298 | 0 | 0 | 182 | 0 | 117 | 0 | 90 | 200 | 135 | 320 | 115 | 90 | 105 | 0 | 305 | 54 | 110 | 52 | 96 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 714 | 0 | 360 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 50 | 39 | 93 | 27 | 43 | 32 | 52 | 34 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 116 | 0 | 178 | 0 | 12 | 0 | 0 | 0 | 374 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 600 | 222 | 0 | 35 | 0 |  | 8727 | 3866 | 12593 | 4360 | 714 | 2277 | 0 | 3567 | 679 | 161 | 216 | 465 | 154 | 0 | 0 | 104.89
23:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 332 |  | 0 | 250 | 280 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 115 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 25 | 0 | 0 | 84 | 69 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 50 | 12 | 47 | 18 | 30 | 110 | 0 | 0 | 290 | 305 | 213 | 26 | 50 | 26 | 52 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 21 | 150 | 185 | 8 | 19 | 0 | 43 | 41 | 47 | 0 | 163 | 160 | 59 | 84 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 298 | 0 | 0 | 191 | 0 | 112 | 0 | 90 | 200 | 130 | 320 | 115 | 90 | 105 | 0 | 305 | 54 | 110 | 52 | 96 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 714 | 0 | 360 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 65 | 35 | 0 | 0 | 0 | 0 | 50 | 38 | 93 | 0 | 0 | 30 | 52 | 34 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 115 | 0 | 179 | 0 | 11 | 0 | 0 | 0 | 382 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 580 | 222 | 0 | 35 | 0 |  | 8715 | 3781 | 12496 | 4361 | 714 | 2286 | 0 | 3495 | 659 | 153 | 216 | 462 | 150 | 0 | 0 | 104.88
24:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 332 |  | 0 | 250 | 270 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 115 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 25 | 0 | 0 | 84 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 50 | 12 | 43 | 18 | 32 | 110 | 0 | 0 | 290 | 305 | 212 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 33 | 21 | 146 | 197 | 8 | 19 | 0 | 43 | 41 | 47 | 0 | 163 | 160 | 56 | 84 | 0 | 220 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 298 | 0 | 0 | 180 | 0 | 110 | 0 | 90 | 200 | 125 | 322 | 98 | 90 | 105 | 0 | 305 | 54 | 110 | 52 | 65 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 360 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 50 | 34 | 93 | 0 | 0 | 15 | 52 | 34 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 120 | 0 | 185 | 0 | 12 | 0 | 0 | 0 | 390 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 570 | 221 | 0 | 35 | 0 |  | 8664 | 3726 | 12390 | 4384 | 706 | 2298 | 0 | 3425 | 649 | 159 | 180 | 443 | 146 | 0 | 0 | 104.88
KWH | 0 | 0 | 0 | 0 | 6037855 | 0 | 0 | 4214790 | 7724000 |  | 0 | 6155050 | 6569804 | 0 | 0 | 1333981 | 5848693 | 0 | 703000 | 0 | 1147968 | 1260000 | 307076 | 0 | 0 | 0 | 1221120 | 1212187 | 1121430 | 321336 | 600000 | 653580 | 812100 | 695600 | 449760 | 0 | 1979400 | 180800 | 2800000 | 0 | 192121 | 0 | 0 | 0 | 0 |  | 330480 | 0 | 730450 | 816240 | 332160 | 741600 | 358512 | 569280 | 2629676 | 0 | 0 | 7359900 | 7204000 | 5039000 | 685818 | 1172950 | 547776 | 1235040 | 0 | 1225724 | 0 | 75728 | 691046 | 509688 | 177660 | 759500 | 374190 | 3245760 | 4455040 | 185280 | 449568 | 15700 | 1024000 | 985920 | 1120200 | 0 | 3470072 | 3550000 | 1418880 | 1939200 | 0 | 5158290 | 382000 | 0 | 222120 | 7133000 | 492345 | 264000 | 138624 | 4860107 | 120401 | 58521 | 4308000 | 103725 | 2507760 | 72360 | 1995840 | 3613440 | 2954036 | 7753000 | 1606800 | 1324800 | 1896036 | 24840 | 6463418 | 1201064 | 2048253 | 807120 | 1422120 | 2288640 | 7686400 | 2100480 | 392660 | 3708000 | 1987200 | 0 | 443520 | 208157 |  | 17038545 | 0 | 8834976 | 0 | 0 | 3540480 | 0 | 0 | 34690 | 0 | 0 | 621000 | 605344 | 0 | 0 | 0 | 0 | 373246 | 186678 | 833992 | 124980 | 210687 | 172827 | 565920 | 283720 | 457200 | 0 | 205758 | 1866763 | 0 | 0 | 0 | 0 | 3180400 | 0 | 4485073 | 0 | 1269835 | 31680 | 1137991 | 0 | 9247672 | 1169280 | 0 | 2269440 | 106272 | 2125401 | 0 | 41146 | 2277024 | 13208500 | 323296 | 0 | 584400 | 2460 |  | 186714766 | 77416676 | 264131442 | 100904447 | 17038545 | 49952655 | 452951 | 67052487 | 15075263 | 2160200 | 3540480 | 3951331 | 3245760 | 757323 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 6702019.05 | 0 | 0 | 4256937.9 | 7955720 |  | 0 | 6709004.5 | 7292482.44 | 0 | 0 | 11285479.26 | 6082640.72 | 0 | 1216190 | 0 | 10469468.16 | 12398400 | 2831240.72 | 0 | 0 | 0 | 8914176 | 9370205.51 | 11057299.8 | 241002 | 450000 | 0 | 0 | 0 | 4349179.2 | 0 | 534438 | 48816 | 5068000 | 0 | 1784804.09 | 0 | 0 | 0 | 0 |  | 0 | 0 | 7085365 | 7795092 | 2889792 | 5873472 | 451725.12 | 1690761.6 | 3891920.48 | 0 | 0 | 5446326 | 7204000 | 4635880 | 884705.22 | 1348892.5 | 618986.88 | 1729056 | 0 | 2095988.04 | 0 | 764852.8 | 6599489.3 | 647303.76 | 133245 | 1329125 | 280642.5 | 24343200 | 4722342.4 | 1682342.4 | 570951.36 | 250258 | 1679360 | 1577472 | 1993956 | 0 | 3955882.08 | 3692000 | 2795193.6 | 3703872 | 0 | 8923841.7 | 836580 | 0 | 453124.8 | 7204330 | 369258.75 | 200640 | 2357994.24 | 36742408.92 | 2044408.98 | 978471.12 | 22401600 | 1734282 | 24676358.4 | 845888.4 | 16266096 | 39205824 | 20825953.8 | 7210290 | 14654016 | 12519360 | 16514473.56 | 0 | 48863440.08 | 10461267.44 | 18004143.87 | 8055057.6 | 12187568.4 | 15242342.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98142019.2 | 0 | 9276724.8 | 0 | 0 | 49071052.8 | 0 | 0 | 363898.1 | 0 | 0 | 701730 | 938283.2 | 0 | 0 | 0 | 0 | 3672740.64 | 1896648.48 | 7380829.2 | 962346 | 2848488.24 | 1674693.63 | 5483764.8 | 2752084 | 877824 | 0 | 155758.806 | 11256580.89 | 0 | 0 | 0 | 0 | 3721068 | 0 | 5920296.36 | 0 | 1904752.5 | 538876.8 | 1331449.47 | 0 | 9155195.28 | 12207283.2 | 0 | 21536985.6 | 1003207.68 | 16493111.76 | 0 | 454663.3 | 16827207.36 | 57985315 | 0 | 0 | 0 | 0 |  | 583159974.85 | 346534879.096 | 929694853.946 | 103689794.156 | 98142019.2 | 58544937.66 | 7654033.14 | 478884345.55 | 69241895.89 | 583254 | 49071052.8 | 37989511.85 | 24343200 | 1550809.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 322 |  | 0 | 250 | 275 | 0 | 0 | 55 | 240 | 0 | 95 | 0 | 32 | 0 | 6 | 0 | 0 | 0 | 35 | 55 | 35 | 21 | 25 | 28 | 33 | 25 | 25 | 0 | 82 | 75 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 18 | 4 | 135 | 0 | 0 | 315 | 305 | 207 | 26 | 50 | 23 | 50 | 0 | 51 | 0 | 0 | 25 | 21 | 5 | 33 | 0 | 136 | 191 | 3 | 22 | 3 | 44 | 42 | 44 | 0 | 163 | 154 | 60 | 77 | 0 | 220 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 163 | 0 | 131 | 10 | 90 | 160 | 112 | 321 | 38 | 17 | 105 | 2 | 304 | 54 | 110 | 17 | 48 | 100 | 320 | 104 | 56 | 162 | 94 | 0 | 17 | 33 |  | 704 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 121 | 0 | 185 | 0 | 82 | 0 | 0 | 0 | 412 | 25 | 0 | 113 | 0 | 113 | 0 | 7 | 113 | 480 | 80 | 0 | 0 | 0 |  | 10815 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 383 | 322 | 0 | 0 | 250 | 255 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 33 | 25 | 50 | 0 | 86 | 75 | 150 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 102 | 100 | 32 | 50 | 18 | 9 | 110 | 0 | 0 | 280 | 300 | 208 | 26 | 48 | 26 | 50 | 0 | 51 | 0 | 50 | 40 | 22 | 8 | 33 | 18 | 154 | 170 | 8 | 19 | 0 | 43 | 40 | 44 | 0 | 163 | 159 | 59 | 83 | 0 | 220 | 18 | 0 | 10 | 270 | 16 | 11 | 30 | 298 | 20 | 0 | 190 | 25 | 131 | 0 | 90 | 200 | 125 | 321 | 115 | 90 | 105 | 0 | 305 | 54 | 110 | 80 | 87 | 90 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 705 | 0 | 360 | 0 | 0 | 215 | 0 | 0 | 11 | 0 | 0 | 65 | 32 | 0 | 0 | 0 | 0 | 50 | 28 | 92 | 27 | 43 | 31 | 52 | 34 | 20 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 113 | 0 | 176 | 0 | 12 | 0 | 0 | 0 | 372 | 105 | 0 | 111 | 15 | 113 | 0 | 0 | 113 | 580 | 220 | 0 | 35 | 0 |  | 12829 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 412 | 300 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 18 | 10 | 110 | 0 | 0 | 350 | 350 | 210 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 202 | 8 | 21 | 0 | 43 | 42 | 47 | 0 | 163 | 160 | 60 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 137 | 320 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 96 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 718 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 33 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 35 | 95 | 28 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 17 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 380 | 280 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 16 | 6 | 110 | 0 | 0 | 320 | 335 | 210 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 138 | 200 | 8 | 21 | 1.6 | 43 | 42 | 47 | 0 | 163 | 160 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 100 | 100 | 190 | 50 | 149 | 20 | 90 | 200 | 135 | 320 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 80 | 95 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 718 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 28 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 17 | 50 | 0 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 622 | 107 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 373 | 280 | 0 | 0 | 250 | 300 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 21 | 25 | 26 | 33 |  | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 11 | 110 | 0 | 0 | 325 | 335 | 202 | 26 | 32 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 17 | 122 | 205 | 8 | 19 | 1 | 43 | 42 | 44 | 0 | 110 | 158 | 60 | 84 | 0 | 186 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 85 | 6 | 90 | 34 | 108 | 322 | 38 | 35 | 51 | 1 | 304 | 40 | 51 | 0 | 59 | 100 | 320 | 92 | 11 | 162 | 53 | 0 | 17 | 15 | 0 | 706 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 128 | 0 | 201 | 0 | 12 | 0 | 0 | 0 | 402 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 470 | 152 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9068 | 7:00
| Highest Generation |  | 12829 | 19:00
| Day Peak Generation |  | 10815 | 12:00
| Evening Peak Generation |  | 12829 | 19:00
| HVDC Max Flow |  | 714 | 22:00
| HVDC EvPeak Flow |  | 705 | 19:00
| Load factor L.F |  | 85.79%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-17
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10815 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9764 | MW
Evening Peak Generation : |  | 12829 | MW Hour : | 19:00 | Available Max Generation : |  | 14754 | MW
E.P. Demand (at gen end) : |  | 12829 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13600 | MW
Maximum Generation : |  | 12829 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1154 | MW
Total Gen. (MKWH) : |  | 264.1314 | System Load Factor : | 85.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -162 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-17
Actual : | 104.82 | Ft.(MSL) , | Rule curve : | 107.5 | Ft.( MSL )
Gas Consumed : | Total = | 1192.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 162234731.816
: |  | Coal : | 69241895.89 | Oil : | 573598943.34 | Total : | 805075571.046
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4840.2485 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1652.4216 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1481.6677 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1339.2211 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1210.009 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 976.4508 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 537.6583 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 251.1895 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 753.1271 |  |  | 0 | 0%
Total | 0 |  | 13041.9937 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar400/230 kV AT-2 transformer was under shut down since 09:35 for D/W.
b) Aminbazar-Kaliakoir 230 kV Ckt-2 was under shut down from 09:46 to 16:26 for A/M.
c) Chapainawabganj 132/33 kV T1 transformer was shutdown from 08:15 to 16:21 for A/M.
d) Cumilla(N) 132/33 kV T3 transformer was shutdown from 08:29 to 10:11 due to red hot maintenance |  |  |  |  | About 50 MW power interruption occurred under Cumilla(N) S/S
at Y-phase bus isolator of 33 kV chandina PBS feeder. |  |  |  |  | area from 08:29 to 10:11.
e) Dohazari-Matarbari 132 kV Ckt was switched on at 08:46.
f) Ishurdi-Pabna 132 kV Ckt was under shut down from 10:05 to 20:51 for A/M.
g) Kabirpur-Manikganj 132 kV Ckt-2 & T2 transformer were under shut down from 11:28 to 14:49 for D/W.
h) Kabirpur-Manikganj 132 kV Ckt-1 & T3 transformer were under shut down from 09:45 to 11:18 for D/W.
i) Kaptai-Chandraghona 132 kV Ckt-1 was under shut down since 08:28 for A/M.
j) Kulshi-Madunaghat 132 kV Ckt-1 tripped at 10:47 from both ends showing Dist relay at Kulshi end &
dist Z1,E/F relay at Madunaghat end and was switched on at 11:03.
k) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:03 to 18:08 for A/M.
l) Sherpur 132/33 kV T1 transformer was shutdown from 08:54 to 16:54 for A/M.
m) Sirajganj 132/33 kV T3 transformer was shutdown from 08:50 to 16:10 for A/M.
n) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 09:18 to 16:13 for A/M.
o) Pabna 132/33 kV T2 transformer was shutdown from 08:21 to 09:10 due to bus isolator maintenance |  |  |  |  | About 15 MW power interruption occurred under Pabna S/S
of 33 kV Maligachha PBS feeder. |  |  |  |  | area from 08:21 to 09:10.
p) Bagerhat-Goalpara 132 kV Ckt was under shut down from 09:59 to 13:34 for D/W.
q) Shariatpur 132 kV bus-1 was under shut down from 09:36 to 16:14.
r) Bagerhat-Orion Rupsha 132 kV Ckt was under shut down from 13:46 to 18:30 for D/W.
s) Bhola 225 MW CCPP GT-1 was synchronized at 13:49.
t) Cumilla(N) 132/33 kV T3 & T4 transformer tripped at 15:58 due to 33 kV feeder fault and were
switched on at 16:36.
u) Ashuganj-Kishoreganj 132 kV Ckt-1 tripped at 20:06 showing dist A-phase at Ashuganj end & auto
reclose at Kishoreganj end and was switched on at 20:09.
v) Kulshi-Madunaghat 132 kV Ckt-1 was under shut down from 15:21 to 16:32 for tree trimming .
w) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 21:53 showing dist RTS,GT,Z1 at Ashuganj end & auto
reclose at Sirajganj end and was switched on at 22:21.
x) Bogura 132/33 kV T3 transformer was shutdown since 07:24(17-10-21) for C/M.
y) Gopalganj 132/33 kV T3 transformer was shutdown since 07:03(17-10-21) for A/M.
z) Khulna(C) 132/33 kV T4 transformer was shutdown since 07:44(17-10-21) for A/M.
aa) Siddhirganj 335 MW EGCB was shut down since 06:36(17-10-21) for GT air inlet filter change.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 255 | 6037855 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 383 | 4214790
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 322 | 7724000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6155050 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 255 | 6569804 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1333981
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 307076 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 321336
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 703000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 5848693 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1147968
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1221120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1260000
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1212187
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1121430
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1253580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 812100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 695600
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 449760
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 4860107
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 20 | 120401 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 58521 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 103725 | Low demand.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 2507760 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1324800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2100480
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3708000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 208157
| Dhaka area Total |  |  |  | 5560 | 3238 | 63381281
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 150 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 192121
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 72360
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 741600
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 161 | 2160200 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1896036
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 730450
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 816240
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1995840 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 358512 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 9 | 569280
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 32 | 332160 | Low demand.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24840
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 6463418
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1201064
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2048253
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 2288640 | Engine problem
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 1987200 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1509 | 26678214
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 110 | 2629676 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 5039000
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7359900 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7204000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 547776 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1235040
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 685818 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1225724
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 2954036 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 75728
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 48 | 1172950 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3613440
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 509688
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 177660
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3245760
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 759500
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 40 | 691046 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 374190 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 30 | 138624 | Low demand.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 807120 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 87 | 1422120 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1963 | 42312316
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 170 | 4455040 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 449568
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 8 | 185280 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15700
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 4308000 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1606800
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 392660
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 330480
| Mymensingh Area Total |  |  |  | 622 | 525 | 11743528
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1024000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 985920 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3470072
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 159 | 3550000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 44 | 1120200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1418880
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1939200
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5158290
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 382000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 492345 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7133000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 321 | 7753000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 222120
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7686400 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1777 | 42599427
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 705 | 17038545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 11 | 34690 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 215 | 3540480
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 8834976 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 31680 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1169280
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 15 | 106272 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1411 | 30755923
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 605344
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 621000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 12 | 1269835 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 13208500
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 323296
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 584400 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 944 | 16612375
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 373246
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 186678 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 124980 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 210687 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 172827 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 113 | 3180400 | FGMO
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 176 | 4485073 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 1137991 | Under maint.
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 372 | 9247672 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 283720 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 457200
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 205758
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 565920
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 833992 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 2269440
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2277024
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 2460
| Rajshahi Area Total |  |  |  | 2179 | 1273 | 26015068
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1866763
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2125401
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41146
| Rangpur Area Total |  |  |  | 605 | 189 | 4033310
| Total |  |  |  | 20934 | 12829 | 264131442
| Eastern Grid Total |  |  |  | 13975 | 9012 | 186714766
| Western Grid Total |  |  |  | 6959 | 3817 | 77416676
| National Grid Total |  |  |  | 20934 | 12829 | 264131442
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-16
(a) ENTIRE EASTERN GRID : |  | 8504 | MW | (b) ENTIRE WESTERN GRID : |  | 3790 | MW
i) Dhaka area |  | 4441 | MW | i) Khulna area |  | 1414 | MW
ii) Chittagong area |  | 1315 | MW | ii) Rajshahi area |  | 1319 | MW
iii) Comilla area |  | 1147 | MW | iii) Barisal area |  | 351 | MW
iv) Mymensingh area |  | 1056 | MW | iv) Rangpur area |  | 706 | MW
v) Sylhet area |  | 545 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12294 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 16:00 | Kishoreganj | 160 | 21:00 | Jessore | 115 | 18:30
Munsiganj | 98 | 0:00 | Netrokona | 124 | 2:00 | Benapol | 58 | 14:00
Sonargaon | 73 | 23:00 | Jamalpur | 139 | 1:00 | Jhenida(Old) | 106 | 18:00
Shyampur | 196 | 0:00 | Sherpur | 136 | 19:00 | Bottail | 108 | 22:00
Bhulta | 204 | 23:00 | Srimongal | 62 | 19:30 | G.K Project | 59 | 18:30
Madanganj | 46 | 19:00 | Shahjibazar | 118 | 18:00 | Faridpur | 136 | 19:00
Shitalakhya | 104 | 16:00 | Fenchuganj | 46 | 1:00 | Rajbari | 52 | 23:00
Rahim steel | 23 | 10:00 | Kulawara | 46 | 18:00 | Madaripur | 101 | 22:00
Matuail | 62 | 15:00 | Sylhet | 152 | 19:30 | Sariatpur | 58 | 21:00
Ghorasal | 81 | 18:00 | Chatak | 33 | 19:30 | Gopalganj | 90 | 20:00
Narsingdi | 181 | 19:30 | Sunamganj | 58 | 21:00 | Bagerhat | 96 | 19:00
Haripur (SBU) | 114 | 11:00 | Biani Bazar | 68 | 22:00 | Mongla | 39 | 11:00
Sreenagar | 42 | 22:00 | Comilla (S) | 158 | 18:00 | Satkhira | 101 | 20:00
Ullon | 67 | 18:00 | Comilla(N) | 109 | 19:30 | Gallamari | 48 | 12:00
Hasnabad | 85 | 22:00 | Chandpur | 70 | 20:00 | Magura | 54 | 19:00
Magbazar | 98 | 16:00 | Feni | 105 | 21:00 | Norail | 43 | 21:00
Maniknagar | 64 | 13:00 | Chowmuhani | 200 | 19:00 | Chuadanga | 101 | 18:30
Bangabhaban | 7 | 11:00 | Ashuganj | 48 | 23:00 | Barisal(N) | 46 | 21:00
Motijheel | 24 | 13:00 | Daudkandi | 154 | 20:00 | Barisal (S) | 106 | 21:00
Narinda | 68 | 18:00 | B.Baria | 165 | 23:00 | Patuakhali | 116 | 24:00
Kazla | 86 | 18:00 | Ramganj | 86 | 22:00 | Bhandaria | 52 | 20:00
Dhanmondi | 191 | 13:00 | Chaddagram | 53 | 21:00 | Borguna | 18 | 23:00
Lalbag | 74 | 18:00 | PHP | 8 | 17:00 | Borhan Uddin | 46 | 20:00
Madartek | 76 | 18:00 | Kochua | 64 | 22:00 | Ishurdi | 73 | 18:30
Dhaka University | 32 | 12:00 | Madunaghat | 63 | 18:00 | Ruppur Paromanobik | 3 | 20:00
Aftabnagar | 16 | 13:00 | Hathazari | 92 | 22:00 | Natore | 126 | 20:00
Fatullah | 63 | 12:00 | Khulshi | 176 | 15:00 | Bogra | 164 | 19:30
Nawabganj | 52 | 20:00 | Halishahar | 94 | 14:00 | Noagaon | 120 | 20:00
Keraniganj | 72 | 19:00 | Baraulia | 134 | 23:00 | Rajshahi | 157 | 20:00
Mirpur | 132 | 18:00 | Sikalbaha | 40 | 13:00 | Rajshahi New | 20 | 20:00
Kalyanpur | 102 | 18:00 | Dohazari | 92 | 23:00 | C.Nawabganj | 65 | 20:00
Gulshan | 118 | 12:00 | Cox'sbazar | 100 | 23:00 | Amnura | 57 | 20:00
Uttara | 90 | 18:00 | Chandraghona | 28 | 18:30 | Pabna | 99 | 18:30
Uttara New | 27 | 12:00 | Kaptai | 4.5 | 18:00 | Shahjadpur | 98 | 20:00
Kamrangirchar | 90 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 102 | 19:30
Savar | 184 | 13:00 | Bakulia | 117 | 18:00 | Niyamatpur | 78 | 1:00
Bhasantec | 147 | 18:00 | Julda | 17 | 1:00 | Joypurhat | 57 | 20:00
Agargaon | 76 | 18:00 | TK chemical | 30 | 18:00 | Sherpur(Bogura) | 58 | 20:00
Satmosjid | 115 | 18:30 | Modern Steel | 4.8 | 14:00 | Mohastangor | 70 | 1:00
Tongi | 130 | 13:00 | Shahmirpur | 22 | 22:00 | Bhangura | 33 | 20:00
Kabirpur | 260 | 15:00 | Khagrachhari | 28 | 16:00 | Rangpur | 114 | 2:00
Basundhara | 205 | 18:00 | Matarbari | 38.5 | 23:00 | Lalmonirhat | 43 | 20:00
Manikganj | 72 | 21:00 | Baroiar Hat | 76 | 19:00 | Saidpur | 95 | 21:00
Joydevpur | 193 | 18:30 | Rangamati | 14 | 18:30 | Purbasadipur | 94 | 21:00
New Tongi | 92 | 14:00 | Abul Khair 230 | 155 | 2:00 | Thakurgaon | 74 | 20:00
Kodda | 262 | 18:00 | BSRM | 151 | 2:00 | Palashbari | 112 | 18:00
Dhamrai | 188 | 14:00 | GPH Ispat | 92 | 20:00 | Barapukuria | 47 | 19:00
Rajendrapur | 100 | 18:00 | Agrabad | 84 | 18:30 | Panchagar | 49 | 19:00
Valuka | 112 | 15:00 | Goalpara | 26 | 23:00 | Joldhaka | 52 | 2:00
Tangail | 220 | 18:30 | Central S/S | 96 | 18:00 | Kurigram | 56 | 6:00
Mymensing | 231 | 18:30 | Noapara | 42 | 19:30 | Mithapukur | 29 | 3:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 5:00 | 402 | 18:30 | Kaliakoir | 396 | 0.29167 | 386 | 0.5
| Bheramara | 404 | 5:00 | 398 | 19:00 | Bhulta | 389 | 0.25 | 377 | 0.45833
| Ashuganj(N) | 395 | 6:00 | 386 | 12:00 | Gopalganj | 402 | 0.625 | 386 | 0.79167
| Payra | 407 | 6:00 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 232 | 12:00 | Hathazari | 238 | 17:00 | 228 | 8:00
| Ishurdi | 235 | 6:00 | 225 | 18:00 | Megnaghat | 235 | 6:00 | 230 | 9:00
| Ashuganj | 243 | 4:00 | 238 | 12:00 | Fenchuganj | 244 | 5:00 | 241 | 15:00
| Serajganj | 231 | 14:00 | 225 | 18:30 | Siddhirganj | 234 | 6:00 | 226 | 11:00
| Baghabari | 232 | 4:00 | 225 | 19:30 | Maniknagar | 232 | 6:00 | 224 | 12:00
| Barapukuria | 234 | 7:00 | 222 | 1:00 | Agargaon | 230 | 7:00 | 220 | 12:00
| Bogra | 223 | 6:00 | 214 | 1:00 | Barisal | 243 | 14:00 | 229 | 22:00
| Rajshahi | 230 | 7:00 | 220 | 13:00 | Bhola 225 MW | 247 | 8:00 | 236 | 19:30
| Khulna South | 234 | 6:00 | 221 | 18:00 | AKSML | 236 | 14:00 | 228 | 2:00
| Rampura | 230 | 3:00 | 225 | 12:00 | BSRM | 234 | 5:00 | 219 | 2:00
| Haripur | 230 | 1:00 | 223 | 12:00 | Bibiyana | 243 | 4:00 | 239 | 17:00
| Hasnabad | 230 | 22:00 | 221 | 12:00 | Bhulta | 234 | 6:00 | 226 | 12:00
| Shyampur | 230 | 6:00 | 222 | 13:00 | Ashuganj (S) | 239 | 7:00 | 234 | 12:00
| Aminbazar | 229 | 1:00 | 223 | 2:00 | Kaliakoir | 230 | 5:00 | 224 | 10:00
| Tongi | 229 | 1:00 | 222 | 12:00 | GPH | 237 | 17:00 | 229 | 8:00
| Comilla (N) | 233 | 18:00 | 228 | 12:00 | Jhenaidah | 230 | 6:00 | 217 | 18:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 129 | 12:00 | Madanhat | 141 | 0.625 | 133 | 0.16667
| Munsiganj | 136 | 1:00 | 129 | 12:00 | Hathazari | 139 | 0.58333 | 135 | 0.29167
| Sonargaon | 135 | 18:00 | 129 | 11:00 | Khulshi | 138 | 0.66667 | 129 | 0.33333
| Shyampur | 137 | 1:00 | 131 | 12:00 | Halishahar | 139 | 0.66667 | 130 | 0.33333
| Bhulta | 131 | 3:00 | 124 | 12:00 | Baraulia | 139 | 0.75 | 133 | 0.25
| Madanganj | 135 | 2:00 | 129 | 0:00 | Sikalbaha | 141 | 0.66667 | 132 | 0.33333
| Shitalakhya | 136 | 1:00 | 130 | 11:00 | Dohazari | 136 | 0.66667 | 125 | 0.083333
| Rahim steal | 134 | 1:00 | 129 | 12:00 | Cox'sbazar | 121 | 0.70833 | 108 | 0.875
| Matuail | 135 | 1:00 | 129 | 12:00 | Chandraghona | 139 | 0.66667 | 134 | 0.125
| Ghorasal | 140 | 1:00 | 136 | 12:00 | Kaptai | 137 | 0.54167 | 135 | 0.041667
| Narsinghdi | 133 | 7:00 | 124 | 18:30 | A. Khaer Stl. | 136 | 0.58333 | 130 | 0.29167
| Haripur (SBU) | 135 | 6:00 | 130 | 0:00 | Bakulia | 139 | 0.66667 | 130 | 0.29167
| Sreenagar | 135 | 6:00 | 129 | 11:00 | Julda | 139 | 0.70833 | 134 | 0.125
| Ullon | 135 | 4:00 | 127 | 12:00 | TK Chemical | 139 | 0.66667 | 134 | 0.041667
| Hasnabad | 136 | 4:00 | 130 | 11:00 | Modern Steel | 138 | 0.70833 | 133 | 0.125
| Magbazar | 135 | 4:00 | 127 | 12:00 | Shahmirpur | 138 | 0.625 | 132 | 0.29167
| Maniknagar | 135 | 1:00 | 129 | 12:00 | Khagrachhari | 137 | 0.66667 | 133 | 0.083333
| Bangabhaban | 135 | 1:00 | 129 | 12:00 | Matarbari | 132 | 0.58333 | 115 | 0.041667
| Motijheel | 135 | 1:00 | 129 | 12:00 | Baroiar Hat | 136 | 0.66667 | 130 | 0.875
| Narinda | 135 | 1:00 | 129 | 12:00 | Rangamati | 139 | 16:00 | 133 | 8:00
| Kazla | 135 | 1:00 | 129 | 12:00 | Agrabad | 137 | 16:00 | 132 | 2:00
| Dhanmondi | 135 | 3:00 | 128 | 12:00 | Goalpara S/S | 139 | 6:00 | 133 | 0.58333
| Lalbag | 136 | 6:00 | 129 | 12:00 | Khulna Central S/S | 138 | 4:00 | 132 | 0.58333
| Madartek | 135 | 6:00 | 127 | 12:00 | Noapara | 137 | 5:00 | 131 | 0.5
| Dhaka University | 134 | 1:00 | 127 | 12:00 | Jessore | 136 | 7:00 | 127 | 0.58333
| Aftabnagar | 134 | 1:00 | 128 | 12:00 | Benapol | 136 | 0.25 | 126 | 0.58333
| Fatullah | 137 | 1:00 | 131 | 12:00 | Jhenida(Old) | 138 | 6:00 | 128 | 0.75
| Nawabganj | 135 | 5:00 | 129 | 11:00 | Bottail | 136 | 0.125 | 130 | 0.75
| Keraniganj | 136 | 5:00 | 129 | 12:00 | G.K Project | 139 | 0.041667 | 134 | 0.77083
| Mirpur | 133 | 4:00 | 126 | 12:00 | Faridpur | 135 | 0.25 | 128 | 0.75
| Kalyanpur | 133 | 5:00 | 127 | 13:00 | Rajbari | 136 | 0.29167 | 127 | 0.79167
| Gulshan | 135 | 6:00 | 127 | 12:00 | Madaripur | 139 | 0.20833 | 131 | 0.75
| Uttara | 133 | 2:00 | 126 | 12:00 | Shariyatpur S/S | 138 | 7:00 | 129 | 0.91667
| Uttara New | 133 | 4:00 | 125 | 12:00 | Gopalganj | 142 | 0.041667 | 131 | 0.83333
| Kamrangirchar | 135 | 1:00 | 128 | 12:00 | Bagerhat | 137 | 6:00 | 120 | 0.75
| Savar | 135 | 1:00 | 127 | 13:00 | Mongla | 135 | 5:00 | 121 | 0.75
| Bhasantec | 136 | 5:00 | 129 | 12:00 | Satkhira | 137 | 6:00 | 129 | 14:00
| Agargaon | 137 | 5:00 | 132 | 10:00 | Gallamari | 135 | 0.25 | 127 | 13:00
| Satmosjid | 137 | 5:00 | 130 | 12:00 | Magura | 138 | 6:00 | 126 | 0.875
| Tongi | 139 | 1:00 | 134 | 15:00 | Narail | 137 | 0.29167 | 125 | 0.75
| Kabirpur | 135 | 20:00 | 128 | 19:00 | Chuadanga | 133 | 1:00 | 121 | 0.75
| Basundhara | 136 | 1:00 | 130 | 16:00 | Barisal(N) | 141 | 7:00 | 129 | 0.8125
| Manikganj | 140 | 6:00 | 130 | 13:00 | Barisal (S) | 138 | 5:00 | 128 | 22:00
| Joydevpur | 140 | 19:30 | 133 | 12:00 | Patuakhali(S) | 140 | 0.041667 | 126 | 0.875
| New Tongi | 138 | 1:00 | 132 | 8:00 | Bhandaria | 136 | 0.20833 | 124 | 0.875
| Kodda | 134 | 18:00 | 126 | 4:00 | Borguna | 138 | 0.29167 | 128 | 0.95833
| Dhamrai | 138 | 6:00 | 131 | 12:00 | Jhenaidah(230kV S/S) | 138 | 4:00 | 128 | 18:00
| Rajendrapur | 133 | 1:00 | 125 | 9:00 | Ishurdi | 137 | 6:00 | 132 | 21:00
| Valuka | 122 | 7:00 | 110 | 19:30 | Ruppur Paromanobik | 136 | 7:00 | 132 | 15:00
| Tangail | 134 | 3:00 | 122 | 19:30 | Natore | 135 | 6:00 | 130 | 18:30
| Mymensing | 126 | 6:00 | 114 | 1:00 | Bogra | 133 | 11:00 | 126 | 21:00
| Kishorganj | 129 | 8:00 | 117 | 19:30 | Noagaon | 130 | 6:00 | 120 | 21:00
| Netrokona | 121 | 8:00 | 109 | 1:00 | Rajshahi | 134 | 6:00 | 129 | 15:00
| Jamalpur | 132 | 5:00 | 120 | 1:00 | Rajshahi New | 135 | 7:00 | 128 | 15:00
| Sherpur | 130 | 17:00 | 117 | 1:00 | C.Nawabganj | 133 | 7:00 | 126 | 14:00
| Srimongal | 138 | 17:00 | 132 | 23:00 | Amnura | 133 | 7:00 | 126 | 13:00
| Shahjibazar | 136 | 7:00 | 130 | 19:00 | Pabna | 135 | 6:00 | 120 | 18:30
| Fenchuganj | 137 | 8:00 | 133 | 1:00 | Shahjadpur | 137 | 6:00 | 133 | 20:00
| Khulawara | 134 | 5:00 | 132 | 1:00 | Serajganj | 135 | 6:00 | 127 | 20:00
| Sylhet | 132 | 5:00 | 129 | 23:00 | Niyamatpur | 130 | 7:00 | 117 | 21:00
| Chatak | 133 | 6:00 | 127 | 21:00 | Joypurhat | 132 | 7:00 | 120 | 21:00
| Sunamganj | 128 | 6:00 | 122 | 21:00 | Sherpur(Bogura) | 134 | 7:00 | 126 | 20:00
| Biani Bazar | 132 | 8:00 | 126 | 1:00 | Mohastangor | 133 | 7:00 | 125 | 1:00
| Comilla(s) | 127 | 6:00 | 123 | 11:00 | Bangura | 137 | 6:00 | 130 | 20:00
| Comilla(n) | 139 | 7:00 | 136 | 21:00 | Rangpur | 132 | 15:00 | 116 | 1:00
| Chandpur | 140 | 11:00 | 134 | 21:00 | Lalmonirhat | 131 | 16:00 | 119 | 1:00
| Feni | 137 | 18:00 | 131 | 1:00 | Saidpur | 132 | 6:00 | 122 | 1:00
| Chowmuhani | 133 | 17:00 | 130 | 1:00 | Purbasadipur | 131 | 7:00 | 115 | 1:00
| Ashuganj | 139 | 8:00 | 134 | 18:00 | Thakurgaon | 132 | 7:00 | 115 | 3:00
| Daudkandi | 137 | 18:00 | 130 | 12:00 | Palashbari | 131 | 16:00 | 120 | 1:00
| B.Baria | 134 | 6:00 | 127 | 1:00 | Barapukuria | 134 | 7:00 | 122 | 1:00
| Ramganj | 135 | 13:00 | 130 | 21:00 | Panchagar | 134 | 0.29167 | 118 | 0.041667
| Chaddagram | 137 | 18:00 | 132 | 3:00 | Joldhaka | 129 | 0.66667 | 116 | 0.041667
| PHP | 136 | 17:00 | 130 | 2:00 | Kurigram | 130 | 0.58333 | 116 | 0.041667
| Kochua | 137 | 7:00 | 133 | 21:00 | Mithapukur | 133 | 0.29167 | 121 | 0.041667
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-10-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 110 | 8664 | 3726 | 12390 |  |  |  | QF-LDC-11
0:30 | 62 | 8143.5 | 3473 | 11616.5 | Date: | 2021-10-16
1:00 | 14 | 7623 | 3220 | 10843
1:30 | 22 | 7588 | 3227.5 | 10815.5
2:00 | 30 | 7553 | 3235 | 10788
2:30 | 36 | 7459 | 3181.5 | 10640.5 | [5 empty] | Gen. at Eve. Peak | 12829 | 12829 MW (19:00 )
3:00 | 42 | 7365 | 3128 | 10493 | [6 empty] | 19:00
3:30 | 88 | 7277 | 3141 | 10418 | [5 empty] | Gen. at Day Peak | 10815 | 10815 MW (12:00 )
4:00 | 134 | 7189 | 3154 | 10343 | [6 empty] | 12:00
4:30 | 144 | 7133.5 | 3137.5 | 10271 | [5 empty] | Highest Generation | 12829
5:00 | 154 | 7078 | 3121 | 10199 | [6 empty] | 19:00
5:30 | 178 | 6845 | 3007.5 | 9852.5
6:00 | 202 | 6612 | 2894 | 9506
6:30 | 176 | 6452.5 | 2834.5 | 9287
7:00 | 150 | 6293 | 2775 | 9068
7:30 | 142 | 6333.5 | 2741.5 | 9075
8:00 | 134 | 6374 | 2708 | 9082
8:30 | 148 | 6531 | 2742.5 | 9273.5
9:00 | 162 | 6688 | 2777 | 9465
9:30 | 168 | 6860.5 | 2799.5 | 9660
10:00 | 174 | 7033 | 2822 | 9855
10:30 | 152 | 7168 | 2902 | 10070
11:00 | 130 | 7303 | 2982 | 10285
11:30 | 90 | 7531 | 3019 | 10550
12:00 | 50 | 7759 | 3056 | 10815
12:30 | 27 | 7885.5 | 3106.5 | 10992
13:00 | 4 | 8012 | 3157 | 11169
13:30 | 14 | 8085 | 3158 | 11243
14:00 | 24 | 8158 | 3159 | 11317
14:30 | 41 | 8242.5 | 3241.5 | 11484
15:00 | 58 | 8327 | 3324 | 11651
15:30 | 97 | 8172.5 | 3224.5 | 11397
16:00 | 136 | 8018 | 3125 | 11143
16:30 | 118 | 7840.5 | 3045.5 | 10886
17:00 | 100 | 7663 | 2966 | 10629
17:30 | 115 | 8300.5 | 3207.5 | 11508
18:00 | 130 | 8938 | 3449 | 12387
18:30 | 146 | 8975 | 3633 | 12608
19:00 | 162 | 9012 | 3817 | 12829
19:30 | 128 | 8895 | 3820 | 12715
20:00 | 132 | 8806 | 3851 | 12657 |  |  |  | Executive Engineer
20:30 | 147 | 8764.5 | 3875 | 12639.5 |  |  |  | Network Operation Division
21:00 | 162 | 8723 | 3899 | 12622
21:30 | 111.5 | 8725 | 3882.5 | 12607.5
22:00 | 61 | 8727 | 3866 | 12593 |  |  |  |  | Page 6 of 7
22:30 | 56.5 | 8721 | 3823.5 | 12544.5
23:00 | 52 | 8715 | 3781 | 12496
23:30 | 81 | 8689.5 | 3753.5 | 12443
24:00 | 110 | 8664 | 3726 | 12390
12829 MW (19:00 )
10815 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-16 |  | Energy |  | 264131442
[13 empty] | 2021-10-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4384 | 706 | 2298 | 0 | 3425 | 649 | 159 | 180 | 443 | 146 | 0 | 0
0:30 | 4367.5 | 706 | 2181.5 | 0 | 3023 | 599 | 159.5 | 150 | 292 | 138 | 0 | 0 | Date: | 2021-10-16
1:00 | 4351 | 706 | 2065 | 0 | 2621 | 549 | 160 | 120 | 141 | 130 | 0 | 0
1:30 | 4361.5 | 706 | 2109 | 0 | 2572 | 549 | 160 | 120 | 109 | 129 | 0 | 0 | [8 empty] | Total Energy | 264.1314 | Total Energy Gen 264.131 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 264.131 MKWHr
2:00 | 4372 | 706 | 2153 | 0 | 2523 | 549 | 160 | 120 | 77 | 128 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4369 | 704.5 | 2166 | 0 | 2406 | 549.5 | 160 | 120 | 38.5 | 127 | 0 | 0 | [8 empty] | Energy Requirement | 264.1314
3:00 | 4366 | 703 | 2179 | 0 | 2289 | 550 | 160 | 120 | 0 | 126 | 0 | 0
3:30 | 4368.5 | 703 | 2202 | 0 | 2190.5 | 549 | 160 | 120 | 0 | 125 | 0 | 0 | [6 empty] | Shortage
4:00 | 4371 | 703 | 2225 | 0 | 2092 | 548 | 160 | 120 | 0 | 124 | 0 | 0
4:30 | 4280 | 703 | 2185 | 0 | 2141 | 559 | 160 | 120 | 0 | 123 | 0 | 0
5:00 | 4189 | 703 | 2145 | 0 | 2190 | 570 | 160 | 120 | 0 | 122 | 0 | 0
5:30 | 4072 | 703.5 | 2116 | 0 | 1997.5 | 565 | 160 | 120 | 0 | 118 | 0.5 | 0
6:00 | 3955 | 704 | 2087 | 0 | 1805 | 560 | 160 | 120 | 0 | 114 | 1 | 0
6:30 | 3905.5 | 704 | 2061.5 | 0 | 1668.5 | 545 | 160.5 | 120 | 0 | 110 | 12 | 0 |  |  |  |  | Coal
7:00 | 3856 | 704 | 2036 | 0 | 1532 | 530 | 161 | 120 | 0 | 106 | 23 | 0
7:30 | 3850 | 703.5 | 2055 | 0 | 1522.5 | 524.5 | 161.5 | 120 | 0 | 108 | 30 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3844 | 703 | 2074 | 0 | 1513 | 519 | 162 | 120 | 0 | 110 | 37 | 0
8:30 | 3837 | 703.5 | 2146 | 0 | 1618 | 518.5 | 162 | 120 | 0 | 114 | 54.5 | 0
9:00 | 3830 | 704 | 2218 | 0 | 1723 | 518 | 162 | 120 | 0 | 118 | 72 | 0
9:30 | 3873 | 703.5 | 2246.5 | 0 | 1833 | 519 | 162 | 120 | 0 | 120 | 83 | 0
10:00 | 3916 | 703 | 2275 | 0 | 1943 | 520 | 162 | 120 | 0 | 122 | 94 | 0
10:30 | 3990.5 | 703 | 2236 | 0 | 2116.5 | 519 | 160.5 | 120 | 0 | 126 | 98.5 | 0
11:00 | 4065 | 703 | 2197 | 0 | 2290 | 518 | 159 | 120 | 0 | 130 | 103 | 0
11:30 | 4070 | 703.5 | 2187.5 | 0 | 2533 | 538 | 158 | 120 | 0 | 133 | 107 | 0
12:00 | 4075 | 704 | 2178 | 0 | 2776 | 558 | 157 | 120 | 0 | 136 | 111 | 0
12:30 | 4073 | 703.5 | 2157 | 0 | 2948 | 588.5 | 157 | 120 | 0 | 138 | 107 | 0
13:00 | 4071 | 703 | 2136 | 0 | 3120 | 619 | 157 | 120 | 0 | 140 | 103 | 0
13:30 | 4071 | 703 | 2136 | 0 | 3120 | 619 | 157 | 120 | 0 | 140 | 103 | 0
14:00 | 4071 | 703 | 2136 | 0 | 3120 | 619 | 157 | 120 | 0 | 140 | 103 | 0
14:30 | 4080 | 703.5 | 2155 | 0 | 3291 | 598.5 | 157 | 120 | 75 | 145 | 85 | 0
15:00 | 4089 | 704 | 2174 | 0 | 3462 | 578 | 157 | 120 | 150 | 150 | 67 | 0
15:30 | 4039 | 704.5 | 2127 | 0 | 3304 | 577.5 | 157.5 | 120 | 167 | 147 | 53.5 | 0
16:00 | 3989 | 705 | 2080 | 0 | 3146 | 577 | 158 | 120 | 184 | 144 | 40 | 0
16:30 | 3995.5 | 704.5 | 2021 | 0 | 2934 | 577 | 158.5 | 120 | 214 | 139 | 22.5 | 0
17:00 | 4002 | 704 | 1962 | 0 | 2722 | 577 | 159 | 120 | 244 | 134 | 5 | 0
17:30 | 4091 | 704 | 2098.5 | 231 | 2980.5 | 587 | 159.5 | 137.5 | 370.5 | 146 | 2.5 | 0
18:00 | 4180 | 704 | 2235 | 462 | 3239 | 597 | 160 | 155 | 497 | 158 | 0 | 0
18:30 | 4266 | 704.5 | 2212 | 268.5 | 3506.5 | 626.5 | 160.5 | 185 | 522.5 | 156 | 0 | 0
19:00 | 4352 | 705 | 2189 | 75 | 3774 | 656 | 161 | 215 | 548 | 154 | 0 | 0
19:30 | 4320 | 704 | 2220 | 0 | 3778 | 658 | 161 | 215 | 503 | 156 | 0 | 0
20:00 | 4334 | 704 | 2251 | 0 | 3663 | 658 | 161 | 215 | 515 | 156 | 0 | 0
20:30 | 4356.5 | 704.5 | 2281 | 0 | 3613.5 | 668 | 161 | 215 | 484 | 156 | 0 | 0
21:00 | 4379 | 705 | 2311 | 0 | 3564 | 678 | 161 | 215 | 453 | 156 | 0 | 0
21:30 | 4369.5 | 709.5 | 2294 | 0 | 3565.5 | 678.5 | 161 | 215.5 | 459 | 155 | 0 | 0
22:00 | 4360 | 714 | 2277 | 0 | 3567 | 679 | 161 | 216 | 465 | 154 | 0 | 0
22:30 | 4360.5 | 714 | 2281.5 | 0 | 3531 | 669 | 157 | 216 | 463.5 | 152 | 0 | 0
23:00 | 4361 | 714 | 2286 | 0 | 3495 | 659 | 153 | 216 | 462 | 150 | 0 | 0
23:30 | 4372.5 | 710 | 2292 | 0 | 3460 | 654 | 156 | 198 | 452.5 | 148 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.5° C
24:00 | 4384 | 706 | 2298 | 0 | 3425 | 649 | 159 | 180 | 443 | 146 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 264.131 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 264.131 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 87 | 87 | 87 | 84 | 82 | 82 | 82 | 82 | 83 | 84 | 85 |  | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 1979400
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 69 | 75 | 180800
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 150 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [13 empty] | 11 | 25 | 25 | 25 | 25 |  | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 192121
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 |  |  | 5 | 7 | 10 | 8 | 15 | 7 | 6 | [10 empty] | 72360
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [15 empty] | 34 | 34 | 102 |  | 102 | 102 | 102 | 88 | 102 | 102 | 102 | 730450
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 38 | 78 | 105 | 105 | 105 | 105 | 105 | 51 | 56 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1896036
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 150 |  | 30 | [6 empty] | 138624
14 | Titas 50 MW Peaking PP | [17 empty] | 47 |  | 50 | [5 empty] | 0 | 75728
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [6 empty] | 31 | 36 | 36 | 36 | 94 | 95 | 95 | 95 | 94 | 33 | [10 empty] | 703000
17 | Siddhirganj 335 MW CCPP | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5848693
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 95 | 45 | 45 | 76 | 90 | 90 | 90 | 90 | 90 | 135 | 280 | 296 | 298 | 298 | 298 | 298 | 298 |  | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 4860107
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 685818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 280 | 280 | 280 | 280 | 265 | 265 | 255 |  | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 6037855
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2629676
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 13 | 23 | 26 | 26 | 23 | 26 | 26 | 26 |  | 26 | 26 | 26 | 23 | 26 | 26 | 26 | 547776
33 | Ashuganj 225 MW CCPP | 213 | 214 | 214 | 213 | 215 | 215 | 181 | 181 | 183 | 188 | 209 | 207 | 209 | 207 | 206 | 210 | 208 | 207 |  | 208 | 210 | 213 | 211 | 213 | 213 | 212 | 5039000
34 | Ashuganj 450 MW CCPP(South) | 280 | 290 | 280 | 280 | 280 | 280 | 275 | 295 | 310 | 285 | 295 | 305 | 310 | 300 | 295 | 300 | 300 | 315 |  | 300 | 305 | 305 | 310 | 305 | 305 | 305 | 7204000
| Ashuganj 450 MW CCPP(North) | 260 | 265 | 260 | 260 | 260 | 260 | 270 | 300 | 270 | 345 | 310 | 315 | 325 | 305 | 325 | 325 | 300 | 295 |  | 280 | 280 | 280 | 315 | 290 | 290 | 290 | 7359900
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 53 | 53 | 53 | 54 | 54 | 54 | 53 | 53 | 50 | 50 | 52 | 52 | 51 | 47 | 49 | 50 |  | 50 | 50 | 49 | 48 | 51 | 52 | 55 | 1235040
36 | Chandpur 150 MW CCPP | 48 | 50 | 50 | 51 | 52 | 49 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 48 | 50 |  | 48 | 50 | 50 | 51 | 48 | 50 | 50 | 1172950
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 340 | 340 | 340 | 191 | 0 | [8 empty] | 10 | 30 | 67 | 216 |  | 383 | 370 | 378 | 371 | 372 | 372 | 372 | 4214790
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6155050
41 | Haripur 360MW CCPP(HPL) | 331 | 332 | 333 | 331 | 332 | 315 | 272 | 272 | 327 | 331 | 322 | 322 | 322 | 322 | 322 | 317 | 280 | 322 |  | 322 | 327 | 331 | 337 | 337 | 332 | 332 | 7724000
42 | RPCL 210MW CCPP | 203 | 206 | 207 | 209 | 212 | 212 | 207 | 205 | 205 | 202 | 202 | 191 | 165 | 163 | 165 | 168 | 174 | 170 |  | 170 | 171 | 174 | 180 | 181 | 185 | 197 | 4455040
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 12 | 26 | 39 | 50 | 53 | 56 | 53 | 46 | 35 | 19 | 3 | [9 empty] | 392660
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 44 | 44 | 44 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1024000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 40 | 42 | 42 | 41 | 41 | 41 | 41 | 985920
46 | Shajibazar 330 MW CCPP | 160 | 160 | 161 | 160 | 160 | 162 | 162 | 161 | 159 | 157 | 157 | 154 | 155 | 155 | 155 | 154 | 157 | 155 |  | 159 | 161 | 160 | 161 | 160 | 160 | 160 | 3550000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 57 | 57 | 62 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 61 | 60 | 58 |  | 59 | 59 | 59 | 59 | 59 | 59 | 56 | 1418880
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 84 | 81 | 77 | 79 | 79 | 78 | 82 | 83 | 83 |  | 83 | 83 | 84 | 84 | 84 | 84 | 84 | 1939200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 205 | 178 | 179 | 179 | 220 | 220 | 220 | 220 | 219 | 214 | 214 | 215 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5158290
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 382000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 222120
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 47 | 47 | 47 | 47 | 44 |  | 44 | 47 | 47 | 47 | 47 | 47 | 47 | 1120200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 492345
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 290 | 290 | 280 | 260 | 270 | 290 | 290 | 320 | 305 | 290 | 300 | 300 | 300 | 280 | 275 | 280 |  | 270 | 285 | 285 | 280 | 290 | 290 | 300 | 7133000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 298 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7686400
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1121430
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 0 | [9 empty] | 4 | 22 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 330480
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  |  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 358512
61 | Narshingdi 22 MW PP (Doreen) | [7 empty] | 16 | 19 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 321336
62 | Tangail 22 MW PP (Doreen) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 |  | 19 | 19 | 19 | 17 | 19 | 19 | 19 | 449568
63 | Impoprt (Tripura) | 130 | 128 | 126 | 124 | 122 | 114 | 106 | 110 | 118 | 122 | 130 | 136 | 140 | 146 | 150 | 144 | 134 | 158 |  | 154 | 156 | 156 | 156 | 154 | 150 | 146 | 3245760
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 36 | 6 | 4 | 7 | 5 | 4 | 9 | 2 | 3 | 6 | 10 | 3 |  | 9 | 9 | 18 | 30 | 30 | 30 | 32 | 569280
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 21 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509688
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 11 | 11 |  | 8 | 8 |  |  | 8 | 8 | 10 | 177660
67 | Jangalia 33MW PP (Summit) | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 10 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 759500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 14 |  |  |  |  | 18 | 18 | 18 | 18 | 6 | 18 |  | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 374190
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 22 | 29 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 20 |  | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 653580
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 812100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 33 | 33 | 33 | 25 | 25 | 695600
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 6 | 0 | [7 empty] | 17 | 51 | 80 | 80 | 58 | 52 | 80 |  | 80 | 86 | 52 | 35 | 52 | 52 | 52 | 807120
| Chowmuhani 113 MW | 47 | 49 | 49 | 48 | 49 | 48 | 49 | 49 | 48 | 47 | 43 | 48 | 48 | 48 | 49 | 48 | 48 | 57 |  | 87 | 96 | 94 | 96 | 96 | 96 | 65 | 1422120
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 144 | 144 | 108 | 108 | 108 | 108 | 131 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3708000
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 25 | 25 | 25 | 25 | 25 | 42 | 49 | 50 | 50 | 50 |  | 50 | 25 | 25 |  |  |  |  | 449760
79 | Kodda 150MW PP | 16 | 0 | [11 empty] | 48 | 150 | 150 | 98 | 150 |  | 150 | 150 | 150 | 115 | 115 | 115 | 115 | 1260000
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 185280
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 10 | 25 | 34 | 43 | 43 | 43 | 43 | 35 |  | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 691046
| Gazipur 100 MW PP | 50 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 50 | 88 | 72 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1324800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 2 | 3 | 2 | 1 | 1 | 0 | [9 empty] | 24840
| Jodiac Power | 54 | 54 | 54 | 40 | 54 | 35 | 35 | 35 | 35 | 35 | 43 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1201064
| Karnaphuli Power Ltd. | 68 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 76 | 110 | 110 | 110 | 110 | 110 | 51 | 63 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2048253
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 10 | 0 | [9 empty] | 6 | 30 | 26 | 26 | 10 | 10 | 30 |  | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 307076
86 | Meghnaghat CCPP ( Summit) | 250 | 280 | 300 | 270 | 250 | 250 | 270 | 285 | 290 | 295 | 260 | 275 | 278 | 250 | 260 | 240 | 265 | 290 |  | 255 | 270 | 270 | 290 | 275 | 280 | 270 | 6569804
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 69 | 54 | 53 | 53 | 53 | 53 | 57 | 99 | 104 | 104 | 104 | 104 | 93 | 84 | 92 |  | 104 | 104 | 97 | 93 | 93 | 92 | 92 | 2100480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | 0 | [8 empty] | 8 | 10 | 70 | 80 | 80 | 20 | 20 | 70 |  | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 816240
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1225724
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 7 | 0 | [6 empty] | 7 | 32 | 102 | 102 | 102 | 48 | 48 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1147968
95 | Patenga 50MW PP (Baraka) | 36 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 25 | 25 | 25 | 26 | 30 | 44 | 50 |  | 50 | 50 | 50 | 47 | 47 | 47 | 43 | 741600
96 | Chattogram 108 MW PP (ECPV) | [12 empty] | 8 | 20 | 70 | 58 | 32 | 32 |  | 32 | 31 | 20 | 12 | 12 | 12 | 12 | 332160
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1333981
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 30 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1212187
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 110 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3470072
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 15700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1221120
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 154 |  | 20 | [6 empty] | 120401
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 | [8 empty] | 58521
106 | Mymensingh 200 MW PP (United) | 191 | 190 | 190 | 192 | 192 | 193 | 150 | 150 | 150 | 150 | 149 | 163 | 175 | 186 | 185 | 185 | 188 | 179 |  | 190 | 189 | 190 | 190 | 182 | 191 | 180 | 4308000
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 98 |  | 25 | [6 empty] | 103725
114 | Kodda 149 MW PP Unit-1 (Summit) | 88 | 86 | 67 | 52 | 50 | 50 | 50 | 50 | 85 | 113 | 131 | 131 | 133 | 132 | 132 | 132 | 131 | 132 |  | 131 | 131 | 131 | 126 | 117 | 112 | 110 | 2507760
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 70 | 40 | 40 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 78 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1995840
116 | Chandpur 200MW (Desh energy) | 120 | 120 | 120 | 120 | 120 | 100 | 68 | 68 | 68 | 68 | 84 | 160 | 200 | 200 | 200 | 200 | 136 | 150 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3613440
117 | Ashuganj 150MW PP (Midland) | 125 | 125 | 130 | 135 | 130 | 135 | 100 | 100 | 110 | 115 | 112 | 112 | 113 | 123 | 118 | 120 | 122 | 123 |  | 125 | 126 | 122 | 132 | 135 | 130 | 125 | 2954036
118 | Bibiyana-III 400 MW CCPP | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 321 |  | 321 | 321 | 321 | 320 | 320 | 320 | 322 | 7753000
| Jamalpur 115 MW PP (United) | 78 | 78 | 78 | 78 | 78 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 98 | 1606800
| Anwara 300 MW PP (United) | 305 | 305 | 305 | 251 | 250 | 196 | 140 | 139 | 175 | 295 | 305 | 304 | 304 | 305 | 305 | 305 | 232 | 290 |  | 305 | 305 | 304 | 305 | 305 | 305 | 305 | 6463418
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 70 | 40 | 40 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 2288640
| Anlima Energy Ltd. | 108 | 90 | 53 | 53 | 53 | 53 | 35 | 35 | 35 | 45 | 86 | 94 | 97 | 97 | 97 | 97 | 72 | 81 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 1987200
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 8 | 23 | 27 | 31 | 33 | 30 | 25 | 18 | 9 | 1 | [9 empty] | 208157
120 | Eastern Zone Total | 7623 | 7553 | 7365 | 7189 | 7078 | 6612 | 6293 | 6374 | 6688 | 7033 | 7303 | 7759 | 8012 | 8158 | 8327 | 8018 | 7663 | 8938 |  | 9012 | 8895 | 8806 | 8723 | 8727 | 8715 | 8664 | 186714766
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 4 |  | 11 | 15 | 26 |  |  |  |  | 34690
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 155 |  | 215 | 215 | 215 | 215 | 216 | 216 | 180 | 3540480
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 1 | 25 | 60 |  | 75 | 35 | 35 | 73 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1169280
130
131
132 | United Payra Power Ltd. | 54 | 54 | 54 | 0 | 35 | 17 | [7 empty] | 10 | 54 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 584400
133 | Bhola Nutan Biddut BD LTD (GAS) | 0 | 38 | 32 | 109 | 106 | 108 | 108 | 107 | 106 | 106 | 105 | 80 | 102 | 130 | 205 | 182 | 151 | 201 |  | 220 | 220 | 221 | 221 | 222 | 222 | 221 | 323296
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 82 | 82 | 82 | 82 | 82 | 82 | 84 | 83 | 81 | 82 | 83 | 82 | 54 | 52 | 12 | 11 | 11 | 11 |  | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 1269835
| Bhola 225 MW CCPP | [13 empty] | 15 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 621000
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 25 | 24 | 20 | 20 | 16 | 18 | 18 | 19 | 21 | 23 | 23 | 25 | 25 | 25 | 24 | 31 |  | 32 | 33 | 34 | 34 | 34 | 35 | 34 | 605344
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 10 | [8 empty] | 31680
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 106272
146 | Bheramara HVDC | 706 | 706 | 703 | 703 | 703 | 704 | 704 | 703 | 704 | 703 | 703 | 704 | 703 | 704 | 704 | 705 | 704 | 704 |  | 705 | 704 | 704 | 705 | 714 | 714 | 706 | 17038545
147 | Bheramara 410 MW CCPP | 360 | 360 | 360 | 360 | 330 | 330 | 330 | 330 | 330 | 330 | 405 | 370 | 380 | 360 | 360 | 360 | 360 | 380 |  | 360 | 360 | 360 | 370 | 360 | 360 | 360 | 8834976
148 | Payra 1320 MW | 470 | 470 | 470 | 470 | 490 | 480 | 450 | 440 | 440 | 440 | 440 | 480 | 540 | 540 | 500 | 500 | 500 | 520 |  | 580 | 580 | 580 | 600 | 600 | 580 | 570 | 13208500
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 80 | 78 | 80 | 80 | 80 | 79 | 78 | 80 | 78 | 78 | 79 | 77 | 78 | 77 | 77 | 77 |  | 76 | 78 | 78 | 78 | 79 | 79 | 79 | 1866763
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 373246
| Sirajgonj 6.55 MW Solar | [15 empty] | 1 | 0 | [9 empty] | 2460
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 130 | 123 | 126 | 121 | 118 | 124 | 118 | 114 | 118 | 104 |  | 113 | 113 | 114 | 115 | 116 | 115 | 120 | 3180400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 168 | 177 | 170 | 170 | 160 | 159 | 158 | 166 | 196 | 200 | 195 | 185 | 187 | 190 | 177 | 175 | 178 | 176 |  | 176 | 178 | 178 | 179 | 178 | 179 | 185 | 4485073
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 160 | 142 | 156 | 160 | 161 | 130 | 70 | [19 empty] | 1137991
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 375 | 410 | 407 | 408 | 365 | 340 | 310 | 343 | 401 | 414 | 403 | 412 | 408 | 410 | 407 | 379 | 303 | 401 |  | 372 | 364 | 380 | 407 | 374 | 382 | 390 | 9247672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 5 |  | 28 | 28 | 28 | 41 | 39 | 38 | 34 | 186678
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 22 | 21 | 22 | 22 | 22 | 21 | 21 | 19 | 19 | 18 | 17 | 17 | 17 | 17 | 19 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 457200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 205758
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 27 | 27 | 27 | 27 | 27 |  |  | 124980
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 32 |  | 43 | 43 | 43 | 43 | 43 |  |  | 210687
167 | Katakhali 50 MW Peaking PP | [17 empty] | 27 |  | 31 | 31 | 32 | 32 | 32 | 30 | 15 | 172827
168 | Santahar 50 MW Peaking PP | 33 | 32 | 0 | [14 empty] | 20 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 283720
169 | Natore 52 MW PP (Rajlanka) | 25 | 25 | 0 | [9 empty] | 8 | 28 | 52 | 52 | 8 | 16 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 565920
170 | Chapainawabganj 100 MW Peaking PP | 92 | 45 | 0 | [13 empty] | 54 | 92 |  | 92 | 93 | 93 | 93 | 93 | 93 | 93 | 833992
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 42 | 76 | 113 | 113 | 113 | 113 | 50 | 50 | 65 |  | 111 | 113 | 113 | 113 | 113 | 113 | 113 | 2269440
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 55 | 100 | 113 | 113 | 113 | 113 | 113 | 50 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2277024
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 63 | 100 | 75 | 70 | 70 | 90 | 113 | 113 | 113 | 113 | 113 | 54 | 80 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2125401
177 | Sympa Solar Power 8MW | [6 empty] | 1 |  | 4 | 6 | 6 | 7 | 7 | 7 | 5 | 3 | 1 | [9 empty] | 41146
178
178