## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-18 | Monday
|  |  | Date (day): | 2021-10-18 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13662.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14762 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-17 | 2021-10-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 397 | 390 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 262 | 301 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 300 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 21 | 21 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 185 | 185 | 200 | 200 | 210
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 296 | 298 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 131 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 46 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 93 | 92 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 155 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 17 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2910 | 3194 | 3518 | 3810 | 1103 | 810
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 17 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 8 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 158 | 161 | 160 | 160 | 70 |  | Low water level & #2 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 90 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 51 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 50 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 16 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 20 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 15 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 304 | 287 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 93 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 79 | 108 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1223 | 1317 | 1474 | 1550 | 135 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 110 | 80 | 110 | 110 | 25 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 191 | 210 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 330 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 300 | 310 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 23 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 54 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 117 | 130 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 50 | 50 | 50 |  | 113 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 152 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 0 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 43 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 22 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 52 | 80 | 80 |  | 34 | Engine problem
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 43 | 95 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1735 | 1865 | 2027 | 2273 | 457 | 231
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 165 | 168 | 200 | 202 | 0
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 8 | 0 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 160 | 190 | 150 | 150 |  | 50 | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 38 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 57 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 13 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 462 | 518 | 567.6 | 518 | 0 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 160 | 160 | 160 |  | 170 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 57 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 81 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 221 | 220 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24 |  | 1
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 321 | 321 | 321 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1776 | 1820 | 1867 | 1867 | 142 | 346
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 706 | 712 | 720 | 720
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 33 |  | 21 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 385 | 370 | 400 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 86 | 37 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1297 | 1239 | 1500 | 1723 | 0 | 90
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 0 | 0 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 30 | 22 | 42 | 42 | 78 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 410 | 450 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 221 | 150 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 724 | 758 | 1022 | 1242 | 78 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 28 | 28 | 50 |  | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 123 | 120 | 144 | 144 |  |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 192 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | under maint
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 412 | 419 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 970 | 1201 | 1486 | 1586 | 220 | 73
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 77 | 75 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 98 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 180 | 188 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 11277 | 12100 | 13662.6 | 14762 | 2135 | 2763
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10892.0908 | 11687 | 13196.265 | 14258.14
| A. |  | 2021-10-17 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12100 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9764 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12100 | MW
| 3 | Day peak Generation : |  |  | 11277 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11687 | MW
| 4 | Evening peak Generation : |  |  | 12100 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 268.1632 | MKWHr | By Solar | 0.63319 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 151.5598 | MKWHr |  | By Oil: | 78.2006 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.7254 | MKWHr |  | By Hydro: | 3.7732 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2135 | MW | Dhaka | 4342 | 4342 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2763 | MW | Chittagong | 1255 | 1255 |  | 0 |  | 18:00 |  | 136
|  |  |  | Total = |  |  | 4898 | MW | Khulna | 1261 | 1261 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1189.6 | MMCFD |  |  | Rajshahi | 1217 | 1217 |  | 0 |  | 19:00 |  | 132
| 8 | Fuel Cost : | i) Gas : | Taka | 162221429.328 | ii) Oil : | Taka | 594444372.75 | Comilla | 1059 | 1059 |  | 0 |  | 19:30 |  | 136
|  |  | iii) Coal : |  | 63283039.73 | Total | Taka | 819948841.808 | Mymensingh | 1050 | 1050 |  | 0 |  | 20:00 |  | 152
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.25 | MKWHr. | Sylhet | 557 | 557 |  | 0 |  | 21:00 |  | 152
|  | ii) During Peak Demand : |  |  | -146 | MW (E to W) at | 21:00 | hrs | Barisal | 259 | 259 |  | 0 |  | 22:00 |  | 146
|  | iii) Maximum : |  |  | -246 | MW at | 2:00 | hrs | Rangpur | 687 | 687 |  | 0 |  | 23:00 |  | 150
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.1° C |  |  | Total | 11687 | 11687 |  | 0
| B. |  | 2021-10-18 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14762 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
| 4 | Reserve(Generation end) |  |  |  | 2162 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 279.2443 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9287 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0771 | MKWHr. | ii) HVDC Flow at Peak Time |  | 712 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1939 | MKWHr. | iii) Maximum HVDC Flow : |  | 712 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.82 |  | (b) Today: | 104.72 |  | (c) Rule Curve: |  | 107.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 333 |  | 0 | 250 | 260 | 0 | 0 | 42 | 240 | 0 | 0 | 0 | 48 | 48 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 50 | 0 | 44 | 18 | 32 | 110 | 0 | 0 | 290 | 305 | 212 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 33 | 18 | 146 | 207 | 8 | 19 | 0 | 43 | 42 | 47 | 0 | 163 | 160 | 56 | 84 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 295 | 0 | 0 | 182 | 0 | 110 | 0 | 90 | 200 | 127 | 321 | 78 | 90 | 105 | 0 | 304 | 40 | 110 | 52 | 59 | 100 | 320 | 92 | 0 | 155 | 108 | 0 | 17 | 0 |  | 707 | 0 | 360 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 0 | 0 | 52 | 34 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 113 | 0 | 178 | 0 | 12 | 0 | 0 | 0 | 377 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 570 | 222 | 0 | 17 | 0 |  | 8408 | 3548 | 11956 | 4385 | 707 | 2267 | 0 | 3274 | 649 | 158 | 140 | 230 | 146 | 0 | 0 | 104.87
2:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 333 |  | 0 | 250 | 260 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 10 | 0 | 47 | 18 | 32 | 110 | 0 | 0 | 290 | 305 | 212 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 33 | 21 | 144 | 207 | 8 | 19 | 0 | 43 | 42 | 47 | 0 | 163 | 161 | 56 | 84 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 291 | 0 | 0 | 182 | 0 | 110 | 0 | 90 | 200 | 127 | 321 | 79 | 52 | 105 | 0 | 305 | 50 | 110 | 17 | 58 | 100 | 320 | 92 | 0 | 150 | 108 | 0 | 17 | 0 |  | 707 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 114 | 0 | 179 | 0 | 12 | 0 | 0 | 0 | 376 | 105 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 530 | 222 | 0 | 0 | 0 |  | 8241 | 3284 | 11525 | 4386 | 707 | 2266 | 0 | 3068 | 609 | 158 | 120 | 67 | 144 | 0 | 0 | 104.86
3:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 332 |  | 0 | 250 | 270 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 29 | 10 | 0 | 30 | 18 | 32 | 110 | 0 | 0 | 290 | 305 | 212 | 26 | 51 | 26 | 55 | 0 | 51 | 0 | 0 | 25 | 22 | 10 | 33 | 21 | 142 | 208 | 8 | 19 | 0 | 43 | 42 | 47 | 0 | 163 | 160 | 56 | 84 | 0 | 220 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 245 | 0 | 0 | 172 | 0 | 112 | 0 | 90 | 200 | 127 | 321 | 78 | 52 | 105 | 0 | 305 | 54 | 110 | 17 | 57 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 707 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 115 | 0 | 181 | 0 | 12 | 0 | 0 | 0 | 357 | 35 | 0 | 113 | 15 | 100 | 0 | 0 | 113 | 500 | 222 | 0 | 0 | 0 |  | 8126 | 3159 | 11285 | 4395 | 707 | 2246 | 0 | 2910 | 578 | 158 | 120 | 29 | 142 | 0 | 0 | 104.85
4:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 331 |  | 0 | 250 | 270 | 0 | 0 | 30 | 240 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 26 | 18 | 41 | 110 | 0 | 0 | 290 | 305 | 212 | 26 | 49 | 26 | 55 | 0 | 51 | 0 | 0 | 25 | 22 | 10 | 33 | 21 | 138 | 208 | 8 | 19 | 0 | 43 | 42 | 47 | 0 | 130 | 161 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 182 | 0 | 107 | 0 | 90 | 170 | 127 | 321 | 78 | 52 | 105 | 0 | 304 | 54 | 110 | 0 | 58 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 115 | 0 | 181 | 0 | 12 | 0 | 0 | 0 | 346 | 17 | 0 | 113 | 15 | 70 | 0 | 0 | 113 | 500 | 221 | 0 | 0 | 0 |  | 7946 | 3099 | 11045 | 4393 | 706 | 2219 | 0 | 2731 | 579 | 159 | 120 | 0 | 138 | 0 | 0 | 104.84
5:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 331 |  | 0 | 250 | 280 | 0 | 0 | 30 | 240 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 26 | 18 | 41 | 110 | 0 | 0 | 290 | 305 | 213 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 21 | 134 | 209 | 8 | 19 | 0 | 43 | 42 | 44 | 0 | 130 | 161 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 182 | 0 | 107 | 0 | 90 | 120 | 127 | 321 | 78 | 35 | 105 | 0 | 304 | 54 | 110 | 0 | 58 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 116 | 0 | 181 | 0 | 12 | 0 | 0 | 0 | 350 | 17 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 500 | 222 | 0 | 0 | 0 |  | 7809 | 2971 | 10780 | 4397 | 706 | 2197 | 0 | 2487 | 580 | 159 | 120 | 0 | 134 | 0 | 0 | 104.83
6:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 372 | 328 |  | 0 | 250 | 240 | 0 | 0 | 30 | 240 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 26 | 18 | 41 | 110 | 0 | 0 | 290 | 305 | 213 | 26 | 49 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 21 | 124 | 212 | 8 | 19 | 0 | 43 | 42 | 44 | 0 | 130 | 161 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 30 | 0 | 0 | 182 | 0 | 90 | 0 | 90 | 120 | 128 | 321 | 38 | 35 | 68 | 0 | 304 | 54 | 68 | 0 | 58 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 6 | 78 | 0 | 0 | 0 | 0 | 117 | 0 | 180 | 0 | 12 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 500 | 200 | 0 | 0 | 0 |  | 7509 | 2842 | 10351 | 4395 | 706 | 2102 | 0 | 2167 | 578 | 159 | 120 | 0 | 124 | 0 | 0 | 104.82
7:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 371 | 281 |  | 0 | 250 | 280 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 21 | 25 | 26 | 33 | 25 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 38 | 110 | 0 | 0 | 310 | 320 | 193 | 26 | 31 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 17 | 118 | 206 | 8 | 19 | 0 | 43 | 42 | 44 | 0 | 110 | 160 | 61 | 84 | 0 | 186 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 88 | 2 | 90 | 34 | 132 | 321 | 38 | 35 | 51 | 0 | 304 | 54 | 60 | 0 | 57 | 100 | 320 | 92 | 6 | 162 | 53 | 0 | 17 | 7 |  | 705 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 120 | 0 | 185 | 0 | 12 | 0 | 0 | 0 | 375 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 470 | 152 | 0 | 0 | 0 |  | 6941 | 2823 | 9764 | 4140 | 705 | 2084 | 0 | 1873 | 548 | 160 | 120 | 0 | 118 | 16 | 0 | 104.81
8:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 373 | 280 |  | 0 | 250 | 300 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 21 | 25 | 26 | 33 | 25 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 11 | 110 | 0 | 0 | 325 | 335 | 202 | 26 | 32 | 26 | 54 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 17 | 122 | 205 | 8 | 19 | 1 | 43 | 42 | 44 | 0 | 110 | 158 | 60 | 84 | 0 | 186 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 85 | 6 | 90 | 34 | 108 | 322 | 38 | 35 | 51 | 1 | 304 | 40 | 51 | 0 | 59 | 100 | 320 | 92 | 11 | 162 | 53 | 0 | 17 | 15 |  | 706 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 128 | 0 | 201 | 0 | 12 | 0 | 0 | 0 | 402 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 470 | 152 | 0 | 0 | 0 |  | 6961 | 2867 | 9828 | 4217 | 706 | 2096 | 0 | 1825 | 548 | 160 | 120 | 0 | 122 | 34 | 0 | 104.8
9:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 382 | 331 |  | 0 | 250 | 280 | 0 | 0 | 30 | 0 | 0 | 36 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 33 | 25 | 25 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 2 | 110 | 0 | 0 | 350 | 305 | 180 | 26 | 30 | 26 | 53 | 0 | 51 | 0 | 0 | 11 | 22 | 0 | 33 | 17 | 130 | 198 | 8 | 19 | 1 | 43 | 42 | 44 | 0 | 110 | 161 | 61 | 81 | 0 | 220 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 99 | 0 | 0 | 150 | 0 | 115 | 13 | 90 | 75 | 122 | 321 | 38 | 35 | 61 | 2 | 304 | 35 | 51 | 0 | 55 | 100 | 320 | 92 | 21 | 162 | 76 | 0 | 17 | 23 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 135 | 0 | 184 | 0 | 11 | 0 | 0 | 0 | 387 | 17 | 0 | 55 | 0 | 34 | 0 | 2 | 100 | 450 | 152 | 0 | 0 | 2 |  | 7311 | 2865 | 10176 | 4201 | 706 | 2088 | 0 | 2179 | 527 | 161 | 120 | 0 | 130 | 64 | 0 | 104.8
10:00 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 333 | 306 |  | 0 | 250 | 285 | 0 | 0 | 30 | 0 | 0 | 185 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 28 | 33 | 8 | 40 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 2 | 110 | 0 | 0 | 295 | 310 | 186 | 26 | 31 | 26 | 51 | 0 | 43 | 0 | 0 | 25 | 22 | 2 | 33 | 17 | 116 | 186 | 8 | 19 | 2 | 43 | 42 | 41 | 0 | 130 | 158 | 60 | 81 | 0 | 166 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 275 | 0 | 0 | 150 | 0 | 132 | 15 | 90 | 121 | 112 | 321 | 38 | 35 | 84 | 3 | 304 | 35 | 55 | 0 | 47 | 100 | 320 | 92 | 28 | 162 | 99 | 0 | 17 | 21 |  | 705 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 114 | 0 | 176 | 0 | 11 | 0 | 0 | 0 | 417 | 17 | 0 | 99 | 0 | 34 | 0 | 3 | 113 | 450 | 182 | 0 | 0 | 1 |  | 7525 | 2954 | 10479 | 4125 | 705 | 2135 | 0 | 2517 | 527 | 161 | 120 | 0 | 116 | 73 | 0 | 104.79
11:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 394 | 271 |  | 0 | 250 | 275 | 0 | 0 | 30 | 0 | 0 | 150 | 0 | 74 | 16 | 7 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 28 | 33 | 25 | 51 | 0 | 84 | 75 | 115 | 0 | 13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 29 | 18 | 2 | 110 | 0 | 0 | 285 | 305 | 181 | 26 | 30 | 26 | 50 | 0 | 43 | 0 | 0 | 25 | 22 | 2 | 33 | 19 | 120 | 170 | 8 | 19 | 1 | 43 | 42 | 41 | 0 | 130 | 157 | 60 | 80 | 0 | 193 | 18 | 0 | 10 | 295 | 24 | 0 | 0 | 280 | 0 | 0 | 150 | 0 | 132 | 10 | 90 | 170 | 115 | 321 | 38 | 35 | 90 | 2 | 304 | 35 | 80 | 17 | 47 | 100 | 320 | 92 | 27 | 162 | 107 | 0 | 17 | 29 |  | 705 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 117 | 0 | 177 | 0 | 13 | 0 | 0 | 0 | 417 | 65 | 0 | 113 | 0 | 98 | 0 | 4 | 113 | 400 | 221 | 0 | 0 | 1 |  | 7738 | 3078 | 10816 | 4177 | 705 | 2124 | 0 | 2843 | 478 | 159 | 120 | 16 | 120 | 74 | 0 | 104.79
12:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 398 | 262 |  | 0 | 250 | 290 | 0 | 0 | 40 | 0 | 0 | 185 | 0 | 102 | 32 | 10 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 25 | 28 | 33 | 25 | 51 | 0 | 83 | 75 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 50 | 15 | 33 | 18 | 3 | 110 | 0 | 0 | 310 | 325 | 191 | 26 | 30 | 26 | 49 | 0 | 43 | 0 | 0 | 25 | 22 | 2 | 33 | 17 | 132 | 165 | 8 | 19 | 2 | 43 | 42 | 44 | 0 | 130 | 157 | 60 | 83 | 0 | 221 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 296 | 0 | 0 | 160 | 0 | 132 | 8 | 90 | 200 | 117 | 321 | 38 | 46 | 90 | 4 | 304 | 35 | 110 | 17 | 43 | 100 | 320 | 93 | 57 | 155 | 79 | 0 | 17 | 17 |  | 706 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 123 | 0 | 181 | 0 | 30 | 0 | 0 | 0 | 412 | 86 | 0 | 113 | 0 | 98 | 0 | 5 | 113 | 410 | 220 | 0 | 0 | 4 |  | 8106 | 3171 | 11277 | 4345 | 706 | 2147 | 0 | 3048 | 487 | 158 | 120 | 37 | 132 | 97 | 0 | 104.78
13:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 402 | 261 |  | 0 | 250 | 290 | 0 | 0 | 40 | 0 | 0 | 185 | 0 | 102 | 48 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 15 | 25 | 28 | 33 | 33 | 51 | 0 | 82 | 75 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 50 | 47 | 43 | 18 | 3 | 110 | 0 | 0 | 305 | 320 | 193 | 26 | 31 | 23 | 50 | 0 | 43 | 0 | 0 | 31 | 22 | 2 | 33 | 18 | 126 | 151 | 0 | 19 | 2 | 43 | 42 | 47 | 0 | 130 | 157 | 60 | 83 | 0 | 206 | 18 | 0 | 10 | 305 | 24 | 8 | 0 | 298 | 0 | 0 | 168 | 0 | 132 | 7 | 90 | 200 | 118 | 321 | 38 | 88 | 105 | 4 | 304 | 35 | 110 | 51 | 38 | 90 | 320 | 92 | 31 | 162 | 79 | 0 | 17 | 31 |  | 706 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 126 | 0 | 188 | 0 | 32 | 0 | 0 | 0 | 408 | 88 | 0 | 113 | 0 | 106 | 0 | 5 | 113 | 440 | 217 | 0 | 0 | 3 |  | 8212 | 3213 | 11425 | 4325 | 706 | 2155 | 0 | 3181 | 519 | 157 | 120 | 53 | 126 | 83 | 0 | 104.78
14:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 401 | 263 |  | 0 | 250 | 285 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 102 | 48 | 10 | 0 | 0 | 0 | 54 | 37 | 55 | 15 | 25 | 27 | 33 | 25 | 51 | 0 | 81 | 75 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 50 | 51 | 45 | 18 | 2 | 110 | 0 | 0 | 290 | 305 | 180 | 26 | 50 | 23 | 50 | 0 | 51 | 0 | 49 | 40 | 22 | 2 | 33 | 18 | 130 | 148 | 0 | 19 | 2 | 43 | 42 | 47 | 0 | 130 | 157 | 60 | 83 | 0 | 206 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 298 | 0 | 0 | 167 | 0 | 132 | 5 | 90 | 200 | 120 | 321 | 38 | 88 | 105 | 2 | 304 | 21 | 110 | 51 | 39 | 90 | 320 | 92 | 43 | 162 | 99 | 0 | 17 | 17 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 124 | 0 | 186 | 0 | 32 | 0 | 0 | 0 | 412 | 88 | 0 | 113 | 0 | 109 | 0 | 5 | 113 | 440 | 216 | 0 | 0 | 2 |  | 8196 | 3247 | 11443 | 4196 | 706 | 2157 | 0 | 3228 | 520 | 156 | 120 | 154 | 130 | 76 | 0 | 104.77
15:00 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 394 | 262 |  | 0 | 250 | 255 | 0 | 0 | 40 | 0 | 0 | 125 | 0 | 102 | 133 | 34 | 0 | 0 | 0 | 54 | 17 | 17 | 15 | 25 | 27 | 33 | 33 | 51 | 0 | 82 | 75 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 80 | 70 | 45 | 18 | 2 | 135 | 0 | 0 | 325 | 305 | 180 | 26 | 48 | 23 | 47 | 0 | 51 | 0 | 49 | 38 | 22 | 2 | 0 | 6 | 130 | 149 | 0 | 19 | 2 | 43 | 42 | 47 | 0 | 130 | 160 | 61 | 84 | 0 | 220 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 298 | 0 | 0 | 177 | 0 | 132 | 2 | 90 | 200 | 123 | 321 | 38 | 88 | 105 | 0 | 304 | 33 | 110 | 98 | 45 | 90 | 320 | 92 | 39 | 162 | 102 | 0 | 17 | 19 |  | 705 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 16 | 0 | 12 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 126 | 0 | 191 | 0 | 33 | 0 | 0 | 0 | 388 | 94 | 0 | 113 | 0 | 113 | 0 | 3 | 113 | 390 | 204 | 0 | 0 | 2 |  | 8357 | 3198 | 11555 | 4194 | 705 | 2101 | 0 | 3340 | 469 | 157 | 120 | 272 | 130 | 67 | 0 | 104.77
16:00 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 396 | 262 |  | 0 | 250 | 270 | 0 | 0 | 40 | 0 | 0 | 129 | 0 | 102 | 115 | 46 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 27 | 33 | 33 | 51 | 0 | 81 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 50 | 83 | 25 | 18 | 2 | 135 | 0 | 0 | 325 | 305 | 180 | 26 | 50 | 23 | 47 | 0 | 51 | 0 | 49 | 40 | 22 | 2 | 0 | 20 | 128 | 153 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 110 | 159 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 298 | 0 | 0 | 167 | 0 | 132 | 2 | 90 | 155 | 125 | 320 | 38 | 52 | 105 | 0 | 304 | 35 | 107 | 77 | 57 | 90 | 320 | 74 | 11 | 162 | 108 | 0 | 17 | 11 |  | 706 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 6 | 25 | 0 | 17 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 134 | 0 | 174 | 0 | 11 | 0 | 0 | 0 | 408 | 17 | 0 | 70 | 0 | 74 | 0 | 2 | 70 | 300 | 120 | 0 | 0 | 0 |  | 8182 | 2799 | 10981 | 4186 | 706 | 2005 | 0 | 3014 | 377 | 156 | 120 | 262 | 128 | 27 | 0 | 104.76
17:00 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 377 | 262 |  | 0 | 250 | 260 | 0 | 0 | 40 | 0 | 0 | 126 | 0 | 102 | 115 | 50 | 0 | 0 | 0 | 54 | 17 | 17 | 20 | 25 | 28 | 33 | 33 | 51 | 0 | 84 | 75 | 120 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 82 | 25 | 18 | 6 | 135 | 0 | 0 | 295 | 275 | 185 | 26 | 48 | 23 | 52 | 0 | 51 | 0 | 49 | 43 | 0 | 2 | 0 | 20 | 110 | 153 | 0 | 19 | 0 | 43 | 42 | 12 | 0 | 110 | 160 | 56 | 10 | 0 | 156 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 298 | 0 | 0 | 177 | 0 | 131 | 0 | 70 | 120 | 128 | 321 | 38 | 52 | 68 | 0 | 233 | 35 | 68 | 70 | 60 | 70 | 320 | 86 | 2 | 126 | 72 | 0 | 17 | 1 |  | 705 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 2 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 50 | 36 | 0 | 0 | 0 | 15 | 25 | 16 | 17 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 118 | 0 | 167 | 0 | 12 | 0 | 0 | 0 | 383 | 17 | 0 | 50 | 0 | 70 | 0 | 2 | 50 | 260 | 117 | 0 | 0 | 0 |  | 7597 | 2658 | 10255 | 3979 | 705 | 1858 | 0 | 2701 | 335 | 159 | 120 | 283 | 110 | 5 | 0 | 104.76
18:00 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 350 | 292 |  | 0 | 250 | 255 | 0 | 0 | 52 | 0 | 0 | 182 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 17 | 35 | 18 | 25 | 20 | 33 | 17 | 51 | 0 | 84 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 100 | 83 | 34 | 18 | 7 | 80 | 0 | 0 | 320 | 300 | 211 | 26 | 50 | 23 | 54 | 0 | 51 | 0 | 49 | 43 | 22 | 0 | 0 | 22 | 136 | 153 | 0 | 22 | 0 | 43 | 42 | 46 | 0 | 163 | 162 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 280 | 24 | 8 | 20 | 298 | 0 | 30 | 186 | 30 | 132 | 0 | 90 | 152 | 128 | 321 | 114 | 105 | 94 | 0 | 285 | 35 | 85 | 90 | 95 | 100 | 320 | 92 | 0 | 128 | 85 | 0 | 17 | 0 |  | 706 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 50 | 36 | 46 | 27 | 32 | 24 | 25 | 33 | 20 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 94 | 0 | 159 | 0 | 12 | 0 | 0 | 0 | 415 | 17 | 0 | 60 | 0 | 88 | 0 | 0 | 90 | 260 | 120 | 0 | 0 | 0 |  | 8619 | 2875 | 11494 | 4070 | 706 | 2082 | 80 | 3311 | 336 | 159 | 120 | 494 | 136 | 0 | 0 | 104.75
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 396 | 301 |  | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 180 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 100 | 74 | 50 | 0 | 12 | 80 | 0 | 0 | 325 | 305 | 210 | 26 | 50 | 23 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 0 | 22 | 132 | 155 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 59 | 78 | 0 | 220 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 298 | 0 | 0 | 187 | 0 | 131 | 0 | 90 | 180 | 128 | 320 | 115 | 105 | 105 | 0 | 304 | 35 | 96 | 114 | 95 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 705 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 31 | 50 | 34 | 20 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 110 | 0 | 173 | 0 | 12 | 0 | 0 | 0 | 392 | 17 | 0 | 105 | 0 | 113 | 0 | 0 | 113 | 350 | 180 | 0 | 0 | 0 |  | 8797 | 3079 | 11876 | 4211 | 705 | 2185 | 0 | 3569 | 425 | 160 | 120 | 369 | 132 | 0 | 0 | 104.74
19:30 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 396 | 291 |  | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 50 | 0 | 50 | 0 | 12 | 80 | 0 | 0 | 350 | 345 | 207 | 26 | 50 | 23 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 0 | 22 | 136 | 156 | 0 | 22 | 0 | 44 | 42 | 50 | 0 | 163 | 157 | 56 | 81 | 0 | 220 | 18 | 0 | 10 | 330 | 24 | 11 | 0 | 298 | 0 | 0 | 190 | 0 | 131 | 0 | 90 | 180 | 128 | 320 | 115 | 105 | 105 | 0 | 304 | 35 | 96 | 52 | 95 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 31 | 52 | 34 | 20 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 114 | 0 | 183 | 0 | 12 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 360 | 220 | 0 | 0 | 0 |  | 8702 | 3277 | 11979 | 4394 | 706 | 2285 | 0 | 3366 | 435 | 160 | 120 | 377 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 397 | 302 |  | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 50 | 0 | 50 | 18 | 16 | 100 | 0 | 0 | 325 | 305 | 211 | 26 | 50 | 23 | 54 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 0 | 22 | 152 | 167 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 298 | 0 | 0 | 191 | 0 | 132 | 0 | 90 | 180 | 128 | 320 | 115 | 105 | 105 | 0 | 304 | 35 | 92 | 52 | 95 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 712 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 32 | 52 | 34 | 20 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 118 | 0 | 189 | 0 | 13 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 370 | 221 | 0 | 0 | 0 |  | 8703 | 3286 | 11989 | 4386 | 712 | 2271 | 0 | 3365 | 445 | 160 | 120 | 378 | 152 | 0 | 0 | 104.74
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 301 |  | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 50 | 0 | 50 | 18 | 20 | 80 | 0 | 0 | 330 | 300 | 210 | 26 | 50 | 23 | 54 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 0 | 22 | 152 | 168 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 298 | 0 | 0 | 190 | 0 | 131 | 0 | 90 | 200 | 130 | 321 | 115 | 105 | 105 | 0 | 287 | 35 | 93 | 52 | 95 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 712 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 32 | 52 | 34 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 120 | 0 | 192 | 0 | 22 | 0 | 0 | 0 | 419 | 37 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 221 | 0 | 0 | 0 |  | 8714 | 3386 | 12100 | 4375 | 712 | 2289 | 0 | 3388 | 525 | 161 | 120 | 378 | 152 | 0 | 0 | 104.74
22:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 311 |  | 0 | 250 | 265 | 0 | 0 | 55 | 0 | 0 | 180 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 50 | 0 | 19 | 18 | 30 | 80 | 0 | 0 | 325 | 305 | 214 | 26 | 48 | 23 | 54 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 0 | 22 | 146 | 168 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 61 | 81 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 296 | 0 | 0 | 190 | 0 | 131 | 0 | 90 | 200 | 132 | 321 | 115 | 105 | 105 | 0 | 287 | 35 | 107 | 52 | 95 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 712 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 30 | 52 | 34 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 114 | 0 | 186 | 0 | 43 | 0 | 0 | 0 | 393 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 221 | 0 | 0 | 0 |  | 8656 | 3439 | 12095 | 4343 | 712 | 2261 | 0 | 3439 | 537 | 161 | 120 | 376 | 146 | 0 | 0 | 104.73
23:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 333 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 86 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 8 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 10 | 0 | 19 | 18 | 35 | 80 | 0 | 0 | 325 | 305 | 216 | 26 | 50 | 23 | 55 | 0 | 5 | 0 | 0 | 43 | 22 | 8 | 0 | 21 | 150 | 170 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 62 | 81 | 0 | 220 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 298 | 0 | 0 | 190 | 0 | 131 | 0 | 90 | 200 | 41 | 320 | 115 | 105 | 105 | 0 | 287 | 35 | 110 | 17 | 96 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 0 | 0 |  | 712 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 30 | 52 | 34 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 114 | 0 | 185 | 0 | 43 | 0 | 0 | 0 | 398 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 221 | 0 | 0 | 0 |  | 8386 | 3403 | 11789 | 4332 | 712 | 2238 | 0 | 3186 | 517 | 158 | 120 | 376 | 150 | 0 | 0 | 104.73
24:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 394 | 332 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 48 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 8 | 0 | 80 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 10 | 0 | 19 | 18 | 32 | 80 | 0 | 0 | 325 | 305 | 215 | 26 | 50 | 23 | 55 | 0 | 35 | 0 | 0 | 43 | 22 | 8 | 0 | 21 | 142 | 169 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 161 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 220 | 0 | 0 | 190 | 0 | 133 | 0 | 90 | 136 | 130 | 322 | 98 | 105 | 105 | 0 | 285 | 35 | 110 | 17 | 62 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 9 | 0 |  | 705 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 16 | 52 | 34 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 113 | 0 | 189 | 0 | 43 | 0 | 0 | 0 | 403 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 221 | 0 | 0 | 0 |  | 8277 | 3323 | 11600 | 4349 | 705 | 2284 | 0 | 2965 | 518 | 155 | 120 | 362 | 142 | 0 | 0 | 104.73
KWH | 0 | 0 | 0 | 0 | 6538982 | 0 | 0 | 9320440 | 7206000 |  | 0 | 6155500 | 6682880 | 0 | 0 | 1052445 | 1553546 | 0 | 2536000 | 0 | 1600560 | 1547520 | 299783 | 0 | 0 | 0 | 1231920 | 1131222 | 1105537 | 412416 | 600000 | 651060 | 817400 | 724000 | 704160 | 0 | 1965218 | 1808000 | 2700000 | 0 | 220809 | 0 | 0 | 0 | 0 |  | 442800 | 0 | 636624 | 799080 | 516480 | 818400 | 419328 | 448320 | 2570360 | 0 | 0 | 7766000 | 7518000 | 4879000 | 652363 | 1055230 | 554400 | 1264320 | 0 | 1157872 | 0 | 218352 | 794160 | 488628 | 152280 | 474200 | 457730 | 3193920 | 4199680 | 87360 | 450252 | 11000 | 1029000 | 1001400 | 1071000 | 0 | 3445609 | 3557000 | 1405248 | 1859520 | 0 | 4957010 | 383000 | 0 | 249660 | 7196500 | 592455 | 191616 | 10944 | 5876289 | 0 | 16538 | 4159200 | 18457 | 2939040 | 82485 | 2097600 | 3931200 | 2912205 | 7717000 | 1623600 | 1704000 | 2325927 | 20881 | 7120800 | 964068 | 2294980 | 861840 | 1547280 | 2351040 | 7636700 | 2198400 | 293750 | 3863520 | 2347255 | 0 | 415800 | 178403 |  | 17077090 | 0 | 8802144 | 0 | 0 | 3070080 | 0 | 0 | 9600 | 0 | 0 | 1488000 | 178507 | 0 | 0 | 0 | 0 | 289424 | 180065 | 627952 | 25790 | 32173 | 191700 | 550560 | 284410 | 317760 | 0 | 239904 | 1846691 | 0 | 0 | 0 | 0 | 2967700 | 0 | 4577709 | 0 | 463663 | 0 | 0 | 0 | 9358909 | 1239360 | 0 | 2310624 | 67536 | 2140128 | 0 | 26453 | 2353248 | 11878700 | 466565 | 0 | 40800 | 20220 |  | 195039757 | 73123465 | 268163222 | 103384818 | 17077090 | 48174948 | 45939 | 71098979 | 13725391 | 3773218 | 3070080 | 3985647 | 3193920 | 633192 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7258270.02 | 0 | 0 | 9413644.4 | 7422180 |  | 0 | 6709495 | 7417996.8 | 0 | 0 | 8903684.7 | 1615687.84 | 0 | 4387280 | 0 | 14597107.2 | 15227596.8 | 2763999.26 | 0 | 0 | 0 | 8993016 | 8744346.06 | 10900594.82 | 309312 | 450000 | 0 | 0 | 0 | 6809227.2 | 0 | 530608.86 | 488160 | 4887000 | 0 | 2051315.61 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6175252.8 | 7631214 | 4493376 | 6481728 | 528353.28 | 1331510.4 | 3804132.8 | 0 | 0 | 5746840 | 7518000 | 4488680 | 841548.27 | 1213514.5 | 626472 | 1770048 | 0 | 1979961.12 | 0 | 2205355.2 | 7584228 | 620557.56 | 114210 | 829850 | 343297.5 | 23954400 | 4451660.8 | 793228.8 | 571820.04 | 175340 | 1687560 | 1602240 | 1906380 | 0 | 3927994.26 | 3699280 | 2768338.56 | 3551683.2 | 0 | 8575627.3 | 838770 | 0 | 509306.4 | 7268465 | 444341.25 | 145628.16 | 186157.44 | 44424744.84 | 0 | 276515.36 | 21627840 | 308601.04 | 28920153.6 | 964249.65 | 17095440 | 42653520 | 20531045.25 | 7176810 | 14807232 | 16102800 | 20258824.17 | 0 | 53833248 | 8397032.28 | 20172874.2 | 8601163.2 | 13260189.6 | 15657926.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98364038.4 | 0 | 9242251.2 | 0 | 0 | 42551308.8 | 0 | 0 | 100704 | 0 | 0 | 1681440 | 276685.85 | 0 | 0 | 0 | 0 | 2847932.16 | 1829460.4 | 5557375.2 | 198583 | 434978.96 | 1857573 | 5334926.4 | 2758777 | 610099.2 | 0 | 181607.328 | 11135546.73 | 0 | 0 | 0 | 0 | 3472209 | 0 | 6042575.88 | 0 | 695494.5 | 0 | 0 | 0 | 9265319.91 | 12938918.4 | 0 | 21927821.76 | 637539.84 | 16607393.28 | 0 | 292305.65 | 17390502.72 | 52147493 | 0 | 0 | 0 | 0 |  | 618337082.8 | 326380861.568 | 944717944.368 | 106737261.418 | 98364038.4 | 55484167.91 | 771273.84 | 512561763.55 | 63283039.73 | 1018768.86 | 42551308.8 | 38560026.56 | 23954400 | 1431895.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 398 | 262 |  | 0 | 250 | 290 | 0 | 0 | 40 | 0 | 0 | 185 | 0 | 102 | 32 | 10 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 25 | 28 | 33 | 25 | 51 | 0 | 83 | 75 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 50 | 15 | 33 | 18 | 3 | 110 | 0 | 0 | 310 | 325 | 191 | 26 | 30 | 26 | 49 | 0 | 43 | 0 | 0 | 25 | 22 | 2 | 33 | 17 | 132 | 165 | 8 | 19 | 2 | 43 | 42 | 44 | 0 | 130 | 157 | 60 | 83 | 0 | 221 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 296 | 0 | 0 | 160 | 0 | 132 | 8 | 90 | 200 | 117 | 321 | 38 | 46 | 90 | 4 | 304 | 35 | 110 | 17 | 43 | 100 | 320 | 93 | 57 | 155 | 79 | 0 | 17 | 17 |  | 706 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 123 | 0 | 181 | 0 | 30 | 0 | 0 | 0 | 412 | 86 | 0 | 113 | 0 | 98 | 0 | 5 | 113 | 410 | 220 | 0 | 0 | 4 |  | 11277 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 301 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 86 | 75 | 115 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 68 | 50 | 0 | 50 | 18 | 20 | 80 | 0 | 0 | 330 | 300 | 210 | 26 | 50 | 23 | 54 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 0 | 22 | 152 | 168 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 298 | 0 | 0 | 190 | 0 | 131 | 0 | 90 | 200 | 130 | 321 | 115 | 105 | 105 | 0 | 287 | 35 | 93 | 52 | 95 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 712 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 32 | 52 | 34 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 120 | 0 | 192 | 0 | 22 | 0 | 0 | 0 | 419 | 37 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 221 | 0 | 0 | 0 |  | 12100 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 300 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 18 | 15 | 110 | 0 | 0 | 330 | 330 | 210 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 202 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 150 | 100 | 149 | 0 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 80 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 720 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 33 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 28 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 42 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 390 | 300 | 0 | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 16 | 5 | 110 | 0 | 0 | 330 | 310 | 210 | 26 | 50 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 138 | 200 | 8 | 21 | 1.6 | 43 | 42 | 50 | 0 | 163 | 160 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 100 | 100 | 150 | 50 | 149 | 20 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 80 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 720 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 28 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 42 | 50 | 0 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 622 | 150 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 321 | 301 | 0 | 0 | 250 | 270 | 0 | 0 | 15 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 55 | 21 | 25 | 29 | 25 |  | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 325 | 305 | 180 | 26 | 52 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 7 | 118 | 194 | 0 | 19 | 0 | 43 | 42 | 44 | 0 | 110 | 160 | 61 | 81 | 0 | 179 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 19 | 0 | 0 | 100 | 0 | 87 | 8 | 90 | 17 | 117 | 321 | 38 | 0 | 51 | 0 | 284 | 35 | 34 | 0 | 58 | 100 | 320 | 92 | 10 | 162 | 53 | 0 | 17 | 6 | 0 | 706 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 118 | 0 | 162 | 0 | 42 | 0 | 0 | 0 | 328 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 300 | 151 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9764 | 7:00
| Highest Generation |  | 12100 | 21:00
| Day Peak Generation |  | 11277 | 12:00
| Evening Peak Generation |  | 12100 | 21:00
| HVDC Max Flow |  | 712 | 20:00
| HVDC EvPeak Flow |  | 712 | 21:00
| Load factor L.F |  | 92.34%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-18
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11277 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9287 | MW
Evening Peak Generation : |  | 12100 | MW Hour : | 21:00 | Available Max Generation : |  | 14762 | MW
E.P. Demand (at gen end) : |  | 12100 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12600 | MW
Maximum Generation : |  | 12100 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2162 | MW
Total Gen. (MKWH) : |  | 268.1632 | System Load Factor : | 92.34% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -246 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-18
Actual : | 104.72 | Ft.(MSL) , | Rule curve : | 107.6 | Ft.( MSL )
Gas Consumed : | Total = | 1189.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 162221429.328
: |  | Coal : | 63283039.73 | Oil : | 594444372.75 | Total : | 819948841.808
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4522.5188 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1542.0724 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1382.388 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1249.3677 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1128.8902 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 910.9849 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 504.0174 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 234.4123 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 702.6225 |  |  | 0 | 0%
Total | 0 |  | 12177.2741 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Kaliakoir 230 kV Ckt-2 was under shut down from 10:04 to 16:50 for A/M.
b) Chapainawabganj 132/33 kV T1 transformer was shutdown from 08:11 to 15:09 for A/M.
c) Hathazari-Sikalbaha 230 kV Ckt-1 was under shut down from 10:18 to 17:12 for D/W.
d) Mymensing 132/33 kV T1, T2 & T3 transformers tripped at 09:08 showing O/C relays as Y-phase, |  |  |  |  | About 175 MW power interruption occurred under Mymensing S/S
CT of 33 kV Akua by pass feeder and were switched on at 09:25,09:26 & 09:36 respectively. |  |  |  |  | area from 09:08 to 09:25.
e) Ishurdi-Pabna 132 kV Ckt was under shut down from 08:50 to 17:11 for A/M.
f) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:56 to 15:29 for A/M.
g) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 08:26 to 15:37 for A/M.
h) Sherpur 132/33 kV T1 transformer was shutdown from 08:28 to 17:16 for A/M.
i) Sirajganj 132/33 kV T4 transformer was shutdown from 08:20 to 15:35 for A/M.
j) Thakurgaon 132/33 kV T1 transformer was shutdown from 08:25 to 15:40 for A/M.
k) Mogbazar 132/33 kV T2 transformer tripped at 14:31 showing Diff. O/C, E/F relays at 33 kV end
and was switched on at 23:13.
l) Nawabganj 132/33 kV T1 transformer was shutdown from 15:23 to 17:06 due to red hot |  |  |  |  | About 18 MW power interruption occurred under Nawabganj S/S
maintenance at 33 kV PBS feeder. |  |  |  |  | area from 15:23 to 17:06.
m) Sherpur 132/33 kV T5 transformer tripped at 17:30 showing O/C, E/F relays at 33 kV end and
was switched on at
n) Benapole 132/33 kV T1 & T2 transformer tripped at 21:36 showing O/C, E/F, relays at 33 kV |  |  |  |  | About 50 MW power interruption occurred under Benapole S/S
end and was switched on at 22:03. |  |  |  |  | area from 21:36 to 22:03.
o) Mymensing 132/33 kV T3 transformer under shutdown from 22:06 to 23:34 due to changing loop |  |  |  |  | About 45 MW power interruption occurred under Mymensing S/S
at 33 kV Bus. |  |  |  |  | area from 22:06 to 23:34.
p) Ashuganj-Sirajganj 230 kV Ckt-1 & 2 tripped at 22:04 from both end showing Dist. Z1,,Gt relays
and was switched on at 22:17.
q) Maniknagar-Narinda 132 kV Ckt-2 tripped at 07:17(18-10-2021) showing main protection, pilot wire
protection at Maniknagar end & REF at 33 kV Narinda end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 6538982 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 9320440
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 301 | 7206000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6155500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 300 | 6682880 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1052445
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 299783 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 412416
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 2536000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1553546 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1600560
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1231920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1547520
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1131222
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1105537
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1251060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 724000
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 704160
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 5876289
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 16538 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 18457 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 2939040 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1704000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 2198400 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3863520
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178403
| Dhaka area Total |  |  |  | 5560 | 3194 | 68666018
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 220809 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 82485
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 818400
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 161 | 3773218 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2325927
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 636624 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 799080 | Low demand.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2097600 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 419328 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 448320
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 516480 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20881
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 287 | 7120800 | Engine problem
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 964068 | Low demand.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 93 | 2294980 | Engine problem
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2351040
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2347255 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1317 | 29937295
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2570360 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4879000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7766000 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7518000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 554400 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1264320
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 652363 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1157872
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 2912205 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 218352 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1055230 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3931200
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 488628
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 152280
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 3193920
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 474200 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 794160 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 457730 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 10944 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 861840 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 1547280 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 415800 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1865 | 42876084
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 168 | 4199680 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 450252
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 87360 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11000
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 4159200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1623600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 293750
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 442800
| Mymensingh Area Total |  |  |  | 622 | 518 | 11267642
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1029000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1001400 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3445609
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3557000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1071000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 191616
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1405248
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1859520
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 4957010
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 383000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 592455
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7196500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 321 | 7717000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 249660
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7636700 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1820 | 42292718
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 712 | 17077090
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 9600 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3070080 | Low demand.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 8802144 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 37 | 1239360 | Low demand.
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 67536 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1239 | 30265810
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 0 | 178507 | Machine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1488000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 463663 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 450 | 11878700 | Low demand.
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 466565
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 40800 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 758 | 14516235
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 289424 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 180065 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 25790 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 32173 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 191700 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 120 | 2967700 | FGMO
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4577709 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Under maint.
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 9358909 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 284410 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 317760
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239904
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 550560
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 627952 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2310624
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2353248
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 20220
| Rajshahi Area Total |  |  |  | 2179 | 1201 | 24328148
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1846691
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2140128
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26453
| Rangpur Area Total |  |  |  | 605 | 188 | 4013272
| Total |  |  |  | 20934 | 12100 | 268163222
| Eastern Grid Total |  |  |  | 13975 | 8714 | 195039757
| Western Grid Total |  |  |  | 6959 | 3386 | 73123465
| National Grid Total |  |  |  | 20934 | 12100 | 268163222
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-17
(a) ENTIRE EASTERN GRID : |  | 8263 | MW | (b) ENTIRE WESTERN GRID : |  | 3424 | MW
i) Dhaka area |  | 4342 | MW | i) Khulna area |  | 1261 | MW
ii) Chittagong area |  | 1255 | MW | ii) Rajshahi area |  | 1217 | MW
iii) Comilla area |  | 1059 | MW | iii) Barisal area |  | 259 | MW
iv) Mymensingh area |  | 1050 | MW | iv) Rangpur area |  | 687 | MW
v) Sylhet area |  | 557 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11687 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 126 | 14:00 | Kishoreganj | 154 | 22:00 | Benapol | 50 | 18:30
Munsiganj | 100 | 1:00 | Netrokona | 119 | 1:00 | Jhenida(Old) | 92 | 1:00
Sonargaon | 71 | 1:00 | Jamalpur | 157 | 20:00 | Bottail | 106 | 21:00
Shyampur | 188 | 11:00 | Sherpur | 142 | 23:00 | G.K Project | 49 | 22:00
Bhulta | 212 | 1:00 | Srimongal | 56 | 22:00 | Faridpur | 119 | 22:00
Madanganj | 42 | 12:00 | Shahjibazar | 120 | 22:00 | Rajbari | 48 | 21:00
Shitalakhya | 117 | 12:00 | Fenchuganj | 45 | 18:30 | Madaripur | 84 | 22:00
Rahim steel | 20 | 8:00 | Kulawara | 48 | 18:00 | Sariatpur | 64 | 1:00
Matuail | 66 | 10:00 | Sylhet | 154 | 18:00 | Gopalganj | 84 | 21:00
Ghorasal | 80 | 18:30 | Chatak | 32 | 21:00 | Bagerhat | 80 | 19:30
Narsingdi | 185 | 21:00 | Sunamganj | 56 | 20:00 | Mongla | 44 | 9:00
Haripur (SBU) | 126 | 15:00 | Biani Bazar | 65 | 19:30 | Satkhira | 88 | 1:00
Sreenagar | 37 | 20:00 | Comilla (S) | 152 | 20:00 | Gallamari | 45 | 8:00
Ullon | 76 | 16:00 | Comilla(N) | 142 | 19:00 | Magura | 46 | 1:00
Hasnabad | 81 | 23:00 | Chandpur | 65 | 21:00 | Norail | 40 | 1:00
Magbazar | 108 | 13:00 | Feni | 103 | 19:00 | Chuadanga | 87 | 22:00
Maniknagar | 74 | 13:00 | Chowmuhani | 190 | 1:00 | Barisal(N) | 41 | 1:00
Bangabhaban | 15 | 10:00 | Ashuganj | 44 | 1:00 | Barisal (S) | 98 | 1:00
Motijheel | 30 | 11:00 | Daudkandi | 146 | 21:00 | Patuakhali | 104 | 1:00
Narinda | 72 | 13:00 | B.Baria | 168 | 19:30 | Bhandaria | 48 | 1:00
Kazla | 77 | 17:00 | Ramganj | 84 | 20:00 | Borguna | 18 | 22:00
Dhanmondi | 221 | 13:00 | Chaddagram | 50 | 19:00 | Borhan Uddin | 38 | 1:00
Lalbag | 76 | 18:00 | PHP | 8 | 5:00 | Ishurdi | 70 | 18:00
Madartek | 74 | 23:00 | Kochua | 58 | 1:00 | Ruppur Paromanobik | 4 | 12:00
Dhaka University | 39 | 13:00 | Madunaghat | 64 | 12:00 | Natore | 129 | 18:30
Aftabnagar | 17 | 17:00 | Hathazari | 89 | 14:00 | Bogra | 170 | 21:00
Fatullah | 62 | 12:00 | Khulshi | 170 | 13:00 | Noagaon | 115 | 21:00
Nawabganj | 48 | 22:00 | Halishahar | 94 | 14:00 | Rajshahi | 146 | 18:00
Keraniganj | 68 | 19:30 | Baraulia | 147 | 12:00 | Rajshahi New | 17 | 1:00
Banani | 34 | 15:00 | Sikalbaha | 41 | 10:00 | C.Nawabganj | 54 | 19:00
Mirpur | 128 | 18:00 | Dohazari | 90 | 21:00 | Amnura | 54 | 19:00
Kalyanpur | 99 | 18:00 | Cox'sbazar | 95 | 1:00 | Pabna | 92 | 21:00
Gulshan | 136 | 13:00 | Chandraghona | 24 | 1:00 | Shahjadpur | 90 | 21:00
Uttara | 92 | 18:00 | Kaptai | 4.2 | 18:00 | Serajganj | 104 | 19:00
Uttara New | 27 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 72 | 1:00
Kamrangirchar | 99 | 13:00 | Bakulia | 125 | 18:00 | Joypurhat | 54 | 21:00
Savar | 192 | 16:00 | Julda | 26 | 9:00 | Sherpur(Bogura) | 60 | 18:00
Bhasantec | 140 | 13:00 | TK chemical | 29.5 | 18:30 | Mohastangor | 68 | 21:00
Agargaon | 87 | 14:00 | Modern Steel | 4.5 | 10:00 | Bhangura | 29 | 20:00
Satmosjid | 113 | 13:00 | Shahmirpur | 34 | 18:00 | Rangpur | 118 | 24:00
Tongi | 131 | 18:00 | Khagrachhari | 24 | 19:00 | Lalmonirhat | 40 | 20:00
Kabirpur | 255 | 11:00 | Matarbari | 39 | 19:30 | Saidpur | 89 | 1:00
Basundhara | 211 | 15:00 | Baroiar Hat | 66 | 15:00 | Purbasadipur | 97 | 21:00
Manikganj | 72 | 21:00 | Rangamati | 14 | 18:00 | Thakurgaon | 78 | 1:00
Joydevpur | 186 | 18:00 | Abul Khair 230 | 7 | 1:00 | Palashbari | 116 | 1:00
New Tongi | 91 | 10:00 | BSRM | 159 | 2:00 | Barapukuria | 50 | 18:00
Kodda | 271 | 18:30 | GPH Ispat | 93 | 18:00 | Panchagar | 48 | 1:00
Dhamrai | 102 | 21:00 | Agrabad | 89 | 15:00 | Joldhaka | 52 | 23:00
Rajendrapur | 110 | 19:00 | Goalpara | 27 | 13:00 | Kurigram | 50 | 19:30
Valuka | 124 | 18:30 | Central S/S | 81 | 1:00 | Mithapukur | 31 | 1:00
Tangail | 215 | 21:00 | Noapara | 39 | 21:00
Mymensing | 213 | 18:00 | Jessore | 100 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 6:00 | 402 | 2:00 | Kaliakoir | 393 | 0.70833 | 385 | 0.8125
| Bheramara | 405 | 22:00 | 400 | 18:30 | Bhulta | 391 | 0.25 | 373 | 0.66667
| Ashuganj(N) | 395 | 2:00 | 384 | 12:00 | Gopalganj | 409 | 0.625 | 388 | 0.875
| Payra | 411 | 5:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 238 | 19:00 | 230 | 10:00
| Ishurdi | 233 | 17:00 | 226 | 2:00 | Megnaghat | 232 | 7:00 | 228 | 10:00
| Ashuganj | 242 | 6:00 | 237 | 15:00 | Fenchuganj | 243 | 4:00 | 240 | 16:00
| Serajganj | 230 | 6:00 | 225 | 20:00 | Siddhirganj | 232 | 6:00 | 224 | 12:00
| Baghabari | 233 | 17:00 | 226 | 21:00 | Maniknagar | 231 | 6:00 | 222 | 12:00
| Barapukuria | 235 | 17:00 | 224 | 24:00 | Agargaon | 230 | 16:00 | 219 | 12:00
| Bogra | 224 | 9:00 | 216 | 23:00 | Barisal | 245 | 19:00 | 228 | 14:00
| Rajshahi | 229 | 17:00 | 220 | 2:00 | Bhola 225 MW | 247 | 17:00 | 235 | 21:00
| Khulna South | 234 | 17:00 | 223 | 20:00 | AKSML | 237 | 19:00 | 230 | 3:00
| Rampura | 229 | 1:00 | 222 | 16:00 | BSRM | 235 | 18:00 | 228 | 10:00
| Haripur | 231 | 3:00 | 222 | 12:00 | Bibiyana | 244 | 6:00 | 239 | 15:00
| Hasnabad | 229 | 23:00 | 221 | 11:00 | Bhulta | 235 | 6:00 | 224 | 12:00
| Shyampur | 229 | 5:00 | 219 | 12:00 | Ashuganj (S) | 239 | 6:00 | 233 | 16:00
| Aminbazar | 230 | 1:00 | 219 | 2:00 | Kaliakoir | 230 | 2:00 | 223 | 16:00
| Tongi | 227 | 5:00 | 221 | 15:00 | GPH | 237 | 18:30 | 229 | 10:00
| Comilla (N) | 233 | 6:00 | 228 | 10:00 | Jhenaidah | 230 | 17:00 | 219 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 4:00 | 129 | 12:00 | Madanhat | 139 | 0.70833 | 135 | 0.41667
| Munsiganj | 136 | 3:00 | 130 | 10:00 | Hathazari | 139 | 0.79167 | 135 | 0.33333
| Sonargaon | 135 | 6:00 | 129 | 13:00 | Khulshi | 137 | 0.79167 | 131 | 0.41667
| Shyampur | 137 | 5:00 | 131 | 11:00 | Halishahar | 138 | 0.75 | 132 | 0.41667
| Bhulta | 130 | 18:00 | 124 | 12:00 | Baraulia | 138 | 0.79167 | 133 | 0.125
| Madanganj | 136 | 4:00 | 130 | 10:00 | Sikalbaha | 139 | 0.8125 | 134 | 0.083333
| Shitalakhya | 136 | 6:00 | 130 | 10:00 | Dohazari | 136 | 0.75 | 128 | 0.16667
| Rahim steal | 135 | 3:00 | 130 | 10:00 | Cox'sbazar | 120 | 0.75 | 108 | 0.95833
| Matuail | 134 | 4:00 | 129 | 12:00 | Chandraghona | 138 | 0.77083 | 135 | 0.20833
| Ghorasal | 138 | 1:00 | 137 | 13:00 | Kaptai | 136 | 0.75 | 135 | 0.041667
| Narsinghdi | 132 | 8:00 | 123 | 21:00 | A. Khaer Stl. | 137 | 0.79167 | 133 | 0.5
| Haripur (SBU) | 134 | 4:00 | 130 | 11:00 | Bakulia | 139 | 0.79167 | 131 | 0.41667
| Sreenagar | 134 | 5:00 | 128 | 12:00 | Julda | 137 | 0.66667 | 136 | 0.041667
| Ullon | 135 | 4:00 | 126 | 11:00 | TK Chemical | 139 | 0.77083 | 132 | 0.41667
| Hasnabad | 135 | 1:00 | 130 | 11:00 | Modern Steel | 136 | 0.70833 | 132 | 0.375
| Magbazar | 135 | 4:00 | 125 | 11:00 | Shahmirpur | 139 | 0.75 | 133 | 0.41667
| Maniknagar | 135 | 2:00 | 128 | 12:00 | Khagrachhari | 138 | 0.79167 | 132 | 0.41667
| Bangabhaban | 135 | 2:00 | 128 | 12:00 | Matarbari | 132 | 0.75 | 123 | 0.125
| Motijheel | 135 | 2:00 | 128 | 12:00 | Baroiar Hat | 137 | 0.70833 | 131 | 0.33333
| Narinda | 135 | 2:00 | 128 | 12:00 | Rangamati | 138 | 19:00 | 133 | 10:00
| Kazla | 135 | 2:00 | 128 | 12:00 | Agrabad | 138 | 19:00 | 131 | 10:00
| Dhanmondi | 135 | 4:00 | 128 | 12:00 | Goalpara S/S | 139 | 17:00 | 134 | 0.041667
| Lalbag | 135 | 4:00 | 128 | 12:00 | Khulna Central S/S | 138 | 17:00 | 133 | 0.8125
| Madartek | 135 | 6:00 | 126 | 12:00 | Noapara | 138 | 17:00 | 131 | 0.8125
| Dhaka University | 134 | 3:00 | 125 | 12:00 | Jessore | 138 | 17:00 | 128 | 0.041667
| Aftabnagar | 134 | 1:00 | 126 | 11:00 | Benapol | 137 | 0.70833 | 128 | 0.041667
| Fatullah | 137 | 6:00 | 131 | 10:00 | Jhenida(Old) | 139 | 17:00 | 130 | 0.875
| Nawabganj | 135 | 6:00 | 128 | 12:00 | Bottail | 137 | 0.70833 | 131 | 0.083333
| Keraniganj | 135 | 5:00 | 128 | 12:00 | G.K Project | 140 | 0.77083 | 135 | 0.041667
| Banani | 132 | 23:00 | 125 | 16:00 | Faridpur | 138 | 0.70833 | 129 | 0.875
| Mirpur | 131 | 1:00 | 124 | 15:00 | Rajbari | 140 | 0.75 | 129 | 0.041667
| Kalyanpur | 131 | 6:00 | 125 | 12:00 | Madaripur | 145 | 0.70833 | 132 | 0.875
| Gulshan | 134 | 6:00 | 125 | 12:00 | Shariyatpur S/S | 144 | 17:00 | 132 | 0.041667
| Uttara | 132 | 3:00 | 124 | 15:00 | Gopalganj | 145 | 0.70833 | 132 | 0.875
| Uttara New | 133 | 6:00 | 125 | 12:00 | Bagerhat | 139 | 16:00 | 128 | 0.83333
| Kamrangirchar | 134 | 5:00 | 128 | 12:00 | Mongla | 137 | 15:00 | 127 | 0.83333
| Savar | 135 | 5:00 | 125 | 15:00 | Satkhira | 138 | 15:00 | 129 | 20:00
| Bhasantec | 136 | 4:00 | 127 | 12:00 | Gallamari | 141 | 0.70833 | 128 | 22:00
| Agargaon | 136 | 3:00 | 129 | 12:00 | Magura | 139 | 17:00 | 130 | 0.041667
| Satmosjid | 137 | 6:00 | 128 | 15:00 | Narail | 139 | 0.70833 | 127 | 0.041667
| Tongi | 137 | 5.00 | 132 | 16:00 | Chuadanga | 136 | 18:00 | 123 | 0.041667
| Kabirpur | 134 | 4.00 | 128 | 21:00 | Barisal(N) | 144 | 16:00 | 131 | 0.041667
| Basundhara | 136 | 18:30 | 129 | 14:00 | Barisal (S) | 143 | 16:00 | 130 | 1:00
| Manikganj | 140 | 6:00 | 132 | 20:00 | Patuakhali(S) | 142 | 0.66667 | 127 | 0.875
| Joydevpur | 140 | 13:00 | 135 | 11:00 | Bhandaria | 145 | 0.66667 | 125 | 0.041667
| New Tongi | 136 | 3:00 | 131 | 8:00 | Borguna | 144 | 0.66667 | 130 | 0.041667
| Kodda | 134 | 13:00 | 126 | 8:00 | Jhenaidah(230kV S/S) | 137 | 18:00 | 130 | 1:00
| Dhamrai | 136 | 2:00 | 131 | 16:00 | Ishurdi | 136 | 17:00 | 132 | 2:00
| Rajendrapur | 130 | 23:00 | 123 | 9:00 | Ruppur Paromanobik | 137 | 17:00 | 132 | 1:00
| Valuka | 124 | 10:00 | 108 | 18:30 | Natore | 134 | 17:00 | 131 | 2:00
| Tangail | 132 | 4:00 | 122 | 19:30 | Bogra | 135 | 17:00 | 129 | 20:00
| Mymensing | 129 | 11:00 | 113 | 1:00 | Noagaon | 132 | 17:00 | 123 | 21:00
| Kishorganj | 130 | 10:00 | 117 | 19:30 | Rajshahi | 134 | 17:00 | 129 | 13:00
| Netrokona | 123 | 11:00 | 105 | 21:00 | Rajshahi New | 135 | 17:00 | 129 | 3:00
| Jamalpur | 133 | 8:00 | 120 | 19:30 | C.Nawabganj | 134 | 20:00 | 127 | 13:00
| Sherpur | 130 | 10:00 | 117 | 2:00 | Amnura | 135 | 18:00 | 126 | 2:00
| Srimongal | 138 | 9:00 | 131 | 19:30 | Pabna | 136 | 18:30 | 123 | 13:00
| Shahjibazar | 136 | 8:00 | 130 | 18:00 | Shahjadpur | 139 | 4:00 | 135 | 10:00
| Fenchuganj | 136 | 7:00 | 132 | 22:00 | Serajganj | 133 | 18:30 | 128 | 20:00
| Khulawara | 134 | 7:00 | 132 | 1:00 | Niyamatpur | 129 | 17:00 | 119 | 19:30
| Sylhet | 132 | 7:00 | 129 | 20:00 | Joypurhat | 131 | 17:00 | 122 | 19:30
| Chatak | 132 | 7:00 | 128 | 1:00 | Sherpur(Bogura) | 134 | 17:00 | 127 | 21:00
| Sunamganj | 129 | 10:00 | 123 | 20:00 | Mohastangor | 134 | 17:00 | 127 | 20:00
| Biani Bazar | 132 | 11:00 | 126 | 1:00 | Bangura | 134 | 17:00 | 130 | 19:30
| Comilla(s) | 128 | 17:00 | 124 | 20:00 | Rangpur | 132 | 17:00 | 123 | 21:00
| Comilla(n) | 139 | 18:00 | 136 | 19:30 | Lalmonirhat | 131 | 6:00 | 123 | 21:00
| Chandpur | 138 | 21:00 | 134 | 1:00 | Saidpur | 133 | 17:00 | 125 | 13:00
| Feni | 137 | 17:00 | 130 | 0:00 | Purbasadipur | 132 | 17:00 | 122 | 21:00
| Chowmuhani | 134 | 18:30 | 128 | 1:00 | Thakurgaon | 134 | 17:00 | 122 | 2:00
| Ashuganj | 139 | 10:00 | 133 | 18:30 | Palashbari | 131 | 6:00 | 119 | 21:00
| Daudkandi | 135 | 18:00 | 130 | 19:30 | Barapukuria | 135 | 17:00 | 127 | 21:00
| B.Baria | 134 | 9:00 | 126 | 19:30 | Panchagar | 134 | 0.70833 | 127 | 0.33333
| Ramganj | 138 | 17:00 | 130 | 7:00 | Joldhaka | 131 | 0.70833 | 119 | 0.875
| Chaddagram | 137 | 19:00 | 133 | 0:00 | Kurigram | 132 | 17:0 | 122 | 0.875
| PHP | 137 | 17:00 | 129 | 4:00 | Mithapukur | 134 | 0.70833 | 127 | 0.83333
| Kochua | 138 | 18:00 | 133 | 19:30

## L-Curve
Date | 2021-10-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 102 | 8277 | 3323 | 11600 |  |  |  | QF-LDC-11
0:30 | 124 | 8342.5 | 3435.5 | 11778 | Date: | 2021-10-17
1:00 | 146 | 8408 | 3548 | 11956
1:30 | 196 | 8324.5 | 3416 | 11740.5
2:00 | 246 | 8241 | 3284 | 11525
2:30 | 232 | 8183.5 | 3221.5 | 11405 | [5 empty] | Gen. at Eve. Peak | 12100 | 12100 MW (21:00 )
3:00 | 218 | 8126 | 3159 | 11285 | [6 empty] | 21:00
3:30 | 202 | 8036 | 3129 | 11165 | [5 empty] | Gen. at Day Peak | 11277 | 11277 MW (12:00 )
4:00 | 186 | 7946 | 3099 | 11045 | [6 empty] | 12:00
4:30 | 179 | 7877.5 | 3035 | 10912.5 | [5 empty] | Highest Generation | 12100
5:00 | 172 | 7809 | 2971 | 10780 | [6 empty] | 21:00
5:30 | 99 | 7659 | 2906.5 | 10565.5
6:00 | 26 | 7509 | 2842 | 10351
6:30 | 48 | 7225 | 2832.5 | 10057.5
7:00 | 70 | 6941 | 2823 | 9764
7:30 | 110 | 6951 | 2845 | 9796
8:00 | 150 | 6961 | 2867 | 9828
8:30 | 150 | 7136 | 2866 | 10002
9:00 | 150 | 7311 | 2865 | 10176
9:30 | 185 | 7418 | 2909.5 | 10327.5
10:00 | 220 | 7525 | 2954 | 10479
10:30 | 218 | 7631.5 | 3016 | 10647.5
11:00 | 216 | 7738 | 3078 | 10816
11:30 | 181 | 7922 | 3124.5 | 11046.5
12:00 | 146 | 8106 | 3171 | 11277
12:30 | 93 | 8159 | 3192 | 11351
13:00 | 40 | 8212 | 3213 | 11425
13:30 | 80 | 8204 | 3230 | 11434
14:00 | 120 | 8196 | 3247 | 11443
14:30 | 195 | 8276.5 | 3222.5 | 11499
15:00 | 270 | 8357 | 3198 | 11555
15:30 | 235 | 8269.5 | 2998.5 | 11268
16:00 | 200 | 8182 | 2799 | 10981
16:30 | 245 | 7889.5 | 2728.5 | 10618
17:00 | 290 | 7597 | 2658 | 10255
17:30 | 150 | 8108 | 2766.5 | 10874.5
18:00 | 10 | 8619 | 2875 | 11494
18:30 | 53 | 8708 | 2977 | 11685
19:00 | 96 | 8797 | 3079 | 11876
19:30 | 10 | 8702 | 3277 | 11979
20:00 | 46 | 8703 | 3286 | 11989 |  |  |  | Executive Engineer
20:30 | 96 | 8708.5 | 3336 | 12044.5 |  |  |  | Network Operation Division
21:00 | 146 | 8714 | 3386 | 12100
21:30 | 158 | 8685 | 3412.5 | 12097.5
22:00 | 170 | 8656 | 3439 | 12095 |  |  |  |  | Page 6 of 7
22:30 | 140 | 8521 | 3421 | 11942
23:00 | 110 | 8386 | 3403 | 11789
23:30 | 106 | 8331.5 | 3363 | 11694.5
24:00 | 102 | 8277 | 3323 | 11600
12100 MW (21:00 )
11277 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-17 |  | Energy |  | 268163222
[13 empty] | 2021-10-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4349 | 705 | 2284 | 0 | 2965 | 518 | 155 | 120 | 362 | 142 | 0 | 0
0:30 | 4367 | 706 | 2275.5 | 0 | 3119.5 | 583.5 | 156.5 | 130 | 296 | 144 | 0 | 0 | Date: | 2021-10-17
1:00 | 4385 | 707 | 2267 | 0 | 3274 | 649 | 158 | 140 | 230 | 146 | 0 | 0
1:30 | 4385.5 | 707 | 2266.5 | 0 | 3171 | 629 | 158 | 130 | 148.5 | 145 | 0 | 0 | [8 empty] | Total Energy | 268.1632 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 4386 | 707 | 2266 | 0 | 3068 | 609 | 158 | 120 | 67 | 144 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4390.5 | 707 | 2256 | 0 | 2989 | 593.5 | 158 | 120 | 48 | 143 | 0 | 0 | [8 empty] | Energy Requirement | 268.1632
3:00 | 4395 | 707 | 2246 | 0 | 2910 | 578 | 158 | 120 | 29 | 142 | 0 | 0
3:30 | 4394 | 706.5 | 2232.5 | 0 | 2820.5 | 578.5 | 158.5 | 120 | 14.5 | 140 | 0 | 0 | [6 empty] | Shortage
4:00 | 4393 | 706 | 2219 | 0 | 2731 | 579 | 159 | 120 | 0 | 138 | 0 | 0
4:30 | 4395 | 706 | 2208 | 0 | 2609 | 579.5 | 159 | 120 | 0 | 136 | 0 | 0
5:00 | 4397 | 706 | 2197 | 0 | 2487 | 580 | 159 | 120 | 0 | 134 | 0 | 0
5:30 | 4396 | 706 | 2149.5 | 0 | 2327 | 579 | 159 | 120 | 0 | 129 | 0 | 0
6:00 | 4395 | 706 | 2102 | 0 | 2167 | 578 | 159 | 120 | 0 | 124 | 0 | 0
6:30 | 4267.5 | 705.5 | 2093 | 0 | 2020 | 563 | 159.5 | 120 | 0 | 121 | 8 | 0 |  |  |  |  | Coal
7:00 | 4140 | 705 | 2084 | 0 | 1873 | 548 | 160 | 120 | 0 | 118 | 16 | 0
7:30 | 4178.5 | 705.5 | 2090 | 0 | 1849 | 548 | 160 | 120 | 0 | 120 | 25 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4217 | 706 | 2096 | 0 | 1825 | 548 | 160 | 120 | 0 | 122 | 34 | 0
8:30 | 4209 | 706 | 2092 | 0 | 2002 | 537.5 | 160.5 | 120 | 0 | 126 | 49 | 0
9:00 | 4201 | 706 | 2088 | 0 | 2179 | 527 | 161 | 120 | 0 | 130 | 64 | 0
9:30 | 4163 | 705.5 | 2111.5 | 0 | 2348 | 527 | 161 | 120 | 0 | 123 | 68.5 | 0
10:00 | 4125 | 705 | 2135 | 0 | 2517 | 527 | 161 | 120 | 0 | 116 | 73 | 0
10:30 | 4151 | 705 | 2129.5 | 0 | 2680 | 502.5 | 160 | 120 | 8 | 118 | 73.5 | 0
11:00 | 4177 | 705 | 2124 | 0 | 2843 | 478 | 159 | 120 | 16 | 120 | 74 | 0
11:30 | 4261 | 705.5 | 2135.5 | 0 | 2945.5 | 482.5 | 158.5 | 120 | 26.5 | 126 | 85.5 | 0
12:00 | 4345 | 706 | 2147 | 0 | 3048 | 487 | 158 | 120 | 37 | 132 | 97 | 0
12:30 | 4335 | 706 | 2151 | 0 | 3114.5 | 503 | 157.5 | 120 | 45 | 129 | 90 | 0
13:00 | 4325 | 706 | 2155 | 0 | 3181 | 519 | 157 | 120 | 53 | 126 | 83 | 0
13:30 | 4325 | 706 | 2155 | 0 | 3181 | 519 | 157 | 120 | 53 | 126 | 83 | 0
14:00 | 4325 | 706 | 2155 | 0 | 3181 | 519 | 157 | 120 | 53 | 126 | 83 | 0
14:30 | 4259.5 | 705.5 | 2128 | 0 | 3260.5 | 494 | 157 | 120 | 162.5 | 128 | 75 | 0
15:00 | 4194 | 705 | 2101 | 0 | 3340 | 469 | 157 | 120 | 272 | 130 | 67 | 0
15:30 | 4190 | 705.5 | 2053 | 0 | 3177 | 423 | 156.5 | 120 | 267 | 129 | 47 | 0
16:00 | 4186 | 706 | 2005 | 0 | 3014 | 377 | 156 | 120 | 262 | 128 | 27 | 0
16:30 | 4082.5 | 705.5 | 1931.5 | 0 | 2857.5 | 356 | 157.5 | 120 | 272.5 | 119 | 16 | 0
17:00 | 3979 | 705 | 1858 | 0 | 2701 | 335 | 159 | 120 | 283 | 110 | 5 | 0
17:30 | 4024.5 | 705.5 | 1970 | 40 | 3006 | 335.5 | 159 | 120 | 388.5 | 123 | 2.5 | 0
18:00 | 4070 | 706 | 2082 | 80 | 3311 | 336 | 159 | 120 | 494 | 136 | 0 | 0
18:30 | 4140.5 | 705.5 | 2133.5 | 40 | 3440 | 380.5 | 159.5 | 120 | 431.5 | 134 | 0 | 0
19:00 | 4211 | 705 | 2185 | 0 | 3569 | 425 | 160 | 120 | 369 | 132 | 0 | 0
19:30 | 4394 | 706 | 2285 | 0 | 3366 | 435 | 160 | 120 | 377 | 136 | 0 | 0
20:00 | 4386 | 712 | 2271 | 0 | 3365 | 445 | 160 | 120 | 378 | 152 | 0 | 0
20:30 | 4380.5 | 712 | 2280 | 0 | 3376.5 | 485 | 160.5 | 120 | 378 | 152 | 0 | 0
21:00 | 4375 | 712 | 2289 | 0 | 3388 | 525 | 161 | 120 | 378 | 152 | 0 | 0
21:30 | 4359 | 712 | 2275 | 0 | 3413.5 | 531 | 161 | 120 | 377 | 149 | 0 | 0
22:00 | 4343 | 712 | 2261 | 0 | 3439 | 537 | 161 | 120 | 376 | 146 | 0 | 0
22:30 | 4337.5 | 712 | 2249.5 | 0 | 3312.5 | 527 | 159.5 | 120 | 376 | 148 | 0 | 0
23:00 | 4332 | 712 | 2238 | 0 | 3186 | 517 | 158 | 120 | 376 | 150 | 0 | 0
23:30 | 4340.5 | 708.5 | 2261 | 0 | 3075.5 | 517.5 | 156.5 | 120 | 369 | 146 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 35.1° C
24:00 | 4349 | 705 | 2284 | 0 | 2965 | 518 | 155 | 120 | 362 | 142 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 83 | 83 | 83 | 84 | 84 | 84 | 85 | 85 | 86 | 86 | 84 | 83 | 82 | 81 | 82 | 81 | 84 | 84 |  | 85 | 85 | 85 | 86 | 86 | 83 | 80 | 1965218
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1808000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 110 | 110 | 110 | 110 | 115 | 120 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 13 | 16 | 16 | 16 | 16 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 220809
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 6 | 13 | 15 | 10 | 8 | 7 | 5 | 2 | 2 | [10 empty] | 82485
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 29 | [14 empty] | 102 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 636624
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 68 | 51 | 51 | 61 | 84 | 90 | 90 | 105 | 105 | 105 | 105 | 68 | 94 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2325927
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 20 | [8 empty] | 10944
14 | Titas 50 MW Peaking PP | [13 empty] | 49 | 49 | 49 | 49 | 49 | [7 empty] | 0 | 218352
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [8 empty] | 36 | 185 | 150 | 185 | 185 | 120 | 125 | 129 | 126 | 182 |  | 180 | 185 | 185 | 185 | 180 | 185 | 185 | 2536000
17 | Siddhirganj 335 MW CCPP | 240 | 240 | 240 | 240 | 240 | 240 | [19 empty] | 0 | 1553546
18 | Kodda 300 MW PP Unit-2 (Summit) | 295 | 291 | 245 | 195 | 145 | 30 | 30 | 30 | 99 | 275 | 280 | 296 | 298 | 298 | 298 | 298 | 298 | 298 |  | 298 | 298 | 298 | 298 | 296 | 298 | 220 | 5876289
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 260 |  | 270 | 280 | 300 | 310 | 300 | 300 | 300 | 6538982
26
28 | Ashuganj TPP Unit- 3 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 135 | 135 | 135 | 80 |  | 80 | 80 | 100 | 80 | 80 | 80 | 80 | 2570360
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 554400
33 | Ashuganj 225 MW CCPP | 212 | 212 | 212 | 212 | 213 | 213 | 193 | 202 | 180 | 186 | 181 | 191 | 193 | 180 | 180 | 180 | 185 | 211 |  | 210 | 207 | 211 | 210 | 214 | 216 | 215 | 4879000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 320 | 335 | 305 | 310 | 305 | 325 | 320 | 305 | 305 | 305 | 275 | 300 |  | 305 | 345 | 305 | 300 | 305 | 305 | 305 | 7518000
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 290 | 310 | 325 | 350 | 295 | 285 | 310 | 305 | 290 | 325 | 325 | 295 | 320 |  | 325 | 350 | 325 | 330 | 325 | 325 | 325 | 7766000
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 53 | 51 | 50 | 49 | 50 | 50 | 47 | 47 | 52 | 54 |  | 55 | 55 | 54 | 54 | 54 | 55 | 55 | 1264320
36 | Chandpur 150 MW CCPP | 50 | 50 | 51 | 49 | 50 | 49 | 31 | 32 | 30 | 31 | 30 | 30 | 31 | 50 | 48 | 50 | 48 | 50 |  | 50 | 50 | 50 | 50 | 48 | 50 | 50 | 1055230
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 372 | 372 | 372 | 372 | 372 | 372 | 371 | 373 | 382 | 333 | 394 | 398 | 402 | 401 | 394 | 396 | 377 | 350 |  | 396 | 396 | 397 | 397 | 396 | 396 | 394 | 9320440
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6155500
41 | Haripur 360MW CCPP(HPL) | 333 | 333 | 332 | 331 | 331 | 328 | 281 | 280 | 331 | 306 | 271 | 262 | 261 | 263 | 262 | 262 | 262 | 292 |  | 301 | 291 | 302 | 301 | 311 | 333 | 332 | 7206000
42 | RPCL 210MW CCPP | 207 | 207 | 208 | 208 | 209 | 212 | 206 | 205 | 198 | 186 | 170 | 165 | 151 | 148 | 149 | 153 | 153 | 153 |  | 155 | 156 | 167 | 168 | 168 | 170 | 169 | 4199680
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 11 | 21 | 28 | 27 | 57 | 31 | 43 | 39 | 11 | 2 | [9 empty] | 293750
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 1029000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1001400
46 | Shajibazar 330 MW CCPP | 160 | 161 | 160 | 161 | 161 | 161 | 160 | 158 | 161 | 158 | 157 | 157 | 157 | 157 | 160 | 159 | 160 | 162 |  | 160 | 157 | 160 | 160 | 160 | 160 | 161 | 3557000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 57 | 61 | 60 | 61 | 60 | 60 | 60 | 60 | 60 | 61 | 60 | 56 | 57 |  | 59 | 56 | 57 | 57 | 61 | 62 | 57 | 1405248
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 80 | 83 | 83 | 83 | 84 | 84 | 10 | 81 |  | 78 | 81 | 81 | 81 | 81 | 81 | 81 | 1859520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 219 | 219 | 219 | 186 | 186 | 220 | 166 | 193 | 221 | 206 | 206 | 220 | 220 | 156 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4957010
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 383000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 249660
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 5 | 8 | 8 | 8 | 8 |  | 8 | 11 |  | 11 | 11 | 11 | 11 | 191616
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 41 | 41 | 44 | 47 | 47 | 47 | 47 | 12 | 46 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1071000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 592455
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 280 | 290 | 290 | 290 | 295 | 310 | 300 | 300 | 295 | 295 | 305 | 300 | 300 | 290 | 280 | 280 |  | 275 | 330 | 300 | 300 | 290 | 285 | 290 | 7196500
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7636700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 1105537
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 23 | 23 | 23 | 23 |  |  |  |  | 0 | 13 | 23 | 23 | 23 | 23 | 22 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 442800
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 419328
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 15 | 15 | 15 | 15 | 18 | 20 | 18 |  | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 412416
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 450252
63 | Impoprt (Tripura) | 146 | 144 | 142 | 138 | 134 | 124 | 118 | 122 | 130 | 116 | 120 | 132 | 126 | 130 | 130 | 128 | 110 | 136 |  | 132 | 136 | 152 | 152 | 146 | 150 | 142 | 3193920
64 | Malancha, Ctg. EPZ (United) | 32 | 32 | 32 | 41 | 41 | 41 | 38 | 11 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 6 | 7 |  | 12 | 12 | 16 | 20 | 30 | 35 | 32 | 448320
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488628
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 152280
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | [11 empty] | 0 | 474200
68 | Cumilla 25 MW PP (Summit) | 18 | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 17 | 17 | 19 | 17 | 18 | 18 | 6 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 457730
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 28 | 20 |  | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 651060
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 8 | 25 | 25 | 33 | 25 | 33 | 33 | 33 | 17 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 724000
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 52 | 17 | 17 | [7 empty] | 17 | 17 | 51 | 51 | 98 | 77 | 70 | 90 |  | 114 | 52 | 52 | 52 | 52 | 17 | 17 | 861840
| Chowmuhani 113 MW | 59 | 58 | 57 | 58 | 58 | 58 | 57 | 59 | 55 | 47 | 47 | 43 | 38 | 39 | 45 | 57 | 60 | 95 |  | 95 | 95 | 95 | 95 | 95 | 96 | 62 | 1547280
| Manikgonj 162MW PP(MPGL) | 155 | 150 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 155 | 162 | 162 | 162 | 162 | 126 | 128 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3863520
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 25 | 40 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 8 | 8 | 704160
79 | Kodda 150MW PP | 48 | 16 | [8 empty] | 16 | 32 | 48 | 48 | 133 | 115 | 115 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1547520
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [13 empty] | 0 | 87360
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 25 | 25 | 8 | 8 | 8 | 8 | 11 | 25 | 25 | 25 | 31 | 40 | 38 | 40 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 794160
| Gazipur 100 MW PP | 90 | 52 | 52 | 52 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 46 | 88 | 88 | 88 | 52 | 52 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1704000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 3 | 2 | 4 | 4 | 2 | 0 | 0 | [10 empty] | 20881
| Jodiac Power | 40 | 50 | 54 | 54 | 54 | 54 | 54 | 40 | 35 | 35 | 35 | 35 | 35 | 21 | 33 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 964068
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 68 | 60 | 51 | 51 | 55 | 80 | 110 | 110 | 110 | 110 | 107 | 68 | 85 |  | 96 | 96 | 92 | 93 | 107 | 110 | 110 | 2294980
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 10 | [9 empty] | 7 | 10 | 10 | 10 | 34 | 46 | 50 | 50 |  | 50 | [5 empty] | 0 | 299783
86 | Meghnaghat CCPP ( Summit) | 260 | 260 | 270 | 270 | 280 | 240 | 280 | 300 | 280 | 285 | 275 | 290 | 290 | 285 | 255 | 270 | 260 | 255 |  | 310 | 300 | 300 | 300 | 265 | 260 | 270 | 6682880
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 93 | 92 | 92 | 92 | 74 | 86 | 92 |  | 92 | 92 | 93 | 92 | 92 | 92 | 92 | 2198400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 50 | 10 | 10 | [7 empty] | 10 | 50 | 50 | 50 | 80 | 50 | 50 | 100 |  | 100 | 50 | 50 | 50 | 50 | 10 | 10 | 799080
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 5 | 35 | 1157872
94 | Gagnagar 102 MW PP (Digital Power) | 48 | 16 | 16 | 16 | 7 | 7 | 7 | 7 | 32 | 32 | 74 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 86 | 48 | 1600560
95 | Patenga 50MW PP (Baraka) | 44 | 47 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 33 | 43 | 45 | 45 | 25 | 25 | 34 |  | 50 | 50 | 50 | 50 | 19 | 19 | 19 | 818400
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | 15 | 47 | 51 | 70 | 83 | 82 | 83 |  | 74 | [5 empty] | 0 | 516480
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 42 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 52 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1052445
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 37 | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1131222
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 130 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3445609
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 11000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1231920
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 30 | [7 empty] | 0 | 16538
106 | Mymensingh 200 MW PP (United) | 182 | 182 | 172 | 182 | 182 | 182 | 150 | 150 | 150 | 150 | 150 | 160 | 168 | 167 | 177 | 167 | 177 | 186 |  | 187 | 190 | 191 | 190 | 190 | 190 | 190 | 4159200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 30 | [7 empty] | 0 | 18457
114 | Kodda 149 MW PP Unit-1 (Summit) | 110 | 110 | 112 | 107 | 107 | 90 | 88 | 85 | 115 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 131 | 132 |  | 131 | 131 | 132 | 131 | 131 | 131 | 133 | 2939040
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2097600
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 170 | 120 | 120 | 34 | 34 | 75 | 121 | 170 | 200 | 200 | 200 | 200 | 155 | 120 | 152 |  | 180 | 180 | 180 | 200 | 200 | 200 | 136 | 3931200
117 | Ashuganj 150MW PP (Midland) | 127 | 127 | 127 | 127 | 127 | 128 | 132 | 108 | 122 | 112 | 115 | 117 | 118 | 120 | 123 | 125 | 128 | 128 |  | 128 | 128 | 128 | 130 | 132 | 41 | 130 | 2912205
118 | Bibiyana-III 400 MW CCPP | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 322 | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 320 | 321 | 321 |  | 320 | 320 | 320 | 321 | 321 | 320 | 322 | 7717000
| Jamalpur 115 MW PP (United) | 78 | 79 | 78 | 78 | 78 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 114 |  | 115 | 115 | 115 | 115 | 115 | 115 | 98 | 1623600
| Anwara 300 MW PP (United) | 304 | 305 | 305 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 233 | 285 |  | 304 | 304 | 304 | 287 | 287 | 287 | 285 | 7120800
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2351040
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 53 | 53 | 76 | 99 | 107 | 79 | 79 | 99 | 102 | 108 | 72 | 85 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2347255
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 9 | 415800
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 7 | 15 | 23 | 21 | 29 | 17 | 31 | 17 | 19 | 11 | 1 | [9 empty] | 178403
120 | Eastern Zone Total | 8408 | 8241 | 8126 | 7946 | 7809 | 7509 | 6941 | 6961 | 7311 | 7525 | 7738 | 8106 | 8212 | 8196 | 8357 | 8182 | 7597 | 8619 |  | 8797 | 8702 | 8703 | 8714 | 8656 | 8386 | 8277 | 195039757
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 2 | 4 | [8 empty] | 9600
| Khulna 225 MW CCPP | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3070080
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 65 | 86 | 88 | 88 | 94 | 17 | 17 | 17 |  | 17 | 17 | 17 | 37 | 105 | 105 | 17 | 1239360
130
131
132 | United Payra Power Ltd. | 17 | [24 empty] | 0 | 40800
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 222 | 222 | 221 | 222 | 200 | 152 | 152 | 152 | 182 | 221 | 220 | 217 | 216 | 204 | 120 | 117 | 120 |  | 180 | 220 | 221 | 221 | 221 | 221 | 221 | 466565
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 13 | 30 | 32 | 32 | 33 | 11 | 12 | 12 |  | 12 | 12 | 13 | 22 | 43 | 43 | 43 | 463663
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 65 | 64 | 64 | 64 | 65 | 65 | 65 | 65 | 40 | 30 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1488000
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 34 | 34 | [5 empty] | 0 | [13 empty] | 2 | 2 | 2 | 178507
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | [21 empty] | 0 | 67536
146 | Bheramara HVDC | 707 | 707 | 707 | 706 | 706 | 706 | 705 | 706 | 706 | 705 | 705 | 706 | 706 | 706 | 705 | 706 | 705 | 706 |  | 705 | 706 | 712 | 712 | 712 | 712 | 705 | 17077090
147 | Bheramara 410 MW CCPP | 360 | 355 | 360 | 360 | 360 | 360 | 390 | 405 | 360 | 360 | 360 | 385 | 380 | 360 | 330 | 300 | 300 | 320 |  | 320 | 410 | 390 | 370 | 360 | 340 | 360 | 8802144
148 | Payra 1320 MW | 570 | 530 | 500 | 500 | 500 | 500 | 470 | 470 | 450 | 450 | 400 | 410 | 440 | 440 | 390 | 300 | 260 | 260 |  | 350 | 360 | 370 | 450 | 460 | 440 | 440 | 11878700
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 78 | 79 | 80 | 78 | 78 | 78 | 77 | 77 | 78 | 77 | 79 | 80 | 79 | 77 | 75 | 76 |  | 75 | 75 | 75 | 75 | 77 | 77 | 78 | 1846691
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | [12 empty] | 50 | 50 | 50 | 50 | 50 | [7 empty] | 0 | 289424
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 1 | 1 | 4 | 3 | 2 | 2 | 0 | 0 | [9 empty] | 20220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 113 | 114 | 115 | 115 | 116 | 117 | 120 | 128 | 135 | 114 | 117 | 123 | 126 | 124 | 126 | 134 | 118 | 94 |  | 110 | 114 | 118 | 120 | 114 | 114 | 113 | 2967700
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 178 | 179 | 181 | 181 | 181 | 180 | 185 | 201 | 184 | 176 | 177 | 181 | 188 | 186 | 191 | 174 | 167 | 159 |  | 173 | 183 | 189 | 192 | 186 | 185 | 189 | 4577709
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 377 | 376 | 357 | 346 | 350 | 320 | 375 | 402 | 387 | 417 | 417 | 412 | 408 | 412 | 388 | 408 | 383 | 415 |  | 392 | 414 | 414 | 419 | 393 | 398 | 403 | 9358909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 5 | 5 | 7 | 40 | 38 | 36 | 36 | [8 empty] | 180065
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 17 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 317760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 6 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 239904
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 | [7 empty] | 0 | 25790
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 32 | [7 empty] | 0 | 32173
167 | Katakhali 50 MW Peaking PP | [15 empty] | 6 | 15 | 24 |  | 31 | 31 | 32 | 32 | 30 | 30 | 16 | 191700
168 | Santahar 50 MW Peaking PP | 34 | [15 empty] | 16 | 33 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 284410
169 | Natore 52 MW PP (Rajlanka) | 52 | [9 empty] | 1 | 8 | 8 | 8 | 16 | 25 | 25 | 25 |  | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 550560
170 | Chapainawabganj 100 MW Peaking PP | 47 | [16 empty] | 46 |  | 86 | 94 | 94 | 94 | 94 | 94 | 94 | 627952
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 35 | 55 | 99 | 113 | 113 | 113 | 113 | 113 | 70 | 50 | 60 |  | 105 | 113 | 113 | 113 | 113 | 113 | 113 | 2310624
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 35 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 50 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2353248
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 100 | 70 | 70 | 70 | 34 | 34 | 34 | 34 | 98 | 98 | 106 | 109 | 113 | 74 | 70 | 88 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2140128
177 | Sympa Solar Power 8MW | [6 empty] | 1 |  | 2 | 3 | 4 | 5 | 5 | 5 | 3 | 2 | 2 | [9 empty] | 26453
178
178