## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-19 | Tuesday
|  |  | Date (day): | 2021-10-19 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13456.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14534 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-18 | 2021-10-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 0 | 0 | 0 |  | 365 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 10 | 60 | 60 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 321 | 348 | 390 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 192 | 233 | 310 | 310 | 50 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 250 | 310 | 310 | 310 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 46 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 21 | 21 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 145 | 75 | 200 | 200 | 210
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 37 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 291 | 296 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 133 | 132 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 92 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2566 | 2687 | 3283 | 3575 | 903 | 1310
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 2 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 159 | 164 | 164 | 164 | 66 |  | Low water level & #2 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 51 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 60 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 16 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 12 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 60 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 286 | 286 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 90 | 96 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1141 | 1412 | 1485 | 1559 | 126 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 110 | 110 | 25 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 170 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 280 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 295 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 21 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 127 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 90 | 90 | 90 |  | 73 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 120 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 9 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 136 | 122 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 43 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 7 | 6 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114 |  | 0
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 58 | 96 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1658 | 1875 | 2121 | 2347 | 457 | 157
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 146 | 200 | 202 | 0
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 158 | 150 | 150 |  | 50 | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 38 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 356 | 461 | 567.6 | 518 | 0 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 162 | 160 | 160 |  | 170 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 47 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 20 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 214 | 219 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24 |  | 1
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 270 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 321 | 321 | 321 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1766 | 1718 | 1867 | 1867 | 142 | 346
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 707 | 707 | 724 | 724
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 33 |  | 21 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 340 | 400 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1144 | 1272 | 1504 | 1727 | 0 | 90
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 1 | 3 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 44 | 42 | 42 | 42 | 78 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 400 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 183 | 224 | 150 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 593 | 734 | 1022 | 1242 | 78 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 28 | 28 | 50 |  | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 101 | 144 | 144 | 144 |  |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 178 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | under maint
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 341 | 363 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 46 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 111 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 870 | 1204 | 1486 | 1586 | 220 | 73
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 80 | 0 | 0 |  |  | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 73 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 154 | 193 | 121 | 113 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 10248 | 11556 | 13456.6 | 14534 | 1926 | 3189
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9862.2368 | 11121 | 12950.0561 | 13986.8998
| A. |  | 2021-10-18 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 11556 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9287 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11556 | MW
| 3 | Day peak Generation : |  |  | 10248 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11121 | MW
| 4 | Evening peak Generation : |  |  | 11556 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 247.0809 | MKWHr | By Solar | 0.45497 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 146.6864 | MKWHr |  | By Oil: | 64.6187 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.3842 | MKWHr |  | By Hydro: | 3.8235 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1926 | MW | Dhaka | 4240 | 4240 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3189 | MW | Chittagong | 1333 | 1333 |  | 0 |  | 18:00 |  | 130
|  |  |  | Total = |  |  | 5115 | MW | Khulna | 1178 | 1178 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1135.34 | MMCFD |  |  | Rajshahi | 1105 | 1105 |  | 0 |  | 19:00 |  | 122
| 8 | Fuel Cost : | i) Gas : | Taka | 157400279.856 | ii) Oil : | Taka | 475831699.82 | Comilla | 989 | 989 |  | 0 |  | 19:30 |  | 120
|  |  | iii) Coal : |  | 53037966.89 | Total | Taka | 686269946.566 | Mymensingh | 845 | 845 |  | 0 |  | 20:00 |  | 120
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.7625 | MKWHr. | Sylhet | 496 | 496 |  | 0 |  | 21:00 |  | 118
|  | ii) During Peak Demand : |  |  | 18 | MW (E to W) at | 19:00 | hrs | Barisal | 269 | 269 |  | 0 |  | 22:00 |  | 124
|  | iii) Maximum : |  |  | -160 | MW at | 2:00 | hrs | Rangpur | 666 | 666 |  | 0 |  | 23:00 |  | 120
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.3° C |  |  | Total | 11121 | 11121 |  | 0
| B. |  | 2021-10-19 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14534 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2534 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 256.5741 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8058 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0844 | MKWHr. | ii) HVDC Flow at Peak Time |  | 707 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0288 | MKWHr. | iii) Maximum HVDC Flow : |  | 711 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.72 |  | (b) Today: | 104.72 |  | (c) Rule Curve: |  | 107.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 394 | 332 |  | 0 | 250 | 275 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 7 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 0 | 33 | 0 | 0 | 80 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 0 | 19 | 18 | 35 | 80 | 0 | 0 | 325 | 305 | 215 | 26 | 50 | 23 | 54 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 0 | 21 | 140 | 184 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 190 | 0 | 104 | 0 | 90 | 100 | 128 | 321 | 0 | 105 | 105 | 0 | 285 | 35 | 110 | 17 | 59 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 109 | 0 | 189 | 0 | 43 | 0 | 0 | 0 | 410 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 221 | 0 | 0 | 0 |  | 7848 | 3215 | 11063 | 4325 | 706 | 2306 | 0 | 2646 | 518 | 155 | 120 | 147 | 140 | 0 | 0 | 104.72
2:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 397 | 332 |  | 0 | 250 | 270 | 0 | 0 | 30 | 0 | 0 | 185 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 0 | 33 | 0 | 0 | 80 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 19 | 18 | 40 | 80 | 0 | 0 | 325 | 305 | 214 | 26 | 50 | 23 | 55 | 0 | 45 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 134 | 189 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 161 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 180 | 0 | 101 | 0 | 90 | 100 | 135 | 321 | 78 | 105 | 105 | 0 | 287 | 35 | 110 | 0 | 58 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 707 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 108 | 0 | 189 | 0 | 43 | 0 | 0 | 0 | 415 | 17 | 0 | 113 | 0 | 66 | 0 | 0 | 113 | 420 | 220 | 0 | 0 | 0 |  | 7818 | 3039 | 10857 | 4324 | 707 | 2282 | 0 | 2553 | 498 | 155 | 120 | 84 | 134 | 0 | 0 | 104.72
3:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 397 | 332 |  | 0 | 250 | 275 | 0 | 0 | 30 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 0 | 33 | 0 | 0 | 81 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 0 | 0 | 325 | 305 | 215 | 26 | 50 | 23 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 130 | 207 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 182 | 0 | 104 | 0 | 90 | 68 | 132 | 320 | 78 | 17 | 105 | 0 | 287 | 35 | 110 | 0 | 58 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 707 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 110 | 0 | 189 | 0 | 43 | 0 | 0 | 0 | 407 | 0 | 0 | 113 | 0 | 49 | 0 | 0 | 113 | 400 | 220 | 0 | 0 | 0 |  | 7531 | 2993 | 10524 | 4338 | 707 | 2306 | 0 | 2289 | 478 | 156 | 120 | 0 | 130 | 0 | 0 | 104.72
4:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 398 | 331 |  | 0 | 250 | 295 | 0 | 0 | 15 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 82 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 0 | 0 | 345 | 320 | 206 | 26 | 51 | 23 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 126 | 212 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 57 | 81 | 0 | 220 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 182 | 0 | 75 | 0 | 90 | 17 | 133 | 321 | 78 | 0 | 51 | 0 | 286 | 35 | 34 | 0 | 57 | 100 | 320 | 92 | 0 | 162 | 53 | 0 | 17 | 0 |  | 707 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 119 | 0 | 197 | 0 | 43 | 0 | 0 | 0 | 421 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 360 | 224 | 0 | 0 | 0 |  | 7227 | 2930 | 10157 | 4413 | 707 | 2358 | 0 | 1838 | 438 | 157 | 120 | 0 | 126 | 0 | 0 | 104.72
5:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 398 | 332 |  | 0 | 250 | 290 | 0 | 0 | 15 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 82 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 0 | 0 | 330 | 310 | 211 | 26 | 51 | 20 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 124 | 212 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 162 | 57 | 81 | 0 | 219 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 182 | 0 | 69 | 0 | 90 | 17 | 136 | 322 | 78 | 0 | 51 | 0 | 286 | 35 | 34 | 0 | 58 | 100 | 320 | 92 | 0 | 162 | 53 | 0 | 17 | 0 |  | 706 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 116 | 0 | 186 | 0 | 43 | 0 | 0 | 0 | 420 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 350 | 180 | 0 | 0 | 0 |  | 7194 | 2830 | 10024 | 4349 | 706 | 2304 | 0 | 1836 | 428 | 157 | 120 | 0 | 124 | 0 | 0 | 104.72
6:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 300 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 82 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 0 | 0 | 325 | 305 | 214 | 26 | 50 | 20 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 12 | 120 | 213 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 159 | 57 | 81 | 0 | 205 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 182 | 0 | 70 | 1 | 90 | 17 | 137 | 322 | 38 | 0 | 51 | 0 | 286 | 35 | 34 | 0 | 58 | 100 | 320 | 92 | 0 | 162 | 53 | 0 | 17 | 0 |  | 706 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 114 | 0 | 185 | 0 | 43 | 0 | 0 | 0 | 351 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 310 | 180 | 0 | 0 | 0 |  | 6958 | 2719 | 9677 | 4223 | 706 | 2164 | 0 | 1798 | 388 | 157 | 120 | 0 | 120 | 1 | 0 | 104.72
7:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 339 | 301 |  | 0 | 250 | 280 | 0 | 0 | 15 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 35 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 80 | 0 | 0 | 325 | 305 | 181 | 26 | 51 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 8 | 114 | 212 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 110 | 159 | 61 | 81 | 0 | 179 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 68 | 3 | 90 | 17 | 135 | 321 | 38 | 0 | 51 | 0 | 286 | 35 | 34 | 0 | 58 | 100 | 320 | 92 | 7 | 162 | 53 | 0 | 17 | 2 |  | 707 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 91 | 0 | 158 | 0 | 43 | 0 | 0 | 0 | 351 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 300 | 151 | 0 | 0 | 0 |  | 6711 | 2612 | 9323 | 4040 | 707 | 2099 | 0 | 1694 | 379 | 158 | 120 | 0 | 114 | 12 | 0 | 104.72
8:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 321 | 301 |  | 0 | 250 | 270 | 0 | 0 | 15 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 55 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 325 | 305 | 180 | 26 | 52 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 7 | 118 | 194 | 0 | 19 | 0 | 43 | 42 | 44 | 0 | 110 | 160 | 61 | 81 | 0 | 179 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 19 | 0 | 0 | 100 | 0 | 87 | 8 | 90 | 17 | 117 | 321 | 38 | 0 | 51 | 0 | 284 | 35 | 34 | 0 | 58 | 100 | 320 | 92 | 10 | 162 | 53 | 0 | 17 | 6 |  | 706 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 118 | 0 | 162 | 0 | 42 | 0 | 0 | 0 | 328 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 300 | 151 | 0 | 0 | 0 |  | 6669 | 2618 | 9287 | 4031 | 706 | 2020 | 0 | 1732 | 378 | 158 | 120 | 0 | 118 | 24 | 0 | 104.71
9:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 322 | 294 |  | 0 | 250 | 285 | 0 | 0 | 15 | 0 | 0 | 100 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 55 | 21 | 25 | 29 | 25 | 33 | 40 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 330 | 335 | 188 | 26 | 52 | 20 | 55 | 0 | 43 | 0 | 0 | 1 | 22 | 8 | 0 | 7 | 114 | 186 | 0 | 19 | 1 | 43 | 42 | 44 | 0 | 110 | 159 | 62 | 81 | 0 | 179 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 67 | 0 | 0 | 100 | 0 | 114 | 9 | 90 | 17 | 125 | 321 | 38 | 0 | 51 | 0 | 286 | 35 | 34 | 0 | 59 | 100 | 320 | 92 | 26 | 162 | 53 | 0 | 17 | 3 |  | 707 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 105 | 0 | 175 | 0 | 42 | 0 | 0 | 0 | 362 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 300 | 151 | 0 | 0 | 2 |  | 6875 | 2655 | 9530 | 4065 | 707 | 2081 | 0 | 1866 | 378 | 158 | 120 | 0 | 114 | 41 | 0 | 104.71
10:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 322 | 242 |  | 0 | 250 | 295 | 0 | 0 | 35 | 0 | 0 | 145 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 37 | 55 | 21 | 25 | 29 | 25 | 33 | 51 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 7 | 0 | 1 | 16 | 3 | 80 | 0 | 0 | 350 | 325 | 207 | 26 | 50 | 20 | 54 | 0 | 43 | 0 | 0 | 10 | 22 | 8 | 0 | 7 | 128 | 170 | 0 | 19 | 2 | 43 | 42 | 42 | 0 | 110 | 158 | 61 | 81 | 0 | 214 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 102 | 0 | 0 | 100 | 0 | 131 | 2 | 90 | 28 | 125 | 321 | 38 | 0 | 59 | 2 | 286 | 35 | 34 | 0 | 58 | 90 | 320 | 92 | 39 | 162 | 57 | 0 | 17 | 10 |  | 706 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 110 | 0 | 184 | 0 | 44 | 0 | 0 | 0 | 363 | 0 | 0 | 113 | 0 | 34 | 0 | 1 | 100 | 300 | 181 | 0 | 0 | 2 |  | 7063 | 2731 | 9794 | 4168 | 706 | 2071 | 0 | 2006 | 378 | 159 | 120 | 0 | 128 | 58 | 0 | 104.71
11:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 322 | 203 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 145 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 35 | 37 | 17 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 0 | 2 | 80 | 0 | 0 | 325 | 300 | 209 | 26 | 50 | 20 | 53 | 0 | 43 | 0 | 0 | 24 | 22 | 8 | 12 | 7 | 132 | 151 | 0 | 19 | 2 | 43 | 42 | 44 | 0 | 130 | 158 | 61 | 77 | 0 | 214 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 215 | 0 | 0 | 100 | 0 | 124 | 6 | 90 | 107 | 125 | 321 | 38 | 17 | 79 | 4 | 286 | 35 | 77 | 17 | 58 | 90 | 320 | 91 | 27 | 162 | 106 | 0 | 17 | 33 |  | 707 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 100 | 0 | 172 | 0 | 44 | 0 | 0 | 0 | 360 | 17 | 0 | 113 | 0 | 60 | 0 | 3 | 113 | 300 | 183 | 0 | 0 | 3 |  | 7358 | 2747 | 10105 | 4081 | 707 | 2006 | 0 | 2443 | 378 | 160 | 120 | 0 | 132 | 78 | 0 | 104.71
12:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 321 | 192 |  | 0 | 250 | 250 | 0 | 0 | 55 | 0 | 0 | 145 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 35 | 37 | 17 | 19 | 25 | 29 | 30 | 33 | 51 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 18 | 4 | 80 | 0 | 0 | 325 | 295 | 204 | 26 | 51 | 21 | 53 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 25 | 7 | 136 | 152 | 0 | 19 | 3 | 43 | 42 | 44 | 0 | 130 | 157 | 55 | 77 | 0 | 214 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 291 | 0 | 0 | 100 | 0 | 133 | 2 | 90 | 120 | 125 | 321 | 38 | 17 | 105 | 4 | 286 | 35 | 90 | 17 | 58 | 90 | 320 | 92 | 44 | 162 | 108 | 0 | 17 | 24 |  | 707 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 101 | 0 | 171 | 0 | 44 | 0 | 0 | 0 | 341 | 17 | 0 | 113 | 0 | 73 | 0 | 3 | 113 | 300 | 183 | 0 | 0 | 3 |  | 7487 | 2761 | 10248 | 4094 | 707 | 1968 | 0 | 2603 | 378 | 159 | 120 | 0 | 136 | 83 | 0 | 104.71
13:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 332 | 192 |  | 0 | 250 | 250 | 0 | 0 | 55 | 0 | 0 | 155 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 35 | 37 | 17 | 19 | 25 | 26 | 30 | 33 | 51 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 18 | 2 | 80 | 0 | 0 | 295 | 295 | 209 | 26 | 48 | 21 | 52 | 0 | 43 | 0 | 0 | 25 | 22 | 6 | 33 | 8 | 124 | 131 | 0 | 0 | 1 | 43 | 42 | 44 | 0 | 163 | 159 | 64 | 77 | 0 | 170 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 298 | 0 | 0 | 100 | 0 | 133 | 3 | 90 | 127 | 125 | 322 | 115 | 17 | 105 | 5 | 286 | 20 | 90 | 17 | 52 | 90 | 320 | 92 | 35 | 162 | 108 | 0 | 8 | 18 |  | 707 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 100 | 0 | 176 | 0 | 43 | 0 | 0 | 0 | 343 | 20 | 0 | 113 | 0 | 80 | 0 | 3 | 113 | 310 | 183 | 0 | 0 | 0 |  | 7466 | 2823 | 10289 | 4063 | 707 | 1990 | 0 | 2674 | 387 | 159 | 120 | 0 | 124 | 65 | 0 | 104.71
14:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 328 | 190 |  | 0 | 250 | 295 | 0 | 0 | 55 | 0 | 0 | 123 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 35 | 37 | 17 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 80 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 18 | 2 | 80 | 0 | 0 | 280 | 265 | 156 | 26 | 92 | 21 | 53 | 0 | 43 | 0 | 0 | 40 | 22 | 6 | 33 | 8 | 140 | 132 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 130 | 158 | 62 | 80 | 0 | 193 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 298 | 0 | 0 | 50 | 0 | 133 | 5 | 90 | 100 | 125 | 322 | 105 | 17 | 105 | 3 | 286 | 35 | 90 | 17 | 48 | 100 | 320 | 92 | 24 | 162 | 108 | 0 | 17 | 17 |  | 707 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 70 | 0 | 140 | 0 | 42 | 0 | 0 | 0 | 340 | 35 | 0 | 70 | 0 | 85 | 0 | 3 | 35 | 320 | 150 | 0 | 0 | 2 |  | 7358 | 2594 | 9952 | 3890 | 707 | 1957 | 0 | 2531 | 398 | 155 | 120 | 0 | 140 | 54 | 0 | 104.71
15:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 328 | 195 |  | 0 | 250 | 275 | 0 | 0 | 55 | 0 | 0 | 128 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 35 | 37 | 17 | 19 | 25 | 26 | 33 | 33 | 42 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 2 | 80 | 0 | 0 | 280 | 265 | 171 | 26 | 92 | 19 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 9 | 33 | 8 | 126 | 142 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 130 | 161 | 62 | 81 | 0 | 193 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 298 | 0 | 0 | 30 | 0 | 133 | 5 | 90 | 100 | 123 | 320 | 106 | 17 | 105 | 1 | 286 | 35 | 96 | 17 | 52 | 90 | 320 | 93 | 12 | 162 | 108 | 0 | 17 | 11 |  | 707 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 70 | 0 | 163 | 0 | 42 | 0 | 0 | 0 | 328 | 35 | 0 | 70 | 0 | 49 | 0 | 3 | 35 | 320 | 150 | 0 | 0 | 1 |  | 7318 | 2568 | 9886 | 3945 | 707 | 1952 | 0 | 2444 | 399 | 160 | 120 | 0 | 126 | 33 | 0 | 104.7
16:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 328 | 194 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 123 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 35 | 37 | 35 | 19 | 25 | 26 | 33 | 33 | 51 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 0 | 1 | 17 | 5 | 80 | 0 | 0 | 280 | 265 | 171 | 26 | 92 | 19 | 51 | 0 | 43 | 0 | 0 | 42 | 22 | 5 | 33 | 14 | 104 | 147 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 110 | 159 | 60 | 81 | 0 | 193 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 200 | 0 | 0 | 30 | 0 | 133 | 2 | 76 | 100 | 125 | 321 | 115 | 17 | 105 | 1 | 286 | 35 | 93 | 17 | 57 | 90 | 320 | 92 | 6 | 162 | 108 | 0 | 17 | 3 |  | 706 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 70 | 0 | 162 | 0 | 42 | 0 | 0 | 0 | 294 | 35 | 0 | 70 | 0 | 49 | 0 | 2 | 35 | 320 | 152 | 0 | 0 | 2 |  | 7176 | 2470 | 9646 | 3881 | 706 | 1889 | 0 | 2369 | 399 | 162 | 120 | 0 | 104 | 16 | 0 | 104.7
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 233 |  | 0 | 250 | 285 | 0 | 0 | 55 | 0 | 0 | 127 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 37 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 17 | 8 | 80 | 0 | 0 | 280 | 265 | 171 | 26 | 92 | 23 | 53 | 0 | 43 | 0 | 0 | 8 | 22 | 5 | 33 | 0 | 114 | 143 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 110 | 156 | 40 | 10 | 0 | 212 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 200 | 0 | 0 | 30 | 0 | 133 | 1 | 76 | 100 | 127 | 321 | 115 | 17 | 105 | 0 | 284 | 35 | 93 | 17 | 60 | 100 | 320 | 92 | 1 | 148 | 108 | 0 | 17 | 1 |  | 707 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 70 | 0 | 163 | 0 | 42 | 0 | 0 | 0 | 417 | 35 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 300 | 152 | 0 | 0 | 0 |  | 6860 | 2612 | 9472 | 3662 | 707 | 2009 | 0 | 2309 | 381 | 162 | 120 | 4 | 114 | 4 | 0 | 104.69
18:00 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 396 | 232 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 71 | 0 | 102 | 100 | 18 | 0 | 0 | 0 | 54 | 37 | 55 | 21 | 25 | 20 | 33 | 33 | 51 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 0 | 97 | 100 | 30 | 36 | 16 | 8 | 100 | 0 | 0 | 280 | 295 | 171 | 26 | 90 | 23 | 56 | 0 | 43 | 0 | 42 | 16 | 22 | 5 | 33 | 6 | 130 | 143 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 110 | 162 | 20 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 233 | 0 | 0 | 72 | 0 | 130 | 0 | 90 | 135 | 127 | 321 | 115 | 34 | 105 | 0 | 285 | 35 | 96 | 70 | 96 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 410 | 0 | 0 | 170 | 0 | 0 | 2 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 50 | 5 | 94 | 27 | 34 | 25 | 6 | 33 | 20 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 85 | 0 | 166 | 0 | 42 | 0 | 0 | 0 | 320 | 62 | 0 | 60 | 0 | 113 | 0 | 0 | 90 | 350 | 209 | 0 | 6 | 0 |  | 7739 | 3241 | 10980 | 3836 | 706 | 2033 | 0 | 3064 | 429 | 164 | 170 | 448 | 130 | 0 | 0 | 104.69
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 348 | 233 |  | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 75 | 0 | 102 | 115 | 46 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 89 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 60 | 60 | 50 | 16 | 12 | 100 | 0 | 0 | 280 | 295 | 170 | 26 | 90 | 26 | 56 | 0 | 43 | 0 | 0 | 43 | 22 | 9 | 33 | 6 | 122 | 146 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 130 | 162 | 20 | 81 | 0 | 219 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 296 | 0 | 0 | 158 | 0 | 132 | 0 | 90 | 200 | 127 | 321 | 115 | 105 | 105 | 0 | 286 | 35 | 96 | 114 | 96 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 707 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 0 | 0 | 40 | 46 | 33 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 178 | 0 | 42 | 0 | 0 | 0 | 363 | 105 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 400 | 224 | 0 | 0 | 0 |  | 8153 | 3403 | 11556 | 3814 | 707 | 2131 | 0 | 3584 | 480 | 164 | 120 | 434 | 122 | 0 | 0 | 104.67
19:30 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 357 | 233 |  | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 75 | 0 | 102 | 82 | 50 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 89 | 75 | 120 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 10 | 5 | 46 | 16 | 12 | 100 | 0 | 0 | 320 | 335 | 170 | 26 | 90 | 21 | 56 | 0 | 51 | 0 | 0 | 43 | 0 | 9 | 33 | 11 | 120 | 146 | 0 | 20 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 30 | 81 | 0 | 219 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 296 | 0 | 0 | 192 | 0 | 132 | 0 | 90 | 200 | 127 | 321 | 115 | 105 | 105 | 0 | 269 | 35 | 96 | 70 | 96 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 707 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 8 | 34 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 170 | 0 | 42 | 0 | 0 | 0 | 420 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 400 | 224 | 0 | 0 | 0 |  | 8092 | 3329 | 11421 | 3882 | 707 | 2255 | 0 | 3398 | 480 | 164 | 120 | 295 | 120 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 365 | 242 |  | 0 | 250 | 305 | 0 | 0 | 55 | 0 | 0 | 120 | 0 | 102 | 48 | 35 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 51 | 0 | 90 | 75 | 120 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 0 | 0 | 46 | 16 | 15 | 100 | 0 | 0 | 280 | 295 | 171 | 26 | 90 | 23 | 55 | 0 | 51 | 0 | 0 | 43 | 0 | 9 | 33 | 6 | 120 | 156 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 161 | 50 | 81 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 245 | 0 | 0 | 199 | 0 | 132 | 0 | 90 | 200 | 130 | 321 | 107 | 105 | 105 | 0 | 270 | 35 | 94 | 0 | 96 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 706 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 174 | 0 | 42 | 0 | 0 | 0 | 383 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 225 | 0 | 0 | 0 |  | 7921 | 3270 | 11191 | 3959 | 706 | 2229 | 0 | 3232 | 480 | 165 | 120 | 180 | 120 | 0 | 0 | 104.68
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 260 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 195 | 0 | 74 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 91 | 75 | 120 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 0 | 76 | 0 | 0 | 46 | 16 | 15 | 100 | 0 | 0 | 280 | 295 | 171 | 26 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 33 | 12 | 118 | 162 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 160 | 62 | 81 | 0 | 165 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 170 | 0 | 0 | 170 | 0 | 132 | 0 | 90 | 178 | 130 | 321 | 115 | 105 | 105 | 0 | 286 | 35 | 94 | 0 | 92 | 100 | 320 | 98 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 213 | 0 | 42 | 0 | 0 | 0 | 398 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 225 | 0 | 0 | 0 |  | 7752 | 3321 | 11073 | 4078 | 710 | 2268 | 0 | 2991 | 530 | 166 | 120 | 92 | 118 | 0 | 0 | 104.67
22:00 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 397 | 280 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 124 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 91 | 75 | 120 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 25 | 16 | 25 | 100 | 0 | 0 | 280 | 295 | 171 | 26 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 12 | 124 | 162 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 160 | 62 | 81 | 0 | 166 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 170 | 0 | 0 | 150 | 0 | 108 | 0 | 90 | 200 | 130 | 321 | 115 | 52 | 105 | 0 | 268 | 35 | 94 | 0 | 96 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 219 | 0 | 17 | 0 | 0 | 0 | 420 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 225 | 0 | 0 | 0 |  | 7594 | 3255 | 10849 | 4020 | 711 | 2317 | 0 | 2796 | 510 | 166 | 120 | 85 | 124 | 0 | 0 | 104.67
23:00 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 397 | 310 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 123 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 91 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 6 | 18 | 20 | 100 | 0 | 0 | 310 | 295 | 170 | 26 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 33 | 12 | 120 | 156 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 160 | 57 | 81 | 0 | 166 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 170 | 0 | 0 | 130 | 0 | 78 | 0 | 90 | 155 | 132 | 322 | 115 | 17 | 105 | 0 | 267 | 35 | 94 | 0 | 98 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 130 | 0 | 219 | 0 | 17 | 0 | 0 | 0 | 420 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 210 | 0 | 0 | 0 |  | 7435 | 3146 | 10581 | 3968 | 710 | 2320 | 0 | 2581 | 511 | 166 | 120 | 85 | 120 | 0 | 0 | 104.66
24:00 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 397 | 326 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 18 | 36 | 135 | 0 | 0 | 310 | 295 | 170 | 26 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 33 | 12 | 118 | 162 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 162 | 62 | 81 | 0 | 165 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 78 | 0 | 90 | 120 | 127 | 321 | 115 | 17 | 105 | 0 | 267 | 35 | 68 | 0 | 63 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 114 | 0 | 220 | 0 | 17 | 0 | 0 | 0 | 417 | 0 | 0 | 113 | 0 | 92 | 0 | 0 | 113 | 420 | 226 | 0 | 0 | 0 |  | 7283 | 3101 | 10384 | 3998 | 711 | 2354 | 0 | 2333 | 501 | 164 | 120 | 85 | 118 | 0 | 0 | 104.66
KWH | 0 | 0 | 0 | 0 | 4938836 | 122318 | 0 | 8790020 | 6402000 |  | 0 | 6155300 | 6761833 | 0 | 0 | 1058130 | 0 | 0 | 3574000 | 0 | 819072 | 490080 | 180864 | 0 | 0 | 0 | 1170360 | 1095771 | 979253 | 457488 | 600000 | 653040 | 656900 | 830000 | 717120 | 0 | 2015509 | 1808000 | 2700000 | 0 | 76249 | 0 | 0 | 0 | 0 |  | 115680 | 0 | 636180 | 208560 | 96960 | 408000 | 391872 | 432960 | 2105718 | 0 | 0 | 7834000 | 7284000 | 4635000 | 652363 | 1607010 | 493056 | 1311840 | 0 | 1093098 | 0 | 22280 | 371568 | 422424 | 194220 | 416800 | 281350 | 3028800 | 3946240 | 0 | 437148 | 9950 | 1023000 | 1008240 | 1134000 | 0 | 3528409 | 3587000 | 1317792 | 1825920 | 0 | 4250460 | 388000 | 0 | 248220 | 7197500 | 584722 | 251904 | 0 | 4062217 | 0 | 0 | 3110400 | 0 | 2666304 | 48600 | 2104320 | 2532000 | 2959041 | 7723000 | 1975200 | 930000 | 2163672 | 26400 | 6809673 | 848198 | 1911089 | 357960 | 1618680 | 2314560 | 7666100 | 2280000 | 228550 | 3928320 | 2251909 | 0 | 433440 | 106528 |  | 17084363 | 0 | 8532000 | 0 | 0 | 3054720 | 0 | 0 | 5760 | 0 | 0 | 1520000 | 127686 | 0 | 0 | 0 | 0 | 83952 | 7817 | 303576 | 25850 | 30000 | 48200 | 146400 | 95537 | 464400 | 0 | 211248 | 1866763 | 0 | 0 | 0 | 0 | 2753200 | 0 | 4591345 | 0 | 975401 | 0 | 0 | 0 | 9135600 | 665760 | 0 | 2506272 | 0 | 1735814 | 0 | 17178 | 2192736 | 9517400 | 460418 | 0 | 13200 | 17760 |  | 178890548 | 68190356 | 247080904 | 98657133 | 17084363 | 48029266 | 0 | 59870602 | 11384163 | 3823509 | 3054720 | 1693382 | 3028800 | 454966 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 5482107.96 | 161459.76 | 0 | 8877920.2 | 6594060 |  | 0 | 6709277 | 7505634.63 | 0 | 0 | 8951779.8 | 0 | 0 | 6183020 | 0 | 7469936.64 | 4822387.2 | 1667566.08 | 0 | 0 | 0 | 8543628 | 8470309.83 | 9655434.58 | 343116 | 450000 | 0 | 0 | 0 | 6934550.4 | 0 | 544187.43 | 488160 | 4887000 | 0 | 708353.21 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6170946 | 1991748 | 843552 | 3231360 | 493758.72 | 1285891.2 | 3116462.64 | 0 | 0 | 5797160 | 7284000 | 4264200 | 841548.27 | 1848061.5 | 557153.28 | 1836576 | 0 | 1869197.58 | 0 | 225028 | 3548474.4 | 536478.48 | 145665 | 729400 | 211012.5 | 22716000 | 4183014.4 | 0 | 555177.96 | 158603 | 1677720 | 1613184 | 2018520 | 0 | 4022386.26 | 3730480 | 2596050.24 | 3487507.2 | 0 | 7353295.8 | 849720 | 0 | 506368.8 | 7269475 | 438541.5 | 191447.04 | 0 | 30710360.52 | 0 | 0 | 16174080 | 0 | 26236431.36 | 568134 | 17150208 | 27472200 | 20861239.05 | 7182390 | 18013824 | 8788500 | 18845583.12 | 0 | 51481127.88 | 7387804.58 | 16798472.31 | 3572440.8 | 13872087.6 | 15414969.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98405930.88 | 0 | 8958600 | 0 | 0 | 42338419.2 | 0 | 0 | 60422.4 | 0 | 0 | 1717600 | 197913.3 | 0 | 0 | 0 | 0 | 826087.68 | 79420.72 | 2686647.6 | 199045 | 405600 | 467058 | 1418616 | 926708.9 | 891648 | 0 | 159914.736 | 11256580.89 | 0 | 0 | 0 | 0 | 3221244 | 0 | 6060575.4 | 0 | 1463101.5 | 0 | 0 | 0 | 9044244 | 6950534.4 | 0 | 23784521.28 | 0 | 13469916.64 | 0 | 189816.9 | 16204319.04 | 41781386 | 0 | 0 | 0 | 0 |  | 516174906.31 | 293165872.466 | 809340778.776 | 101695471.356 | 98405930.88 | 55704808.5 | 0 | 417228574.12 | 53037966.89 | 1032347.43 | 42338419.2 | 16264706.5 | 22716000 | 916553.9 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 321 | 192 |  | 0 | 250 | 250 | 0 | 0 | 55 | 0 | 0 | 145 | 0 | 48 | 0 | 10 | 0 | 0 | 0 | 35 | 37 | 17 | 19 | 25 | 29 | 30 | 33 | 51 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 18 | 4 | 80 | 0 | 0 | 325 | 295 | 204 | 26 | 51 | 21 | 53 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 25 | 7 | 136 | 152 | 0 | 19 | 3 | 43 | 42 | 44 | 0 | 130 | 157 | 55 | 77 | 0 | 214 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 291 | 0 | 0 | 100 | 0 | 133 | 2 | 90 | 120 | 125 | 321 | 38 | 17 | 105 | 4 | 286 | 35 | 90 | 17 | 58 | 90 | 320 | 92 | 44 | 162 | 108 | 0 | 17 | 24 |  | 707 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 101 | 0 | 171 | 0 | 44 | 0 | 0 | 0 | 341 | 17 | 0 | 113 | 0 | 73 | 0 | 3 | 113 | 300 | 183 | 0 | 0 | 3 |  | 10248 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 348 | 233 | 0 | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 75 | 0 | 102 | 115 | 46 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 89 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 102 | 60 | 60 | 50 | 16 | 12 | 100 | 0 | 0 | 280 | 295 | 170 | 26 | 90 | 26 | 56 | 0 | 43 | 0 | 0 | 43 | 22 | 9 | 33 | 6 | 122 | 146 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 130 | 162 | 20 | 81 | 0 | 219 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 296 | 0 | 0 | 158 | 0 | 132 | 0 | 90 | 200 | 127 | 321 | 115 | 105 | 105 | 0 | 286 | 35 | 96 | 114 | 96 | 100 | 320 | 92 | 0 | 162 | 108 | 0 | 17 | 0 |  | 707 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 0 | 0 | 40 | 46 | 33 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 178 | 0 | 42 | 0 | 0 | 0 | 363 | 105 | 0 | 111 | 0 | 113 | 0 | 0 | 113 | 400 | 224 | 0 | 0 | 0 |  | 11556 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 412 | 310 | 0 | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 18 | 15 | 110 | 0 | 0 | 330 | 330 | 210 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 202 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 160 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 150 | 100 | 149 | 0 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 724 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 33 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 28 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 42 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 390 | 310 | 0 | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 18 | 5 | 110 | 0 | 0 | 330 | 330 | 210 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 138 | 200 | 8 | 21 | 1.6 | 43 | 42 | 50 | 0 | 163 | 160 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 100 | 100 | 150 | 50 | 149 | 20 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 724 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 28 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 42 | 50 | 0 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 622 | 150 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 362 | 308 | 0 | 0 | 250 | 310 | 0 | 0 | 30 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 17 | 21 | 25 | 30 | 33 |  | 0 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 80 | 0 | 0 | 320 | 315 | 140 | 26 | 30 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 6 | 96 | 162 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 110 | 111 | 61 | 78 | 0 | 166 | 18 | 0 | 10 | 310 | 24 | 0 | 0 | 15 | 0 | 0 | 35 | 0 | 78 | 4 | 50 | 17 | 10 | 321 | 55 | 0 | 17 | 2 | 159 | 35 | 17 | 0 | 58 | 60 | 320 | 17 | 11 | 17 | 17 | 0 | 17 | 2 | 0 | 711 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 153 | 0 | 17 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 140 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 9287 | 8:00
| Highest Generation |  | 11556 | 19:00
| Day Peak Generation |  | 10248 | 12:00
| Evening Peak Generation |  | 11556 | 19:00
| HVDC Max Flow |  | 711 | 22:00
| HVDC EvPeak Flow |  | 707 | 19:00
| Load factor L.F |  | 89.09%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-19
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10248 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8058 | MW
Evening Peak Generation : |  | 11556 | MW Hour : | 19:00 | Available Max Generation : |  | 14534 | MW
E.P. Demand (at gen end) : |  | 11556 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11556 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2534 | MW
Total Gen. (MKWH) : |  | 247.0809 | System Load Factor : | 89.09% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -160 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-19
Actual : | 104.72 | Ft.(MSL) , | Rule curve : | 107.6 | Ft.( MSL )
Gas Consumed : | Total = | 1135.34 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157400279.856
: |  | Coal : | 53037966.89 | Oil : | 475831699.82 | Total : | 686269946.566
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4294.448 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1462.8622 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1311.1237 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1184.8697 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1070.662 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 863.9927 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 479.8694 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 222.3693 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 666.3695 |  |  | 0 | 0%
Total | 0 |  | 11556.5665 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2 ,3
2) Ghorasal-3,4,5,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj-Comilla(N) 230 kV Ckt-1 was under shut down from 08:23 to 10:06 for C/M.
b) Barishal(N) 132/33 kV T5 transformer was shutdown from 08:36 to 10:39 for C/M.
c) Bheramara-Baharampur 400 kV Ckt-1 was shut down at 11:34 for D/W.
d) Gopalganj 132/33 kV T1 transformer was shutdown from 08:46 to 17:20 for A/M.
e) Hathazari-Sikalbaha 230 kV Ckt-2 was under shut down from 09:35 to 17:03 for D/W.
f) Khulna© 132/33 kV T2 transformer was shutdown from 08:06 to 14:04 for A/M.
g) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 09:50 to 18:18 for A/M.
h) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:22 to 17:09 for A/M.
i) Sherpur 132/33 kV T1 transformer was shutdown from 08:45 to 16:29 for A/M.
j) Sirajganj 132/33 kV T2 transformer was shutdown from 10:57 to 11:39 for A/M.
k) Thakurgaon 132/33 kV T1 transformer was shutdown from 08:35 to 15:45 for A/M.
l) Bheramara-Baharampur 400 kV Ckt-3 tripped at 11:34 from Baharampur end and was switched
on at 11:40.
m) Shahjadpur-Pabna 132 kV Ckt was under shut down from 08:39 to 17:47 for A/M.
n) Meghnaghat-Shyampur 230 kV Ckt-2 tripped at 14:36 showing L/O at Meghnaghat end and was
switched on at 14:54.
o) Ghorasal unit-7 tripped at 16:52 due to problem with air compressor.
p) Bhola CCPP GT-2 was synchronized at 16:06.
q) Bhola CCPP GT-1 was synchronized at 16:33.
r) Shahjibazar 330 MW ST was shut down at 04:09(19-10-2021).
s) Ashuganj 225 MW ST was shut down at 06:02(19-10-2021).
t) Barapukuria unit-1 tripped at 06:51(19-10-2021). |  |  | .
u) Dohazari-Cox'sbazar 132 kv Ckt-1 was shut down from 07:02(19/10/2021) to 10:45(19-10-2021) |  |  |  |  | About 11 MW power interruption occurred under Cox'sbazar S/S
for C/M. |  |  |  |  | area from 07:02(19-10-2021) to 10:45(19-10-2021).
v) Ashuganj-Ashuganj 225 MW ST 132 kV Ckt was shut down at 06:02(19-10-2021) foe C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 4938836 | Tripped at 16:52
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 10 | 122318 | Synchronized at 17:45
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 348 | 8790020 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 233 | 6402000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6155300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 310 | 6761833 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1058130
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 46 | 180864 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 457488
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 75 | 3574000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 819072
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1170360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 490080 | High voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1095771
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 979253
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1253040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 656900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 830000
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 717120
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 296 | 4062217
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 2666304 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 930000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 2280000 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3928320
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 106528
| Dhaka area Total |  |  |  | 5560 | 2687 | 60425754
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 76249 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 48600
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 408000
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 164 | 3823509 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2163672
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 636180
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 60 | 208560 | Low demand.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2104320 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 391872 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 432960
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 96960 | Low demand.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26400
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 286 | 6809673 | Engine problem
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 848198 | Low demand.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 96 | 1911089 | Engine problem
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2314560
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2251909 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1412 | 27252711
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2105718 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 170 | 4635000 | R/H at ST line
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7834000 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7284000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 493056 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1311840
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 652363 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1093098
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 127 | 2959041 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 22280 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1607010 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2532000
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 422424
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 194220
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 3028800
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 416800
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 371568 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 6 | 281350 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 357960
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1618680 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 433440 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1875 | 39654648
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 146 | 3946240 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 437148
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9950
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 158 | 3110400 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1975200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 228550
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 115680
| Mymensingh Area Total |  |  |  | 622 | 461 | 9823168
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1023000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1008240 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3528409 | Frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 162 | 3587000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1134000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 251904
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 1317792
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1825920
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4250460
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 388000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 584722
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7197500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 321 | 7723000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248220
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7666100 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1718 | 41734267
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 707 | 17084363
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 5760 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3054720 | Low demand.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 8532000 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 665760
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1272 | 29342603
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 3 | 127686 | Machine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1520000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 42 | 975401 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 400 | 9517400 | Low demand.
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 460418
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 13200 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 734 | 12614105
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 83952
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 7817 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 25850 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 30000 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 48200 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 144 | 2753200
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4591345
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Under maint.
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 363 | 9135600
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 95537 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 464400
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 211248
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 46 | 146400
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 303576 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 2506272
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2192736
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17760
| Rajshahi Area Total |  |  |  | 2179 | 1204 | 22613893
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1866763
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1735814
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 17178
| Rangpur Area Total |  |  |  | 605 | 193 | 3619755
| Total |  |  |  | 20934 | 11556 | 247080904
| Eastern Grid Total |  |  |  | 13975 | 8153 | 178890548
| Western Grid Total |  |  |  | 6959 | 3403 | 68190356
| National Grid Total |  |  |  | 20934 | 11556 | 247080904
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-18
(a) ENTIRE EASTERN GRID : |  | 7903 | MW | (b) ENTIRE WESTERN GRID : |  | 3218 | MW
i) Dhaka area |  | 4240 | MW | i) Khulna area |  | 1178 | MW
ii) Chittagong area |  | 1333 | MW | ii) Rajshahi area |  | 1105 | MW
iii) Comilla area |  | 989 | MW | iii) Barisal area |  | 269 | MW
iv) Mymensingh area |  | 845 | MW | iv) Rangpur area |  | 666 | MW
v) Sylhet area |  | 496 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11121 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 15:00 | Kishoreganj | 140 | 1:00 | Benapol | 42 | 18:00
Munsiganj | 84 | 1:00 | Netrokona | 109 | 4:00 | Jhenida(Old) | 90 | 18:00
Sonargaon | 68 | 0:00 | Jamalpur | 142 | 1:00 | Bottail | 103 | 18:30
Shyampur | 196 | 11:00 | Sherpur | 126 | 1:00 | G.K Project | 46 | 19:30
Bhulta | 202 | 10:00 | Srimongal | 51 | 22:00 | Faridpur | 118 | 19:00
Madanganj | 50 | 12:00 | Shahjibazar | 109 | 18:00 | Rajbari | 46 | 18:30
Shitalakhya | 110 | 15:00 | Fenchuganj | 40 | 1:00 | Madaripur | 76 | 20:00
Rahim steel | 12 | 8:00 | Kulawara | 42 | 1:00 | Sariatpur | 54 | 21:00
Matuail | 66 | 10:00 | Sylhet | 150 | 18:00 | Gopalganj | 75 | 18:30
Ghorasal | 75 | 19:30 | Chatak | 32 | 1:00 | Bagerhat | 80 | 19:00
Narsingdi | 172 | 1:00 | Sunamganj | 56 | 23:00 | Mongla | 38 | 12:00
Haripur (SBU) | 115 | 14:00 | Biani Bazar | 63 | 18:30 | Satkhira | 72 | 20:00
Sreenagar | 34 | 21:00 | Comilla (S) | 140 | 1:00 | Gallamari | 38 | 12:00
Ullon | 71 | 18:00 | Comilla(N) | 103 | 19:00 | Magura | 42 | 18:30
Hasnabad | 78 | 1:00 | Chandpur | 58 | 20:00 | Norail | 37 | 18:00
Magbazar | 92 | 13:00 | Feni | 93 | 21:00 | Chuadanga | 75 | 18:00
Maniknagar | 70 | 13:00 | Chowmuhani | 160 | 19:00 | Barisal(N) | 32 | 21:00
Bangabhaban | 14 | 10:00 | Ashuganj | 40 | 14:00 | Barisal (S) | 88 | 13:00
Motijheel | 28 | 11:00 | Daudkandi | 128 | 18:00 | Patuakhali | 79 | 21:00
Narinda | 49 | 10:00 | B.Baria | 135 | 21:00 | Bhandaria | 40 | 19:00
Kazla | 77 | 10:00 | Ramganj | 70 | 22:00 | Borguna | 14 | 4:00
Dhanmondi | 206 | 13:00 | Chaddagram | 51 | 21:00 | Borhan Uddin | 45 | 1:00
Lalbag | 99 | 13:00 | PHP | 10 | 15:00 | Ishurdi | 61 | 18:00
Madartek | 67 | 1:00 | Kochua | 52 | 19:30 | Ruppur Paromanobik | 4 | 8:00
Dhaka University | 35 | 13:00 | Madunaghat | 57 | 19:00 | Natore | 111 | 18:00
Aftabnagar | 15 | 10:00 | Hathazari | 91 | 19:00 | Bogra | 160 | 1:00
Fatullah | 61 | 11:00 | Khulshi | 170 | 12:00 | Noagaon | 106 | 1:00
Nawabganj | 44 | 21:00 | Halishahar | 91 | 9:00 | Rajshahi | 128 | 1:00
Keraniganj | 72 | 19:00 | Baraulia | 135 | 13:00 | Rajshahi New | 16 | 1:00
Banani | 30 | 11:00 | Sikalbaha | 44 | 20:00 | C.Nawabganj | 50 | 1:00
Mirpur | 118 | 18:00 | Dohazari | 86 | 19:30 | Amnura | 37 | 20:00
Kalyanpur | 93 | 18:00 | Cox'sbazar | 95 | 18:00 | Pabna | 89 | 18:30
Gulshan | 118 | 13:00 | Chandraghona | 58 | 7:00 | Shahjadpur | 85 | 19:00
Uttara | 93 | 11:00 | Kaptai | 4.5 | 18:00 | Serajganj | 90 | 19:00
Uttara New | 21 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 63 | 1:00
Kamrangirchar | 95 | 13:00 | Bakulia | 115 | 17:00 | Joypurhat | 52 | 1:00
Savar | 166 | 16:00 | Julda | 23 | 1:00 | Sherpur(Bogura) | 52 | 1:00
Bhasantec | 135 | 13:00 | TK chemical | 27 | 22:00 | Mohastangor | 64 | 1:00
Agargaon | 82 | 11:00 | Modern Steel | 6 | 10:00 | Bhangura | 27 | 19:30
Satmosjid | 103 | 13:00 | Shahmirpur | 28 | 18:00 | Rangpur | 114 | 20:00
Tongi | 120 | 8:00 | Khagrachhari | 24 | 18:30 | Lalmonirhat | 40 | 19:00
Kabirpur | 236 | 11:00 | Matarbari | 32 | 1:00 | Saidpur | 78 | 13:00
Basundhara | 199 | 13:00 | Baroiar Hat | 48 | 18:00 | Purbasadipur | 92 | 20:00
Manikganj | 66 | 1:00 | Rangamati | 14 | 18:00 | Thakurgaon | 72 | 1:00
Joydevpur | 169 | 18:30 | Abul Khair 230 | 6 | 17:00 | Palashbari | 110 | 1:00
New Tongi | 89 | 11:00 | BSRM | 156 | 9:00 | Barapukuria | 46 | 1:00
Kodda | 268 | 15:00 | GPH Ispat | 97 | 0:00 | Panchagar | 50 | 20:00
Dhamrai | 96 | 18:30 | Agrabad | 84 | 12:00 | Joldhaka | 53 | 19:30
Rajendrapur | 92 | 19:30 | Goalpara | 25 | 13:00 | Kurigram | 52 | 1:00
Valuka | 114 | 18:30 | Central S/S | 78 | 18:30 | Mithapukur | 31 | 19:00
Tangail | 176 | 4:00 | Noapara | 38 | 19:30
Mymensing | 207 | 1:00 | Jessore | 91 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 18:00 | 403 | 2:00 | Kaliakoir | 397 | 0.20833 | 388 | 0.375
| Bheramara | 404 | 21:00 | 396 | 18:00 | Bhulta | 387 | 0.25 | 379 | 0.41667
| Ashuganj(N) | 394 | 13:00 | 387 | 10:00 | Gopalganj | 407 | 0.625 | 393 | 0.875
| Payra | 411 | 6:00 | 44 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 237 | 18:00 | 231 | 8:00
| Ishurdi | 234 | 16:00 | 227 | 1:00 | Megnaghat | 234 | 18:00 | 230 | 1:00
| Ashuganj | 242 | 6:00 | 239 | 10:00 | Fenchuganj | 244 | 6:00 | 240 | 1:00
| Serajganj | 230 | 6:00 | 225 | 1:00 | Siddhirganj | 232 | 6:00 | 226 | 9:00
| Baghabari | 233 | 14:00 | 227 | 1:00 | Maniknagar | 230 | 6:00 | 224 | 10:00
| Barapukuria | 235 | 16:00 | 224 | 1:00 | Agargaon | 229 | 7:00 | 222 | 10:00
| Bogra | 227 | 18:00 | 216 | 1:00 | Barisal | 243 | 21:00 | 236 | 1:00
| Rajshahi | 230 | 18:00 | 219 | 3:00 | Bhola 225 MW | 246 | 7:00 | 238 | 2:00
| Khulna South | 234 | 16:00 | 225 | 1:00 | AKSML | 238 | 21:00 | 228 | 4:00
| Rampura | 229 | 4:00 | 222 | 10:00 | BSRM | 235 | 18:30 | 229 | 4:00
| Haripur | 229 | 6:00 | 222 | 11:00 | Bibiyana | 243 | 22:00 | 239 | 19:30
| Hasnabad | 230 | 1:00 | 223 | 13:00 | Bhulta | 232 | 18:00 | 226 | 10:00
| Shyampur | 228 | 6:00 | 222 | 10:00 | Ashuganj (S) | 238 | 6:00 | 235 | 10:00
| Aminbazar | 230 | 1:00 | 225 | 2:00 | Kaliakoir | 231 | 13:00 | 224 | 9:00
| Tongi | 228 | 13:00 | 221 | 7:00 | GPH | 237 | 21:00 | 228 | 4:00
| Comilla (N) | 233 | 13:00 | 229 | 9:00 | Jhenaidah | 230 | 16:00 | 220 | 1:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 5:00 | 131 | 10:00 | Madanhat | 140 | 0.75 | 135 | 0.29167
| Munsiganj | 136 | 18:00 | 131 | 10:00 | Hathazari | 139 | 0.75 | 134 | 0.29167
| Sonargaon | 135 | 6:00 | 132 | 1:00 | Khulshi | 136 | 0.79167 | 130 | 0.41667
| Shyampur | 137 | 19:00 | 133 | 10:00 | Halishahar | 137 | 0.79167 | 132 | 0.375
| Bhulta | 130 | 4:00 | 126 | 10:00 | Baraulia | 138 | 0.75 | 132 | 0.375
| Madanganj | 136 | 19:00 | 131 | 9:00 | Sikalbaha | 139 | 0.875 | 133 | 0.125
| Shitalakhya | 139 | 19:00 | 131 | 10:00 | Dohazari | 134 | 0.77083 | 128 | 0.375
| Rahim steal | 134 | 5:00 | 131 | 9:00 | Cox'sbazar | 121 | 0.45833 | 110 | 0.041667
| Matuail | 134 | 5:00 | 131 | 10:00 | Chandraghona | 138 | 0.79167 | 134 | 0.41667
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 136 | 0.041667 | 135 | 0.29167
| Narsinghdi | 133 | 8:00 | 128 | 1:00 | A. Khaer Stl. | 136 | 0.75 | 132 | 0.58333
| Haripur (SBU) | 135 | 20:00 | 131 | 9:00 | Bakulia | 138 | 0.79167 | 131 | 0.41667
| Sreenagar | 134 | 6:00 | 129 | 11:00 | Julda | 138 | 0.77083 | 132 | 0.29167
| Ullon | 134 | 4:00 | 128 | 10:00 | TK Chemical | 139 | 0.79167 | 134 | 0.25
| Hasnabad | 135 | 1:00 | 130 | 11:00 | Modern Steel | 137 | 0.875 | 133 | 0.375
| Magbazar | 134 | 5:00 | 129 | 12:00 | Shahmirpur | 138 | 0.77083 | 133 | 0.66667
| Maniknagar | 135 | 2:00 | 130 | 9:00 | Khagrachhari | 136 | 0.77083 | 132 | 0.41667
| Bangabhaban | 135 | 2:00 | 130 | 9:00 | Matarbari | 132 | 0.79167 | 120 | 0.125
| Motijheel | 135 | 2:00 | 130 | 9:00 | Baroiar Hat | 136 | 0.77083 | 132 | 0.375
| Narinda | 135 | 2:00 | 130 | 9:00 | Rangamati | 137 | 18:30 | 134 | 4:00
| Kazla | 135 | 2:00 | 130 | 9:00 | Agrabad | 136 | 18:00 | 131 | 8:00
| Dhanmondi | 135 | 3:00 | 130 | 10:00 | Goalpara S/S | 139 | 15:00 | 134 | 0.8125
| Lalbag | 134 | 3:00 | 129 | 10:00 | Khulna Central S/S | 138 | 13:00 | 134 | 0.041667
| Madartek | 134 | 6:00 | 128 | 10:00 | Noapara | 137 | 13:00 | 132 | 0.041667
| Dhaka University | 134 | 7:00 | 128 | 10:00 | Jessore | 136 | 17:00 | 130 | 0.041667
| Aftabnagar | 134 | 4:00 | 128 | 10:00 | Benapol | 135 | 0.54167 | 130 | 0.041667
| Fatullah | 137 | 20:00 | 132 | 10:00 | Jhenida(Old) | 139 | 16:00 | 131 | 0.041667
| Nawabganj | 134 | 3:00 | 130 | 10:00 | Bottail | 136 | 0.33333 | 132 | 0.041667
| Keraniganj | 135 | 6:00 | 130 | 10:00 | G.K Project | 140 | 0.66667 | 136 | 0.083333
| Banani | 133 | 4:00 | 126 | 15:00 | Faridpur | 137 | 0.29167 | 130 | 0.875
| Mirpur | 132 | 4:00 | 127 | 10:00 | Rajbari | 137 | 0.29167 | 131 | 0.125
| Kalyanpur | 132 | 1:00 | 128 | 10:00 | Madaripur | 141 | 0.66667 | 134 | 0.875
| Gulshan | 133 | 5:00 | 128 | 10:00 | Shariyatpur S/S | 141 | 6:00 | 133 | 0.875
| Uttara | 132 | 19:30 | 127 | 10:00 | Gopalganj | 142 | 0.25 | 136 | 0.83333
| Uttara New | 133 | 6:00 | 127 | 10:00 | Bagerhat | 138 | 15:00 | 130 | 0.083333
| Kamrangirchar | 134 | 4:00 | 130 | 10:00 | Mongla | 137 | 15:00 | 129 | 0.125
| Savar | 134 | 4:00 | 129 | 10:00 | Satkhira | 137 | 14:00 | 131 | 1:00
| Bhasantec | 135 | 2:00 | 129 | 10:00 | Gallamari | 138 | 0.20833 | 131 | 221:00
| Agargaon | 136 | 3:00 | 131 | 10:00 | Magura | 138 | 6:00 | 130 | 0.041667
| Satmosjid | 136 | 6:00 | 131 | 10:00 | Narail | 137 | 0.66667 | 130 | 0.041667
| Tongi | 138 | 19:30 | 133 | 10:00 | Chuadanga | 136 | 16:00 | 126 | 0.041667
| Kabirpur | 137 | 13:00 | 131 | 1:00 | Barisal(N) | 142 | 16:00 | 136 | 0.041667
| Basundhara | 136 | 18:30 | 130 | 8:00 | Barisal (S) | 140 | 7:00 | 134 | 1:00
| Manikganj | 140 | 17:00 | 134 | 1:00 | Patuakhali(S) | 138 | 0.25 | 130 | 0.875
| Joydevpur | 140 | 18:00 | 134 | 15:00 | Bhandaria | 139 | 0.25 | 132 | 0.041667
| New Tongi | 137 | 13:00 | 131 | 8:00 | Borguna | 140 | 0.375 | 132 | 0.875
| Kodda | 138 | 13:00 | 128 | 168:00 | Jhenaidah(230kV S/S) | 138 | 16:00 | 132 | 1:00
| Dhamrai | 138 | 13:00 | 132 | 10:00 | Ishurdi | 137 | 16:00 | 132 | 1:00
| Rajendrapur | 138 | 14:00 | 124 | 9:00 | Ruppur Paromanobik | 136 | 7:00 | 132 | 1:00
| Valuka | 127 | 14:00 | 115 | 1:00 | Natore | 136 | 18:00 | 129 | 2:00
| Tangail | 135 | 13:00 | 127 | 1:00 | Bogra | 135 | 5:00 | 132 | 20:00
| Mymensing | 129 | 14:00 | 116 | 1:00 | Noagaon | 132 | 14:00 | 120 | 1:00
| Kishorganj | 131 | 14:00 | 122 | 1:00 | Rajshahi | 137 | 18:00 | 130 | 1:00
| Netrokona | 126 | 17:00 | 108 | 1:00 | Rajshahi New | 138 | 18:00 | 128 | 3:00
| Jamalpur | 138 | 15:00 | 125 | 1:00 | C.Nawabganj | 139 | 18:00 | 127 | 1:00
| Sherpur | 137 | 14:00 | 118 | 1:00 | Amnura | 139 | 18:00 | 125 | 3:00
| Srimongal | 138 | 13:00 | 134 | 1:00 | Pabna | 134 | 7:00 | 130 | 1:00
| Shahjibazar | 136 | 6:00 | 132 | 1:00 | Shahjadpur | 138 | 7:00 | 134 | 19:30
| Fenchuganj | 137 | 8:00 | 132 | 1:00 | Serajganj | 135 | 15:00 | 130 | 1:00
| Khulawara | 135 | 7:00 | 132 | 1:00 | Niyamatpur | 131 | 9:00 | 118 | 1:00
| Sylhet | 133 | 7:00 | 130 | 1:00 | Joypurhat | 134 | 15:00 | 120 | 1:00
| Chatak | 133 | 9:00 | 128 | 1:00 | Sherpur(Bogura) | 135 | 16:00 | 128 | 1:00
| Sunamganj | 130 | 9:00 | 122 | 23:00 | Mohastangor | 134 | 16:00 | 125 | 2:00
| Biani Bazar | 134 | 8:00 | 128 | 1:00 | Bangura | 136 | 17:00 | 132 | 20:00
| Comilla(s) | 128 | 5:00 | 124 | 12:00 | Rangpur | 131 | 18:00 | 121 | 1:00
| Comilla(n) | 140 | 18:30 | 136 | 1:00 | Lalmonirhat | 130 | 11:00 | 121 | 1:00
| Chandpur | 139 | 18:00 | 133 | 7:00 | Saidpur | 130 | 7:00 | 122 | 1:00
| Feni | 138 | 18:00 | 130 | 1:00 | Purbasadipur | 131 | 6:00 | 120 | 1:00
| Chowmuhani | 136 | 12:00 | 131 | 21:00 | Thakurgaon | 132 | 17:00 | 117 | 3:00
| Ashuganj | 139 | 19:00 | 134 | 1:00 | Palashbari | 134 | 16:00 | 120 | 1:00
| Daudkandi | 135 | 18:00 | 130 | 1:00 | Barapukuria | 135 | 16:00 | 124 | 1:00
| B.Baria | 134 | 13:00 | 130 | 1:00 | Panchagar | 137 | 0.25 | 122 | 0.041667
| Ramganj | 138 | 18:30 | 128 | 4:00 | Joldhaka | 129 | 0.70833 | 117 | 0.041667
| Chaddagram | 140 | 18:30 | 132 | 3:00 | Kurigram | 133 | 0.66667 | 119 | 0.041667
| PHP | 138 | 18:30 | 129 | 4:00 | Mithapukur | 134 | 0.66667 | 122 | 0.083333
| Kochua | 139 | 13:00 | 132 | 3:00

## L-Curve
Date | 2021-10-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 186 | 7283 | 3101 | 10384 |  |  |  | QF-LDC-11
0:30 | 153 | 7565.5 | 3158 | 10723.5 | Date: | 2021-10-18
1:00 | 120 | 7848 | 3215 | 11063
1:30 | 140 | 7833 | 3127 | 10960
2:00 | 160 | 7818 | 3039 | 10857
2:30 | 121 | 7674.5 | 3016 | 10690.5 | [5 empty] | Gen. at Eve. Peak | 11556 | 11556 MW (19:00 )
3:00 | 82 | 7531 | 2993 | 10524 | [6 empty] | 19:00
3:30 | 44 | 7379 | 2961.5 | 10340.5 | [5 empty] | Gen. at Day Peak | 10248 | 10248 MW (12:00 )
4:00 | 6 | 7227 | 2930 | 10157 | [6 empty] | 12:00
4:30 | 26 | 7210.5 | 2880 | 10090.5 | [5 empty] | Highest Generation | 11556
5:00 | 46 | 7194 | 2830 | 10024 | [6 empty] | 19:00
5:30 | 38 | 7076 | 2774.5 | 9850.5
6:00 | 30 | 6958 | 2719 | 9677
6:30 | 49 | 6834.5 | 2665.5 | 9500
7:00 | 68 | 6711 | 2612 | 9323
7:30 | 84 | 6690 | 2615 | 9305
8:00 | 100 | 6669 | 2618 | 9287
8:30 | 204 | 6772 | 2636.5 | 9408.5
9:00 | 308 | 6875 | 2655 | 9530
9:30 | 324 | 6969 | 2693 | 9662
10:00 | 340 | 7063 | 2731 | 9794
10:30 | 266 | 7210.5 | 2739 | 9949.5
11:00 | 192 | 7358 | 2747 | 10105
11:30 | 144 | 7422.5 | 2754 | 10176.5
12:00 | 96 | 7487 | 2761 | 10248
12:30 | 103 | 7476.5 | 2792 | 10268.5
13:00 | 110 | 7466 | 2823 | 10289
13:30 | 55 | 7412 | 2708.5 | 10120.5
14:00 | 0 | 7358 | 2594 | 9952
14:30 | 122 | 7338 | 2581 | 9919
15:00 | 244 | 7318 | 2568 | 9886
15:30 | 250 | 7247 | 2519 | 9766
16:00 | 256 | 7176 | 2470 | 9646
16:30 | 275 | 7018 | 2541 | 9559
17:00 | 294 | 6860 | 2612 | 9472
17:30 | 269 | 7299.5 | 2926.5 | 10226
18:00 | 244 | 7739 | 3241 | 10980
18:30 | 131 | 7946 | 3322 | 11268
19:00 | 18 | 8153 | 3403 | 11556
19:30 | 44 | 8092 | 3329 | 11421
20:00 | 74 | 7921 | 3270 | 11191 |  |  |  | Executive Engineer
20:30 | 47 | 7836.5 | 3295.5 | 11132 |  |  |  | Network Operation Division
21:00 | 20 | 7752 | 3321 | 11073
21:30 | 53 | 7673 | 3288 | 10961
22:00 | 86 | 7594 | 3255 | 10849 |  |  |  |  | Page 6 of 7
22:30 | 78 | 7514.5 | 3200.5 | 10715
23:00 | 70 | 7435 | 3146 | 10581
23:30 | 128 | 7359 | 3123.5 | 10482.5
24:00 | 186 | 7283 | 3101 | 10384
11556 MW (19:00 )
10248 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-18 |  | Energy |  | 247080904
[13 empty] | 2021-10-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3998 | 711 | 2354 | 0 | 2333 | 501 | 164 | 120 | 85 | 118 | 0 | 0
0:30 | 4161.5 | 708.5 | 2330 | 0 | 2489.5 | 509.5 | 159.5 | 120 | 116 | 129 | 0 | 0 | Date: | 2021-10-18
1:00 | 4325 | 706 | 2306 | 0 | 2646 | 518 | 155 | 120 | 147 | 140 | 0 | 0
1:30 | 4324.5 | 706.5 | 2294 | 0 | 2599.5 | 508 | 155 | 120 | 115.5 | 137 | 0 | 0 | [8 empty] | Total Energy | 247.0809 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 4324 | 707 | 2282 | 0 | 2553 | 498 | 155 | 120 | 84 | 134 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4331 | 707 | 2294 | 0 | 2421 | 488 | 155.5 | 120 | 42 | 132 | 0 | 0 | [8 empty] | Energy Requirement | 247.0809
3:00 | 4338 | 707 | 2306 | 0 | 2289 | 478 | 156 | 120 | 0 | 130 | 0 | 0
3:30 | 4375.5 | 707 | 2332 | 0 | 2063.5 | 458 | 156.5 | 120 | 0 | 128 | 0 | 0 | [6 empty] | Shortage
4:00 | 4413 | 707 | 2358 | 0 | 1838 | 438 | 157 | 120 | 0 | 126 | 0 | 0
4:30 | 4381 | 706.5 | 2331 | 0 | 1837 | 433 | 157 | 120 | 0 | 125 | 0 | 0
5:00 | 4349 | 706 | 2304 | 0 | 1836 | 428 | 157 | 120 | 0 | 124 | 0 | 0
5:30 | 4286 | 706 | 2234 | 0 | 1817 | 408 | 157 | 120 | 0 | 122 | 0.5 | 0
6:00 | 4223 | 706 | 2164 | 0 | 1798 | 388 | 157 | 120 | 0 | 120 | 1 | 0
6:30 | 4131.5 | 706.5 | 2131.5 | 0 | 1746 | 383.5 | 157.5 | 120 | 0 | 117 | 6.5 | 0 |  |  |  |  | Coal
7:00 | 4040 | 707 | 2099 | 0 | 1694 | 379 | 158 | 120 | 0 | 114 | 12 | 0
7:30 | 4035.5 | 706.5 | 2059.5 | 0 | 1713 | 378.5 | 158 | 120 | 0 | 116 | 18 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4031 | 706 | 2020 | 0 | 1732 | 378 | 158 | 120 | 0 | 118 | 24 | 0
8:30 | 4048 | 706.5 | 2050.5 | 0 | 1799 | 378 | 158 | 120 | 0 | 116 | 32.5 | 0
9:00 | 4065 | 707 | 2081 | 0 | 1866 | 378 | 158 | 120 | 0 | 114 | 41 | 0
9:30 | 4116.5 | 706.5 | 2076 | 0 | 1936 | 378 | 158.5 | 120 | 0 | 121 | 49.5 | 0
10:00 | 4168 | 706 | 2071 | 0 | 2006 | 378 | 159 | 120 | 0 | 128 | 58 | 0
10:30 | 4124.5 | 706.5 | 2038.5 | 0 | 2224.5 | 378 | 159.5 | 120 | 0 | 130 | 68 | 0
11:00 | 4081 | 707 | 2006 | 0 | 2443 | 378 | 160 | 120 | 0 | 132 | 78 | 0
11:30 | 4087.5 | 707 | 1987 | 0 | 2523 | 378 | 159.5 | 120 | 0 | 134 | 80.5 | 0
12:00 | 4094 | 707 | 1968 | 0 | 2603 | 378 | 159 | 120 | 0 | 136 | 83 | 0
12:30 | 4078.5 | 707 | 1979 | 0 | 2638.5 | 382.5 | 159 | 120 | 0 | 130 | 74 | 0
13:00 | 4063 | 707 | 1990 | 0 | 2674 | 387 | 159 | 120 | 0 | 124 | 65 | 0
13:30 | 4063 | 707 | 1990 | 0 | 2674 | 387 | 159 | 120 | 0 | 124 | 65 | 0
14:00 | 4063 | 707 | 1990 | 0 | 2674 | 387 | 159 | 120 | 0 | 124 | 65 | 0
14:30 | 4004 | 707 | 1971 | 0 | 2559 | 393 | 159.5 | 120 | 0 | 125 | 49 | 0
15:00 | 3945 | 707 | 1952 | 0 | 2444 | 399 | 160 | 120 | 0 | 126 | 33 | 0
15:30 | 3913 | 706.5 | 1920.5 | 0 | 2406.5 | 399 | 161 | 120 | 0 | 115 | 24.5 | 0
16:00 | 3881 | 706 | 1889 | 0 | 2369 | 399 | 162 | 120 | 0 | 104 | 16 | 0
16:30 | 3771.5 | 706.5 | 1949 | 0 | 2339 | 390 | 162 | 120 | 2 | 109 | 10 | 0
17:00 | 3662 | 707 | 2009 | 0 | 2309 | 381 | 162 | 120 | 4 | 114 | 4 | 0
17:30 | 3749 | 706.5 | 2021 | 0 | 2686.5 | 405 | 163 | 145 | 226 | 122 | 2 | 0
18:00 | 3836 | 706 | 2033 | 0 | 3064 | 429 | 164 | 170 | 448 | 130 | 0 | 0
18:30 | 3825 | 706.5 | 2082 | 0 | 3324 | 454.5 | 164 | 145 | 441 | 126 | 0 | 0
19:00 | 3814 | 707 | 2131 | 0 | 3584 | 480 | 164 | 120 | 434 | 122 | 0 | 0
19:30 | 3882 | 707 | 2255 | 0 | 3398 | 480 | 164 | 120 | 295 | 120 | 0 | 0
20:00 | 3959 | 706 | 2229 | 0 | 3232 | 480 | 165 | 120 | 180 | 120 | 0 | 0
20:30 | 4018.5 | 708 | 2248.5 | 0 | 3111.5 | 505 | 165.5 | 120 | 136 | 119 | 0 | 0
21:00 | 4078 | 710 | 2268 | 0 | 2991 | 530 | 166 | 120 | 92 | 118 | 0 | 0
21:30 | 4049 | 710.5 | 2292.5 | 0 | 2893.5 | 520 | 166 | 120 | 88.5 | 121 | 0 | 0
22:00 | 4020 | 711 | 2317 | 0 | 2796 | 510 | 166 | 120 | 85 | 124 | 0 | 0
22:30 | 3994 | 710.5 | 2318.5 | 0 | 2688.5 | 510.5 | 166 | 120 | 85 | 122 | 0 | 0
23:00 | 3968 | 710 | 2320 | 0 | 2581 | 511 | 166 | 120 | 85 | 120 | 0 | 0
23:30 | 3983 | 710.5 | 2337 | 0 | 2457 | 506 | 165 | 120 | 85 | 119 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.3° C
24:00 | 3998 | 711 | 2354 | 0 | 2333 | 501 | 164 | 120 | 85 | 118 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 80 | 80 | 81 | 82 | 82 | 82 | 83 | 83 | 83 | 84 | 85 | 84 | 84 | 80 | 85 | 87 | 87 | 89 |  | 89 | 89 | 90 | 91 | 91 | 91 | 89 | 2015509
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1808000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 8 | 17 | 17 | 17 | 17 | 8 | 0 | 76249
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 8 | 9 | 2 | 6 | 2 | 3 | 5 | 5 | 2 | 1 | [9 empty] | 48600
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 97 |  | 102 | 85 | 85 | 76 | 85 | 85 | 85 | 636180
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 51 | 51 | 51 | 51 | 51 | 51 | 59 | 79 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2163672
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 42 | [7 empty] | 0 | 22280
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 185 | 185 | 185 | 184 | 185 | 97 | 104 | 102 | 100 | 145 | 145 | 145 | 155 | 123 | 128 | 123 | 127 | 71 |  | 75 | 75 | 120 | 195 | 124 | 123 | 123 | 3574000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 145 | 145 | 95 |  |  |  |  | 19 | 67 | 102 | 215 | 291 | 298 | 298 | 298 | 200 | 200 | 233 |  | 296 | 296 | 245 | 170 | 170 | 170 | 95 | 4062217
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | [10 empty] | 4938836
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 2105718
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 19 | 19 | 23 | 23 |  | 26 | 21 | 23 | 26 | 26 | 25 | 25 | 493056
33 | Ashuganj 225 MW CCPP | 215 | 214 | 215 | 206 | 211 | 214 | 181 | 180 | 188 | 207 | 209 | 204 | 209 | 156 | 171 | 171 | 171 | 171 |  | 170 | 170 | 171 | 171 | 171 | 170 | 170 | 4635000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 320 | 310 | 305 | 305 | 305 | 335 | 325 | 300 | 295 | 295 | 265 | 265 | 265 | 265 | 295 |  | 295 | 335 | 295 | 295 | 295 | 295 | 295 | 7284000
| Ashuganj 450 MW CCPP(North) | 325 | 325 | 325 | 345 | 330 | 325 | 325 | 325 | 330 | 350 | 325 | 325 | 295 | 280 | 280 | 280 | 280 | 280 |  | 280 | 320 | 280 | 280 | 280 | 310 | 310 | 7834000
35 | Ashuganj 55 MW PP (Precision) | 54 | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 55 | 54 | 53 | 53 | 52 | 53 | 55 | 51 | 53 | 56 |  | 56 | 56 | 55 | 56 | 56 | 56 | 56 | 1311840
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 51 | 51 | 50 | 51 | 52 | 52 | 50 | 50 | 51 | 48 | 92 | 92 | 92 | 92 | 90 |  | 90 | 90 | 90 | 90 | 92 | 92 | 92 | 1607010
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 394 | 397 | 397 | 398 | 398 | 396 | 339 | 321 | 322 | 322 | 322 | 321 | 332 | 328 | 328 | 328 | 321 | 396 |  | 348 | 357 | 365 | 397 | 397 | 397 | 397 | 8790020
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6155300
41 | Haripur 360MW CCPP(HPL) | 332 | 332 | 332 | 331 | 332 | 300 | 301 | 301 | 294 | 242 | 203 | 192 | 192 | 190 | 195 | 194 | 233 | 232 |  | 233 | 233 | 242 | 260 | 280 | 310 | 326 | 6402000
42 | RPCL 210MW CCPP | 184 | 189 | 207 | 212 | 212 | 213 | 212 | 194 | 186 | 170 | 151 | 152 | 131 | 132 | 142 | 147 | 143 | 143 |  | 146 | 146 | 156 | 162 | 162 | 156 | 162 | 3946240
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 10 | 26 | 39 | 27 | 44 | 35 | 24 | 12 | 6 | 1 | [9 empty] | 228550
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1008240
46 | Shajibazar 330 MW CCPP | 160 | 161 | 160 | 160 | 162 | 159 | 159 | 160 | 159 | 158 | 158 | 157 | 159 | 158 | 161 | 159 | 156 | 162 |  | 162 | 160 | 161 | 160 | 160 | 160 | 162 | 3587000
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 57 | 57 | 57 | 57 | 61 | 61 | 62 | 61 | 61 | 55 | 64 | 62 | 62 | 60 | 40 | 20 |  | 20 | 30 | 50 | 62 | 62 | 57 | 62 | 1317792
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 77 | 77 | 77 | 80 | 81 | 81 | 10 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1825920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 219 | 205 | 179 | 179 | 179 | 214 | 214 | 214 | 170 | 193 | 193 | 193 | 212 | 219 |  | 219 | 219 | 219 | 165 | 166 | 166 | 165 | 4250460
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 388000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248220
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251904
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 44 | 44 | 42 | 44 | 44 | 44 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1134000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 584722
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 290 | 305 | 300 | 290 | 290 | 280 | 300 | 305 | 300 | 300 | 290 | 275 | 295 | 290 | 300 | 290 |  | 270 | 315 | 280 | 310 | 295 | 295 | 295 | 7197500
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7666100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 35 | 55 | 55 |  | 55 | 35 | 35 | 35 | 55 | 55 | 55 | 979253
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | [15 empty] | 10 |  | 23 | 23 | 23 |  |  |  | 0 | 115680
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 |  | 18 | 18 | 18 | 18 | 17 | 17 | 16 |  | 16 | 16 | 16 | 16 | 16 | 18 | 18 | 391872
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 457488
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 |  | 19 | 20 | 22 | 22 | 22 | 22 | 22 | 437148
63 | Impoprt (Tripura) | 140 | 134 | 130 | 126 | 124 | 120 | 114 | 118 | 114 | 128 | 132 | 136 | 124 | 140 | 126 | 104 | 114 | 130 |  | 122 | 120 | 120 | 118 | 124 | 120 | 118 | 3028800
64 | Malancha, Ctg. EPZ (United) | 35 | 40 | 40 | 40 | 40 | 40 | 38 | 5 | 5 | 3 | 2 | 4 | 2 | 2 | 2 | 5 | 8 | 8 |  | 12 | 12 | 15 | 15 | 25 | 20 | 36 | 432960
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 |  |  |  | 22 |  | 0 | 422424
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 9 | 5 | 5 | 5 |  | 9 | 9 | 9 | 9 | 11 | 11 | 10 | 194220
67 | Jangalia 33MW PP (Summit) | [10 empty] | 12 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 416800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 12 | 8 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 14 |  | 6 |  | 6 | 11 | 6 | 12 | 12 | 12 | 12 | 281350
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 29 | 20 |  | 29 | 29 | 28 | 29 | 29 | 29 | 29 | 653040
71 | Maona 33 MW PP(Summit) |  |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 656900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 830000
73 | Ghorashal 108MW PP (Regent) | [17 empty] | 5 |  | 10 | 15 | 20 | 0 | 32 | 35 | 47 | 122318
| Feni Lanka Power | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 70 |  | 114 | 70 |  |  |  |  | 0 | 357960
| Chowmuhani 113 MW | 59 | 58 | 58 | 57 | 58 | 58 | 58 | 58 | 59 | 58 | 58 | 58 | 52 | 48 | 52 | 57 | 60 | 96 |  | 96 | 96 | 96 | 92 | 96 | 98 | 63 | 1618680
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 148 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3928320
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 40 | 51 | 51 | 51 | 51 | 51 | 42 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 25 | 25 | 25 | 717120
79 | Kodda 150MW PP | 115 | 84 | [15 empty] | 100 |  | 115 | 82 | 48 | 16 |  |  | 0 | 490080
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | [7 empty] | 1 | 10 | 24 | 25 | 25 | 40 | 43 | 42 | 8 | 16 |  | 43 | 43 | 43 | 8 |  |  |  | 371568
| Gazipur 100 MW PP | 105 | 105 | 17 | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 105 | 105 | 105 | 105 | 52 | 17 | 17 | 930000
| Kaptai 7 MW Solar PP | [9 empty] | 2 | 4 | 4 | 5 | 3 | 1 | 1 | 0 | [9 empty] | 26400
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848198
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 77 | 90 | 90 | 90 | 96 | 93 | 93 | 96 |  | 96 | 96 | 94 | 94 | 94 | 94 | 68 | 1911089
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  | 18 |  | 46 | 50 | 35 |  |  |  | 0 | 180864
86 | Meghnaghat CCPP ( Summit) | 275 | 270 | 275 | 295 | 290 | 260 | 280 | 270 | 285 | 295 | 280 | 250 | 250 | 295 | 275 | 280 | 285 | 280 |  | 310 | 310 | 305 | 290 | 290 | 290 | 280 | 6761833
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 92 | 92 | 92 | 93 | 92 | 92 | 92 |  | 92 | 92 | 92 | 98 | 104 | 104 | 104 | 2280000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | [8 empty] | 7 | 10 | 10 | 10 | 10 | 10 | 8 |  | 100 |  | 60 | 10 |  |  |  |  | 0 | 208560
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 45 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 1093098
94 | Gagnagar 102 MW PP (Digital Power) | 7 | [7 empty] | 7 | 24 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 102 |  | 102 | 102 | 102 | 74 | 32 | 7 | 0 | 819072
95 | Patenga 50MW PP (Baraka) | 19 | 19 | [7 empty] | 1 | 19 | 25 | 25 | 25 |  | 1 | 24 | 36 |  | 50 | 46 | 46 | 46 | 25 | 6 | 0 | 408000
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 30 |  | 60 | 5 |  |  |  |  | 0 | 96960
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1058130
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1095771
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 130 | 130 | 163 | 130 | 130 | 110 | 110 | 110 |  | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 3528409
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 3 | 1 |  | 0 | 0 | 0 | [9 empty] | 9950
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1170360
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 190 | 180 | 182 | 182 | 182 | 182 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 30 | 30 | 30 | 72 |  | 158 | 192 | 199 | 170 | 150 | 130 | 100 | 3110400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 104 | 101 | 104 | 75 | 69 | 70 | 68 | 87 | 114 | 131 | 124 | 133 | 133 | 133 | 133 | 133 | 133 | 130 |  | 132 | 132 | 132 | 132 | 108 | 78 | 78 | 2666304
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2104320
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 68 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 107 | 120 | 127 | 100 | 100 | 100 | 100 | 135 |  | 200 | 200 | 200 | 178 | 200 | 155 | 120 | 2532000
117 | Ashuganj 150MW PP (Midland) | 128 | 135 | 132 | 133 | 136 | 137 | 135 | 117 | 125 | 125 | 125 | 125 | 125 | 125 | 123 | 125 | 127 | 127 |  | 127 | 127 | 130 | 130 | 130 | 132 | 127 | 2959041
118 | Bibiyana-III 400 MW CCPP | 321 | 321 | 320 | 321 | 322 | 322 | 321 | 321 | 321 | 321 | 321 | 321 | 322 | 322 | 320 | 321 | 321 | 321 |  | 321 | 321 | 321 | 321 | 321 | 322 | 321 | 7723000
| Jamalpur 115 MW PP (United) |  | 78 | 78 | 78 | 78 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 115 | 105 | 106 | 115 | 115 | 115 |  | 115 | 115 | 107 | 115 | 115 | 115 | 115 | 1975200
| Anwara 300 MW PP (United) | 285 | 287 | 287 | 286 | 286 | 286 | 286 | 284 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 286 | 284 | 285 |  | 286 | 269 | 270 | 286 | 268 | 267 | 267 | 6809673
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 100 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2314560
| Anlima Energy Ltd. | 108 | 108 | 108 | 53 | 53 | 53 | 53 | 53 | 53 | 57 | 106 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2251909
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433440
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 6 | 3 | 10 | 33 | 24 | 18 | 17 | 11 | 3 | 1 | [9 empty] | 106528
120 | Eastern Zone Total | 7848 | 7818 | 7531 | 7227 | 7194 | 6958 | 6711 | 6669 | 6875 | 7063 | 7358 | 7487 | 7466 | 7358 | 7318 | 7176 | 6860 | 7739 |  | 8153 | 8092 | 7921 | 7752 | 7594 | 7435 | 7283 | 178890548
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 2 | [8 empty] | 5760
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 170 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3054720
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | [8 empty] | 17 | 17 | 20 | 35 | 35 | 35 | 35 | 62 |  | 105 | 105 | 90 | 70 | 35 |  | 0 | 665760
130
131
132 | United Payra Power Ltd. | [17 empty] | 6 | [7 empty] | 0 | 13200
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 220 | 220 | 224 | 180 | 180 | 151 | 151 | 151 | 181 | 183 | 183 | 183 | 150 | 150 | 152 | 152 | 209 |  | 224 | 224 | 225 | 225 | 225 | 210 | 226 | 460418
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 44 | 44 | 44 | 43 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 17 | 17 | 17 | 975401
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 30 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1520000
140 | Bhola 33 MW PP (Venture) | 2 | 2 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 2 | 2 | 3 | 4 |  | 3 | 12 | 13 | 23 | 27 | 17 | 5 | 127686
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 706 | 707 | 707 | 707 | 706 | 706 | 707 | 706 | 707 | 706 | 707 | 707 | 707 | 707 | 707 | 706 | 707 | 706 |  | 707 | 707 | 706 | 710 | 711 | 710 | 711 | 17084363
147 | Bheramara 410 MW CCPP | 360 | 355 | 350 | 350 | 320 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 340 | 300 | 300 | 280 | 320 | 410 |  | 340 | 340 | 410 | 410 | 390 | 355 | 355 | 8532000
148 | Payra 1320 MW | 440 | 420 | 400 | 360 | 350 | 310 | 300 | 300 | 300 | 300 | 300 | 300 | 310 | 320 | 320 | 320 | 300 | 350 |  | 400 | 400 | 400 | 450 | 430 | 430 | 420 | 9517400
149
150 | Barapukuria TPP Unit-1 | 78 | 78 | 78 | 78 | 78 | 78 | 79 | 78 | 78 | 78 | 78 | 78 | 77 | 78 | 79 | 79 | 81 | 79 |  | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 1866763
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | [6 empty] | 83952
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 2 | 3 | 3 | 0 | 2 | 1 | 2 | 0 | [9 empty] | 17760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 109 | 108 | 110 | 119 | 116 | 114 | 91 | 118 | 105 | 110 | 100 | 101 | 100 | 70 | 70 | 70 | 70 | 85 |  | 144 | 144 | 144 | 144 | 144 | 130 | 114 | 2753200
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 189 | 189 | 189 | 197 | 186 | 185 | 158 | 162 | 175 | 184 | 172 | 171 | 176 | 140 | 163 | 162 | 163 | 166 |  | 178 | 170 | 174 | 213 | 219 | 219 | 220 | 4591345
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 410 | 415 | 407 | 421 | 420 | 351 | 351 | 328 | 362 | 363 | 360 | 341 | 343 | 340 | 328 | 294 | 417 | 320 |  | 363 | 420 | 383 | 398 | 420 | 420 | 417 | 9135600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 | [8 empty] | 7817
162 | Bogra 22 MW PP (GBB) | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 21 | 0 | 20 | 20 | 21 | 21 | 12 | 20 | 20 |  | 21 | 21 | 21 | 21 | 22 | 22 | 21 | 464400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 211248
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 | [7 empty] | 0 | 25850
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 34 | [7 empty] | 0 | 30000
167 | Katakhali 50 MW Peaking PP | [17 empty] | 25 |  | 40 | [6 empty] | 48200
168 | Santahar 50 MW Peaking PP | [17 empty] | 33 |  | 33 | 34 | [5 empty] | 95537
169 | Natore 52 MW PP (Rajlanka) | 52 | [16 empty] | 6 |  | 46 | 8 |  |  |  |  | 0 | 146400
170 | Chapainawabganj 100 MW Peaking PP | 32 | [16 empty] | 94 |  | 94 | 94 | 47 |  |  |  |  | 303576
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 35 | 60 |  | 111 | 113 | 113 | 113 | 113 | 113 | 113 | 2506272
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2192736
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 66 | 49 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 60 | 73 | 80 | 85 | 49 | 49 | 34 | 113 |  | 113 | 106 | 113 | 113 | 113 | 113 | 92 | 1735814
177 | Sympa Solar Power 8MW | [9 empty] | 1 | 3 | 3 | 3 | 3 | 3 | 2 | 1 | [9 empty] | 17178
178
178