## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-20 | Wednesday
|  |  | Date (day): | 2021-10-20 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13485.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14569 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-19 | 2021-10-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 62 | 87 | 90 | 90 |  | 18 | Machine problem.
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 346 | 331 | 360 | 390
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 276 | 243 | 310 | 310 | 50 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 240 | 253 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 32 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 5 | 0 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 18 | 21 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 150 | 152 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 32 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 37 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 183 | 298 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 114 | 133 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 52 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 90 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 13 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2279 | 2508 | 3273 | 3573 | 585 | 1328
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 11 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 40 | 46 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 165 | 165 | 165 | 65 |  | Low water level & #2 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 75 | 51 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 10 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 0 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 14 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 269 | 271 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 33 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 80 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 76 | 102 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1028 | 1247 | 1481 | 1555 | 130 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 110 | 110 | 25 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 138 | 103 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 265 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 30 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 120 | 108 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 31 | 84 | 90 | 90 |  | 73 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 96 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 138 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 17 | 25 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 17 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 51 | 96 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1478 | 1601 | 2121 | 2347 | 457 | 157
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 160 | 162 | 160 | 160 | 42
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 8 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 48 | 160 | 190 | 190 |  | 10 | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 73 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 23 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 324 | 490 | 567.6 | 516 | 42 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 110 | 110 | 110 | 110 |  | 220 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 46 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 50 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 219 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 16 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 265 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 321 | 321 | 321 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1718 | 1713 | 1817 | 1817 | 142 | 395
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 710 | 711 | 723 | 723
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 33 |  | 21 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 205 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 410 | 400 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1165 | 1431 | 1503 | 1726 | 0 | 90
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 24 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 17 | 17 | 42 | 42 | 53 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 340 | 430 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 152 | 181 | 150 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 589 | 717 | 1022 | 1242 | 53 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42 | 8 |  | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 150 | 90 | 144 | 144 |  |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 168 | 198 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | under maint
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 325 | 383 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 55 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 821 | 1110 | 1500 | 1600 | 178 | 73
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 79 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 35 | 192 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 9437 | 11009 | 13485.6 | 14569 | 1587 | 3256
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9208.1255 | 10742 | 13158.5353 | 14215.6597
| A. |  | 2021-10-19 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 11009 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 8058 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11009 | MW
| 3 | Day peak Generation : |  |  | 9437 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10742 | MW
| 4 | Evening peak Generation : |  |  | 11009 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 229.4405 | MKWHr | By Solar | 0.3568 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 139.9602 | MKWHr |  | By Oil: | 54.9841 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 10.4284 | MKWHr |  | By Hydro: | 3.9049 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1587 | MW | Dhaka | 4120 | 4120 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3256 | MW | Chittagong | 1243 | 1243 |  | 0 |  | 18:00 |  | 132
|  |  |  | Total = |  |  | 4843 | MW | Khulna | 1162 | 1162 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1142.2 | MMCFD |  |  | Rajshahi | 1086 | 1086 |  | 0 |  | 19:00 |  | 138
| 8 | Fuel Cost : | i) Gas : | Taka | 151554094.126 | ii) Oil : | Taka | 415182295.04 | Comilla | 915 | 915 |  | 0 |  | 19:30 |  | 136
|  |  | iii) Coal : |  | 47755674.92 | Total | Taka | 614492064.086 | Mymensingh | 887 | 887 |  | 0 |  | 20:00 |  | 132
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.103 | MKWHr. | Sylhet | 435 | 435 |  | 0 |  | 21:00 |  | 130
|  | ii) During Peak Demand : |  |  | 196 | MW (E to W) at | 19:00 | hrs | Barisal | 263 | 263 |  | 0 |  | 22:00 |  | 128
|  | iii) Maximum : |  |  | -24 | MW at | 21:00 | hrs | Rangpur | 631 | 631 |  | 0 |  | 23:00 |  | 128
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.5° C |  |  | Total | 10742 | 10742 |  | 0
| B. |  | 2021-10-20 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14569 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9300 | MW
| 4 | Reserve(Generation end) |  |  |  | 3069 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 239.6735 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8096 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0269 | MKWHr. | ii) HVDC Flow at Peak Time |  | 711 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7792 | MKWHr. | iii) Maximum HVDC Flow : |  | 711 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.64 |  | (b) Today: | 104.58 |  | (c) Rule Curve: |  | 107.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 397 | 318 |  | 0 | 250 | 270 | 0 | 0 | 30 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 18 | 36 | 135 | 0 | 0 | 310 | 295 | 170 | 26 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 10 | 8 | 33 | 12 | 110 | 162 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 161 | 62 | 81 | 0 | 166 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 78 | 0 | 90 | 68 | 122 | 323 | 115 | 0 | 68 | 0 | 267 | 35 | 34 | 0 | 63 | 100 | 320 | 104 | 0 | 162 | 100 | 0 | 17 | 0 |  | 711 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 113 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 382 | 0 | 0 | 113 | 0 | 44 | 0 | 0 | 113 | 370 | 226 | 0 | 0 | 0 |  | 6982 | 2951 | 9933 | 3978 | 711 | 2315 | 0 | 2002 | 450 | 162 | 120 | 85 | 110 | 0 | 0 | 104.65
2:00 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 396 | 326 |  | 0 | 250 | 260 | 0 | 0 | 30 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 18 | 33 | 135 | 0 | 0 | 310 | 295 | 170 | 26 | 93 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 106 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 162 | 62 | 81 | 0 | 166 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 78 | 0 | 90 | 34 | 125 | 323 | 115 | 0 | 34 | 0 | 215 | 35 | 17 | 0 | 63 | 100 | 320 | 104 | 0 | 162 | 35 | 0 | 17 | 0 |  | 710 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 110 | 0 | 184 | 0 | 17 | 0 | 0 | 0 | 377 | 0 | 0 | 70 | 0 | 27 | 0 | 0 | 70 | 350 | 226 | 0 | 0 | 0 |  | 6746 | 2815 | 9561 | 3983 | 710 | 2303 | 0 | 1662 | 430 | 162 | 120 | 85 | 106 | 0 | 0 | 104.65
3:00 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 395 | 326 |  | 0 | 250 | 265 | 0 | 0 | 30 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 18 | 33 | 135 | 0 | 0 | 310 | 300 | 170 | 26 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 102 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 160 | 62 | 81 | 0 | 166 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 78 | 0 | 90 | 34 | 50 | 323 | 115 | 0 | 34 | 0 | 215 | 35 | 17 | 0 | 59 | 100 | 320 | 65 | 0 | 17 | 35 | 0 | 17 | 0 |  | 710 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 110 | 0 | 184 | 0 | 17 | 0 | 0 | 0 | 315 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 350 | 225 | 0 | 0 | 0 |  | 6428 | 2648 | 9076 | 3980 | 710 | 2205 | 0 | 1284 | 430 | 160 | 120 | 85 | 102 | 0 | 0 | 104.65
4:00 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 395 | 326 |  | 0 | 250 | 295 | 0 | 0 | 30 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 18 | 33 | 135 | 0 | 0 | 310 | 300 | 170 | 26 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 100 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 146 | 62 | 81 | 0 | 166 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 78 | 0 | 90 | 34 | 10 | 322 | 115 | 0 | 34 | 0 | 183 | 35 | 17 | 0 | 58 | 100 | 320 | 17 | 0 | 17 | 35 | 0 | 17 | 0 |  | 711 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 111 | 0 | 184 | 0 | 17 | 0 | 0 | 0 | 306 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 300 | 226 | 0 | 0 | 0 |  | 6326 | 2593 | 8919 | 3967 | 711 | 2232 | 0 | 1163 | 381 | 160 | 120 | 85 | 100 | 0 | 0 | 104.65
5:00 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 396 | 326 |  | 0 | 250 | 285 | 0 | 0 | 30 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 33 | 135 | 0 | 0 | 310 | 295 | 170 | 26 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 102 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 111 | 62 | 81 | 0 | 166 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 35 | 0 | 78 | 0 | 90 | 17 | 10 | 321 | 115 | 0 | 17 | 0 | 178 | 35 | 17 | 0 | 58 | 100 | 320 | 17 | 0 | 17 | 17 | 0 | 17 | 0 |  | 711 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 113 | 0 | 186 | 0 | 17 | 0 | 0 | 0 | 340 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 300 | 172 | 0 | 0 | 0 |  | 6142 | 2521 | 8663 | 3879 | 711 | 2216 | 0 | 1041 | 381 | 162 | 120 | 51 | 102 | 0 | 0 | 104.64
6:00 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 396 | 326 |  | 0 | 250 | 280 | 0 | 0 | 30 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 35 | 135 | 0 | 0 | 290 | 275 | 62 | 26 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 98 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 111 | 62 | 81 | 0 | 166 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 35 | 0 | 78 | 1 | 50 | 17 | 10 | 321 | 55 | 0 | 17 | 0 | 159 | 35 | 17 | 0 | 59 | 50 | 320 | 17 | 0 | 17 | 17 | 0 | 17 | 0 |  | 710 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 113 | 0 | 187 | 0 | 17 | 0 | 0 | 0 | 317 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 300 | 172 | 0 | 0 | 0 |  | 5757 | 2497 | 8254 | 3728 | 710 | 2180 | 0 | 873 | 381 | 163 | 120 | 0 | 98 | 1 | 0 | 104.64
7:00 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 363 | 305 |  | 0 | 250 | 300 | 0 | 0 | 30 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 80 | 0 | 0 | 295 | 305 | 108 | 26 | 31 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 94 | 162 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 110 | 113 | 61 | 81 | 0 | 166 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 35 | 0 | 78 | 5 | 50 | 17 | 10 | 321 | 55 | 0 | 17 | 1 | 159 | 35 | 17 | 0 | 58 | 50 | 320 | 17 | 1 | 17 | 17 | 0 | 17 | 3 |  | 711 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 173 | 0 | 17 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 140 | 0 | 0 | 0 |  | 5730 | 2328 | 8058 | 3708 | 711 | 2189 | 0 | 802 | 260 | 164 | 120 | 0 | 94 | 10 | 0 | 104.64
8:00 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 362 | 308 |  | 0 | 250 | 310 | 0 | 0 | 30 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 80 | 0 | 0 | 320 | 315 | 140 | 26 | 30 | 25 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 6 | 96 | 162 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 110 | 111 | 61 | 78 | 0 | 166 | 18 | 0 | 10 | 310 | 24 | 0 | 0 | 15 | 0 | 0 | 35 | 0 | 78 | 4 | 50 | 17 | 10 | 321 | 55 | 0 | 17 | 2 | 159 | 35 | 17 | 0 | 58 | 60 | 320 | 17 | 11 | 17 | 17 | 0 | 17 | 2 |  | 711 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 153 | 0 | 17 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 140 | 0 | 0 | 1 |  | 5799 | 2392 | 8191 | 3787 | 711 | 2231 | 0 | 812 | 250 | 164 | 120 | 0 | 96 | 20 | 0 | 104.64
9:00 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 399 | 323 |  | 0 | 250 | 240 | 0 | 0 | 30 | 0 | 0 | 124 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 35 | 15 | 25 | 28 | 0 | 33 | 7 | 0 | 91 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 18 | 3 | 80 | 0 | 0 | 330 | 270 | 144 | 26 | 30 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 6 | 102 | 163 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 130 | 111 | 62 | 78 | 0 | 166 | 18 | 0 | 10 | 305 | 8 | 0 | 0 | 15 | 0 | 0 | 35 | 0 | 96 | 0 | 76 | 24 | 23 | 321 | 55 | 0 | 27 | 3 | 240 | 35 | 24 | 0 | 58 | 100 | 320 | 24 | 20 | 72 | 27 | 0 | 17 | 1 |  | 710 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 177 | 0 | 17 | 0 | 0 | 0 | 384 | 2 | 0 | 14 | 0 | 0 | 0 | 0 | 30 | 300 | 179 | 0 | 0 | 1 |  | 5973 | 2513 | 8486 | 3700 | 710 | 2188 | 0 | 1174 | 300 | 166 | 120 | 0 | 102 | 26 | 0 | 104.63
10:00 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 401 | 317 |  | 0 | 250 | 255 | 0 | 0 | 30 | 0 | 0 | 125 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 15 | 25 | 28 | 0 | 33 | 25 | 0 | 91 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 18 | 3 | 80 | 0 | 0 | 280 | 335 | 142 | 26 | 30 | 23 | 56 | 0 | 51 | 0 | 0 | 9 | 22 | 8 | 33 | 17 | 114 | 160 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 130 | 111 | 61 | 78 | 0 | 190 | 18 | 0 | 9 | 285 | 24 | 5 | 0 | 125 | 0 | 0 | 35 | 0 | 114 | 0 | 76 | 70 | 90 | 321 | 55 | 0 | 51 | 4 | 250 | 17 | 34 | 0 | 59 | 90 | 320 | 81 | 27 | 157 | 53 | 0 | 17 | 2 |  | 711 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 159 | 0 | 17 | 0 | 0 | 0 | 371 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 280 | 150 | 0 | 0 | 2 |  | 6534 | 2478 | 9012 | 3732 | 711 | 2144 | 0 | 1709 | 280 | 166 | 120 | 0 | 114 | 36 | 0 | 104.63
11:00 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 374 | 287 |  | 0 | 250 | 295 | 0 | 0 | 30 | 0 | 0 | 127 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 37 | 35 | 15 | 25 | 30 | 33 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 38 | 18 | 7 | 80 | 0 | 0 | 355 | 320 | 138 | 26 | 32 | 23 | 55 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 17 | 122 | 158 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 130 | 110 | 60 | 78 | 0 | 166 | 18 | 0 | 9 | 300 | 24 | 5 | 0 | 148 | 0 | 0 | 35 | 0 | 114 | 0 | 76 | 70 | 107 | 322 | 55 | 0 | 51 | 2 | 250 | 17 | 34 | 0 | 58 | 100 | 320 | 90 | 34 | 162 | 53 | 0 | 17 | 12 |  | 711 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 163 | 0 | 17 | 0 | 0 | 0 | 409 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 300 | 152 | 0 | 0 | 0 |  | 6713 | 2532 | 9245 | 3770 | 711 | 2206 | 0 | 1801 | 300 | 166 | 120 | 0 | 122 | 49 | 0 | 104.63
12:00 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 346 | 276 |  | 0 | 250 | 240 | 0 | 0 | 32 | 0 | 0 | 150 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 54 | 37 | 35 | 15 | 25 | 30 | 33 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 40 | 18 | 7 | 80 | 0 | 0 | 250 | 285 | 138 | 26 | 31 | 23 | 56 | 0 | 51 | 0 | 0 | 17 | 22 | 9 | 33 | 17 | 122 | 160 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 163 | 110 | 61 | 78 | 0 | 166 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 183 | 0 | 0 | 48 | 0 | 114 | 19 | 76 | 96 | 120 | 321 | 73 | 17 | 0 | 5 | 269 | 17 | 80 | 34 | 51 | 90 | 320 | 92 | 23 | 162 | 76 | 0 | 17 | 13 |  | 710 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 168 | 0 | 17 | 0 | 0 | 0 | 325 | 35 | 0 | 55 | 0 | 35 | 0 | 0 | 90 | 340 | 152 | 0 | 0 | 4 |  | 6827 | 2610 | 9437 | 3633 | 710 | 2106 | 0 | 2175 | 340 | 166 | 120 | 0 | 122 | 65 | 0 | 104.63
13:00 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 346 | 255 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 58 | 0 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 30 | 33 | 33 | 25 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 40 | 18 | 12 | 80 | 0 | 0 | 245 | 295 | 129 | 26 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 40 | 22 | 9 | 33 | 14 | 112 | 162 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 110 | 109 | 61 | 78 | 0 | 166 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 273 | 0 | 0 | 85 | 0 | 117 | 8 | 76 | 136 | 123 | 321 | 96 | 17 | 0 | 4 | 269 | 17 | 110 | 34 | 58 | 100 | 321 | 90 | 11 | 162 | 108 | 0 | 17 | 27 |  | 710 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 63 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 143 | 0 | 17 | 0 | 0 | 0 | 324 | 70 | 0 | 90 | 0 | 37 | 0 | 1 | 113 | 350 | 140 | 0 | 0 | 3 |  | 7116 | 2678 | 9794 | 3660 | 710 | 2023 | 0 | 2602 | 350 | 162 | 120 | 0 | 112 | 55 | 0 | 104.62
14:00 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 340 | 242 |  | 0 | 250 | 250 | 0 | 0 | 55 | 0 | 0 | 124 | 0 | 58 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 28 | 33 | 33 | 25 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 46 | 18 | 10 | 80 | 0 | 0 | 245 | 290 | 117 | 26 | 86 | 26 | 30 | 0 | 51 | 0 | 0 | 43 | 22 | 9 | 33 | 14 | 112 | 151 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 110 | 111 | 40 | 81 | 0 | 166 | 18 | 0 | 10 | 270 | 24 | 5 | 0 | 273 | 0 | 0 | 50 | 0 | 131 | 11 | 90 | 100 | 133 | 321 | 98 | 17 | 0 | 1 | 269 | 17 | 110 | 17 | 58 | 100 | 320 | 90 | 19 | 162 | 108 | 0 | 17 | 10 |  | 711 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 143 | 0 | 17 | 0 | 0 | 0 | 293 | 35 | 0 | 70 | 0 | 41 | 0 | 0 | 70 | 320 | 152 | 0 | 0 | 0 |  | 6890 | 2536 | 9426 | 3580 | 711 | 1951 | 0 | 2428 | 320 | 162 | 120 | 0 | 112 | 42 | 0 | 104.62
15:00 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 322 | 243 |  | 0 | 250 | 265 | 0 | 0 | 45 | 0 | 0 | 128 | 0 | 58 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 28 | 33 | 33 | 25 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 48 | 18 | 2 | 80 | 0 | 0 | 245 | 290 | 135 | 26 | 86 | 26 | 30 | 0 | 51 | 0 | 0 | 25 | 22 | 0 | 33 | 14 | 108 | 150 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 163 | 110 | 50 | 81 | 0 | 166 | 18 | 0 | 10 | 290 | 24 | 0 | 0 | 220 | 0 | 0 | 50 | 0 | 132 | 8 | 90 | 100 | 132 | 322 | 97 | 17 | 68 | 0 | 269 | 17 | 68 | 17 | 58 | 100 | 320 | 94 | 13 | 162 | 108 | 0 | 17 | 5 |  | 710 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 149 | 0 | 148 | 0 | 17 | 0 | 0 | 0 | 417 | 35 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 320 | 152 | 0 | 0 | 1 |  | 6896 | 2588 | 9484 | 3582 | 710 | 2146 | 0 | 2302 | 328 | 160 | 120 | 0 | 108 | 28 | 0 | 104.62
16:00 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 341 | 242 |  | 0 | 250 | 282 | 0 | 0 | 40 | 0 | 0 | 131 | 0 | 24 | 0 | 10 | 0 | 0 | 0 | 35 | 55 | 17 | 15 | 25 | 29 | 33 | 25 | 25 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 5 | 80 | 0 | 0 | 245 | 310 | 121 | 26 | 85 | 26 | 30 | 0 | 51 | 0 | 0 | 25 | 22 | 0 | 33 | 6 | 112 | 157 | 0 | 19 | 0 | 43 | 42 | 47 | 0 | 163 | 111 | 50 | 81 | 0 | 166 | 18 | 0 | 10 | 285 | 24 | 0 | 0 | 195 | 0 | 0 | 24 | 0 | 98 | 7 | 90 | 68 | 130 | 322 | 107 | 17 | 34 | 0 | 272 | 17 | 51 | 17 | 52 | 90 | 320 | 72 | 9 | 108 | 35 | 0 | 17 | 4 |  | 711 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 57 | 0 | 0 | 0 | 0 | 147 | 0 | 151 | 0 | 17 | 0 | 0 | 0 | 417 | 17 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 320 | 152 | 0 | 0 | 0 |  | 6525 | 2620 | 9145 | 3603 | 711 | 2160 | 0 | 1880 | 377 | 161 | 120 | 0 | 112 | 21 | 0 | 104.62
17:00 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 338 | 244 |  | 0 | 250 | 225 | 0 | 0 | 50 | 0 | 0 | 124 | 0 | 58 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 29 | 33 | 33 | 25 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 14 | 25 | 18 | 8 | 80 | 0 | 0 | 250 | 265 | 122 | 26 | 85 | 26 | 30 | 0 | 51 | 0 | 0 | 25 | 22 | 0 | 33 | 10 | 118 | 160 | 8 | 19 | 0 | 43 | 30 | 44 | 0 | 130 | 109 | 50 | 81 | 0 | 165 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 205 | 0 | 0 | 46 | 0 | 95 | 1 | 90 | 83 | 132 | 321 | 97 | 20 | 34 | 0 | 272 | 17 | 66 | 17 | 49 | 100 | 320 | 43 | 1 | 108 | 35 | 0 | 17 | 1 |  | 711 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 21 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 144 | 0 | 176 | 0 | 17 | 0 | 0 | 0 | 333 | 17 | 0 | 35 | 0 | 41 | 0 | 0 | 60 | 330 | 152 | 0 | 0 | 0 |  | 6562 | 2649 | 9211 | 3595 | 711 | 1997 | 0 | 2077 | 408 | 161 | 120 | 21 | 118 | 3 | 0 | 104.62
18:00 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 308 | 242 |  | 0 | 250 | 235 | 0 | 0 | 55 | 0 | 0 | 122 | 0 | 102 | 32 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 18 | 33 | 33 | 31 | 0 | 88 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 50 | 39 | 35 | 18 | 13 | 80 | 0 | 0 | 250 | 265 | 108 | 24 | 84 | 26 | 30 | 0 | 51 | 0 | 50 | 40 | 22 | 9 | 33 | 21 | 132 | 156 | 8 | 22 | 0 | 43 | 42 | 44 | 0 | 163 | 111 | 50 | 81 | 0 | 199 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 275 | 0 | 0 | 120 | 0 | 117 | 0 | 90 | 159 | 133 | 321 | 107 | 68 | 67 | 0 | 272 | 18 | 87 | 70 | 94 | 100 | 320 | 61 | 0 | 136 | 55 | 0 | 17 | 0 |  | 710 | 0 | 350 | 0 | 0 | 220 | 0 | 0 | 4 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 50 | 5 | 90 | 27 | 34 | 35 | 25 | 36 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 70 | 0 | 160 | 0 | 17 | 0 | 0 | 0 | 312 | 63 | 0 | 80 | 0 | 100 | 0 | 0 | 113 | 380 | 181 | 0 | 2 | 0 |  | 7504 | 3256 | 10760 | 3544 | 710 | 2043 | 0 | 3085 | 459 | 163 | 220 | 404 | 132 | 0 | 0 | 104.61
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 331 | 243 |  | 0 | 250 | 253 | 0 | 0 | 55 | 0 | 0 | 152 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 11 | 0 | 0 | 0 | 0 |  | 23 | 0 | 75 | 10 | 0 | 46 | 0 | 14 | 80 | 0 | 0 | 250 | 265 | 103 | 26 | 84 | 26 | 30 | 0 | 51 | 0 | 0 | 25 | 22 | 9 | 33 | 21 | 138 | 162 | 8 | 22 | 0 | 44 | 42 | 46 | 0 | 163 | 110 | 50 | 81 | 0 | 219 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 298 | 0 | 0 | 160 | 0 | 133 | 0 | 90 | 200 | 108 | 321 | 115 | 52 | 105 | 0 | 271 | 33 | 110 | 17 | 96 | 100 | 320 | 90 | 0 | 162 | 102 | 0 | 17 | 0 |  | 711 | 0 | 410 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 0 | 0 | 0 | 0 | 37 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 90 | 0 | 198 | 0 | 17 | 0 | 0 | 0 | 383 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 181 | 0 | 0 | 0 |  | 7559 | 3450 | 11009 | 3736 | 711 | 2145 | 0 | 3128 | 509 | 165 | 205 | 272 | 138 | 0 | 0 | 104.61
19:30 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 325 | 243 |  | 0 | 250 | 262 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 20 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 53 | 0 | 0 | 25 | 0 | 20 | 80 | 0 | 0 | 245 | 265 | 98 | 26 | 86 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 21 | 136 | 162 | 8 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 110 | 50 | 81 | 0 | 206 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 298 | 0 | 0 | 160 | 0 | 133 | 0 | 90 | 200 | 126 | 322 | 115 | 52 | 105 | 0 | 275 | 33 | 110 | 0 | 96 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 410 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 31 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 127 | 0 | 191 | 0 | 16 | 0 | 0 | 0 | 421 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 223 | 0 | 0 | 0 |  | 7526 | 3445 | 10971 | 3765 | 711 | 2277 | 0 | 3054 | 519 | 165 | 150 | 194 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 331 | 241 |  | 0 | 250 | 252 | 0 | 0 | 55 | 0 | 0 | 183 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 20 | 33 | 33 | 51 | 0 | 88 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 49 | 0 | 0 | 0 | 18 | 14 | 80 | 0 | 0 | 245 | 265 | 94 | 26 | 85 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 22 | 132 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 163 | 110 | 62 | 81 | 0 | 206 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 298 | 0 | 0 | 160 | 0 | 133 | 0 | 90 | 200 | 128 | 322 | 115 | 52 | 105 | 0 | 278 | 35 | 110 | 0 | 96 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 711 | 0 | 380 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 31 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 137 | 0 | 187 | 0 | 17 | 0 | 0 | 0 | 406 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 224 | 0 | 0 | 0 |  | 7488 | 3417 | 10905 | 3772 | 711 | 2230 | 0 | 3028 | 529 | 163 | 150 | 190 | 132 | 0 | 0 | 104.61
21:00 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 365 | 252 |  | 0 | 250 | 310 | 0 | 0 | 55 | 0 | 0 | 155 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 10 | 0 | 7 | 18 | 28 | 80 | 0 | 0 | 240 | 290 | 93 | 26 | 84 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 22 | 130 | 162 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 109 | 61 | 81 | 0 | 193 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 296 | 0 | 0 | 180 | 0 | 132 | 0 | 90 | 200 | 135 | 323 | 115 | 52 | 105 | 0 | 278 | 35 | 110 | 17 | 96 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 473 | 0 | 380 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 31 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 144 | 0 | 180 | 0 | 17 | 0 | 0 | 0 | 421 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 224 | 0 | 0 | 0 |  | 7615 | 3220 | 10835 | 3799 | 473 | 2281 | 0 | 3086 | 559 | 165 | 150 | 192 | 130 | 0 | 0 | 104.61
22:00 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 377 | 270 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 155 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 10 | 0 | 25 | 18 | 28 | 80 | 0 | 0 | 250 | 265 | 94 | 26 | 83 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 22 | 128 | 163 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 110 | 62 | 81 | 0 | 163 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 245 | 0 | 0 | 190 | 0 | 132 | 0 | 90 | 155 | 133 | 322 | 115 | 52 | 105 | 0 | 286 | 35 | 110 | 17 | 96 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 145 | 0 | 160 | 0 | 17 | 0 | 0 | 0 | 377 | 53 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 440 | 224 | 0 | 0 | 0 |  | 7475 | 3082 | 10557 | 3753 | 710 | 2219 | 0 | 2875 | 519 | 166 | 120 | 67 | 128 | 0 | 0 | 104.6
23:00 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 368 | 290 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 130 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 33 | 80 | 0 | 0 | 25 | 290 | 144 | 26 | 86 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 22 | 128 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 111 | 62 | 81 | 0 | 152 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 245 | 0 | 0 | 191 | 0 | 110 | 0 | 90 | 155 | 133 | 322 | 115 | 52 | 105 | 0 | 273 | 35 | 110 | 0 | 98 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 145 | 0 | 167 | 0 | 17 | 0 | 0 | 0 | 406 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 410 | 226 | 0 | 0 | 0 |  | 7189 | 3035 | 10224 | 3569 | 710 | 2285 | 0 | 2741 | 489 | 166 | 120 | 16 | 128 | 0 | 0 | 104.6
24:00 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 377 | 326 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 100 | 0 | 0 | 25 | 310 | 144 | 26 | 86 | 26 | 40 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 21 | 122 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 111 | 61 | 81 | 0 | 152 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 170 | 0 | 110 | 0 | 90 | 100 | 128 | 321 | 115 | 52 | 105 | 0 | 292 | 35 | 110 | 0 | 66 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 145 | 0 | 179 | 0 | 17 | 0 | 0 | 0 | 408 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 380 | 226 | 0 | 0 | 0 |  | 6985 | 3019 | 10004 | 3627 | 710 | 2362 | 0 | 2439 | 459 | 165 | 120 | 0 | 122 | 0 | 0 | 104.6
KWH | 0 | 0 | 0 | 0 | 0 | 1557727 | 0 | 8867840 | 6846000 |  | 0 | 6158300 | 6492858 | 0 | 0 | 1037057 | 0 | 0 | 3576000 | 0 | 515376 | 135360 | 112720 | 0 | 0 | 0 | 1223640 | 1108536 | 873608 | 426672 | 600000 | 674640 | 706700 | 832800 | 494880 | 0 | 2080904 | 1824000 | 2800000 | 0 | 55832 | 0 | 0 | 0 | 0 |  | 137280 | 0 | 734824 | 167280 | 63630 | 496320 | 410880 | 450720 | 2382526 | 0 | 0 | 6623500 | 7074000 | 3182000 | 635636 | 1765040 | 565416 | 1100640 | 0 | 1261786 | 0 | 63648 | 321624 | 477288 | 187020 | 794900 | 336360 | 2779200 | 3768720 | 21120 | 466488 | 5550 | 1017000 | 1002000 | 1133400 | 0 | 3423027 | 2631000 | 1396336 | 1914240 | 0 | 4222940 | 396000 | 0 | 239040 | 7147000 | 524784 | 168240 | 0 | 3741053 | 0 | 0 | 2253600 | 0 | 2556720 | 76410 | 1965120 | 2270880 | 2335117 | 7728000 | 2295600 | 516000 | 1332327 | 23760 | 5878800 | 703958 | 1581556 | 243960 | 1633800 | 2262720 | 7679500 | 1791360 | 155390 | 2952000 | 1664782 | 0 | 443520 | 76727 |  | 17026909 | 0 | 8247168 | 0 | 0 | 3265920 | 0 | 0 | 4800 | 0 | 0 | 1561000 | 405300 | 0 | 0 | 0 | 0 | 85006 | 9188 | 376536 | 40030 | 39213 | 43472 | 44160 | 132549 | 491760 | 0 | 217098 | 1204364 | 0 | 0 | 0 | 0 | 3311400 | 0 | 4311972 | 0 | 418951 | 0 | 0 | 0 | 8909090 | 800640 | 0 | 1544832 | 0 | 1062883 | 0 | 5220 | 1530048 | 9224000 | 441537 | 0 | 19200 | 13740 |  | 164652513 | 64787986 | 229440499 | 90933228 | 17026909 | 49027012 | 0 | 50132782 | 10428364 | 3904904 | 3265920 | 1585383 | 2779200 | 356797 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 2056199.64 | 0 | 8956518.4 | 7051380 |  | 0 | 6712547 | 7207072.38 | 0 | 0 | 8773502.22 | 0 | 0 | 6186480 | 0 | 4700229.12 | 1331942.4 | 1039278.4 | 0 | 0 | 0 | 8932572 | 8568983.28 | 8613774.88 | 320004 | 450000 | 0 | 0 | 0 | 4785489.6 | 0 | 561844.08 | 492480 | 5068000 | 0 | 518679.28 | 0 | 0 | 0 | 0 |  | 0 | 0 | 7127792.8 | 1597524 | 553581 | 3930854.4 | 517708.8 | 1338638.4 | 3526138.48 | 0 | 0 | 4901390 | 7074000 | 2927440 | 819970.44 | 2029796 | 638920.08 | 1540896 | 0 | 2157654.06 | 0 | 642844.8 | 3071509.2 | 606155.76 | 140265 | 1391075 | 252270 | 20844000 | 3994843.2 | 191769.6 | 592439.76 | 88467 | 1667880 | 1603200 | 2017452 | 0 | 3902250.78 | 2736240 | 2750781.92 | 3656198.4 | 0 | 7305686.2 | 867240 | 0 | 487641.6 | 7218470 | 393588 | 127862.4 | 0 | 28282360.68 | 0 | 0 | 11718720 | 0 | 25158124.8 | 893232.9 | 16015728 | 24639048 | 16462574.85 | 7187040 | 20935872 | 4876200 | 11604568.17 | 0 | 44443728 | 6131474.18 | 13901877.24 | 2434720.8 | 14001666 | 15069715.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98074995.84 | 0 | 8659526.4 | 0 | 0 | 45265651.2 | 0 | 0 | 50352 | 0 | 0 | 1763930 | 628215 | 0 | 0 | 0 | 0 | 836459.04 | 93350.08 | 3332343.6 | 308231 | 530159.76 | 421243.68 | 427910.4 | 1285725.3 | 944179.2 | 0 | 164343.186 | 7262314.92 | 0 | 0 | 0 | 0 | 3874338 | 0 | 5691803.04 | 0 | 628426.5 | 0 | 0 | 0 | 8819999.1 | 8358681.6 | 0 | 14660455.68 | 0 | 8247972.08 | 0 | 57681 | 11307054.72 | 40493360 | 0 | 0 | 0 | 0 |  | 463316062.58 | 272188702.326 | 735504764.906 | 94366903.626 | 98074995.84 | 57187190.5 | 0 | 354794590.14 | 47755674.92 | 1054324.08 | 45265651.2 | 15122053.7 | 20844000 | 1039380.9 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 346 | 276 |  | 0 | 250 | 240 | 0 | 0 | 32 | 0 | 0 | 150 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 54 | 37 | 35 | 15 | 25 | 30 | 33 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 40 | 18 | 7 | 80 | 0 | 0 | 250 | 285 | 138 | 26 | 31 | 23 | 56 | 0 | 51 | 0 | 0 | 17 | 22 | 9 | 33 | 17 | 122 | 160 | 0 | 19 | 1 | 43 | 42 | 47 | 0 | 163 | 110 | 61 | 78 | 0 | 166 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 183 | 0 | 0 | 48 | 0 | 114 | 19 | 76 | 96 | 120 | 321 | 73 | 17 | 0 | 5 | 269 | 17 | 80 | 34 | 51 | 90 | 320 | 92 | 23 | 162 | 76 | 0 | 17 | 13 |  | 710 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 168 | 0 | 17 | 0 | 0 | 0 | 325 | 35 | 0 | 55 | 0 | 35 | 0 | 0 | 90 | 340 | 152 | 0 | 0 | 4 |  | 9437 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 331 | 243 | 0 | 0 | 250 | 253 | 0 | 0 | 55 | 0 | 0 | 152 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 75 | 10 | 0 | 46 | 0 | 14 | 80 | 0 | 0 | 250 | 265 | 103 | 26 | 84 | 26 | 30 | 0 | 51 | 0 | 0 | 25 | 22 | 9 | 33 | 21 | 138 | 162 | 8 | 22 | 0 | 44 | 42 | 46 | 0 | 163 | 110 | 50 | 81 | 0 | 219 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 298 | 0 | 0 | 160 | 0 | 133 | 0 | 90 | 200 | 108 | 321 | 115 | 52 | 105 | 0 | 271 | 33 | 110 | 17 | 96 | 100 | 320 | 90 | 0 | 162 | 102 | 0 | 17 | 0 |  | 711 | 0 | 410 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 0 | 0 | 0 | 0 | 37 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 90 | 0 | 198 | 0 | 17 | 0 | 0 | 0 | 383 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 181 | 0 | 0 | 0 |  | 11009 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 390 | 310 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 18 | 15 | 110 | 0 | 0 | 330 | 330 | 210 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 160 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 723 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 33 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 42 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 42 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 360 | 310 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 18 | 5 | 110 | 0 | 0 | 330 | 330 | 210 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 138 | 160 | 8 | 21 | 1.6 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 100 | 100 | 190 | 50 | 149 | 20 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 723 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 42 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 144 | 0 | 210 | 0 | 42 | 50 | 0 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 622 | 150 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 352 | 307 | 0 | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 33 |  | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 80 | 0 | 0 | 335 | 270 | 146 | 26 | 85 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 16 | 94 | 201 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 109 | 40 | 81 | 0 | 152 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 78 | 15 | 50 | 0 | 10 | 323 | 115 | 0 | 0 | 1 | 104 | 0 | 0 | 0 | 58 | 100 | 320 | 0 | 23 | 35 | 0 | 0 | 17 | 6 | 0 | 709 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 100 | 0 | 165 | 0 | 17 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 280 | 226 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 8058 | 7:00
| Highest Generation |  | 11009 | 19:00
| Day Peak Generation |  | 9437 | 12:00
| Evening Peak Generation |  | 11009 | 19:00
| HVDC Max Flow |  | 711 | 1:00
| HVDC EvPeak Flow |  | 711 | 19:00
| Load factor L.F |  | 86.84%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-20
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9437 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8096 | MW
Evening Peak Generation : |  | 11009 | MW Hour : | 19:00 | Available Max Generation : |  | 14569 | MW
E.P. Demand (at gen end) : |  | 11009 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11009 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3069 | MW
Total Gen. (MKWH) : |  | 229.4405 | System Load Factor : | 86.84% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -24 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-20
Actual : | 104.58 | Ft.(MSL) , | Rule curve : | 107.8 | Ft.( MSL )
Gas Consumed : | Total = | 1142.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151554094.126
: |  | Coal : | 47755674.92 | Oil : | 415182295.04 | Total : | 614492064.086
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4173.0068 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1420.685 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1273.1774 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1150.5264 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1039.6571 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 838.9706 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 467.0113 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 215.9568 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 647.0659 |  |  | 0 | 0%
Total | 0 |  | 11226.0573 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2 ,3
2) Ghorasal-3,4,5,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kishoreganj 132/33 kV T3 transformer was under shutdown from 09:36 to 15:45 for C/M.
b) Munshiganj 132/33 kV T1 transformer was under shutdown from 12:29 to 13:49 due to high temperature
at 33 kV B-phase isolator.
c) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 10:49 to 15:28 for A/M.
d) Naogaon 132/33 kV T3 transformer was under shutdown from 08:30 to 10:05 for C/M. |  |  |  |  | About 20 MW power interruption occurred under Naogaon S/S area
from 08:30 to 10:05.
e) Rangamati 132/33 kV T1 transformer was under shutdown from 09:49 to 11:54 for C/M.
f) Satkhira 132/33 kV T2 transformer was under shutdown from 08:10 to 09:25 for C/M.
g) Tongi-Uttara 3rd 132 kV Ckt was under shut down from 12:31 to 16:12 for protection test.
h) Munshiganj 132/33 kV T2 transformer was under shutdown from 13:50 to 17:04 due to high temperature.
i) Bheramara-Baharampur 400 kV Line-4 was shut down at 11:58 for D/W.
j) Hathazari-Rampur 230 kV Bay-1 was under shut down from 10:09 to 17:34 for D/W.
k) Chowmuhuni 132/33 kV T2 transformer was under shutdown from 14:38 to 15:55 due to R/H maintenance.
l) Feni 132/33 kV T2 transformer was under shutdown from 14:47 to 16:05 due to R/H maintenance.
m) Pabna 132/33 kV T1 transformer along with 33 kV Bus was under shutdown from 21:22 to 21:48 |  |  |  |  | About 31 MW power interruption occurred under Pabna S/S area
for C/M by NESCO. |  |  |  |  | from 21:22 to 21:48.
n) Madanganj-Charsayedpur 132 kV Ckt-1 was charged at 18:10 from Madanganj end.
o) Madanganj-Charsayedpur 132 kV Ckt-2 was charged at 18:13 from Madanganj end.
p) After maintenance Saidpur 132/33 kV T5 transformer was switched on at 22:30.
q) After maintenance Ashuganj(N) CCPP ST was synchronized at 02:10(20/10/2021).
r) Rangamati-Khagrachari 132 kV Ckt-2 tripped at 06:35(20/10/2021) from both ends showing Dist. Z-1,
R,Y-phase at both ends and was switched on at 06:50(20/10/2021).
s) Khulna(C) 132/33 kV T3 transformer was shutdown at 07:41(20/10/2021) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 87 | 1557727 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 331 | 8867840 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 243 | 6846000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6158300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 253 | 6492858 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1037057 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 112720 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 426672
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 152 | 3576000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 515376 | Low demand.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1223640
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 135360 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1108536
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 873608
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1274640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 706700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 832800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 494880
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 3741053
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 2556720 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 516000 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1791360 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2952000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 76727
| Dhaka area Total |  |  |  | 5560 | 2508 | 53874574
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 11 | 55832 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 76410
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 496320
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 165 | 3904904 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1332327
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 75 | 734824 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 167280 | Low demand.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1965120 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 410880 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 450720
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 63630 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23760
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 271 | 5878800 | Engine problem
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 33 | 703958 | Low demand.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1581556
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2262720
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 102 | 1664782 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1247 | 24573823
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2382526 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 103 | 3182000 | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 250 | 6623500 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 7074000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 565416 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 1100640 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 635636 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1261786
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 108 | 2335117 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 63648 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 84 | 1765040 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2270880
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 477288
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 187020
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 138 | 2779200
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 794900
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 321624 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 336360 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 243960 | Low demand.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1633800 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1601 | 36477861
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 162 | 3768720 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 466488
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 8 | 21120
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5550
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 160 | 2253600 | Low demand.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2295600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 155390
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 137280
| Mymensingh Area Total |  |  |  | 622 | 490 | 9103748
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1017000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1002000 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3423027
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2631000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 46 | 1133400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 168240 | Engine problem
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 1396336 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1914240
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4222940
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 396000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 524784 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 7147000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 321 | 7728000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 239040
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7679500 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1713 | 40622507
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 711 | 17026909
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 4800 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 205 | 3265920 | Low demand.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8247168 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 800640
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1431 | 29345437
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 24 | 405300 | Machine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1561000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 418951 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 9224000
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 181 | 441537
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 19200 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 717 | 12069988
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 85006
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 9188 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 40030 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 39213 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 43472 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 90 | 3311400 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 198 | 4311972
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Under maint.
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 383 | 8909090
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 132549 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 491760
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217098
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 44160 | Reserve.
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 376536 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1544832
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1530048
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 13740
| Rajshahi Area Total |  |  |  | 2179 | 1110 | 21100094
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1204364
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1062883
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 5220
| Rangpur Area Total |  |  |  | 605 | 192 | 2272467
| Total |  |  |  | 20934 | 11009 | 229440499
| Eastern Grid Total |  |  |  | 13975 | 7559 | 164652513
| Western Grid Total |  |  |  | 6959 | 3450 | 64787986
| National Grid Total |  |  |  | 20934 | 11009 | 229440499
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-19
(a) ENTIRE EASTERN GRID : |  | 7600 | MW | (b) ENTIRE WESTERN GRID : |  | 3142 | MW
i) Dhaka area |  | 4120 | MW | i) Khulna area |  | 1162 | MW
ii) Chittagong area |  | 1243 | MW | ii) Rajshahi area |  | 1086 | MW
iii) Comilla area |  | 915 | MW | iii) Barisal area |  | 263 | MW
iv) Mymensingh area |  | 887 | MW | iv) Rangpur area |  | 631 | MW
v) Sylhet area |  | 435 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10742 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 9:00 | Kishoreganj | 122 | 21:00 | Benapol | 44 | 18:00
Munsiganj | 80 | 20:00 | Netrokona | 100 | 18:30 | Jhenida(Old) | 88 | 18:00
Sonargaon | 73 | 23:00 | Jamalpur | 129 | 18:30 | Bottail | 104 | 18:00
Shyampur | 178 | 1:00 | Sherpur | 106 | 22:00 | G.K Project | 46 | 18:00
Bhulta | 180 | 1:00 | Srimongal | 54 | 18:30 | Faridpur | 111 | 19:00
Madanganj | 46 | 18:00 | Shahjibazar | 103 | 22:00 | Rajbari | 42 | 18:30
Shitalakhya | 109 | 12:00 | Fenchuganj | 36 | 21:00 | Madaripur | 72 | 21:00
Rahim steel | 20 | 8:00 | Kulawara | 42 | 21:00 | Sariatpur | 50 | 19:30
Matuail | 60 | 15:00 | Sylhet | 137 | 13:00 | Gopalganj | 69 | 18:30
Ghorasal | 69 | 18:00 | Chatak | 27 | 1:00 | Bagerhat | 72 | 19:30
Narsingdi | 154 | 23:00 | Sunamganj | 43 | 20:00 | Mongla | 34 | 2:00
Haripur (SBU) | 120 | 15:00 | Biani Bazar | 53 | 21:00 | Satkhira | 74 | 18:00
Sreenagar | 34 | 21:00 | Comilla (S) | 144 | 18:30 | Gallamari | 30 | 1:00
Ullon | 69 | 14:00 | Comilla(N) | 91 | 19:30 | Magura | 42 | 19:00
Hasnabad | 69 | 19:30 | Chandpur | 55 | 22:00 | Norail | 38 | 19:00
Magbazar | 77 | 13:00 | Feni | 100 | 16:00 | Chuadanga | 78 | 18:30
Maniknagar | 64 | 13:00 | Chowmuhani | 147 | 22:00 | Barisal(N) | 30 | 19:00
Bangabhaban | 12 | 10:00 | Ashuganj | 39 | 1:00 | Barisal (S) | 84 | 19:00
Motijheel | 26 | 16:00 | Daudkandi | 122 | 22:00 | Patuakhali | 82 | 19:00
Narinda | 52 | 12:00 | B.Baria | 142 | 21:00 | Bhandaria | 40 | 20:00
Kazla | 79 | 11:00 | Ramganj | 64 | 22:00 | Borguna | 14 | 18:30
Dhanmondi | 166 | 13:00 | Chaddagram | 45 | 1:00 | Borhan Uddin | 29 | 22:00
Lalbag | 87 | 13:00 | PHP | 8 | 10:00 | Ishurdi | 56 | 18:30
Madartek | 62 | 18:30 | Kochua | 48 | 18:00 | Ruppur Paromanobik | 4 | 10:00
Dhaka University | 32 | 12:00 | Madunaghat | 55 | 12:00 | Natore | 109 | 18:30
Aftabnagar | 14 | 12:00 | Hathazari | 99 | 18:00 | Bogra | 155 | 18:30
Fatullah | 58 | 12:00 | Khulshi | 168 | 17:00 | Noagaon | 97 | 18:30
Nawabganj | 43 | 21:00 | Halishahar | 102 | 13:00 | Rajshahi | 123 | 20:00
Keraniganj | 70 | 18:00 | Baraulia | 148 | 13:00 | Rajshahi New | 14 | 20:00
Banani | 29 | 14:00 | Sikalbaha | 38 | 14:00 | C.Nawabganj | 50 | 20:00
Mirpur | 114 | 18:00 | Dohazari | 100 | 21:00 | Amnura | 38 | 20:00
Kalyanpur | 90 | 18:00 | Cox'sbazar | 91 | 21:00 | Pabna | 86 | 18:00
Gulshan | 108 | 14:00 | Chandraghona | 28 | 18:00 | Shahjadpur | 81 | 19:00
Uttara | 86 | 18:00 | Kaptai | 4.5 | 18:00 | Serajganj | 84 | 20:00
Uttara New | 15 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 58 | 20:00
Kamrangirchar | 92 | 13:00 | Bakulia | 114 | 14:00 | Joypurhat | 47 | 21:00
Savar | 158 | 15:00 | Julda | 27 | 12:00 | Sherpur(Bogura) | 52 | 18:30
Bhasantec | 126 | 13:00 | TK chemical | 30.5 | 18:00 | Mohastangor | 56 | 19:00
Agargaon | 74 | 13:00 | Modern Steel | 4.5 | 12:00 | Bhangura | 25 | 20:00
Satmosjid | 98 | 15:00 | Shahmirpur | 29 | 18:30 | Rangpur | 114 | 18:00
Tongi | 112 | 18:00 | Khagrachhari | 22 | 18:00 | Lalmonirhat | 31 | 18:00
Kabirpur | 221 | 11:00 | Matarbari | 39 | 19:30 | Saidpur | 85 | 18:00
Basundhara | 183 | 18:00 | Baroiar Hat | 48 | 0:00 | Purbasadipur | 91 | 18:00
Manikganj | 62 | 22:00 | Rangamati | 12 | 12:00 | Thakurgaon | 61 | 18:30
Joydevpur | 164 | 18:00 | Abul Khair 230 | 7 | 9:00 | Palashbari | 99 | 19:30
New Tongi | 84 | 12:00 | BSRM | 155 | 2:00 | Barapukuria | 46 | 21:00
Kodda | 264 | 16:00 | GPH Ispat | 93 | 4:00 | Panchagar | 38 | 18:00
Dhamrai | 94 | 18:30 | Agrabad | 85 | 15:00 | Joldhaka | 40 | 18:00
Rajendrapur | 98 | 18:30 | Goalpara | 20 | 1:00 | Kurigram | 46 | 20:00
Valuka | 112 | 21:00 | Central S/S | 78 | 13:00 | Mithapukur | 25 | 18:00
Tangail | 180 | 19:30 | Noapara | 37 | 18:00
Mymensing | 177 | 18:00 | Jessore | 87 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 22:00 | 404 | 10:00 | Kaliakoir | 397 | 0.29167 | 388 | 0.33333
| Bheramara | 405 | 13:00 | 392 | 19:00 | Bhulta | 391 | 0.91667 | 379 | 0.375
| Ashuganj(N) | 394 | 12:00 | 384 | 23:00 | Gopalganj | 409 | 0.625 | 393 | 0.83333
| Payra | 412 | 22:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 237 | 18:00 | 226 | 5:00
| Ishurdi | 235 | 6:00 | 228 | 8:00 | Megnaghat | 234 | 12:00 | 230 | 9:00
| Ashuganj | 242 | 13:00 | 236 | 8:00 | Fenchuganj | 245 | 3:00 | 241 | 15:00
| Serajganj | 230 | 1:00 | 225 | 7:00 | Siddhirganj | 232 | 22:00 | 228 | 10:00
| Baghabari | 234 | 17:00 | 226 | 9:00 | Maniknagar | 232 | 22:00 | 224 | 16:00
| Barapukuria | 237 | 6:00 | 226 | 8:00 | Agargaon | 230 | 6:00 | 223 | 10:00
| Bogra | 227 | 6:00 | 216 | 8:00 | Barisal | 245 | 18:30 | 236 | 22:00
| Rajshahi | 232 | 18:00 | 221 | 23:00 | Bhola 225 MW | 246 | 8:00 | 240 | 24:00
| Khulna South | 235 | 6:00 | 228 | 8:00 | AKSML | 236 | 18:30 | 227 | 6:00
| Rampura | 231 | 5:00 | 226 | 16:00 | BSRM | 235 | 18:00 | 226 | 11:00
| Haripur | 231 | 22:00 | 225 | 10:00 | Bibiyana | 243 | 4:00 | 239 | 16:00
| Hasnabad | 230 | 17:00 | 223 | 7:00 | Bhulta | 234 | 17:00 | 228 | 9:00
| Shyampur | 229 | 22:00 | 223 | 10:00 | Ashuganj (S) | 239 | 21:00 | 233 | 9:00
| Aminbazar | 232 | 1:00 | 225 | 2:00 | Kaliakoir | 232 | 20:00 | 223 | 8:00
| Tongi | 230 | 19:30 | 220 | 7:00 | GPH | 236 | 18:00 | 226 | 8:00
| Comilla (N) | 234 | 17:00 | 228 | 11:00 | Jhenaidah | 230 | 6:00 | 223 | 22:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 18:00 | 131 | 10:00 | Madanhat | 137 | 0.77083 | 132 | 0.625
| Munsiganj | 137 | 22:00 | 132 | 10:00 | Hathazari | 139 | 0.75 | 133 | 0.20833
| Sonargaon | 135 | 2:00 | 131 | 16:00 | Khulshi | 135 | 0.75 | 128 | 0.16667
| Shyampur | 137 | 18:00 | 133 | 10:00 | Halishahar | 138 | 0.83333 | 130 | 0.25
| Bhulta | 130 | 2:00 | 126 | 10:00 | Baraulia | 137 | 0.75 | 130 | 0.45833
| Madanganj | 136 | 18:00 | 130 | 12:00 | Sikalbaha | 138 | 0.75 | 130 | 0.29167
| Shitalakhya | 137 | 18:00 | 132 | 9:00 | Dohazari | 134 | 0.75 | 126 | 0.16667
| Rahim steal | 135 | 21:00 | 132 | 10:00 | Cox'sbazar | 125 | 0.75 | 110 | 0.16667
| Matuail | 135 | 18:00 | 131 | 10:00 | Chandraghona | 138 | 0.75 | 132 | 0.25
| Ghorasal | 140 | 1:00 | 140 | 1:00 | Kaptai | 137 | 0.75 | 135 | 0.041667
| Narsinghdi | 134 | 17:00 | 129 | 1:00 | A. Khaer Stl. | 136 | 0.75 | 131 | 0.20833
| Haripur (SBU) | 136 | 22:00 | 131 | 16:00 | Bakulia | 137 | 0.75 | 129 | 0.45833
| Sreenagar | 135 | 21:00 | 131 | 10:00 | Julda | 139 | 0.75 | 131 | 0.25
| Ullon | 135 | 2:00 | 129 | 10:00 | TK Chemical | 137 | 0.75 | 131 | 0.20833
| Hasnabad | 135 | 1:00 | 134 | 11:00 | Modern Steel | 135 | 0.375 | 130 | 0.45833
| Magbazar | 135 | 6:00 | 129 | 10:00 | Shahmirpur | 136 | 0.041667 | 129 | 0.45833
| Maniknagar | 135 | 3:00 | 130 | 10:00 | Khagrachhari | 136 | 0.75 | 131 | 0.25
| Bangabhaban | 135 | 3:00 | 130 | 10:00 | Matarbari | 129 | 0.25 | 120 | 0.83333
| Motijheel | 135 | 3:00 | 130 | 10:00 | Baroiar Hat | 137 | 0.75 | 131 | 0.041667
| Narinda | 135 | 3:00 | 130 | 10:00 | Rangamati | 136 | 18:00 | 131 | 11:00
| Kazla | 135 | 3:00 | 130 | 10:00 | Agrabad | 137 | 18:00 | 130 | 7:00
| Dhanmondi | 135 | 3:00 | 131 | 10:00 | Goalpara S/S | 139 | 4:00 | 136 | 0.77083
| Lalbag | 135 | 22:00 | 130 | 10:00 | Khulna Central S/S | 138 | 2:00 | 135 | 0.33333
| Madartek | 134 | 1:00 | 129 | 10:00 | Noapara | 138 | 5:00 | 134 | 0.75
| Dhaka University | 134 | 2:00 | 130 | 9:00 | Jessore | 137 | 6:00 | 132 | 0.95833
| Aftabnagar | 134 | 1:00 | 129 | 10:00 | Benapol | 137 | 0.25 | 131 | 0.95833
| Fatullah | 138 | 22:00 | 133 | 10:00 | Jhenida(Old) | 138 | 6:00 | 133 | 0.95833
| Nawabganj | 134 | 5:00 | 130 | 11:00 | Bottail | 137 | 0.70833 | 133 | 0.95833
| Keraniganj | 134 | 2:00 | 130 | 16:00 | G.K Project | 140 | 0.20833 | 136 | 0.45833
| Banani | 134 | 2:00 | 128 | 10:00 | Faridpur | 138 | 0.29167 | 130 | 0.875
| Mirpur | 134 | 22:00 | 127 | 8:00 | Rajbari | 138 | 0.29167 | 130 | 0.875
| Kalyanpur | 134 | 21:00 | 129 | 8:00 | Madaripur | 141 | 0.25 | 134 | 0.875
| Gulshan | 134 | 6:00 | 129 | 10:00 | Shariyatpur S/S | 141 | 7:00 | 133 | 0.875
| Uttara | 133 | 21:00 | 129 | 11:00 | Gopalganj | 144 | 0.25 | 135 | 0.83333
| Uttara New | 133 | 22:00 | 127 | 16:00 | Bagerhat | 137 | 9:00 | 133 | 0.91667
| Kamrangirchar | 135 | 22:00 | 130 | 16:00 | Mongla | 136 | 9:00 | 130 | 0.95833
| Savar | 134 | 1:00 | 128 | 8:00 | Satkhira | 137 | 6:00 | 132 | 23:00
| Bhasantec | 137 | 22:00 | 131 | 10:00 | Gallamari | 139 | 0.25 | 132 | 20:00
| Agargaon | 137 | 2:00 | 132 | 10:00 | Magura | 139 | 17:00 | 134 | 0.8125
| Satmosjid | 137 | 22:00 | 131 | 17:00 | Narail | 137 | 0.25 | 132 | 0.95833
| Tongi | 140 | 21:00 | 132 | 7:00 | Chuadanga | 135 | 6:00 | 129 | 0.95833
| Kabirpur | 136 | 13:00 | 133 | 19:30 | Barisal(N) | 134 | 6:00 | 135 | 0.91667
| Basundhara | 138 | 22:00 | 130 | 16:00 | Barisal (S) | 140 | 6:00 | 134 | 19:30
| Manikganj | 141 | 13:00 | 138 | 21:00 | Patuakhali(S) | 139 | 0.25 | 130 | 0.91667
| Joydevpur | 140 | 22:00 | 133 | 10:00 | Bhandaria | 140 | 0.45833 | 131 | 0.83333
| New Tongi | 139 | 20:00 | 130 | 8:00 | Borguna | 139 | 0.25 | 132 | 0.875
| Kodda | 135 | 21:00 | 123 | 8:00 | Jhenaidah(230kV S/S) | 138 | 5:00 | 133 | 22:00
| Dhamrai | 138 | 21:00 | 133 | 16:00 | Ishurdi | 137 | 6:00 | 133 | 8:00
| Rajendrapur | 134 | 21:00 | 122 | 7:00 | Ruppur Paromanobik | 137 | 18:00 | 133 | 13:00
| Valuka | 126 | 13:00 | 118 | 18:30 | Natore | 136 | 18:00 | 131 | 11:00
| Tangail | 135 | 4:00 | 130 | 10:00 | Bogra | 136 | 6:00 | 129 | 11:00
| Mymensing | 130 | 13:00 | 124 | 1:00 | Noagaon | 132 | 17:00 | 124 | 8:00
| Kishorganj | 133 | 13:00 | 126 | 19:30 | Rajshahi | 136 | 17:00 | 130 | 8:00
| Netrokona | 128 | 17:00 | 121 | 19:30 | Rajshahi New | 137 | 18:00 | 132 | 8:00
| Jamalpur | 137 | 13:00 | 127 | 7:00 | C.Nawabganj | 134 | 18:00 | 129 | 8:00
| Sherpur | 135 | 4:00 | 125 | 7:00 | Amnura | 138 | 18:00 | 129 | 8:00
| Srimongal | 138 | 1:00 | 135 | 18:30 | Pabna | 136 | 6:00 | 131 | 11:00
| Shahjibazar | 137 | 7:00 | 133 | 23:00 | Shahjadpur | 139 | 18:00 | 135 | 10:00
| Fenchuganj | 138 | 17:00 | 135 | 11:00 | Serajganj | 135 | 18:00 | 132 | 15:00
| Khulawara | 136 | 7:00 | 133 | 23:00 | Niyamatpur | 131 | 17:00 | 123 | 8:00
| Sylhet | 133 | 5:00 | 132 | 1:00 | Joypurhat | 133 | 17:00 | 125 | 11:00
| Chatak | 133 | 8:00 | 131 | 1:00 | Sherpur(Bogura) | 135 | 18:00 | 128 | 8:00
| Sunamganj | 131 | 17:00 | 127 | 1:00 | Mohastangor | 134 | 18:00 | 125 | 8:00
| Biani Bazar | 133 | 7:00 | 130 | 3:00 | Bangura | 137 | 18:00 | 132 | 8:00
| Comilla(s) | 128 | 4:00 | 125 | 10:00 | Rangpur | 132 | 17:00 | 119 | 13:00
| Comilla(n) | 143 | 21:00 | 136 | 11:00 | Lalmonirhat | 132 | 6:00 | 124 | 8:00
| Chandpur | 142 | 12:00 | 135 | 4:00 | Saidpur | 132 | 5:00 | 124 | 11:00
| Feni | 138 | 18:00 | 131 | 3:00 | Purbasadipur | 131 | 6:00 | 120 | 1:00
| Chowmuhani | 134 | 14:00 | 130 | 0:00 | Thakurgaon | 133 | 6:00 | 125 | 11:00
| Ashuganj | 140 | 6:00 | 137 | 1:00 | Palashbari | 133 | 6:00 | 126 | 11:00
| Daudkandi | 136 | 13:00 | 132 | 1:00 | Barapukuria | 137 | 6:00 | 126 | 8:00
| B.Baria | 134 | 6:00 | 130 | 23:00 | Panchagar | 137 | 0.25 | 126 | 0.45833
| Ramganj | 137 | 19:00 | 132 | 1:00 | Joldhaka | 132 | 0.25 | 121 | 0.45833
| Chaddagram | 139 | 13:00 | 133 | 4:00 | Kurigram | 133 | 0.70833 | 124 | 0.33333
| PHP | 138 | 18:00 | 130 | 8:00 | Mithapukur | 134 | 0.20833 | 126 | 0.33333
| Kochua | 138 | 12:00 | 133 | 11:00

## L-Curve
Date | 2021-10-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 170 | 6985 | 3019 | 10004 |  |  |  | QF-LDC-11
0:30 | 165 | 6983.5 | 2985 | 9968.5 | Date: | 2021-10-19
1:00 | 160 | 6982 | 2951 | 9933
1:30 | 176 | 6864 | 2883 | 9747
2:00 | 192 | 6746 | 2815 | 9561
2:30 | 192 | 6587 | 2731.5 | 9318.5 | [5 empty] | Gen. at Eve. Peak | 11009 | 11009 MW (19:00 )
3:00 | 192 | 6428 | 2648 | 9076 | [6 empty] | 19:00
3:30 | 199 | 6377 | 2620.5 | 8997.5 | [5 empty] | Gen. at Day Peak | 9437 | 9437 MW (12:00 )
4:00 | 206 | 6326 | 2593 | 8919 | [6 empty] | 12:00
4:30 | 235 | 6234 | 2557 | 8791 | [5 empty] | Highest Generation | 11009
5:00 | 264 | 6142 | 2521 | 8663 | [6 empty] | 19:00
5:30 | 276 | 5949.5 | 2509 | 8458.5
6:00 | 288 | 5757 | 2497 | 8254
6:30 | 219 | 5743.5 | 2412.5 | 8156
7:00 | 150 | 5730 | 2328 | 8058
7:30 | 128 | 5764.5 | 2360 | 8124.5
8:00 | 106 | 5799 | 2392 | 8191
8:30 | 258 | 5886 | 2452.5 | 8338.5
9:00 | 410 | 5973 | 2513 | 8486
9:30 | 374 | 6253.5 | 2495.5 | 8749
10:00 | 338 | 6534 | 2478 | 9012
10:30 | 330 | 6623.5 | 2505 | 9128.5
11:00 | 322 | 6713 | 2532 | 9245
11:30 | 327 | 6770 | 2571 | 9341
12:00 | 332 | 6827 | 2610 | 9437
12:30 | 245 | 6971.5 | 2644 | 9615.5
13:00 | 158 | 7116 | 2678 | 9794
13:30 | 189 | 7003 | 2607 | 9610
14:00 | 220 | 6890 | 2536 | 9426
14:30 | 256 | 6893 | 2562 | 9455
15:00 | 292 | 6896 | 2588 | 9484
15:30 | 346 | 6710.5 | 2604 | 9314.5
16:00 | 400 | 6525 | 2620 | 9145
16:30 | 350 | 6543.5 | 2634.5 | 9178
17:00 | 300 | 6562 | 2649 | 9211
17:30 | 216 | 7033 | 2952.5 | 9985.5
18:00 | 132 | 7504 | 3256 | 10760
18:30 | 164 | 7531.5 | 3353 | 10884.5
19:00 | 196 | 7559 | 3450 | 11009
19:30 | 174 | 7526 | 3445 | 10971
20:00 | 140 | 7488 | 3417 | 10905 |  |  |  | Executive Engineer
20:30 | 82 | 7551.5 | 3318.5 | 10870 |  |  |  | Network Operation Division
21:00 | 24 | 7615 | 3220 | 10835
21:30 | 15 | 7545 | 3151 | 10696
22:00 | 6 | 7475 | 3082 | 10557 |  |  |  |  | Page 6 of 7
22:30 | 63 | 7332 | 3058.5 | 10390.5
23:00 | 120 | 7189 | 3035 | 10224
23:30 | 145 | 7087 | 3027 | 10114
24:00 | 170 | 6985 | 3019 | 10004
11009 MW (19:00 )
9437 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-19 |  | Energy |  | 229440499
[13 empty] | 2021-10-19 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3627 | 710 | 2362 | 0 | 2439 | 459 | 165 | 120 | 0 | 122 | 0 | 0
0:30 | 3802.5 | 710.5 | 2338.5 | 0 | 2220.5 | 454.5 | 163.5 | 120 | 42.5 | 116 | 0 | 0 | Date: | 2021-10-19
1:00 | 3978 | 711 | 2315 | 0 | 2002 | 450 | 162 | 120 | 85 | 110 | 0 | 0
1:30 | 3980.5 | 710.5 | 2309 | 0 | 1832 | 440 | 162 | 120 | 85 | 108 | 0 | 0 | [8 empty] | Total Energy | 229.4405 | Total Energy Gen 229.440 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 229.440 MKWHr
2:00 | 3983 | 710 | 2303 | 0 | 1662 | 430 | 162 | 120 | 85 | 106 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3981.5 | 710 | 2254 | 0 | 1473 | 430 | 161 | 120 | 85 | 104 | 0 | 0 | [8 empty] | Energy Requirement | 229.4405
3:00 | 3980 | 710 | 2205 | 0 | 1284 | 430 | 160 | 120 | 85 | 102 | 0 | 0
3:30 | 3973.5 | 710.5 | 2218.5 | 0 | 1223.5 | 405.5 | 160 | 120 | 85 | 101 | 0 | 0 | [6 empty] | Shortage
4:00 | 3967 | 711 | 2232 | 0 | 1163 | 381 | 160 | 120 | 85 | 100 | 0 | 0
4:30 | 3923 | 711 | 2224 | 0 | 1102 | 381 | 161 | 120 | 68 | 101 | 0 | 0
5:00 | 3879 | 711 | 2216 | 0 | 1041 | 381 | 162 | 120 | 51 | 102 | 0 | 0
5:30 | 3803.5 | 710.5 | 2198 | 0 | 957 | 381 | 162.5 | 120 | 25.5 | 100 | 0.5 | 0
6:00 | 3728 | 710 | 2180 | 0 | 873 | 381 | 163 | 120 | 0 | 98 | 1 | 0
6:30 | 3718 | 710.5 | 2184.5 | 0 | 837.5 | 320.5 | 163.5 | 120 | 0 | 96 | 5.5 | 0 |  |  |  |  | Coal
7:00 | 3708 | 711 | 2189 | 0 | 802 | 260 | 164 | 120 | 0 | 94 | 10 | 0
7:30 | 3747.5 | 711 | 2210 | 0 | 807 | 255 | 164 | 120 | 0 | 95 | 15 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3787 | 711 | 2231 | 0 | 812 | 250 | 164 | 120 | 0 | 96 | 20 | 0
8:30 | 3743.5 | 710.5 | 2209.5 | 0 | 993 | 275 | 165 | 120 | 0 | 99 | 23 | 0
9:00 | 3700 | 710 | 2188 | 0 | 1174 | 300 | 166 | 120 | 0 | 102 | 26 | 0
9:30 | 3716 | 710.5 | 2166 | 0 | 1441.5 | 290 | 166 | 120 | 0 | 108 | 31 | 0
10:00 | 3732 | 711 | 2144 | 0 | 1709 | 280 | 166 | 120 | 0 | 114 | 36 | 0
10:30 | 3751 | 711 | 2175 | 0 | 1755 | 290 | 166 | 120 | 0 | 118 | 42.5 | 0
11:00 | 3770 | 711 | 2206 | 0 | 1801 | 300 | 166 | 120 | 0 | 122 | 49 | 0
11:30 | 3701.5 | 710.5 | 2156 | 0 | 1988 | 320 | 166 | 120 | 0 | 122 | 57 | 0
12:00 | 3633 | 710 | 2106 | 0 | 2175 | 340 | 166 | 120 | 0 | 122 | 65 | 0
12:30 | 3646.5 | 710 | 2064.5 | 0 | 2388.5 | 345 | 164 | 120 | 0 | 117 | 60 | 0
13:00 | 3660 | 710 | 2023 | 0 | 2602 | 350 | 162 | 120 | 0 | 112 | 55 | 0
13:30 | 3660 | 710 | 2023 | 0 | 2602 | 350 | 162 | 120 | 0 | 112 | 55 | 0
14:00 | 3660 | 710 | 2023 | 0 | 2602 | 350 | 162 | 120 | 0 | 112 | 55 | 0
14:30 | 3621 | 710 | 2084.5 | 0 | 2452 | 339 | 161 | 120 | 0 | 110 | 41.5 | 0
15:00 | 3582 | 710 | 2146 | 0 | 2302 | 328 | 160 | 120 | 0 | 108 | 28 | 0
15:30 | 3592.5 | 710.5 | 2153 | 0 | 2091 | 352.5 | 160.5 | 120 | 0 | 110 | 24.5 | 0
16:00 | 3603 | 711 | 2160 | 0 | 1880 | 377 | 161 | 120 | 0 | 112 | 21 | 0
16:30 | 3599 | 711 | 2078.5 | 0 | 1978.5 | 392.5 | 161 | 120 | 10.5 | 115 | 12 | 0
17:00 | 3595 | 711 | 1997 | 0 | 2077 | 408 | 161 | 120 | 21 | 118 | 3 | 0
17:30 | 3569.5 | 710.5 | 2020 | 0 | 2581 | 433.5 | 162 | 170 | 212.5 | 125 | 1.5 | 0
18:00 | 3544 | 710 | 2043 | 0 | 3085 | 459 | 163 | 220 | 404 | 132 | 0 | 0
18:30 | 3640 | 710.5 | 2094 | 0 | 3106.5 | 484 | 164 | 212.5 | 338 | 135 | 0 | 0
19:00 | 3736 | 711 | 2145 | 0 | 3128 | 509 | 165 | 205 | 272 | 138 | 0 | 0
19:30 | 3765 | 711 | 2277 | 0 | 3054 | 519 | 165 | 150 | 194 | 136 | 0 | 0
20:00 | 3772 | 711 | 2230 | 0 | 3028 | 529 | 163 | 150 | 190 | 132 | 0 | 0
20:30 | 3785.5 | 592 | 2255.5 | 0 | 3057 | 544 | 164 | 150 | 191 | 131 | 0 | 0
21:00 | 3799 | 473 | 2281 | 0 | 3086 | 559 | 165 | 150 | 192 | 130 | 0 | 0
21:30 | 3776 | 591.5 | 2250 | 0 | 2980.5 | 539 | 165.5 | 135 | 129.5 | 129 | 0 | 0
22:00 | 3753 | 710 | 2219 | 0 | 2875 | 519 | 166 | 120 | 67 | 128 | 0 | 0
22:30 | 3661 | 710 | 2252 | 0 | 2808 | 504 | 166 | 120 | 41.5 | 128 | 0 | 0
23:00 | 3569 | 710 | 2285 | 0 | 2741 | 489 | 166 | 120 | 16 | 128 | 0 | 0
23:30 | 3598 | 710 | 2323.5 | 0 | 2590 | 474 | 165.5 | 120 | 8 | 125 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 29.5° C
24:00 | 3627 | 710 | 2362 | 0 | 2439 | 459 | 165 | 120 | 0 | 122 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 229.440 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 229.440 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 87 | 87 | 85 | 85 | 87 | 88 | 89 | 89 | 91 | 91 | 91 | 91 | 87 | 87 | 85 | 86 | 86 | 88 |  | 90 | 90 | 88 | 90 | 91 | 91 | 90 | 2080904
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1824000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 8 |  | 11 | 8 | 8 | 8 | 8 | 8 | 0 | 55832
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 4 |  |  |  | 19 | 8 | 11 | 8 | 7 | 1 | [9 empty] | 76410
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 85 | 85 | 51 | [12 empty] | 102 |  | 75 | 53 | 49 | 51 | 51 |  |  | 734824
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 27 | 51 | 51 |  |  |  | 68 | 34 | 34 | 67 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1332327
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 50 | [7 empty] | 0 | 63648
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 121 | 121 | 122 | 123 | 126 | 122 | 185 | 184 | 124 | 125 | 127 | 150 | 150 | 124 | 128 | 131 | 124 | 122 |  | 152 | 185 | 183 | 155 | 155 | 130 | 130 | 3576000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 125 | 148 | 183 | 273 | 273 | 220 | 195 | 205 | 275 |  | 298 | 298 | 298 | 296 | 245 | 245 | 95 | 3741053
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 635636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 2382526
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 23 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 565416
33 | Ashuganj 225 MW CCPP | 170 | 170 | 170 | 170 | 170 | 62 | 108 | 140 | 144 | 142 | 138 | 138 | 129 | 117 | 135 | 121 | 122 | 108 |  | 103 | 98 | 94 | 93 | 94 | 144 | 144 | 3182000
34 | Ashuganj 450 MW CCPP(South) | 295 | 295 | 300 | 300 | 295 | 275 | 305 | 315 | 270 | 335 | 320 | 285 | 295 | 290 | 290 | 310 | 265 | 265 |  | 265 | 265 | 265 | 290 | 265 | 290 | 310 | 7074000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 290 | 295 | 320 | 330 | 280 | 355 | 250 | 245 | 245 | 245 | 245 | 250 | 250 |  | 250 | 245 | 245 | 240 | 250 | 25 | 25 | 6623500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 55 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 1100640
36 | Chandpur 150 MW CCPP | 92 | 93 | 92 | 92 | 92 | 92 | 31 | 30 | 30 | 30 | 32 | 31 | 86 | 86 | 86 | 85 | 85 | 84 |  | 84 | 86 | 85 | 84 | 83 | 86 | 86 | 1765040
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 397 | 396 | 395 | 395 | 396 | 396 | 363 | 362 | 399 | 401 | 374 | 346 | 346 | 340 | 322 | 341 | 338 | 308 |  | 331 | 325 | 331 | 365 | 377 | 368 | 377 | 8867840
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6158300
41 | Haripur 360MW CCPP(HPL) | 318 | 326 | 326 | 326 | 326 | 326 | 305 | 308 | 323 | 317 | 287 | 276 | 255 | 242 | 243 | 242 | 244 | 242 |  | 243 | 243 | 241 | 252 | 270 | 290 | 326 | 6846000
42 | RPCL 210MW CCPP | 162 | 163 | 163 | 163 | 163 | 163 | 162 | 162 | 163 | 160 | 158 | 160 | 162 | 151 | 150 | 157 | 160 | 156 |  | 162 | 162 | 163 | 162 | 163 | 163 | 163 | 3768720
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 11 | 20 | 27 | 34 | 23 | 11 | 19 | 13 | 9 | 1 | [9 empty] | 155390
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1017000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 30 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1002000
46 | Shajibazar 330 MW CCPP | 161 | 162 | 160 | 146 | 111 | 111 | 113 | 111 | 111 | 111 | 110 | 110 | 109 | 111 | 110 | 111 | 109 | 111 |  | 110 | 110 | 110 | 109 | 110 | 111 | 111 | 2631000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 62 | 61 | 60 | 61 | 61 | 40 | 50 | 50 | 50 | 50 |  | 50 | 50 | 62 | 61 | 62 | 62 | 61 | 1396336
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 81 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1914240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 166 | 190 | 166 | 166 | 166 | 166 | 166 | 166 | 165 | 199 |  | 219 | 206 | 206 | 193 | 163 | 152 | 152 | 4222940
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 396000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239040
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 168240
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 |  | 46 | 47 | 47 | 47 | 50 | 47 | 47 | 1133400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 |  | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 524784
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 280 | 285 | 300 | 290 | 290 | 310 | 305 | 285 | 300 | 310 | 280 | 270 | 290 | 285 | 290 | 270 |  | 265 | 300 | 285 | 270 | 275 | 280 | 310 | 7147000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7679500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 873608
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 6 | 23 |  | 23 | 23 | 23 | 23 | 23 |  | 0 | 137280
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  |  |  | 18 | 18 | 18 | 18 | 18 | 410880
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 18 |  | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 426672
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 466488
63 | Impoprt (Tripura) | 110 | 106 | 102 | 100 | 102 | 98 | 94 | 96 | 102 | 114 | 122 | 122 | 112 | 112 | 108 | 112 | 118 | 132 |  | 138 | 136 | 132 | 130 | 128 | 128 | 122 | 2779200
64 | Malancha, Ctg. EPZ (United) | 36 | 33 | 33 | 33 | 33 | 35 | 33 | 6 | 3 | 3 | 7 | 7 | 12 | 10 | 2 | 5 | 8 | 13 |  | 14 | 20 | 14 | 28 | 28 | 33 | 38 | 450720
65 | Feni 22MW PP (Doreen) | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 477288
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 |  |  |  | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 187020
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 794900
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 6 | 17 | 17 | 17 | 14 | 14 | 14 | 6 | 10 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 21 | 336360
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 30 | 30 | 30 | 28 | 28 | 29 | 29 | 18 |  | 30 | 20 | 20 | 30 | 30 | 30 | 30 | 674640
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 706700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 832800
73 | Ghorashal 108MW PP (Regent) | 53 | 54 | 54 | 54 | 54 | 55 | 54 | 54 | 52 | 60 | 60 | 62 | 70 | 72 | 70 | 70 | 72 | 80 |  | 87 | 87 | 87 | 92 | 92 | 92 | 96 | 1557727
| Feni Lanka Power | [11 empty] | 34 | 34 | 17 | 17 | 17 | 17 | 70 |  | 17 |  |  | 17 | 17 |  | 0 | 243960
| Chowmuhani 113 MW | 63 | 63 | 59 | 58 | 58 | 59 | 58 | 58 | 58 | 59 | 58 | 51 | 58 | 58 | 58 | 52 | 49 | 94 |  | 96 | 96 | 96 | 96 | 96 | 98 | 66 | 1633800
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 17 | 17 | 17 | 17 | 17 | 17 | 72 | 157 | 162 | 162 | 162 | 162 | 162 | 108 | 108 | 136 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2952000
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 7 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 |  | 51 | 51 | 51 | 51 | 25 | 25 | 8 | 494880
79 | Kodda 150MW PP | [16 empty] | 16 | 32 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 135360
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 8 | 8 |  | 8 | 8 |  |  |  |  | 0 | 21120
81 | Jangalia 52 MW PP (Lakdanavi) | [9 empty] | 9 | 16 | 17 | 40 | 43 | 25 | 25 | 25 | 40 |  | 25 | [6 empty] | 321624
| Gazipur 100 MW PP | [11 empty] | 17 | 17 | 17 | 17 | 17 | 20 | 68 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 516000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 2 | 5 | 4 | 1 | 0 | 0 | 0 | [9 empty] | 23760
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 33 | 33 | 35 | 35 | 35 | 35 | 35 | 703958
| Karnaphuli Power Ltd. | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 34 | 34 | 80 | 110 | 110 | 68 | 51 | 66 | 87 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1581556
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 5 | 11 | 10 | 10 | 10 | 10 | 40 | [7 empty] | 0 | 112720
86 | Meghnaghat CCPP ( Summit) | 270 | 260 | 265 | 295 | 285 | 280 | 300 | 310 | 240 | 255 | 295 | 240 | 260 | 250 | 265 | 282 | 225 | 235 |  | 253 | 262 | 252 | 310 | 260 | 290 | 280 | 6492858
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 65 | 17 | 17 | 17 | 17 | 17 | 24 | 81 | 90 | 92 | 90 | 90 | 94 | 72 | 43 | 61 |  | 90 | 104 | 104 | 104 | 104 | 104 | 104 | 1791360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 50 | 50 | 10 | 10 |  | 10 | 50 |  | 10 |  |  | 10 | 10 |  | 0 | 167280
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1261786
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 16 | 24 | 24 | 50 | 58 | 58 | 58 | 24 | 58 | 102 |  | 32 | 7 | 7 | 7 | 7 | 7 | 0 | 515376
95 | Patenga 50MW PP (Baraka) | [8 empty] | 1 | 36 | 38 | 40 | 40 | 46 | 48 | 33 | 25 | 35 |  | 46 | 25 |  | 7 | 25 | 26 | 0 | 496320
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 14 | 39 | [7 empty] | 0 | 63630
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 55 | 55 | 45 | 40 | 50 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1037057
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 17 | 37 | 37 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1108536
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 130 | 130 | 110 | 110 | 130 | 130 | 130 | 163 | 110 | 110 | 163 | 163 | 130 | 163 |  | 163 | 163 | 163 | 130 | 130 | 110 | 110 | 3423027
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | [9 empty] | 5550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1223640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 100 | 100 | 100 | 100 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 48 | 85 | 50 | 50 | 24 | 46 | 120 |  | 160 | 160 | 160 | 180 | 190 | 191 | 170 | 2253600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 96 | 114 | 114 | 114 | 117 | 131 | 132 | 98 | 95 | 117 |  | 133 | 133 | 133 | 132 | 132 | 110 | 110 | 2556720
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 76 | 76 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1965120
116 | Chandpur 200MW (Desh energy) | 68 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 24 | 70 | 70 | 96 | 136 | 100 | 100 | 68 | 83 | 159 |  | 200 | 200 | 200 | 200 | 155 | 155 | 100 | 2270880
117 | Ashuganj 150MW PP (Midland) | 122 | 125 | 50 | 10 | 10 | 10 | 10 | 10 | 23 | 90 | 107 | 120 | 123 | 133 | 132 | 130 | 132 | 133 |  | 108 | 126 | 128 | 135 | 133 | 133 | 128 | 2335117
118 | Bibiyana-III 400 MW CCPP | 323 | 323 | 323 | 322 | 321 | 321 | 321 | 321 | 321 | 321 | 322 | 321 | 321 | 321 | 322 | 322 | 321 | 321 |  | 321 | 322 | 322 | 323 | 322 | 322 | 321 | 7728000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 55 | 55 | 55 | 55 | 55 | 55 | 73 | 96 | 98 | 97 | 107 | 97 | 107 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2295600
| Anwara 300 MW PP (United) | 267 | 215 | 215 | 183 | 178 | 159 | 159 | 159 | 240 | 250 | 250 | 269 | 269 | 269 | 269 | 272 | 272 | 272 |  | 271 | 275 | 278 | 278 | 286 | 273 | 292 | 5878800
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 60 | 100 | 90 | 100 | 90 | 100 | 100 | 100 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2262720
| Anlima Energy Ltd. | 100 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 27 | 53 | 53 | 76 | 108 | 108 | 108 | 35 | 35 | 55 |  | 102 | 108 | 108 | 108 | 108 | 108 | 108 | 1664782
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 2 | 1 | 2 | 12 | 13 | 27 | 10 | 5 | 4 | 1 | [9 empty] | 76727
120 | Eastern Zone Total | 6982 | 6746 | 6428 | 6326 | 6142 | 5757 | 5730 | 5799 | 5973 | 6534 | 6713 | 6827 | 7116 | 6890 | 6896 | 6525 | 6562 | 7504 |  | 7559 | 7526 | 7488 | 7615 | 7475 | 7189 | 6985 | 164652513
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 | [8 empty] | 4800
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 220 |  | 205 | 150 | 150 | 150 | 120 | 120 | 120 | 3265920
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 2 | 35 | 35 | 35 | 70 | 35 | 35 | 17 | 17 | 63 |  | 105 | 90 | 90 | 90 | 53 |  | 0 | 800640
130
131
132 | United Payra Power Ltd. | [17 empty] | 2 | [7 empty] | 0 | 19200
133 | Bhola Nutan Biddut BD LTD (GAS) | 226 | 226 | 225 | 226 | 172 | 172 | 140 | 140 | 179 | 150 | 152 | 152 | 140 | 152 | 152 | 152 | 152 | 181 |  | 181 | 223 | 224 | 224 | 224 | 226 | 226 | 441537
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 418951
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 63 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1561000
140 | Bhola 33 MW PP (Venture) | 19 | 19 | 17 | 17 | 16 | 15 | 15 | 15 | 16 | 18 | 12 | 15 | 17 | 19 | 11 | 11 | 13 | 19 |  | 24 | 26 | 25 | 21 | 26 | 24 | 24 | 405300
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 711 | 710 | 710 | 711 | 711 | 710 | 711 | 711 | 710 | 711 | 711 | 710 | 710 | 711 | 710 | 711 | 711 | 710 |  | 711 | 711 | 711 | 473 | 710 | 710 | 710 | 17026909
147 | Bheramara 410 MW CCPP | 355 | 360 | 355 | 355 | 300 | 300 | 280 | 320 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 350 |  | 410 | 410 | 380 | 380 | 380 | 380 | 380 | 8247168
148 | Payra 1320 MW | 370 | 350 | 350 | 300 | 300 | 300 | 260 | 250 | 300 | 280 | 300 | 340 | 350 | 320 | 320 | 320 | 330 | 380 |  | 430 | 440 | 450 | 480 | 440 | 410 | 380 | 9224000
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 80 | 81 | 81 | 81 | [8 empty] | 8 | 57 | 78 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1204364
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | [6 empty] | 85006
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 2 | 0 | 4 | 3 | 0 | 1 | 0 | 0 | [9 empty] | 13740
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 113 | 110 | 110 | 111 | 113 | 113 | 135 | 149 | 149 | 151 | 149 | 150 | 151 | 151 | 149 | 147 | 144 | 70 |  | 90 | 127 | 137 | 144 | 145 | 145 | 145 | 3311400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 195 | 184 | 184 | 184 | 186 | 187 | 173 | 153 | 177 | 159 | 163 | 168 | 143 | 143 | 148 | 151 | 176 | 160 |  | 198 | 191 | 187 | 180 | 160 | 167 | 179 | 4311972
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 382 | 377 | 315 | 306 | 340 | 317 | 383 | 422 | 384 | 371 | 409 | 325 | 324 | 293 | 417 | 417 | 333 | 312 |  | 383 | 421 | 406 | 421 | 377 | 406 | 408 | 8909090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 5 | [8 empty] | 9188
162 | Bogra 22 MW PP (GBB) | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 491760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 217098
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 | [7 empty] | 0 | 40030
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 34 | [8 empty] | 39213
167 | Katakhali 50 MW Peaking PP | [17 empty] | 35 | [8 empty] | 43472
168 | Santahar 50 MW Peaking PP | [17 empty] | 36 |  | 37 | 31 | 31 | 31 |  |  | 0 | 132549
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 3 | 25 | [7 empty] | 0 | 44160
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 90 |  | 94 | 94 | 94 | 94 |  |  |  | 376536
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | 35 | 35 | 35 | 35 |  |  | 14 | 35 | 35 | 55 | 90 | 70 | 35 | 35 | 35 | 80 |  | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 1544832
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 70 | 35 | 35 | 35 | 35 |  |  | 30 | 35 | 35 | 90 | 113 | 70 | 35 | 35 | 60 | 113 |  | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 1530048
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | [5 empty] | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 44 | 27 | [9 empty] | 35 | 37 | 41 | 35 | 35 | 41 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1062883
177 | Sympa Solar Power 8MW | [9 empty] | 0 | 0 | 0 | 1 |  | 1 | 1 | 0 | [9 empty] | 5220
178
178