## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-21 | Thursday
|  |  | Date (day): | 2021-10-21 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13550.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14579 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-20 | 2021-10-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 105 | 105 | 105 | 85 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 104 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 400 | 397 | 390 | 390
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 308 | 333 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 255 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 14 | 21 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 130 | 154 | 155 | 160 | 50 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 40 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 25 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 8 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 195 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 80 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 52 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 25 | 74 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 130 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 21 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2023 | 2543 | 3363 | 3668 | 700 | 1120
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 28 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 145 | 130 | 130 | 100 |  | Unit 2 & 5 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 7 | 68 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 16 | 31 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 302 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 7 | 68 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 7 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 847 | 1117 | 1446 | 1520 | 165 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 140 | 146 | 146 | 146 |  |  | ST under maint
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 280 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 285 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 98 | 135 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 138 | 138 | 138 |  | 25 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 120 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 7 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 114 | 136 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 22 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 58 | 96 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1435 | 1701 | 2075 | 2301 | 487 | 109
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 166 | 173 | 160 | 170 | 32 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 24 | 40 | 190 | 190 |  | 10 | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 106 | 85 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 345 | 320 | 567.6 | 526 | 32 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 109 | 111 | 110 | 110 |  | 220 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 219 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 20 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 322 | 321 | 321 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1754 | 1771 | 1817 | 1817 | 142 | 395
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 709 | 505 | 727 | 727
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 33 |  | 21 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 380 | 410 | 400 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 52 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 15 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1209 | 1102 | 1507 | 1730 | 0 | 90
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 29 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 17 | 17 | 42 | 42 | 53 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 310 | 490 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 224 | 225 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 633 | 826 | 1092 | 1242 | 53 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 126 | 117 | 126 | 126
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 199 | 186 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | under maint
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 401 | 398 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 90 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 9 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 25 | 70 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 793 | 1020 | 1482 | 1582 | 170 | 301
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 70 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 115 | 150 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 9154 | 10550 | 13550.6 | 14579 | 1749 | 3228
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8784.3693 | 10124 | 13003.4383 | 13990.3124
| A. |  | 2021-10-20 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 10550 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8096 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10550 | MW
| 3 | Day peak Generation : |  |  | 9154 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10124 | MW
| 4 | Evening peak Generation : |  |  | 10550 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 223.8447 | MKWHr | By Solar | 0.4671 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 149.1271 | MKWHr |  | By Oil: | 40.158 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.3074 | MKWHr |  | By Hydro: | 3.8181 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1749 | MW | Dhaka | 3748 | 3748 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3228 | MW | Chittagong | 1153 | 1153 |  | 0 |  | 18:00 |  | 142
|  |  |  | Total = |  |  | 4977 | MW | Khulna | 1289 | 1289 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1187.67 | MMCFD |  |  | Rajshahi | 978 | 978 |  | 0 |  | 19:00 |  | 136
| 8 | Fuel Cost : | i) Gas : | Taka | 156976530.226 | ii) Oil : | Taka | 293727669.52 | Comilla | 993 | 993 |  | 0 |  | 19:30 |  | 140
|  |  | iii) Coal : |  | 52766856.27 | Total | Taka | 503471056.016 | Mymensingh | 732 | 732 |  | 0 |  | 20:00 |  | 138
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.341 | MKWHr. | Sylhet | 414 | 414 |  | 0 |  | 21:00 |  | 136
|  | ii) During Peak Demand : |  |  | -120 | MW (E to W) at | 21:00 | hrs | Barisal | 301 | 301 |  | 0 |  | 22:00 |  | 138
|  | iii) Maximum : |  |  | -264 | MW at | 19:00 | hrs | Rangpur | 516 | 516 |  | 0 |  | 23:00 |  | 136
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.2° C |  |  | Total | 10124 | 10124 |  | 0
| B. |  | 2021-10-21 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 31.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14579 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
| 4 | Reserve(Generation end) |  |  |  | 2179 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 263.0971 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7981 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.16 | MKWHr. | ii) HVDC Flow at Peak Time |  | 505 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.807 | MKWHr. | iii) Maximum HVDC Flow : |  | 710 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.58 |  | (b) Today: | 104.55 |  | (c) Rule Curve: |  | 107.9
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 402 | 326 |  | 0 | 250 | 265 | 0 | 0 | 40 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 100 | 0 | 0 | 35 | 295 | 146 | 26 | 86 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 22 | 116 | 163 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 130 | 111 | 61 | 81 | 0 | 152 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 95 | 0 | 90 | 17 | 122 | 321 | 115 | 0 | 105 | 0 | 292 | 35 | 110 | 0 | 60 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 709 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 145 | 0 | 187 | 0 | 17 | 0 | 0 | 0 | 418 | 0 | 0 | 70 | 0 | 90 | 0 | 0 | 35 | 350 | 226 | 0 | 0 | 0 |  | 6684 | 2944 | 9628 | 3678 | 709 | 2383 | 0 | 2031 | 429 | 162 | 120 | 0 | 116 | 0 | 0 | 104.59
2:00 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 402 | 326 |  | 0 | 250 | 275 | 0 | 0 | 40 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 100 | 0 | 0 | 35 | 320 | 144 | 26 | 85 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 21 | 116 | 172 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 112 | 62 | 81 | 0 | 152 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 78 | 0 | 90 | 0 | 122 | 321 | 115 | 0 | 51 | 0 | 305 | 35 | 17 | 0 | 62 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 710 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 145 | 0 | 188 | 0 | 16 | 0 | 0 | 0 | 421 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 320 | 225 | 0 | 0 | 0 |  | 6417 | 2827 | 9244 | 3713 | 710 | 2400 | 0 | 1624 | 400 | 161 | 120 | 0 | 116 | 0 | 0 | 104.59
3:00 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 402 | 326 |  | 0 | 250 | 260 | 0 | 0 | 40 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 100 | 0 | 0 | 130 | 265 | 146 | 26 | 86 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 21 | 112 | 196 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 110 | 110 | 62 | 81 | 0 | 152 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 78 | 0 | 90 | 0 | 122 | 321 | 115 | 0 | 17 | 0 | 305 | 35 | 0 | 0 | 60 | 100 | 320 | 104 | 0 | 162 | 17 | 0 | 17 | 0 |  | 710 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 145 | 0 | 188 | 0 | 17 | 0 | 0 | 0 | 396 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 310 | 226 | 0 | 0 | 0 |  | 6285 | 2762 | 9047 | 3748 | 710 | 2336 | 0 | 1473 | 389 | 159 | 120 | 0 | 112 | 0 | 0 | 104.59
4:00 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 401 | 326 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 100 | 0 | 0 | 160 | 270 | 146 | 26 | 88 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 21 | 110 | 199 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 112 | 62 | 81 | 0 | 152 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 78 | 0 | 90 | 0 | 125 | 321 | 115 | 0 | 0 | 0 | 270 | 35 | 0 | 0 | 58 | 100 | 320 | 75 | 0 | 162 | 0 | 0 | 17 | 0 |  | 709 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 145 | 0 | 188 | 0 | 17 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 225 | 0 | 0 | 0 |  | 6166 | 2668 | 8834 | 3769 | 709 | 2336 | 0 | 1252 | 379 | 159 | 120 | 0 | 110 | 0 | 0 | 104.58
5:00 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 395 | 326 |  | 0 | 250 | 265 | 0 | 0 | 15 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 39 | 100 | 0 | 0 | 200 | 265 | 146 | 26 | 88 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 21 | 108 | 212 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 110 | 62 | 81 | 0 | 152 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 78 | 0 | 90 | 0 | 125 | 321 | 115 | 0 | 0 | 0 | 104 | 35 | 0 | 0 | 58 | 100 | 320 | 35 | 0 | 162 | 0 | 0 | 17 | 0 |  | 709 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 145 | 0 | 188 | 0 | 17 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 225 | 0 | 0 | 0 |  | 6004 | 2682 | 8686 | 3808 | 709 | 2352 | 0 | 1046 | 382 | 161 | 120 | 0 | 108 | 0 | 0 | 104.58
6:00 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 390 | 330 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 39 | 100 | 0 | 0 | 290 | 265 | 146 | 26 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 21 | 100 | 213 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 110 | 62 | 81 | 0 | 152 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 78 | 0 | 50 | 0 | 10 | 321 | 115 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 58 | 100 | 320 | 0 | 0 | 90 | 0 | 0 | 17 | 0 |  | 709 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 145 | 0 | 177 | 0 | 17 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 300 | 226 | 0 | 0 | 0 |  | 5756 | 2561 | 8317 | 3856 | 709 | 2263 | 0 | 726 | 380 | 163 | 120 | 0 | 100 | 0 | 0 | 104.58
7:00 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 357 | 310 |  | 0 | 250 | 270 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | 100 | 0 | 0 | 285 | 265 | 146 | 26 | 86 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 17 | 92 | 205 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 111 | 61 | 81 | 0 | 152 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 78 | 2 | 50 | 0 | 10 | 321 | 115 | 0 | 0 | 1 | 105 | 0 | 0 | 0 | 58 | 100 | 320 | 0 | 2 | 35 | 0 | 0 | 17 | 2 |  | 709 | 0 | 330 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 100 | 0 | 165 | 0 | 17 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 226 | 0 | 0 | 0 |  | 5638 | 2480 | 8118 | 3749 | 709 | 2268 | 0 | 661 | 359 | 163 | 110 | 0 | 92 | 7 | 0 | 104.57
8:00 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 352 | 307 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 80 | 0 | 0 | 335 | 270 | 146 | 26 | 85 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 16 | 94 | 201 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 109 | 40 | 81 | 0 | 152 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 78 | 15 | 50 | 0 | 10 | 323 | 115 | 0 | 0 | 1 | 104 | 0 | 0 | 0 | 58 | 100 | 320 | 0 | 23 | 35 | 0 | 0 | 17 | 6 |  | 709 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 100 | 0 | 165 | 0 | 17 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 280 | 226 | 0 | 0 | 1 |  | 5619 | 2477 | 8096 | 3702 | 709 | 2207 | 0 | 695 | 359 | 164 | 120 | 0 | 94 | 46 | 0 | 104.57
9:00 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 352 | 309 |  | 0 | 250 | 270 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 90 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 80 | 0 | 0 | 355 | 290 | 144 | 26 | 85 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 9 | 33 | 16 | 98 | 187 | 0 | 22 | 0 | 33 | 42 | 47 | 0 | 110 | 110 | 40 | 81 | 0 | 152 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 79 | 17 | 50 | 0 | 10 | 323 | 115 | 0 | 0 | 2 | 104 | 0 | 0 | 0 | 59 | 100 | 320 | 0 | 11 | 35 | 0 | 0 | 17 | 22 |  | 709 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 100 | 0 | 168 | 0 | 17 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 280 | 224 | 0 | 0 | 1 |  | 5673 | 2505 | 8178 | 3731 | 709 | 2245 | 0 | 697 | 360 | 165 | 120 | 0 | 98 | 53 | 0 | 104.57
10:00 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 372 | 307 |  | 0 | 250 | 268 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 91 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 80 | 0 | 0 | 355 | 290 | 142 | 26 | 86 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 6 | 33 | 12 | 102 | 171 | 0 | 22 | 1 | 43 | 42 | 49 | 0 | 110 | 110 | 60 | 81 | 0 | 200 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 100 | 18 | 90 | 0 | 16 | 323 | 115 | 0 | 0 | 3 | 104 | 7 | 0 | 0 | 58 | 100 | 320 | 2 | 22 | 35 | 0 | 0 | 17 | 14 |  | 710 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 100 | 0 | 179 | 0 | 17 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 290 | 221 | 0 | 0 | 0 |  | 5860 | 2607 | 8467 | 3855 | 710 | 2297 | 0 | 789 | 370 | 166 | 120 | 0 | 102 | 58 | 0 | 104.57
11:00 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 400 | 307 |  | 0 | 250 | 270 | 0 | 0 | 22 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 21 | 25 | 29 | 33 | 33 | 10 | 0 | 91 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 80 | 0 | 0 | 330 | 290 | 141 | 26 | 87 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 6 | 33 | 12 | 120 | 167 | 0 | 22 | 2 | 43 | 42 | 50 | 0 | 140 | 110 | 60 | 81 | 0 | 220 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 100 | 13 | 90 | 0 | 55 | 322 | 106 | 0 | 0 | 2 | 172 | 17 | 0 | 0 | 57 | 100 | 320 | 17 | 22 | 45 | 0 | 0 | 17 | 13 |  | 710 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 112 | 0 | 189 | 0 | 17 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 310 | 223 | 0 | 0 | 2 |  | 6064 | 2650 | 8714 | 3890 | 710 | 2327 | 0 | 938 | 389 | 166 | 120 | 0 | 120 | 54 | 0 | 104.56
12:00 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 400 | 308 |  | 0 | 250 | 270 | 0 | 0 | 30 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 25 | 15 | 25 | 20 | 33 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 80 | 0 | 0 | 325 | 290 | 140 | 26 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 25 | 15 | 114 | 166 | 0 | 22 | 1 | 43 | 41 | 49 | 0 | 163 | 109 | 60 | 83 | 0 | 220 | 18 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 100 | 0 | 90 | 0 | 98 | 322 | 106 | 0 | 7 | 2 | 302 | 17 | 7 | 0 | 58 | 100 | 320 | 25 | 26 | 130 | 7 | 0 | 17 | 21 |  | 709 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 126 | 0 | 199 | 0 | 17 | 0 | 0 | 0 | 401 | 0 | 0 | 9 | 0 | 35 | 0 | 0 | 25 | 310 | 224 | 0 | 0 | 4 |  | 6404 | 2750 | 9154 | 3925 | 709 | 2350 | 0 | 1326 | 390 | 166 | 120 | 0 | 114 | 54 | 0 | 104.56
13:00 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 400 | 303 |  | 0 | 250 | 255 | 0 | 0 | 30 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 15 | 25 | 28 | 33 | 33 | 25 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 80 | 0 | 0 | 310 | 270 | 142 | 26 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 33 | 21 | 118 | 151 | 0 | 22 | 1 | 43 | 42 | 50 | 0 | 163 | 109 | 60 | 83 | 0 | 220 | 18 | 0 | 10 | 305 | 16 | 0 | 0 | 12 | 0 | 0 | 24 | 0 | 100 | 4 | 90 | 0 | 107 | 322 | 106 | 0 | 17 | 1 | 305 | 17 | 17 | 0 | 58 | 100 | 320 | 70 | 11 | 162 | 17 | 0 | 17 | 15 |  | 709 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 126 | 0 | 195 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 310 | 224 | 0 | 0 | 4 |  | 6494 | 2783 | 9277 | 3891 | 709 | 2345 | 0 | 1503 | 391 | 164 | 120 | 0 | 118 | 36 | 0 | 104.56
14:00 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 392 | 283 |  | 0 | 250 | 265 | 0 | 0 | 30 | 0 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 28 | 35 | 0 | 25 | 28 | 33 | 33 | 25 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 80 | 0 | 0 | 305 | 270 | 147 | 26 | 85 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 33 | 0 | 124 | 144 | 0 | 22 | 1 | 43 | 42 | 50 | 0 | 110 | 110 | 61 | 83 | 0 | 220 | 18 | 0 | 10 | 280 | 16 | 0 | 0 | 15 | 0 | 0 | 24 | 0 | 98 | 6 | 90 | 0 | 112 | 322 | 105 | 0 | 17 | 4 | 305 | 17 | 17 | 0 | 58 | 100 | 320 | 73 | 32 | 162 | 17 | 0 | 17 | 31 |  | 709 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 105 | 0 | 182 | 0 | 17 | 0 | 0 | 0 | 314 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 320 | 202 | 0 | 0 | 3 |  | 6402 | 2646 | 9048 | 3806 | 709 | 2147 | 0 | 1503 | 400 | 162 | 120 | 0 | 124 | 77 | 0 | 104.56
15:00 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 352 | 284 |  | 0 | 250 | 250 | 0 | 0 | 30 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 30 | 33 | 33 | 25 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 | 0 | 18 | 15 | 80 | 0 | 0 | 290 | 270 | 148 | 26 | 83 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 25 | 0 | 116 | 143 | 0 | 22 | 0 | 43 | 43 | 47 | 0 | 110 | 111 | 40 | 84 | 0 | 220 | 18 | 0 | 10 | 280 | 16 | 3 | 0 | 15 | 0 | 0 | 24 | 0 | 95 | 14 | 90 | 0 | 118 | 322 | 105 | 0 | 17 | 1 | 305 | 17 | 17 | 0 | 58 | 100 | 315 | 74 | 22 | 162 | 17 | 0 | 17 | 3 |  | 710 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 90 | 0 | 161 | 0 | 17 | 0 | 0 | 0 | 309 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 340 | 170 | 0 | 0 | 0 |  | 6236 | 2519 | 8755 | 3677 | 710 | 2093 | 0 | 1409 | 422 | 161 | 120 | 6 | 116 | 41 | 0 | 0
16:00 | 0 | 0 | 0 | 10 | 0 | 95 | 0 | 352 | 313 |  | 0 | 250 | 295 | 0 | 0 | 30 | 0 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 15 | 80 | 0 | 0 | 260 | 270 | 144 | 26 | 85 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 25 | 5 | 112 | 160 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 111 | 40 | 84 | 0 | 186 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 15 | 0 | 0 | 8 | 0 | 58 | 4 | 40 | 0 | 123 | 322 | 45 | 0 | 17 | 0 | 159 | 17 | 17 | 0 | 57 | 40 | 320 | 17 | 0 | 162 | 17 | 0 | 17 | 0 |  | 709 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 91 | 0 | 140 | 0 | 17 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 180 | 0 | 0 | 0 |  | 5794 | 2460 | 8254 | 3585 | 709 | 2218 | 0 | 927 | 401 | 161 | 120 | 17 | 112 | 4 | 0 | 0
17:00 | 0 | 0 | 0 | 25 | 0 | 91 | 0 | 353 | 323 |  | 0 | 250 | 300 | 0 | 0 | 30 | 0 | 0 | 185 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 30 | 33 | 33 | 4 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 5 | 0 | 0 | 18 | 18 | 80 | 0 | 0 | 290 | 300 | 144 | 26 | 87 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 33 | 12 | 116 | 173 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 110 | 110 | 40 | 84 | 0 | 186 | 18 | 0 | 10 | 310 | 16 | 5 | 0 | 15 | 0 | 0 | 9 | 0 | 49 | 1 | 40 | 0 | 130 | 321 | 55 | 0 | 18 | 0 | 159 | 17 | 18 | 0 | 68 | 40 | 320 | 17 | 0 | 162 | 17 | 0 | 17 | 0 |  | 710 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 82 | 0 | 0 | 0 | 0 | 100 | 0 | 140 | 0 | 18 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 180 | 0 | 0 | 0 |  | 6049 | 2477 | 8526 | 3754 | 710 | 2282 | 0 | 963 | 402 | 161 | 120 | 17 | 116 | 1 | 0 | 0
18:00 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 366 | 323 |  | 0 | 250 | 230 | 0 | 0 | 42 | 0 | 0 | 184 | 0 | 40 | 32 | 8 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 18 | 33 | 33 | 8 | 0 | 86 | 75 | 115 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 10 | 0 | 13 | 18 | 26 | 80 | 0 | 0 | 260 | 290 | 147 | 26 | 136 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 12 | 142 | 169 | 0 | 22 | 0 | 43 | 4 | 50 | 0 | 163 | 110 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 270 | 17 | 5 | 0 | 70 | 0 | 0 | 24 | 0 | 80 | 0 | 60 | 59 | 128 | 321 | 57 | 29 | 63 | 0 | 230 | 17 | 62 | 17 | 96 | 100 | 320 | 54 | 0 | 162 | 80 | 0 | 17 | 0 |  | 706 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 12 | 8 | 0 | 0 | 0 | 22 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 98 | 0 | 148 | 0 | 17 | 0 | 0 | 0 | 344 | 35 | 0 | 35 | 0 | 70 | 0 | 0 | 70 | 350 | 221 | 0 | 0 | 0 |  | 6889 | 2947 | 9836 | 3846 | 706 | 2268 | 0 | 1929 | 431 | 161 | 120 | 233 | 142 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 55 | 0 | 101 | 0 | 397 | 326 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 154 | 0 | 40 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 8 | 0 | 70 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 10 | 0 | 18 | 18 | 33 | 80 | 0 | 0 | 285 | 290 | 144 | 26 | 137 | 26 | 56 | 0 | 51 | 0 | 0 | 25 | 22 | 7 | 33 | 21 | 136 | 168 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 109 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 17 | 5 | 0 | 195 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 120 | 135 | 321 | 75 | 70 | 68 | 0 | 230 | 17 | 68 | 17 | 96 | 100 | 320 | 74 | 0 | 162 | 116 | 0 | 17 | 0 |  | 481 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 43 | 0 | 95 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 114 | 0 | 166 | 0 | 17 | 0 | 0 | 0 | 400 | 35 | 0 | 70 | 15 | 70 | 0 | 0 | 70 | 450 | 225 | 0 | 0 | 0 |  | 7431 | 2992 | 10423 | 4011 | 481 | 2401 | 0 | 2376 | 531 | 145 | 120 | 222 | 136 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 65 | 0 | 104 | 0 | 398 | 333 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 154 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 28 | 33 | 33 | 8 | 0 | 72 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 19 | 18 | 35 | 80 | 0 | 0 | 315 | 320 | 143 | 26 | 137 | 26 | 56 | 0 | 51 | 0 | 0 | 25 | 22 | 7 | 33 | 21 | 140 | 168 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 315 | 17 | 11 | 0 | 195 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 120 | 135 | 321 | 75 | 52 | 68 | 0 | 230 | 17 | 68 | 0 | 96 | 100 | 320 | 74 | 0 | 162 | 116 | 0 | 17 | 0 |  | 472 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 122 | 0 | 194 | 0 | 17 | 0 | 0 | 0 | 400 | 35 | 0 | 70 | 15 | 70 | 0 | 0 | 70 | 490 | 225 | 0 | 0 | 0 |  | 7392 | 3018 | 10410 | 4127 | 472 | 2438 | 0 | 2267 | 570 | 147 | 120 | 129 | 140 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 75 | 0 | 104 | 0 | 397 | 332 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 153 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 28 | 33 | 33 | 8 | 0 | 70 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 19 | 18 | 37 | 80 | 0 | 0 | 290 | 300 | 145 | 26 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 25 | 22 | 7 | 33 | 21 | 138 | 174 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 310 | 20 | 11 | 0 | 193 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 120 | 135 | 321 | 85 | 52 | 68 | 0 | 300 | 17 | 68 | 0 | 96 | 100 | 320 | 73 | 0 | 162 | 116 | 0 | 17 | 0 |  | 472 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 123 | 0 | 196 | 0 | 17 | 0 | 0 | 0 | 401 | 35 | 0 | 90 | 15 | 70 | 0 | 0 | 70 | 480 | 225 | 0 | 0 | 0 |  | 7419 | 3032 | 10451 | 4105 | 472 | 2435 | 0 | 2364 | 560 | 145 | 120 | 112 | 138 | 0 | 0 | 0
21:00 | 0 | 0 | 0 | 105 | 0 | 104 | 0 | 397 | 333 |  | 0 | 250 | 255 | 0 | 0 | 55 | 0 | 0 | 154 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 14 | 25 | 30 | 33 | 33 | 8 | 0 | 70 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 28 | 18 | 31 | 80 | 0 | 0 | 280 | 285 | 146 | 26 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 25 | 22 | 7 | 33 | 22 | 136 | 173 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 111 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 20 | 8 | 0 | 195 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 120 | 135 | 321 | 85 | 52 | 68 | 0 | 304 | 17 | 68 | 0 | 96 | 100 | 320 | 74 | 0 | 162 | 116 | 0 | 17 | 0 |  | 505 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 117 | 0 | 186 | 0 | 17 | 0 | 0 | 0 | 398 | 52 | 0 | 113 | 15 | 70 | 0 | 0 | 70 | 490 | 225 | 0 | 0 | 0 |  | 7452 | 3098 | 10550 | 4111 | 505 | 2404 | 0 | 2447 | 570 | 145 | 120 | 112 | 136 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 105 | 0 | 101 | 0 | 395 | 332 |  | 0 | 250 | 245 | 0 | 0 | 55 | 0 | 0 | 126 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 80 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 18 | 42 | 80 | 0 | 0 | 280 | 290 | 146 | 26 | 135 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 17 | 138 | 179 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 112 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 20 | 8 | 0 | 195 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 120 | 132 | 321 | 85 | 34 | 68 | 0 | 304 | 17 | 68 | 0 | 96 | 100 | 320 | 74 | 0 | 162 | 116 | 0 | 17 | 0 |  | 608 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 108 | 0 | 169 | 0 | 16 | 0 | 0 | 0 | 316 | 52 | 0 | 113 | 0 | 70 | 0 | 0 | 70 | 490 | 225 | 0 | 0 | 0 |  | 7311 | 2982 | 10293 | 4063 | 608 | 2265 | 0 | 2374 | 570 | 155 | 120 | 0 | 138 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 105 | 0 | 101 | 0 | 386 | 333 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 128 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 280 | 290 | 145 | 26 | 138 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 33 | 21 | 136 | 180 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 109 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 270 | 22 | 8 | 0 | 90 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 85 | 130 | 321 | 85 | 17 | 68 | 0 | 304 | 17 | 68 | 0 | 97 | 100 | 320 | 73 | 0 | 162 | 112 | 0 | 17 | 0 |  | 573 | 0 | 415 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 110 | 0 | 158 | 0 | 17 | 0 | 0 | 0 | 358 | 17 | 0 | 70 | 0 | 35 | 0 | 0 | 70 | 490 | 225 | 0 | 0 | 0 |  | 7109 | 2864 | 9973 | 4057 | 573 | 2320 | 0 | 2033 | 570 | 164 | 120 | 0 | 136 | 0 | 0 | 0
24:00 | 0 | 0 | 0 | 105 | 0 | 102 | 0 | 351 | 333 |  | 0 | 250 | 255 | 0 | 0 | 55 | 0 | 0 | 130 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 22 | 33 | 33 | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 280 | 285 | 146 | 26 | 136 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 33 | 21 | 128 | 194 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 111 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 60 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 85 | 132 | 321 | 85 | 17 | 68 | 0 | 304 | 17 | 68 | 0 | 63 | 100 | 320 | 80 | 0 | 162 | 116 | 0 | 17 | 0 |  | 607 | 0 | 415 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 110 | 0 | 160 | 0 | 17 | 0 | 0 | 0 | 322 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 470 | 225 | 0 | 0 | 0 |  | 7021 | 2755 | 9776 | 4034 | 607 | 2279 | 0 | 1894 | 550 | 164 | 120 | 0 | 128 | 0 | 0 | 0
KWH | 0 | 0 | 0 | 535500 | 0 | 2251909 | 0 | 9293820 | 7614000 |  | 0 | 6159000 | 6437993 | 0 | 0 | 834160 | 0 | 0 | 3647000 | 0 | 213264 | 30714 | 21655 | 0 | 0 | 0 | 1304640 | 668084 | 510380 | 324828 | 600000 | 675540 | 811000 | 837400 | 162240 | 0 | 2022076 | 1796000 | 2700000 | 0 | 18446 | 0 | 0 | 0 | 0 |  | 0 | 0 | 201393 | 25800 | 0 | 134880 | 429360 | 593600 | 2174920 | 0 | 0 | 6463300 | 6921000 | 3530000 | 669090 | 2382230 | 592992 | 1326240 | 0 | 1264286 | 0 | 0 | 111754 | 515952 | 191340 | 754100 | 416920 | 2807040 | 4147120 | 0 | 491436 | 7200 | 1016000 | 895680 | 1179000 | 0 | 3278127 | 2457000 | 1362816 | 1969920 | 0 | 4512650 | 398000 | 0 | 244800 | 7195500 | 442484 | 181248 | 0 | 1219418 | 0 | 0 | 972000 | 0 | 2019456 | 98550 | 1815360 | 822720 | 2438825 | 7732000 | 2348400 | 343200 | 800399 | 18719 | 5477345 | 449587 | 780323 | 37620 | 1662360 | 2284840 | 7658300 | 1286400 | 189980 | 3267360 | 1139128 | 0 | 444240 | 133871 |  | 16160000 | 0 | 8941824 | 0 | 0 | 2961600 | 0 | 0 | 0 | 0 | 0 | 1560000 | 491663 | 0 | 0 | 0 | 0 | 69690 | 0 | 338080 | 15320 | 9793 | 0 | 36000 | 0 | 501360 | 0 | 192888 | 1906909 | 0 | 0 | 0 | 0 | 2965200 | 0 | 4415564 | 0 | 419478 | 0 | 0 | 0 | 9119709 | 240480 | 0 | 894528 | 48960 | 1038604 | 0 | 2819 | 658560 | 9400500 | 5244000 | 0 | 0 | 15960 |  | 156195228 | 67649489 | 223844717 | 93167412 | 16160000 | 55959675 | 0 | 36556529 | 11307409 | 3818076 | 2961600 | 639877 | 2807040 | 467099 | 0
Fuel Cost | 0 | 0 | 0 | 787185 | 0 | 2972519.88 | 0 | 9386758.2 | 7842420 |  | 0 | 6713310 | 7146172.23 | 0 | 0 | 7056993.6 | 0 | 0 | 6309310 | 0 | 1944967.68 | 302225.76 | 199659.1 | 0 | 0 | 0 | 9523872 | 5164289.32 | 5032346.8 | 243621 | 450000 | 0 | 0 | 0 | 1568860.8 | 0 | 545960.52 | 484920 | 4887000 | 0 | 171363.34 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1953512.1 | 246390 | 0 | 1068249.6 | 540993.6 | 1762992 | 3218881.6 | 0 | 0 | 4782842 | 6921000 | 3247600 | 863126.1 | 2739564.5 | 670080.96 | 1856736 | 0 | 2161929.06 | 0 | 0 | 1067250.7 | 655259.04 | 143505 | 1319675 | 312690 | 21052800 | 4395947.2 | 0 | 624123.72 | 114768 | 1666240 | 1433088 | 2098620 | 0 | 3737064.78 | 2555280 | 2684747.52 | 3762547.2 | 0 | 7806884.5 | 871620 | 0 | 499392 | 7267455 | 331863 | 137748.48 | 0 | 9218800.08 | 0 | 0 | 5054400 | 0 | 19871447.04 | 1152049.5 | 14795184 | 8926512 | 17193716.25 | 7190760 | 21417408 | 3243240 | 6971475.29 | 0 | 41408728.2 | 3915902.77 | 6859039.17 | 375447.6 | 14246425.2 | 15217034.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 93081600 | 0 | 9388915.2 | 0 | 0 | 41047776 | 0 | 0 | 0 | 0 | 0 | 1762800 | 762077.65 | 0 | 0 | 0 | 0 | 685749.6 | 0 | 2992008 | 117964 | 132401.36 | 0 | 348840 | 0 | 962611.2 | 0 | 146016.216 | 11498661.27 | 0 | 0 | 0 | 0 | 3469284 | 0 | 5828544.48 | 0 | 629217 | 0 | 0 | 0 | 9028511.91 | 2510611.2 | 0 | 8489070.72 | 462182.4 | 8059567.04 | 0 | 31149.95 | 4866758.4 | 41268195 | 0 | 0 | 0 | 0 |  | 372363791.39 | 247570512.596 | 619934303.986 | 96909828.216 | 93081600 | 60066702.01 | 0 | 246746398.06 | 52766856.27 | 1030880.52 | 41047776 | 5933495.46 | 21052800 | 1297967.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 400 | 308 |  | 0 | 250 | 270 | 0 | 0 | 30 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 25 | 15 | 25 | 20 | 33 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 80 | 0 | 0 | 325 | 290 | 140 | 26 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 25 | 15 | 114 | 166 | 0 | 22 | 1 | 43 | 41 | 49 | 0 | 163 | 109 | 60 | 83 | 0 | 220 | 18 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 100 | 0 | 90 | 0 | 98 | 322 | 106 | 0 | 7 | 2 | 302 | 17 | 7 | 0 | 58 | 100 | 320 | 25 | 26 | 130 | 7 | 0 | 17 | 21 |  | 709 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 126 | 0 | 199 | 0 | 17 | 0 | 0 | 0 | 401 | 0 | 0 | 9 | 0 | 35 | 0 | 0 | 25 | 310 | 224 | 0 | 0 | 4 |  | 9154 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 105 | 0 | 104 | 0 | 397 | 333 | 0 | 0 | 250 | 255 | 0 | 0 | 55 | 0 | 0 | 154 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 14 | 25 | 30 | 33 | 33 | 8 | 0 | 70 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 28 | 18 | 31 | 80 | 0 | 0 | 280 | 285 | 146 | 26 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 25 | 22 | 7 | 33 | 22 | 136 | 173 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 111 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 20 | 8 | 0 | 195 | 0 | 0 | 40 | 0 | 80 | 0 | 90 | 120 | 135 | 321 | 85 | 52 | 68 | 0 | 304 | 17 | 68 | 0 | 96 | 100 | 320 | 74 | 0 | 162 | 116 | 0 | 17 | 0 |  | 505 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 117 | 0 | 186 | 0 | 17 | 0 | 0 | 0 | 398 | 52 | 0 | 113 | 15 | 70 | 0 | 0 | 70 | 490 | 225 | 0 | 0 | 0 |  | 10550 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 105 | 0 | 100 | 0 | 390 | 330 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 160 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 18 | 15 | 80 | 0 | 0 | 330 | 330 | 146 | 26 | 138 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 170 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 727 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 33 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 42 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 126 | 0 | 210 | 0 | 42 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 105 | 0 | 100 | 0 | 390 | 300 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 155 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 18 | 5 | 80 | 0 | 0 | 330 | 330 | 146 | 26 | 138 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 138 | 160 | 8 | 21 | 1.6 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 100 | 100 | 190 | 50 | 149 | 20 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 727 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 42 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 126 | 0 | 210 | 0 | 42 | 50 | 0 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 105 | 0 | 22 | 0 | 301 | 302 | 0 | 0 | 250 | 250 | 0 | 0 | 30 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 29 | 33 |  | 4 | 0 | 87 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 80 | 0 | 0 | 270 | 275 | 146 | 26 | 137 | 26 | 56 | 0 | 26 | 0 | 0 | 0 | 22 | 7 | 31 | 12 | 108 | 212 | 0 | 22 | 1 | 43 | 42 | 14 | 0 | 130 | 112 | 40 | 81 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 77 | 1 | 70 | 34 | 65 | 322 | 65 | 0 | 17 | 1 | 87 | 17 | 17 | 0 | 58 | 100 | 290 | 17 | 0 | 62 | 17 | 0 | 17 | 14 | 0 | 714 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 99 | 0 | 175 | 0 | 17 | 0 | 0 | 0 | 302 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 380 | 151 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 8096 | 8:00
| Highest Generation |  | 10550 | 21:00
| Day Peak Generation |  | 9154 | 12:00
| Evening Peak Generation |  | 10550 | 21:00
| HVDC Max Flow |  | 710 | 2:00
| HVDC EvPeak Flow |  | 505 | 21:00
| Load factor L.F |  | 88.41%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-21
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9154 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7981 | MW
Evening Peak Generation : |  | 10550 | MW Hour : | 21:00 | Available Max Generation : |  | 14579 | MW
E.P. Demand (at gen end) : |  | 10550 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12400 | MW
Maximum Generation : |  | 10550 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2179 | MW
Total Gen. (MKWH) : |  | 223.8447 | System Load Factor : | 88.41% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -264 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-21
Actual : | 104.55 | Ft.(MSL) , | Rule curve : | 107.9 | Ft.( MSL )
Gas Consumed : | Total = | 1187.67 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 156976530.226
: |  | Coal : | 52766856.27 | Oil : | 293727669.52 | Total : | 503471056.016
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4423.6611 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1507.7386 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1351.4984 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1221.411 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1103.6511 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 890.6161 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 493.5504 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 229.1922 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 686.9086 |  |  | 0 | 0%
Total | 0 |  | 11908.2274 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2 ,3
2) Ghorasal-3,4,5,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Hathazari-Rampur 230 kV Bay-1 was under shut down from 10:01 to 12:58 for D/W.
b) HVDC Bheramara-Jhenaidah(New) 230 kV Ckt-1 was under shut down from 08:52 to 17:06 for A/M.
c) Thakurgaon-Thakurgaon P.P. 132 kV both Ckts tripped at 08:34 due to bad weather/thundering |  |  |  |  | About 59 MW power interruption occurred under Thakurgaon &
and was switched on at 09:16. |  |  |  |  | Panchagar S/S area from 08:34 to 09:16.
d) Thakurgaon-Panchagar 132 kV Ckt tripped at 08:34 from Thakurgaon end showing Dist. Z1
and was switched on at 09:16.
e) Rangamati 132/33 kV T2 transformer was under shutdown from 10:30 to 11:30 for D/W.
f) Sherpur 132/33 kV T1 transformer was under shutdown from 08:27 to 13:28 for D/W. |  |  |  |  | About 35 MW power interruption occurred under Sherpur S/S area
g) Sherpur 132/33 kV T2 transformer was under shutdown from 08:32 to 13:29 for D/W. |  |  |  |  | from 08:32 to 13:28.
h) Mymensingh-Jamalpur 132 kV Ckt-2 was shut down at 09:35 for D/W.
i) Goalpara 132/33 kV T6 transformer was under shutdown from 16:50 to 17:24 for C/M.
j) Hathazari-Kaptai 132 kV both Ckts tripped at 18:28 from Hathazari end showing Dist. Z1 R,B
and was switched on at 18:43.
k) After maintenance Ghorashal Unit-5 was synchronized at 15:28.
l) Kaptai Unit-5 was shutdown at 06:03(21/10/2021) for maintenance.
m) Chowmuhoni 132/33 kV T-1 transformer along with 33 kV Bus was under shut down from 06:35(21/10/2021) |  |  |  |  | About 20 MW power interruption occurred under Chowmuhoni S/S area
to 08:53(21/10/2021) due to R/H maintenance. |  |  |  |  | from 06:35(21/10/2021) to 08:53(21/10/2021).
n) Gopalganj 132/33 kV T2 transformer was shutdown at 07:25(21/10/2021) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 105 | 535500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 2251909
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 9293820 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 333 | 7614000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6159000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 255 | 6437993 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 834160
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 21655 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 14 | 324828 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 154 | 3647000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 213264 | Low demand.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1304640
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 30714 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 668084
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 510380 | Low demand.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1275540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 837400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 162240 | Low demand.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 1219418 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 80 | 2019456 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 343200 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 74 | 1286400 | Low demand.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3267360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 133871
| Dhaka area Total |  |  |  | 5560 | 2543 | 51202832
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 18446 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 98550
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 28 | 134880 | Low demand.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 145 | 3818076 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 68 | 800399 | Low demand.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 201393 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 25800 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1815360 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 429360 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 593600
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18719
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 5477345
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 449587 | Low demand.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 68 | 780323 | Low demand.
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2284840
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1139128 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1117 | 20785806
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2174920 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 146 | 3530000 | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 6463300 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 6921000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 592992 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1326240
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 669090 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1264286
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 2438825 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 2382230 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 822720 | Low demand.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 515952
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 191340 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 2807040
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 754100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 111754 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 416920
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 37620 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1662360 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1701 | 35526929
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 173 | 4147120 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 491436
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7200
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 40 | 972000 | Low demand.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 85 | 2348400 | Low demand.
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 189980
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Reserve.
| Mymensingh Area Total |  |  |  | 622 | 320 | 8156136
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1016000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 895680 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3278127
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 111 | 2457000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1179000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 181248 | Engine problem
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1362816
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1969920
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4512650
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 398000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 20 | 442484 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7195500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 321 | 7732000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244800
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7658300 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1771 | 40523525
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 505 | 16160000
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 2961600 | Low demand.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8941824 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 240480 | Low demand.
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 15 | 48960 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1102 | 28352864
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 491663
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1560000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 419478 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 490 | 9400500
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 225 | 5244000
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 826 | 17115641
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 69690 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 15320 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 9793 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 117 | 2965200 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 186 | 4415564
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Under maint.
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 398 | 9119709
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 501360
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 192888
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 36000 | Low demand.
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 338080
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 894528
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 658560 | Low demand.
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 15960
| Rajshahi Area Total |  |  |  | 2179 | 1020 | 19232652
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1906909
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 1038604 | Low demand.
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 2819
| Rangpur Area Total |  |  |  | 605 | 150 | 2948332
| Total |  |  |  | 20934 | 10550 | 223844717
| Eastern Grid Total |  |  |  | 13975 | 7452 | 156195228
| Western Grid Total |  |  |  | 6959 | 3098 | 67649489
| National Grid Total |  |  |  | 20934 | 10550 | 223844717
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-20
(a) ENTIRE EASTERN GRID : |  | 7040 | MW | (b) ENTIRE WESTERN GRID : |  | 3084 | MW
i) Dhaka area |  | 3748 | MW | i) Khulna area |  | 1289 | MW
ii) Chittagong area |  | 1153 | MW | ii) Rajshahi area |  | 978 | MW
iii) Comilla area |  | 993 | MW | iii) Barisal area |  | 301 | MW
iv) Mymensingh area |  | 732 | MW | iv) Rangpur area |  | 516 | MW
v) Sylhet area |  | 414 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10124 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 13:00 | Kishoreganj | 120 | 1:00 | Benapol | 50 | 18:30
Munsiganj | 86 | 19:30 | Netrokona | 82 | 1:00 | Jhenida(Old) | 97 | 18:00
Sonargaon | 67 | 1:00 | Jamalpur | 102 | 1:00 | Bottail | 96 | 18:30
Shyampur | 188 | 1:00 | Sherpur | 92 | 1:00 | G.K Project | 47 | 20:00
Bhulta | 177 | 0:00 | Srimongal | 46 | 13:00 | Faridpur | 126 | 18:30
Madanganj | 39 | 21:00 | Shahjibazar | 101 | 22:00 | Rajbari | 44 | 18:00
Shitalakhya | 102 | 11:00 | Fenchuganj | 42 | 20:00 | Madaripur | 91 | 22:00
Rahim steel | 12 | 1:00 | Kulawara | 36 | 1:00 | Sariatpur | 56 | 20:00
Matuail | 63 | 12:00 | Sylhet | 127 | 13:00 | Gopalganj | 84 | 18:30
Ghorasal | 65 | 18:30 | Chatak | 22 | 1:00 | Bagerhat | 87 | 18:00
Narsingdi | 151 | 1:00 | Sunamganj | 39 | 1:00 | Mongla | 34 | 1:00
Haripur (SBU) | 107 | 15:00 | Biani Bazar | 46 | 1:00 | Satkhira | 90 | 19:00
Sreenagar | 36 | 19:30 | Comilla (S) | 142 | 18:00 | Gallamari | 32 | 12:00
Ullon | 65 | 13:00 | Comilla(N) | 89 | 19:30 | Magura | 46 | 19:00
Hasnabad | 75 | 23:00 | Chandpur | 61 | 22:00 | Norail | 46 | 18:00
Magbazar | 72 | 18:30 | Feni | 94 | 23:00 | Chuadanga | 81 | 19:30
Maniknagar | 52 | 13:00 | Chowmuhani | 168 | 21:00 | Barisal(N) | 37 | 19:30
Bangabhaban | 4 | 10:00 | Ashuganj | 38 | 23:00 | Barisal (S) | 90 | 14:00
Motijheel | 20 | 12:00 | Daudkandi | 126 | 18:30 | Patuakhali | 98 | 22:00
Narinda | 48 | 13:00 | B.Baria | 135 | 18:00 | Bhandaria | 44 | 20:00
Kazla | 74 | 12:00 | Ramganj | 72 | 22:00 | Borguna | 16 | 22:00
Dhanmondi | 141 | 13:00 | Chaddagram | 39 | 21:00 | Borhan Uddin | 39 | 2:00
Lalbag | 69 | 13:00 | PHP | 9 | 11:00 | Ishurdi | 55 | 18:00
Madartek | 64 | 19:30 | Kochua | 54 | 20:00 | Ruppur Paromanobik | 4 | 12:00
Dhaka University | 22 | 13:00 | Madunaghat | 55 | 14:00 | Natore | 101 | 18:30
Aftabnagar | 13 | 18:00 | Hathazari | 83 | 21:00 | Bogra | 128 | 1:00
Fatullah | 59 | 10:00 | Khulshi | 152 | 23:00 | Noagaon | 91 | 18:30
Nawabganj | 45 | 21:00 | Halishahar | 96 | 18:30 | Rajshahi | 119 | 20:00
Keraniganj | 64 | 20:00 | Baraulia | 121 | 6:00 | Rajshahi New | 15 | 20:00
Banani | 22 | 12:00 | Sikalbaha | 31 | 0:00 | C.Nawabganj | 49 | 21:00
Mirpur | 109 | 14:00 | Dohazari | 86 | 18:30 | Amnura | 37 | 20:00
Kalyanpur | 87 | 18:30 | Cox'sbazar | 85 | 18:30 | Pabna | 87 | 19:00
Gulshan | 84 | 13:00 | Chandraghona | 26 | 18:00 | Shahjadpur | 86 | 19:00
Uttara | 76 | 13:00 | Kaptai | 3.8 | 18:00 | Serajganj | 77 | 19:00
Uttara New | 21 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 50 | 20:00
Kamrangirchar | 89 | 13:00 | Bakulia | 99 | 18:00 | Joypurhat | 41 | 20:00
Savar | 147 | 3:00 | Julda | 20 | 1:00 | Sherpur(Bogura) | 41 | 1:00
Bhasantec | 118 | 13:00 | TK chemical | 28 | 18:00 | Mohastangor | 46 | 1:00
Agargaon | 62 | 13:00 | Modern Steel | 7 | 8:00 | Bhangura | 25 | 19:00
Satmosjid | 96 | 13:00 | Shahmirpur | 31 | 18:00 | Rangpur | 96 | 18:00
Tongi | 114 | 11:00 | Khagrachhari | 24 | 19:00 | Lalmonirhat | 27 | 18:00
Kabirpur | 200 | 14:00 | Matarbari | 39.5 | 19:00 | Saidpur | 87 | 19:00
Basundhara | 162 | 13:00 | Baroiar Hat | 46 | 1:00 | Purbasadipur | 84 | 18:30
Manikganj | 58 | 21:00 | Rangamati | 12 | 18:00 | Thakurgaon | 56 | 18:30
Joydevpur | 153 | 12:00 | Abul Khair 230 | 11 | 12:00 | Palashbari | 81 | 1:00
New Tongi | 78 | 15:00 | BSRM | 155 | 12:00 | Barapukuria | 39 | 1:00
Kodda | 233 | 12:00 | GPH Ispat | 90 | 22:00 | Panchagar | 39 | 18:00
Dhamrai | 86 | 18:00 | Agrabad | 62 | 1:00 | Joldhaka | 30 | 18:00
Rajendrapur | 80 | 1:00 | Goalpara | 24 | 13:00 | Kurigram | 39 | 18:00
Valuka | 102 | 15:00 | Central S/S | 90 | 18:30 | Mithapukur | 31 | 17:00
Tangail | 156 | 20:00 | Noapara | 39 | 18:00
Mymensing | 155 | 1:00 | Jessore | 97 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 18:00 | 402 | 10:00 | Kaliakoir | 398 | 0.33333 | 386 | 0.5
| Bheramara | 404 | 22:00 | 396 | 8:00 | Bhulta | 391 | 0.75 | 377 | 0.45833
| Ashuganj(N) | 396 | 18:30 | 383 | 1:00 | Gopalganj | 406 | 0.625 | 389 | 0.95833
| Payra | 410 | 18:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 236 | 4:00 | 220 | 16:00
| Ishurdi | 233 | 14:00 | 229 | 2:00 | Megnaghat | 236 | 18:00 | 228 | 9:00
| Ashuganj | 243 | 18:00 | 236 | 12:00 | Fenchuganj | 247 | 17:00 | 241 | 2:00
| Serajganj | 230 | 14:00 | 226 | 1:00 | Siddhirganj | 233 | 18:00 | 226 | 10:00
| Baghabari | 233 | 14:00 | 229 | 1:00 | Maniknagar | 232 | 18:00 | 224 | 10:00
| Barapukuria | 238 | 14:00 | 231 | 17:00 | Agargaon | 231 | 8:00 | 221 | 10:00
| Bogra | 228 | 14:00 | 222 | 7:00 | Barisal | 243 | 18:00 | 232 | 23:00
| Rajshahi | 231 | 15:00 | 223 | 1:00 | Bhola 225 MW | 245 | 9:00 | 239 | 22:00
| Khulna South | 231 | 6:00 | 225 | 13:00 | AKSML | 234 | 18:00 | 223 | 10:00
| Rampura | 231 | 21:00 | 225 | 10:00 | BSRM | 236 | 18:00 | 222 | 11:00
| Haripur | 231 | 18:30 | 223 | 10:00 | Bibiyana | 245 | 18:00 | 238 | 9:00
| Hasnabad | 230 | 17:00 | 220 | 8:00 | Bhulta | 236 | 18:00 | 226 | 11:00
| Shyampur | 230 | 18:00 | 221 | 10:00 | Ashuganj (S) | 240 | 18:00 | 232 | 10:00
| Aminbazar | 232 | 1:00 | 223 | 2:00 | Kaliakoir | 232 | 22:00 | 221 | 10:00
| Tongi | 230 | 19:00 | 217 | 10:00 | GPH | 238 | 18:00 | 221 | 10:00
| Comilla (N) | 234 | 18:00 | 225 | 10:00 | Jhenaidah | 227 | 6:00 | 220 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 18:00 | 131 | 10:00 | Madanhat | 139 | 0.70833 | 130 | 0.375
| Munsiganj | 137 | 18:00 | 131 | 10:00 | Hathazari | 138 | 0.125 | 132 | 0.33333
| Sonargaon | 135 | 18:00 | 130 | 10:00 | Khulshi | 135 | 0.75 | 126 | 0.20833
| Shyampur | 138 | 18:00 | 132 | 10:00 | Halishahar | 138 | 0.75 | 127 | 0.41667
| Bhulta | 131 | 18:00 | 127 | 10:00 | Baraulia | 138 | 0.75 | 128 | 0.41667
| Madanganj | 136 | 21:00 | 130 | 10:00 | Sikalbaha | 138 | 0.75 | 128 | 0.375
| Shitalakhya | 136 | 18:30 | 130 | 11:00 | Dohazari | 134 | 0.75 | 123 | 0.66667
| Rahim steal | 135 | 18:30 | 130 | 10:00 | Cox'sbazar | 122 | 0.75 | 115 | 0.70833
| Matuail | 136 | 18:00 | 131 | 10:00 | Chandraghona | 137 | 0.75 | 130 | 0.66667
| Ghorasal | 140 | 1:00 | 140 | 1:00 | Kaptai | 136 | 0.75 | 132 | 0.54167
| Narsinghdi | 135 | 15:00 | 130 | 1:00 | A. Khaer Stl. | 136 | 0.77083 | 129 | 0.25
| Haripur (SBU) | 136 | 18:00 | 131 | 11:00 | Bakulia | 136 | 0.79167 | 127 | 0.25
| Sreenagar | 135 | 18:00 | 130 | 10:00 | Julda | 137 | 0.75 | 128 | 0.625
| Ullon | 135 | 21:00 | 129 | 12:00 | TK Chemical | 138 | 0.75 | 128 | 0.33333
| Hasnabad | 135 | 1:00 | 130 | 17:00 | Modern Steel | 136 | 0.77083 | 128 | 0.25
| Magbazar | 135 | 4:00 | 130 | 10:00 | Shahmirpur | 137 | 0.77083 | 127 | 0.66667
| Maniknagar | 135 | 2:00 | 130 | 12:00 | Khagrachhari | 136 | 0.79167 | 129 | 0.41667
| Bangabhaban | 135 | 2:00 | 130 | 12:00 | Matarbari | 125 | 0.77083 | 117 | 0.20833
| Motijheel | 135 | 2:00 | 130 | 12:00 | Baroiar Hat | 135 | 0.75 | 129 | 0.25
| Narinda | 135 | 2:00 | 130 | 12:00 | Rangamati | 137 | 18:00 | 129 | 10:00
| Kazla | 135 | 2:00 | 130 | 12:00 | Agrabad | 138 | 18:00 | 127 | 16:00
| Dhanmondi | 135 | 19:00 | 130 | 10:00 | Goalpara S/S | 138 | 6:00 | 135 | 0.45833
| Lalbag | 136 | 18:00 | 130 | 10:00 | Khulna Central S/S | 137 | 6:00 | 134 | 0.5
| Madartek | 134 | 3:00 | 129 | 11:00 | Noapara | 136 | 6:00 | 132 | 0.54167
| Dhaka University | 134 | 2:00 | 129 | 11:00 | Jessore | 135 | 4:00 | 129 | 0.77083
| Aftabnagar | 135 | 7:00 | 130 | 10:00 | Benapol | 134 | 0.20833 | 129 | 0.54167
| Fatullah | 137 | 18:30 | 131 | 11:00 | Jhenida(Old) | 137 | 6:00 | 129 | 0.8125
| Nawabganj | 135 | 18:00 | 129 | 11:00 | Bottail | 136 | 0.20833 | 133 | 0.41667
| Keraniganj | 130 | 13:00 | 130 | 10:00 | G.K Project | 139 | 0.20833 | 129 | 0.29167
| Banani | 135 | 22:00 | 129 | 11:00 | Faridpur | 136 | 0.29167 | 130 | 0.8125
| Mirpur | 133 | 3:00 | 125 | 10:00 | Rajbari | 136 | 0.25 | 130 | 0.8125
| Kalyanpur | 133 | 18:00 | 128 | 9:00 | Madaripur | 140 | 0.20833 | 131 | 0.95833
| Gulshan | 134 | 3:00 | 129 | 11:00 | Shariyatpur S/S | 139 | 7:00 | 131 | 0.91667
| Uttara | 134 | 23:00 | 125 | 10:00 | Gopalganj | 142 | 0.29167 | 132 | 0.8125
| Uttara New | 134 | 22:00 | 126 | 9:00 | Bagerhat | 135 | 4:00 | 130 | 0.5
| Kamrangirchar | 135 | 2:00 | 130 | 10:00 | Mongla | 133 | 17:00 | 129 | 0.125
| Savar | 136 | 18:00 | 126 | 9:00 | Satkhira | 135 | 4:00 | 130 | 18:00
| Bhasantec | 137 | 22:00 | 130 | 11:00 | Gallamari | 138 | 0.25 | 129 | 22:00
| Agargaon | 137 | 3:00 | 131 | 11:00 | Magura | 137 | 6:00 | 130 | 0.66667
| Satmosjid | 137 | 18:00 | 131 | 11:00 | Narail | 136 | 0.25 | 128 | 0.77083
| Tongi | 139 | 15:00 | 131 | 14:00 | Chuadanga | 134 | 6:00 | 127 | 0.77083
| Kabirpur | 139 | 15:00 | 133 | 18:29 | Barisal(N) | 140 | 4:00 | 133 | 0.95833
| Basundhara | 136 | 18:30 | 128 | 10:00 | Barisal (S) | 139 | 6:00 | 131 | 22:00
| Manikganj | 142 | 16:00 | 136 | 2:00 | Patuakhali(S) | 138 | 0.20833 | 127 | 0.91667
| Joydevpur | 140 | 18:00 | 132 | 7.00 | Bhandaria | 138 | 0.20833 | 126 | 0.91667
| New Tongi | 137 | 18:00 | 129 | 10:00 | Borguna | 139 | 0.29167 | 129 | 0.95833
| Kodda | 135 | 15:00 | 122 | 10:00 | Jhenaidah(230kV S/S) | 137 | 6:00 | 132 | 12:00
| Dhamrai | 139 | 00:00 | 131 | 1:00 | Ishurdi | 136 | 21:00 | 134 | 13:00
| Rajendrapur | 133 | 16:00 | 123 | 10:00 | Ruppur Paromanobik | 136 | 17:00 | 134 | 12:00
| Valuka | 132 | 16:00 | 118 | 1:00 | Natore | 135 | 18:00 | 130 | 1:00
| Tangail | 137 | 16:00 | 129 | 11:00 | Bogra | 138 | 14:00 | 131 | 7:00
| Mymensing | 135 | 17:00 | 126 | 1:00 | Noagaon | 132 | 15:00 | 127 | 5:00
| Kishorganj | 135 | 17:00 | 127 | 1:00 | Rajshahi | 134 | 18:00 | 131 | 12:00
| Netrokona | 135 | 17:00 | 123 | 11:00 | Rajshahi New | 136 | 18:00 | 130 | 1:00
| Jamalpur | 139 | 16:00 | 127 | 3:00 | C.Nawabganj | 134 | 20:00 | 129 | 1:00
| Sherpur | 139 | 16:00 | 125 | 3:00 | Amnura | 135 | 18:00 | 127 | 1:00
| Srimongal | 140 | 17:00 | 136 | 1:00 | Pabna | 135 | 15:00 | 132 | 1:00
| Shahjibazar | 138 | 8:00 | 133 | 1:00 | Shahjadpur | 137 | 6:00 | 135 | 21:00
| Fenchuganj | 139 | 18:00 | 134 | 1:00 | Serajganj | 136 | 15:00 | 133 | 12:00
| Khulawara | 137 | 17:00 | 133 | 1:00 | Niyamatpur | 132 | 14:00 | 122 | 18:00
| Sylhet | 134 | 7:00 | 131 | 12:00 | Joypurhat | 135 | 14:00 | 126 | 1:00
| Chatak | 134 | 17:00 | 131 | 1:00 | Sherpur(Bogura) | 136 | 14:00 | 130 | 2:00
| Sunamganj | 134 | 18:00 | 127 | 1:00 | Mohastangor | 138 | 14:00 | 130 | 2:00
| Biani Bazar | 135 | 18:00 | 130 | 1:00 | Bangura | 136 | 14:00 | 134 | 17:00
| Comilla(s) | 128 | 1:00 | 124 | 11:00 | Rangpur | 132 | 6:00 | 126 | 7:00
| Comilla(n) | 139 | 18:00 | 135 | 4:00 | Lalmonirhat | 135 | 14:00 | 128 | 7:00
| Chandpur | 139 | 1:00 | 132 | 16:00 | Saidpur | 132 | 20:00 | 126 | 7:00
| Feni | 136 | 18:00 | 129 | 11:00 | Purbasadipur | 132 | 13:00 | 125 | 18:30
| Chowmuhani | 134 | 18:30 | 128 | 6:00 | Thakurgaon | 133 | 6:00 | 127 | 16:00
| Ashuganj | 140 | 6:00 | 137 | 1:00 | Palashbari | 133 | 21:00 | 128 | 17:00
| Daudkandi | 134 | 18:00 | 130 | 10:00 | Barapukuria | 138 | 14:00 | 131 | 19:00
| B.Baria | 136 | 8:00 | 131 | 1:00 | Panchagar | 135 | 0.25 | 127 | 0.41667
| Ramganj | 135 | 17:00 | 129 | 3:00 | Joldhaka | 134 | 0.58333 | 125 | 0.70833
| Chaddagram | 137 | 18:00 | 131 | 5:00 | Kurigram | 135 | 0.58333 | 125 | 0.70833
| PHP | 134 | 18:00 | 128 | 11:00 | Mithapukur | 137 | 0.58333 | 129 | 0.70833
| Kochua | 137 | 18:00 | 131 | 5:00

## L-Curve
Date | 2021-10-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 86 | 7021 | 2755 | 9776 |  |  |  | QF-LDC-11
0:30 | 146 | 6852.5 | 2849.5 | 9702 | Date: | 2021-10-20
1:00 | 206 | 6684 | 2944 | 9628
1:30 | 219 | 6550.5 | 2885.5 | 9436
2:00 | 232 | 6417 | 2827 | 9244
2:30 | 232 | 6351 | 2794.5 | 9145.5 | [5 empty] | Gen. at Eve. Peak | 10550 | 10550 MW (21:00 )
3:00 | 232 | 6285 | 2762 | 9047 | [6 empty] | 21:00
3:30 | 239 | 6225.5 | 2715 | 8940.5 | [5 empty] | Gen. at Day Peak | 9154 | 9154 MW (12:00 )
4:00 | 246 | 6166 | 2668 | 8834 | [6 empty] | 12:00
4:30 | 269 | 6085 | 2675 | 8760 | [5 empty] | Highest Generation | 10550
5:00 | 292 | 6004 | 2682 | 8686 | [6 empty] | 21:00
5:30 | 286 | 5880 | 2621.5 | 8501.5
6:00 | 280 | 5756 | 2561 | 8317
6:30 | 220 | 5697 | 2520.5 | 8217.5
7:00 | 160 | 5638 | 2480 | 8118
7:30 | 156 | 5628.5 | 2478.5 | 8107
8:00 | 152 | 5619 | 2477 | 8096
8:30 | 251 | 5646 | 2491 | 8137
9:00 | 350 | 5673 | 2505 | 8178
9:30 | 438 | 5766.5 | 2556 | 8322.5
10:00 | 526 | 5860 | 2607 | 8467
10:30 | 475 | 5962 | 2628.5 | 8590.5
11:00 | 424 | 6064 | 2650 | 8714
11:30 | 386 | 6234 | 2700 | 8934
12:00 | 348 | 6404 | 2750 | 9154
12:30 | 347 | 6449 | 2766.5 | 9215.5
13:00 | 346 | 6494 | 2783 | 9277
13:30 | 411 | 6448 | 2714.5 | 9162.5
14:00 | 476 | 6402 | 2646 | 9048
14:30 | 434 | 6319 | 2582.5 | 8901.5
15:00 | 392 | 6236 | 2519 | 8755
15:30 | 339 | 6015 | 2489.5 | 8504.5
16:00 | 286 | 5794 | 2460 | 8254
16:30 | 204 | 5921.5 | 2468.5 | 8390
17:00 | 122 | 6049 | 2477 | 8526
17:30 | 147 | 6469 | 2712 | 9181
18:00 | 172 | 6889 | 2947 | 9836
18:30 | 218 | 7160 | 2969.5 | 10129.5
19:00 | 264 | 7431 | 2992 | 10423
19:30 | 202 | 7392 | 3018 | 10410
20:00 | 204 | 7419 | 3032 | 10451 |  |  |  | Executive Engineer
20:30 | 162 | 7435.5 | 3065 | 10500.5 |  |  |  | Network Operation Division
21:00 | 120 | 7452 | 3098 | 10550
21:30 | 109 | 7381.5 | 3040 | 10421.5
22:00 | 98 | 7311 | 2982 | 10293 |  |  |  |  | Page 6 of 7
22:30 | 76 | 7210 | 2923 | 10133
23:00 | 54 | 7109 | 2864 | 9973
23:30 | 70 | 7065 | 2809.5 | 9874.5
24:00 | 86 | 7021 | 2755 | 9776
10550 MW (21:00 )
9154 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-20 |  | Energy |  | 223844717
[13 empty] | 2021-10-20 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4034 | 607 | 2279 | 0 | 1894 | 550 | 164 | 120 | 0 | 128 | 0 | 0
0:30 | 3856 | 658 | 2331 | 0 | 1962.5 | 489.5 | 163 | 120 | 0 | 122 | 0 | 0 | Date: | 2021-10-20
1:00 | 3678 | 709 | 2383 | 0 | 2031 | 429 | 162 | 120 | 0 | 116 | 0 | 0
1:30 | 3695.5 | 709.5 | 2391.5 | 0 | 1827.5 | 414.5 | 161.5 | 120 | 0 | 116 | 0 | 0 | [8 empty] | Total Energy | 223.8447 | Total Energy Gen 223.845 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 223.845 MKWHr
2:00 | 3713 | 710 | 2400 | 0 | 1624 | 400 | 161 | 120 | 0 | 116 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3730.5 | 710 | 2368 | 0 | 1548.5 | 394.5 | 160 | 120 | 0 | 114 | 0 | 0 | [8 empty] | Energy Requirement | 223.8447
3:00 | 3748 | 710 | 2336 | 0 | 1473 | 389 | 159 | 120 | 0 | 112 | 0 | 0
3:30 | 3758.5 | 709.5 | 2336 | 0 | 1362.5 | 384 | 159 | 120 | 0 | 111 | 0 | 0 | [6 empty] | Shortage
4:00 | 3769 | 709 | 2336 | 0 | 1252 | 379 | 159 | 120 | 0 | 110 | 0 | 0
4:30 | 3788.5 | 709 | 2344 | 0 | 1149 | 380.5 | 160 | 120 | 0 | 109 | 0 | 0
5:00 | 3808 | 709 | 2352 | 0 | 1046 | 382 | 161 | 120 | 0 | 108 | 0 | 0
5:30 | 3832 | 709 | 2307.5 | 0 | 886 | 381 | 162 | 120 | 0 | 104 | 0 | 0
6:00 | 3856 | 709 | 2263 | 0 | 726 | 380 | 163 | 120 | 0 | 100 | 0 | 0
6:30 | 3802.5 | 709 | 2265.5 | 0 | 693.5 | 369.5 | 163 | 115 | 0 | 96 | 3.5 | 0 |  |  |  |  | Coal
7:00 | 3749 | 709 | 2268 | 0 | 661 | 359 | 163 | 110 | 0 | 92 | 7 | 0
7:30 | 3725.5 | 709 | 2237.5 | 0 | 678 | 359 | 163.5 | 115 | 0 | 93 | 26.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3702 | 709 | 2207 | 0 | 695 | 359 | 164 | 120 | 0 | 94 | 46 | 0
8:30 | 3716.5 | 709 | 2226 | 0 | 696 | 359.5 | 164.5 | 120 | 0 | 96 | 49.5 | 0
9:00 | 3731 | 709 | 2245 | 0 | 697 | 360 | 165 | 120 | 0 | 98 | 53 | 0
9:30 | 3793 | 709.5 | 2271 | 0 | 743 | 365 | 165.5 | 120 | 0 | 100 | 55.5 | 0
10:00 | 3855 | 710 | 2297 | 0 | 789 | 370 | 166 | 120 | 0 | 102 | 58 | 0
10:30 | 3872.5 | 710 | 2312 | 0 | 863.5 | 379.5 | 166 | 120 | 0 | 111 | 56 | 0
11:00 | 3890 | 710 | 2327 | 0 | 938 | 389 | 166 | 120 | 0 | 120 | 54 | 0
11:30 | 3907.5 | 709.5 | 2338.5 | 0 | 1132 | 389.5 | 166 | 120 | 0 | 117 | 54 | 0
12:00 | 3925 | 709 | 2350 | 0 | 1326 | 390 | 166 | 120 | 0 | 114 | 54 | 0
12:30 | 3908 | 709 | 2347.5 | 0 | 1414.5 | 390.5 | 165 | 120 | 0 | 116 | 45 | 0
13:00 | 3891 | 709 | 2345 | 0 | 1503 | 391 | 164 | 120 | 0 | 118 | 36 | 0
13:30 | 3891 | 709 | 2345 | 0 | 1503 | 391 | 164 | 120 | 0 | 118 | 36 | 0
14:00 | 3891 | 709 | 2345 | 0 | 1503 | 391 | 164 | 120 | 0 | 118 | 36 | 0
14:30 | 3784 | 709.5 | 2219 | 0 | 1456 | 406.5 | 162.5 | 120 | 3 | 117 | 38.5 | 0
15:00 | 3677 | 710 | 2093 | 0 | 1409 | 422 | 161 | 120 | 6 | 116 | 41 | 0
15:30 | 3631 | 709.5 | 2155.5 | 0 | 1168 | 411.5 | 161 | 120 | 11.5 | 114 | 22.5 | 0
16:00 | 3585 | 709 | 2218 | 0 | 927 | 401 | 161 | 120 | 17 | 112 | 4 | 0
16:30 | 3669.5 | 709.5 | 2250 | 0 | 945 | 401.5 | 161 | 120 | 17 | 114 | 2.5 | 0
17:00 | 3754 | 710 | 2282 | 0 | 963 | 402 | 161 | 120 | 17 | 116 | 1 | 0
17:30 | 3800 | 708 | 2275 | 0 | 1446 | 416.5 | 161 | 120 | 125 | 129 | 0.5 | 0
18:00 | 3846 | 706 | 2268 | 0 | 1929 | 431 | 161 | 120 | 233 | 142 | 0 | 0
18:30 | 3928.5 | 593.5 | 2334.5 | 0 | 2152.5 | 481 | 153 | 120 | 227.5 | 139 | 0 | 0
19:00 | 4011 | 481 | 2401 | 0 | 2376 | 531 | 145 | 120 | 222 | 136 | 0 | 0
19:30 | 4127 | 472 | 2438 | 0 | 2267 | 570 | 147 | 120 | 129 | 140 | 0 | 0
20:00 | 4105 | 472 | 2435 | 0 | 2364 | 560 | 145 | 120 | 112 | 138 | 0 | 0
20:30 | 4108 | 488.5 | 2419.5 | 0 | 2405.5 | 565 | 145 | 120 | 112 | 137 | 0 | 0
21:00 | 4111 | 505 | 2404 | 0 | 2447 | 570 | 145 | 120 | 112 | 136 | 0 | 0
21:30 | 4087 | 556.5 | 2334.5 | 0 | 2410.5 | 570 | 150 | 120 | 56 | 137 | 0 | 0
22:00 | 4063 | 608 | 2265 | 0 | 2374 | 570 | 155 | 120 | 0 | 138 | 0 | 0
22:30 | 4060 | 590.5 | 2292.5 | 0 | 2203.5 | 570 | 159.5 | 120 | 0 | 137 | 0 | 0
23:00 | 4057 | 573 | 2320 | 0 | 2033 | 570 | 164 | 120 | 0 | 136 | 0 | 0
23:30 | 4045.5 | 590 | 2299.5 | 0 | 1963.5 | 560 | 164 | 120 | 0 | 132 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.2° C
24:00 | 4034 | 607 | 2279 | 0 | 1894 | 550 | 164 | 120 | 0 | 128 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 223.845 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 223.845 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 87 | 86 | 84 | 84 | 86 | 88 | 88 | 89 | 90 | 91 | 91 | 91 | 89 | 87 | 86 | 86 | 86 | 86 |  | 70 | 72 | 70 | 70 | 80 | 89 | 89 | 2022076
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1796000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 8 | 8 | 8 |  |  |  |  | 18446
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 15 | 17 | 18 | 13 |  | 4 | 6 | 14 | 4 | 1 | [9 empty] | 98550
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [14 empty] | 6 | 17 | 17 | 68 |  | 68 | 34 | 17 | 17 |  |  |  | 201393
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 51 | 17 | [8 empty] | 7 | 17 | 17 | 17 | 17 | 18 | 63 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 800399
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 155 | 155 | 155 | 155 | 155 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 129 | 128 | 129 | 185 | 184 |  | 154 | 154 | 153 | 154 | 126 | 128 | 130 | 3647000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 12 | 15 | 15 | 15 | 15 | 70 |  | 195 | 195 | 193 | 195 | 195 | 90 | 60 | 1219418
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 669090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | [15 empty] | 10 | 25 | 35 |  | 55 | 65 | 75 | 105 | 105 | 105 | 105 | 535500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2174920
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 592992
33 | Ashuganj 225 MW CCPP | 146 | 144 | 146 | 146 | 146 | 146 | 146 | 146 | 144 | 142 | 141 | 140 | 142 | 147 | 148 | 144 | 144 | 147 |  | 144 | 143 | 145 | 146 | 146 | 145 | 146 | 3530000
34 | Ashuganj 450 MW CCPP(South) | 295 | 320 | 265 | 270 | 265 | 265 | 265 | 270 | 290 | 290 | 290 | 290 | 270 | 270 | 270 | 270 | 300 | 290 |  | 290 | 320 | 300 | 285 | 290 | 290 | 285 | 6921000
| Ashuganj 450 MW CCPP(North) | 35 | 35 | 130 | 160 | 200 | 290 | 285 | 335 | 355 | 355 | 330 | 325 | 310 | 305 | 290 | 260 | 290 | 260 |  | 285 | 315 | 290 | 280 | 280 | 280 | 280 | 6463300
35 | Ashuganj 55 MW PP (Precision) | 52 | 56 | 56 | 56 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 56 | 53 | 54 | 56 |  | 56 | 56 | 56 | 56 | 56 | 53 | 53 | 1326240
36 | Chandpur 150 MW CCPP | 86 | 85 | 86 | 88 | 88 | 86 | 86 | 85 | 85 | 86 | 87 | 86 | 86 | 85 | 83 | 85 | 87 | 136 |  | 137 | 137 | 138 | 138 | 135 | 138 | 136 | 2382230
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 402 | 402 | 401 | 395 | 390 | 357 | 352 | 352 | 372 | 400 | 400 | 400 | 392 | 352 | 352 | 353 | 366 |  | 397 | 398 | 397 | 397 | 395 | 386 | 351 | 9293820
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6159000
41 | Haripur 360MW CCPP(HPL) | 326 | 326 | 326 | 326 | 326 | 330 | 310 | 307 | 309 | 307 | 307 | 308 | 303 | 283 | 284 | 313 | 323 | 323 |  | 326 | 333 | 332 | 333 | 332 | 333 | 333 | 7614000
42 | RPCL 210MW CCPP | 163 | 172 | 196 | 199 | 212 | 213 | 205 | 201 | 187 | 171 | 167 | 166 | 151 | 144 | 143 | 160 | 173 | 169 |  | 168 | 168 | 174 | 173 | 179 | 180 | 194 | 4147120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 2 | 23 | 11 | 22 | 22 | 26 | 11 | 32 | 22 | 0 | 0 | [9 empty] | 189980
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 33 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1016000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 42 | 42 | 43 | 42 | 42 | 4 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 895680
46 | Shajibazar 330 MW CCPP | 111 | 112 | 110 | 112 | 110 | 110 | 111 | 109 | 110 | 110 | 110 | 109 | 109 | 110 | 111 | 111 | 110 | 110 |  | 109 | 110 | 110 | 111 | 112 | 109 | 111 | 2457000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 62 | 62 | 62 | 62 | 62 | 61 | 40 | 40 | 60 | 60 | 60 | 60 | 61 | 40 | 40 | 40 | 62 |  | 61 | 61 | 61 | 62 | 62 | 61 | 62 | 1362816
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 83 | 83 | 83 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1969920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 200 | 220 | 220 | 220 | 220 | 220 | 186 | 186 | 219 |  | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 4512650
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 398000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244800
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 5 | 5 | 5 |  |  | 3 | 5 | 5 | 5 |  | 5 | 11 | 11 | 8 | 8 | 8 | 11 | 181248
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 49 | 50 | 49 | 50 | 50 | 47 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1179000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 |  | 17 | 17 | 20 | 20 | 20 | 22 | 24 | 442484
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 305 | 300 | 295 | 295 | 290 | 290 | 280 | 290 | 305 | 305 | 295 | 305 | 280 | 280 | 270 | 310 | 270 |  | 290 | 315 | 310 | 300 | 280 | 270 | 280 | 7195500
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 315 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7658300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | 17 | [8 empty] | 25 | 35 | 35 | 17 | 17 | 17 | 55 |  | 55 |  |  | 35 | 35 | 35 | 35 | 510380
59 | Tangail Palli Power Gen 22 MW | [26 empty] | 0
60 | Barabkunda 22 MW PP (Regent) | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 429360
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | [9 empty] | 14 | 18 | 18 | 18 | 324828
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491436
63 | Impoprt (Tripura) | 116 | 116 | 112 | 110 | 108 | 100 | 92 | 94 | 98 | 102 | 120 | 114 | 118 | 124 | 116 | 112 | 116 | 142 |  | 136 | 140 | 138 | 136 | 138 | 136 | 128 | 2807040
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 39 | 39 | 36 | 21 | 14 | 15 | 14 | 16 | 20 | 17 | 15 | 15 | 18 | 26 |  | 33 | 35 | 37 | 31 | 42 | 42 | 42 | 593600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515952
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 191340
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 754100
68 | Cumilla 25 MW PP (Summit) | 22 | 21 | 21 | 21 | 21 | 21 | 17 | 16 | 16 | 12 | 12 | 15 | 21 |  |  | 5 | 12 | 12 |  | 21 | 21 | 21 | 22 | 17 | 21 | 21 | 416920
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 20 | 28 | 28 | 30 | 30 | 30 | 18 |  | 28 | 28 | 28 | 30 | 30 | 30 | 22 | 675540
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 837400
73 | Ghorashal 108MW PP (Regent) | 96 | 96 | 96 | 96 | 96 | 97 | 97 | 93 | 93 | 90 | 88 | 94 | 94 | 97 | 95 | 95 | 91 | 98 |  | 101 | 104 | 104 | 104 | 101 | 101 | 102 | 2251909
| Feni Lanka Power | [17 empty] | 17 |  | 17 | [6 empty] | 37620
| Chowmuhani 113 MW | 60 | 62 | 60 | 58 | 58 | 58 | 58 | 58 | 59 | 58 | 57 | 58 | 58 | 58 | 58 | 57 | 68 | 96 |  | 96 | 96 | 96 | 96 | 96 | 97 | 63 | 1662360
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 90 | 35 | 35 | 35 | 35 | 45 | 130 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3267360
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [10 empty] | 10 | 25 | 25 | 25 | 25 |  | 4 | 8 |  | 8 | 8 | 8 | 8 |  |  |  | 162240
79 | Kodda 150MW PP | [17 empty] | 32 |  | 16 | [6 empty] | 30714
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 8 |  | 25 | 25 | 25 | 25 | 8 |  |  | 111754
| Gazipur 100 MW PP | [17 empty] | 29 |  | 70 | 52 | 52 | 52 | 34 | 17 | 17 | 343200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 2 | 3 | 2 | 2 | 1 | 4 | 1 | 0 | 0 | [9 empty] | 18719
| Jodiac Power | 35 | 35 | 35 | 35 | 35 |  |  |  |  | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 449587
| Karnaphuli Power Ltd. | 110 | 17 | [9 empty] | 7 | 17 | 17 | 17 | 17 | 18 | 62 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 780323
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 8 |  | 10 | [6 empty] | 21655
86 | Meghnaghat CCPP ( Summit) | 265 | 275 | 260 | 260 | 265 | 260 | 270 | 260 | 270 | 268 | 270 | 270 | 255 | 265 | 250 | 295 | 300 | 230 |  | 270 | 270 | 270 | 255 | 245 | 270 | 255 | 6437993
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 75 | 35 |  |  |  |  | 2 | 17 | 25 | 70 | 73 | 74 | 17 | 17 | 54 |  | 74 | 74 | 73 | 74 | 74 | 73 | 80 | 1286400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 5 | 10 |  | 10 | [6 empty] | 25800
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1264286
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 5 | 40 |  | 40 | 40 | 40 | 40 | 24 | 7 | 7 | 213264
95 | Patenga 50MW PP (Baraka) | [17 empty] | 13 |  | 18 | 19 | 19 | 28 | 32 |  |  | 134880
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 22 | 30 | 30 | 30 | 30 | 30 | 30 | 42 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 834160
100 | Manikganj 55 MW PP (Northern) | 55 | 17 | [7 empty] | 17 | 17 | 35 | 35 | 28 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 668084
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 140 | 163 | 163 | 110 | 110 | 110 | 110 | 163 |  | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 3278127
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | [10 empty] | 7200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1304640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 100 | 80 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 9 | 24 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 95 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 79 | 100 | 100 | 100 | 100 | 98 | 95 | 58 | 49 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2019456
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 50 | 90 | 90 | 90 | 90 | 90 | 90 | 40 | 40 | 60 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1815360
116 | Chandpur 200MW (Desh energy) | 17 | [15 empty] | 0 | 59 |  | 120 | 120 | 120 | 120 | 120 | 85 | 85 | 822720
117 | Ashuganj 150MW PP (Midland) | 122 | 122 | 122 | 125 | 125 | 10 | 10 | 10 | 10 | 16 | 55 | 98 | 107 | 112 | 118 | 123 | 130 | 128 |  | 135 | 135 | 135 | 135 | 132 | 130 | 132 | 2438825
118 | Bibiyana-III 400 MW CCPP | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 323 | 323 | 323 | 322 | 322 | 322 | 322 | 322 | 322 | 321 | 321 |  | 321 | 321 | 321 | 321 | 321 | 321 | 321 | 7732000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 106 | 106 | 106 | 105 | 105 | 45 | 55 | 57 |  | 75 | 75 | 85 | 85 | 85 | 85 | 85 | 2348400
| Anwara 300 MW PP (United) | 292 | 305 | 305 | 270 | 104 | 105 | 105 | 104 | 104 | 104 | 172 | 302 | 305 | 305 | 305 | 159 | 159 | 230 |  | 230 | 230 | 300 | 304 | 304 | 304 | 304 | 5477345
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 40 | 40 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2284840
| Anlima Energy Ltd. | 108 | 53 | 17 | [8 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 80 |  | 116 | 116 | 116 | 116 | 116 | 112 | 116 | 1139128
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 6 | 22 | 14 | 13 | 21 | 15 | 31 | 3 | 0 | 0 | [9 empty] | 133871
120 | Eastern Zone Total | 6684 | 6417 | 6285 | 6166 | 6004 | 5756 | 5638 | 5619 | 5673 | 5860 | 6064 | 6404 | 6494 | 6402 | 6236 | 5794 | 6049 | 6889 |  | 7431 | 7392 | 7419 | 7452 | 7311 | 7109 | 7021 | 156195228
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2961600
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 35 |  | 35 | 35 | 35 | 52 | 52 | 17 | 0 | 240480
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 226 | 225 | 226 | 225 | 225 | 226 | 226 | 226 | 224 | 221 | 223 | 224 | 224 | 202 | 170 | 180 | 180 | 221 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5244000
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 |  | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 419478
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560000
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 18 | 20 | 19 | 15 | 14 | 17 | 17 | 16 | 17 | 18 | 19 | 18 | 16 | 19 | 27 |  | 27 | 27 | 27 | 29 | 29 | 28 | 27 | 491663
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 15 | 15 | 15 | 15 |  |  |  | 48960
146 | Bheramara HVDC | 709 | 710 | 710 | 709 | 709 | 709 | 709 | 709 | 709 | 710 | 710 | 709 | 709 | 709 | 710 | 709 | 710 | 706 |  | 481 | 472 | 472 | 505 | 608 | 573 | 607 | 16160000
147 | Bheramara 410 MW CCPP | 380 | 380 | 350 | 330 | 330 | 330 | 330 | 300 | 300 | 340 | 340 | 380 | 380 | 380 | 380 | 330 | 330 | 380 |  | 410 | 410 | 410 | 410 | 410 | 415 | 415 | 8941824
148 | Payra 1320 MW | 350 | 320 | 310 | 300 | 300 | 300 | 280 | 280 | 280 | 290 | 310 | 310 | 310 | 320 | 340 | 320 | 320 | 350 |  | 450 | 490 | 480 | 490 | 490 | 490 | 470 | 9400500
149
150 | Barapukuria TPP Unit-1 | 79 | 80 | 79 | 79 | 82 | 80 | 79 | 79 | 80 | 80 | 79 | 80 | 81 | 80 | 82 | 81 | 82 | 81 |  | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 1906909
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 43 |  | 43 | [6 empty] | 69690
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 0 | 2 | 4 | 4 | 3 | 0 | 0 | 0 | [9 empty] | 15960
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 145 | 145 | 145 | 145 | 145 | 145 | 100 | 100 | 100 | 100 | 112 | 126 | 126 | 105 | 90 | 91 | 100 | 98 |  | 114 | 122 | 123 | 117 | 108 | 110 | 110 | 2965200
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 187 | 188 | 188 | 188 | 188 | 177 | 165 | 165 | 168 | 179 | 189 | 199 | 195 | 182 | 161 | 140 | 140 | 148 |  | 166 | 194 | 196 | 186 | 169 | 158 | 160 | 4415564
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 418 | 421 | 396 | 408 | 417 | 333 | 354 | 336 | 359 | 403 | 403 | 401 | 400 | 314 | 309 | 364 | 367 | 344 |  | 400 | 400 | 401 | 398 | 316 | 358 | 322 | 9119709
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 18 | 21 | 22 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 5 | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 192888
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 | [8 empty] | 15320
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 | [8 empty] | 9793
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 8 | 8 | 8 |  |  | 36000
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 90 |  | 95 | 95 | 95 | 95 |  |  |  | 338080
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | 35 | [8 empty] | 9 | 35 | 35 | 35 |  |  | 35 |  | 70 | 70 | 90 | 113 | 113 | 70 | 35 | 894528
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [10 empty] | 25 | 35 | 35 |  |  |  | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 658560
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 90 | 70 | 70 | 34 | 34 | 10 |  | 35 | 35 | 35 | 35 | 35 | 35 | 34 |  |  |  | 70 |  | 70 | 70 | 70 | 70 | 70 | 35 | 34 | 1038604
177 | Sympa Solar Power 8MW | [10 empty] | 0 | 0 | 0 |  | 1 | [11 empty] | 2819
178
178