## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-22 | Friday
|  |  | Date (day): | 2021-10-22 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13366.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14404 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-21 | 2021-10-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 105 | 170 | 170 | 170 | 20 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 21 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 368 | 337 | 390 | 390
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 292 | 323 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 260 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 50 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 30 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 21 | 21 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 200 | 185 | 155 | 185 | 25 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 42 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 135 | 278 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 133 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 93 | 94 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 108 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 15 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2491 | 2842 | 3428 | 3758 | 610 | 1120
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 16 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 4 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 130 | 160 | 130 | 130 | 100 |  | Unit 2 & 5 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 99 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 51 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 10 | 21 | 25
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 35 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 304 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 107 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 105 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1118 | 1448 | 1462 | 1530 | 165 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 105 | 105 | 105 | 30 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 140 | 144 | 146 | 146 |  |  | ST under maint
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 280 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 270 | 0 | 0 |  |  | Under maint.
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 130 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 135 | 138 | 138 |  | 25 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 80 | 197 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 7 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 148 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 10 | 43 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 55 | 88 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1635 | 1904 | 1770 | 1996 | 462 | 109
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 165 | 154 | 200 | 200 | 2 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 1 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 32 | 130 | 190 | 190 |  | 10 | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 98 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 365 | 445 | 607.6 | 556 | 2 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 110 | 110 | 110 | 110 |  | 220 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 49 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 81 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 219 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 270 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 80 | 322 | 321 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 365 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1485 | 1744 | 1817 | 1817 | 142 | 395
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 710 | 710 | 727 | 727
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 11 | 0 | 33 |  | 21 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 40 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 410 | 400 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1205 | 1276 | 1507 | 1730 | 0 | 90
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 28 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 18 | 17 | 42 | 42 | 53 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 510 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 222 | 222 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 695 | 859 | 1092 | 1242 | 53 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 22 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 42 | 42 |  | 8 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 96 | 115 | 126 | 126
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 152 | 178 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | under maint
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 346 | 346 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 90 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 100 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 820 | 1165 | 1482 | 1582 | 170 | 301
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 79 | 78 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 116 | 191 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 9930 | 11874 | 13366.6 | 14404 | 1604 | 3228
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9431.5766 | 11278 | 12695.6809 | 13681.0099
| A. |  | 2021-10-21 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 11874 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7981 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11874 | MW
| 3 | Day peak Generation : |  |  | 9930 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11278 | MW
| 4 | Evening peak Generation : |  |  | 11874 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 246.1398 | MKWHr | By Solar | 0.6003 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 150.3339 | MKWHr |  | By Oil: | 58.509 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.8576 | MKWHr |  | By Hydro: | 3.5789 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1604 | MW | Dhaka | 4236 | 4236 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3228 | MW | Chittagong | 1295 | 1295 |  | 0 |  | 18:00 |  | 150
|  |  |  | Total = |  |  | 4832 | MW | Khulna | 1302 | 1302 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1197.66 | MMCFD |  |  | Rajshahi | 1053 | 1053 |  | 0 |  | 19:00 |  | 148
| 8 | Fuel Cost : | i) Gas : | Taka | 160085496.552 | ii) Oil : | Taka | 441410929.74 | Comilla | 1056 | 1056 |  | 0 |  | 19:30 |  | 148
|  |  | iii) Coal : |  | 59539433.08 | Total | Taka | 661035859.372 | Mymensingh | 892 | 892 |  | 0 |  | 20:00 |  | 148
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.151 | MKWHr. | Sylhet | 486 | 486 |  | 0 |  | 21:00 |  | 146
|  | ii) During Peak Demand : |  |  | -16 | MW (E to W) at | 19:00 | hrs | Barisal | 314 | 314 |  | 0 |  | 22:00 |  | 142
|  | iii) Maximum : |  |  | -84 | MW at | 20:00 | hrs | Rangpur | 644 | 644 |  | 0 |  | 23:00 |  | 140
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.3° C |  |  | Total | 11278 | 11278 |  | 0
| B. |  | 2021-10-22 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 31.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14404 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
| 4 | Reserve(Generation end) |  |  |  | 3404 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 228.0224 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7573 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1382 | MKWHr. | ii) HVDC Flow at Peak Time |  | 710 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1219 | MKWHr. | iii) Maximum HVDC Flow : |  | 714 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.55 |  | (b) Today: | 104.7 |  | (c) Rule Curve: |  | 108
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 105 | 0 | 102 | 0 | 350 | 332 |  | 0 | 250 | 240 | 0 | 0 | 55 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 280 | 295 | 146 | 26 | 136 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 31 | 22 | 126 | 209 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 111 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 79 | 0 | 90 | 36 | 125 | 322 | 85 | 0 | 34 | 0 | 304 | 17 | 17 | 0 | 59 | 100 | 320 | 93 | 0 | 162 | 53 | 0 | 17 | 0 |  | 711 | 0 | 415 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 109 | 0 | 160 | 0 | 18 | 0 | 0 | 0 | 314 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 450 | 224 | 0 | 0 | 0 |  | 6727 | 2756 | 9483 | 4062 | 711 | 2243 | 0 | 1529 | 530 | 162 | 120 | 0 | 126 | 0 | 0 | 104.55
2:00 | 0 | 0 | 0 | 105 | 0 | 100 | 0 | 350 | 331 |  | 0 | 250 | 235 | 0 | 0 | 55 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 280 | 275 | 147 | 26 | 137 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 31 | 22 | 122 | 211 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 112 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 65 | 0 | 90 | 34 | 122 | 322 | 85 | 0 | 0 | 0 | 196 | 17 | 0 | 0 | 58 | 100 | 320 | 73 | 0 | 162 | 35 | 0 | 17 | 0 |  | 713 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 92 | 0 | 163 | 0 | 17 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 207 | 0 | 0 | 0 |  | 6446 | 2607 | 9053 | 3998 | 713 | 2190 | 0 | 1241 | 510 | 159 | 120 | 0 | 122 | 0 | 0 | 104.55
3:00 | 0 | 0 | 0 | 105 | 0 | 95 | 0 | 351 | 332 |  | 0 | 250 | 255 | 0 | 0 | 40 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 18 | 25 | 29 | 33 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 280 | 275 | 145 | 26 | 136 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 31 | 22 | 120 | 213 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 110 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 50 | 34 | 122 | 321 | 85 | 0 | 0 | 0 | 103 | 17 | 0 | 0 | 58 | 100 | 250 | 61 | 0 | 150 | 0 | 0 | 17 | 0 |  | 712 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 88 | 0 | 163 | 0 | 17 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 225 | 0 | 0 | 0 |  | 6107 | 2635 | 8742 | 3901 | 712 | 2240 | 0 | 981 | 510 | 158 | 120 | 0 | 120 | 0 | 0 | 104.55
4:00 | 0 | 0 | 0 | 105 | 0 | 94 | 0 | 351 | 332 |  | 0 | 250 | 245 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 280 | 275 | 146 | 26 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 31 | 22 | 118 | 213 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 110 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 265 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 34 | 80 | 321 | 65 | 0 | 0 | 0 | 85 | 17 | 0 | 0 | 58 | 70 | 250 | 54 | 0 | 108 | 0 | 0 | 17 | 0 |  | 713 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 89 | 0 | 163 | 0 | 17 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 184 | 0 | 0 | 0 |  | 5892 | 2535 | 8427 | 3892 | 713 | 2173 | 0 | 774 | 479 | 158 | 120 | 0 | 118 | 0 | 0 | 104.55
5:00 | 0 | 0 | 0 | 105 | 0 | 94 | 0 | 352 | 332 |  | 0 | 250 | 280 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 310 | 300 | 144 | 26 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 31 | 22 | 116 | 211 | 0 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 111 | 62 | 20 | 0 | 166 | 18 | 0 | 10 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 30 | 34 | 50 | 321 | 65 | 0 | 0 | 0 | 51 | 17 | 0 | 0 | 58 | 70 | 250 | 24 | 0 | 54 | 0 | 0 | 17 | 0 |  | 714 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 92 | 0 | 165 | 0 | 17 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 180 | 0 | 0 | 0 |  | 5719 | 2579 | 8298 | 3897 | 714 | 2207 | 0 | 606 | 479 | 159 | 120 | 0 | 116 | 0 | 0 | 104.55
6:00 | 0 | 0 | 0 | 105 | 0 | 22 | 0 | 352 | 302 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 280 | 275 | 146 | 26 | 139 | 26 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 7 | 31 | 22 | 110 | 212 | 0 | 22 | 0 | 43 | 42 | 14 | 0 | 130 | 110 | 40 | 20 | 0 | 140 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 30 | 34 | 50 | 321 | 65 | 0 | 5 | 0 | 87 | 17 | 0 | 0 | 58 | 70 | 260 | 17 | 0 | 54 | 13 | 0 | 17 | 0 |  | 714 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 95 | 0 | 169 | 0 | 17 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 180 | 0 | 0 | 0 |  | 5480 | 2501 | 7981 | 3791 | 714 | 1973 | 0 | 653 | 459 | 161 | 120 | 0 | 110 | 0 | 0 | 104.55
7:00 | 0 | 0 | 0 | 105 | 0 | 22 | 0 | 322 | 301 |  | 0 | 250 | 275 | 0 | 0 | 15 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 37 | 80 | 0 | 0 | 300 | 285 | 144 | 26 | 138 | 26 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 7 | 31 | 16 | 102 | 210 | 0 | 22 | 0 | 43 | 42 | 14 | 0 | 130 | 111 | 40 | 20 | 0 | 205 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 30 | 34 | 50 | 321 | 65 | 0 | 16 | 1 | 88 | 17 | 0 | 0 | 58 | 70 | 260 | 17 | 2 | 54 | 17 | 0 | 17 | 4 |  | 713 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 97 | 0 | 171 | 0 | 17 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 151 | 0 | 0 | 0 |  | 5558 | 2507 | 8065 | 3877 | 713 | 1990 | 0 | 671 | 459 | 126 | 120 | 0 | 102 | 7 | 0 | 104.55
8:00 | 0 | 0 | 0 | 105 | 0 | 22 | 0 | 301 | 302 |  | 0 | 250 | 250 | 0 | 0 | 30 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 29 | 33 | 33 | 4 | 0 | 87 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 80 | 0 | 0 | 270 | 275 | 146 | 26 | 137 | 26 | 56 | 0 | 26 | 0 | 0 | 0 | 22 | 7 | 31 | 12 | 108 | 212 | 0 | 22 | 1 | 43 | 42 | 14 | 0 | 130 | 112 | 40 | 81 | 0 | 218 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 77 | 1 | 70 | 34 | 65 | 322 | 65 | 0 | 17 | 1 | 87 | 17 | 17 | 0 | 58 | 100 | 290 | 17 | 6 | 62 | 17 | 0 | 17 | 14 |  | 714 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 99 | 0 | 175 | 0 | 17 | 0 | 0 | 0 | 302 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 380 | 151 | 0 | 0 | 1 |  | 5765 | 2485 | 8250 | 3870 | 714 | 1980 | 0 | 848 | 458 | 127 | 120 | 0 | 108 | 25 | 0 | 0
9:00 | 0 | 0 | 0 | 105 | 0 | 22 | 0 | 302 | 303 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 28 | 33 | 33 | 25 | 0 | 88 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 80 | 0 | 0 | 355 | 300 | 143 | 26 | 137 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 33 | 12 | 114 | 209 | 0 | 22 | 0 | 43 | 42 | 14 | 0 | 130 | 110 | 40 | 81 | 0 | 218 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 132 | 3 | 70 | 34 | 115 | 323 | 65 | 0 | 17 | 1 | 88 | 17 | 17 | 0 | 58 | 100 | 320 | 48 | 22 | 108 | 17 | 0 | 17 | 23 |  | 714 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 94 | 0 | 193 | 0 | 17 | 0 | 0 | 0 | 337 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 360 | 151 | 0 | 0 | 3 |  | 6217 | 2510 | 8727 | 3995 | 714 | 2059 | 0 | 1103 | 441 | 128 | 120 | 0 | 114 | 53 | 0 | 0
10:00 | 0 | 0 | 0 | 105 | 0 | 74 | 0 | 345 | 293 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 25 | 0 | 25 | 29 | 33 | 33 | 25 | 0 | 88 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 80 | 0 | 0 | 280 | 275 | 142 | 26 | 138 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 25 | 12 | 124 | 182 | 0 | 22 | 2 | 43 | 42 | 44 | 0 | 130 | 110 | 60 | 81 | 0 | 218 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 132 | 7 | 76 | 34 | 115 | 323 | 65 | 0 | 24 | 5 | 174 | 17 | 17 | 0 | 57 | 100 | 320 | 60 | 41 | 108 | 35 | 0 | 17 | 24 |  | 714 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 123 | 0 | 196 | 0 | 17 | 0 | 0 | 0 | 407 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 360 | 151 | 0 | 0 | 5 |  | 6419 | 2613 | 9032 | 3976 | 714 | 2187 | 0 | 1257 | 440 | 128 | 120 | 0 | 124 | 86 | 0 | 0
11:00 | 0 | 0 | 0 | 105 | 0 | 90 | 0 | 378 | 304 |  | 0 | 250 | 240 | 0 | 0 | 45 | 0 | 0 | 205 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 33 | 33 | 25 | 0 | 90 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 7 | 0 | 0 | 18 | 10 | 135 | 0 | 0 | 310 | 275 | 145 | 26 | 134 | 26 | 51 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 25 | 12 | 126 | 166 | 0 | 22 | 2 | 43 | 42 | 44 | 0 | 163 | 111 | 61 | 81 | 0 | 218 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 15 | 108 | 0 | 5 | 0 | 132 | 1 | 76 | 37 | 128 | 15 | 73 | 5 | 39 | 1 | 250 | 17 | 23 | 8 | 49 | 100 | 384 | 85 | 42 | 108 | 59 | 0 | 17 | 35 |  | 714 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 130 | 0 | 197 | 0 | 17 | 0 | 0 | 0 | 362 | 30 | 0 | 10 | 0 | 10 | 0 | 2 | 50 | 370 | 222 | 0 | 0 | 5 |  | 6650 | 2741 | 9391 | 3864 | 714 | 2239 | 108 | 1552 | 450 | 130 | 120 | 0 | 126 | 88 | 0 | 0
12:00 | 0 | 0 | 0 | 105 | 0 | 97 | 0 | 368 | 292 |  | 0 | 250 | 280 | 0 | 0 | 50 | 0 | 0 | 200 | 0 | 32 | 0 | 10 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 33 | 33 | 25 | 0 | 90 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 18 | 12 | 135 | 0 | 0 | 285 | 285 | 140 | 26 | 137 | 26 | 51 | 0 | 51 | 0 | 0 | 10 | 22 | 7 | 16 | 16 | 134 | 165 | 0 | 22 | 2 | 43 | 42 | 45 | 0 | 110 | 110 | 60 | 80 | 0 | 218 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 135 | 0 | 0 | 32 | 0 | 132 | 4 | 76 | 80 | 125 | 80 | 98 | 17 | 99 | 2 | 304 | 17 | 107 | 17 | 55 | 100 | 365 | 93 | 46 | 108 | 105 | 0 | 17 | 15 |  | 710 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 96 | 0 | 152 | 0 | 18 | 0 | 0 | 0 | 346 | 35 | 0 | 100 | 0 | 35 | 0 | 2 | 100 | 370 | 222 | 0 | 0 | 0 |  | 7094 | 2836 | 9930 | 3821 | 710 | 2208 | 0 | 2287 | 449 | 130 | 120 | 0 | 134 | 71 | 0 | 0
13:00 | 0 | 0 | 0 | 170 | 0 | 10 | 0 | 339 | 287 |  | 0 | 250 | 250 | 0 | 0 | 55 | 0 | 0 | 205 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 26 | 33 | 33 | 25 | 0 | 90 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 26 | 18 | 25 | 105 | 0 | 0 | 265 | 270 | 143 | 26 | 135 | 26 | 51 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 16 | 20 | 128 | 140 | 0 | 22 | 2 | 43 | 42 | 45 | 0 | 110 | 110 | 61 | 78 | 0 | 206 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 215 | 0 | 0 | 16 | 0 | 132 | 8 | 76 | 125 | 125 | 319 | 108 | 0 | 105 | 3 | 304 | 17 | 109 | 17 | 59 | 100 | 345 | 91 | 51 | 108 | 108 | 0 | 17 | 31 |  | 710 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 107 | 0 | 172 | 0 | 17 | 0 | 0 | 0 | 339 | 53 | 0 | 110 | 0 | 39 | 0 | 2 | 113 | 370 | 212 | 0 | 0 | 0 |  | 7269 | 2967 | 10236 | 4083 | 710 | 2071 | 0 | 2447 | 450 | 130 | 120 | 0 | 128 | 97 | 0 | 0
14:00 | 0 | 0 | 0 | 170 | 0 | 10 | 0 | 340 | 287 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 198 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 26 | 33 | 33 | 25 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 25 | 105 | 0 | 0 | 270 | 270 | 140 | 26 | 135 | 26 | 52 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 25 | 20 | 138 | 138 | 0 | 22 | 2 | 43 | 42 | 49 | 0 | 110 | 109 | 60 | 78 | 0 | 167 | 18 | 0 | 10 | 270 | 18 | 8 | 0 | 270 | 0 | 0 | 8 | 0 | 131 | 8 | 90 | 155 | 128 | 322 | 108 | 0 | 105 | 2 | 304 | 17 | 110 | 0 | 57 | 100 | 330 | 92 | 37 | 108 | 108 | 0 | 17 | 28 |  | 709 | 0 | 410 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 80 | 0 | 159 | 0 | 17 | 0 | 0 | 0 | 337 | 17 | 0 | 113 | 0 | 34 | 0 | 4 | 113 | 320 | 220 | 0 | 0 | 0 |  | 7318 | 2808 | 10126 | 3995 | 709 | 2093 | 0 | 2468 | 401 | 161 | 80 | 0 | 138 | 81 | 0 | 104.57
15:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 339 | 288 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 201 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 33 | 33 | 25 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 10 | 105 | 0 | 0 | 280 | 270 | 139 | 26 | 137 | 26 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 25 | 20 | 140 | 141 | 0 | 22 | 2 | 43 | 42 | 46 | 0 | 130 | 110 | 61 | 78 | 0 | 166 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 270 | 0 | 0 | 8 | 0 | 115 | 7 | 90 | 155 | 133 | 323 | 107 | 0 | 105 | 1 | 304 | 17 | 110 | 0 | 58 | 100 | 330 | 94 | 27 | 108 | 108 | 0 | 17 | 20 |  | 709 | 0 | 410 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 97 | 0 | 167 | 0 | 17 | 0 | 0 | 0 | 363 | 17 | 0 | 113 | 0 | 34 | 0 | 4 | 113 | 360 | 222 | 0 | 0 | 3 |  | 7359 | 2864 | 10223 | 4047 | 709 | 2163 | 0 | 2459 | 441 | 160 | 40 | 0 | 140 | 64 | 0 | 104.57
16:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 339 | 323 |  | 0 | 250 | 275 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 33 | 33 | 25 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 5 | 105 | 0 | 0 | 285 | 275 | 139 | 26 | 137 | 26 | 53 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 25 | 21 | 138 | 140 | 0 | 22 | 1 | 43 | 42 | 44 | 0 | 130 | 110 | 61 | 78 | 0 | 166 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 276 | 0 | 0 | 8 | 0 | 121 | 3 | 90 | 85 | 128 | 322 | 115 | 0 | 51 | 0 | 304 | 17 | 51 | 0 | 59 | 100 | 320 | 95 | 14 | 108 | 108 | 0 | 17 | 9 |  | 709 | 0 | 405 | 0 | 0 | 40 | 0 | 0 | 4 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 118 | 0 | 180 | 0 | 17 | 0 | 0 | 0 | 390 | 17 | 0 | 50 | 0 | 34 | 0 | 3 | 50 | 370 | 222 | 0 | 0 | 1 |  | 7205 | 2803 | 10008 | 4074 | 709 | 2234 | 0 | 2167 | 451 | 160 | 40 | 4 | 138 | 31 | 0 | 104.58
17:00 | 0 | 0 | 0 | 170 | 0 | 23 | 0 | 339 | 329 |  | 0 | 250 | 245 | 0 | 0 | 55 | 0 | 0 | 127 | 0 | 32 | 16 | 5 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 10 | 4 | 19 | 18 | 6 | 105 | 0 | 0 | 280 | 270 | 142 | 26 | 136 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 25 | 21 | 132 | 155 | 0 | 22 | 0 | 43 | 42 | 47 | 0 | 110 | 110 | 62 | 84 | 0 | 166 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 281 | 0 | 0 | 8 | 0 | 132 | 1 | 90 | 85 | 130 | 322 | 115 | 4 | 51 | 0 | 304 | 17 | 51 | 17 | 58 | 100 | 320 | 94 | 2 | 108 | 108 | 0 | 17 | 1 |  | 709 | 0 | 340 | 0 | 0 | 40 | 0 | 0 | 4 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | 8 | 0 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 117 | 0 | 178 | 0 | 17 | 0 | 0 | 0 | 303 | 17 | 0 | 50 | 0 | 34 | 0 | 2 | 50 | 370 | 218 | 0 | 0 | 0 |  | 7157 | 2659 | 9816 | 3944 | 709 | 2114 | 0 | 2232 | 449 | 160 | 40 | 30 | 132 | 6 | 0 | 104.58
18:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 338 | 328 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 163 | 0 | 70 | 98 | 20 | 0 | 0 | 0 | 54 | 50 | 35 | 21 | 25 | 17 | 33 | 33 | 34 | 0 | 85 | 75 | 115 | 0 | 7 | 0 | 0 | 0 | 0 |  | 10 | 0 | 102 | 72 | 34 | 26 | 18 | 12 | 105 | 0 | 0 | 280 | 265 | 141 | 26 | 138 | 26 | 55 | 0 | 51 | 0 | 50 | 10 | 22 | 7 | 25 | 21 | 150 | 155 | 0 | 22 | 0 | 43 | 42 | 49 | 0 | 163 | 109 | 61 | 84 | 0 | 205 | 18 | 0 | 10 | 290 | 24 | 8 | 50 | 278 | 57 | 50 | 50 | 50 | 132 | 0 | 90 | 105 | 130 | 322 | 115 | 42 | 70 | 0 | 304 | 17 | 72 | 86 | 85 | 100 | 320 | 95 | 0 | 108 | 108 | 0 | 17 | 0 |  | 709 | 0 | 405 | 0 | 0 | 40 | 0 | 0 | 4 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 17 | 22 | 90 | 27 | 24 | 34 | 16 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 122 | 0 | 179 | 0 | 17 | 0 | 0 | 0 | 402 | 103 | 0 | 63 | 0 | 92 | 0 | 0 | 113 | 400 | 223 | 0 | 2 | 0 |  | 8140 | 3303 | 11443 | 4071 | 709 | 2290 | 207 | 2921 | 478 | 160 | 40 | 417 | 150 | 0 | 0 | 104.59
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 337 | 323 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 64 | 30 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 85 | 75 | 115 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 102 | 100 | 35 | 50 | 18 | 10 | 105 | 0 | 0 | 280 | 270 | 144 | 26 | 135 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 7 | 25 | 21 | 148 | 154 | 1 | 22 | 0 | 43 | 42 | 49 | 0 | 163 | 110 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 278 | 0 | 0 | 130 | 0 | 133 | 0 | 90 | 197 | 130 | 322 | 115 | 105 | 105 | 0 | 304 | 17 | 110 | 114 | 88 | 100 | 320 | 94 | 0 | 108 | 116 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 40 | 0 | 0 | 11 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 43 | 22 | 95 | 27 | 0 | 40 | 43 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 115 | 0 | 178 | 0 | 17 | 0 | 0 | 0 | 346 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 510 | 222 | 0 | 17 | 0 |  | 8383 | 3491 | 11874 | 4124 | 710 | 2204 | 0 | 3523 | 588 | 160 | 40 | 377 | 148 | 0 | 0 | 104.6
19:30 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 337 | 323 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 160 | 0 | 102 | 32 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 100 | 12 | 50 | 18 | 10 | 105 | 0 | 0 | 280 | 270 | 143 | 26 | 137 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 22 | 7 | 25 | 21 | 148 | 155 | 8 | 22 | 0 | 43 | 42 | 49 | 0 | 130 | 111 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 285 | 0 | 0 | 110 | 0 | 133 | 0 | 90 | 200 | 130 | 322 | 115 | 105 | 105 | 0 | 304 | 17 | 110 | 114 | 97 | 100 | 320 | 94 | 0 | 108 | 116 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 115 | 0 | 180 | 0 | 17 | 0 | 0 | 0 | 383 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 222 | 0 | 17 | 0 |  | 8209 | 3398 | 11607 | 4106 | 710 | 2229 | 0 | 3440 | 598 | 160 | 40 | 176 | 148 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 337 | 323 |  | 0 | 250 | 250 | 0 | 0 | 55 | 0 | 0 | 160 | 0 | 102 | 32 | 27 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 23 | 100 | 12 | 50 | 18 | 17 | 105 | 0 | 0 | 285 | 265 | 144 | 26 | 135 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 22 | 7 | 25 | 21 | 148 | 158 | 8 | 22 | 0 | 43 | 42 | 49 | 0 | 130 | 110 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 110 | 0 | 133 | 0 | 90 | 200 | 128 | 322 | 115 | 105 | 105 | 0 | 304 | 17 | 110 | 95 | 96 | 100 | 320 | 95 | 0 | 108 | 116 | 0 | 17 | 0 |  | 709 | 0 | 410 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 116 | 0 | 180 | 0 | 17 | 0 | 0 | 0 | 356 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 222 | 0 | 17 | 0 |  | 8167 | 3335 | 11502 | 4109 | 709 | 2190 | 0 | 3437 | 599 | 160 | 40 | 110 | 148 | 0 | 0 | 104.59
21:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 337 | 322 |  | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 160 | 0 | 64 | 0 | 14 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 26 | 33 | 33 | 8 | 0 | 88 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 17 | 50 | 0 | 27 | 18 | 30 | 105 | 0 | 0 | 280 | 265 | 144 | 26 | 136 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 22 | 7 | 25 | 21 | 146 | 161 | 8 | 22 | 0 | 43 | 42 | 49 | 0 | 130 | 110 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 296 | 0 | 0 | 110 | 0 | 133 | 0 | 90 | 200 | 130 | 322 | 115 | 70 | 105 | 0 | 304 | 17 | 110 | 52 | 98 | 100 | 320 | 95 | 0 | 108 | 116 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 117 | 0 | 179 | 0 | 17 | 0 | 0 | 0 | 382 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 222 | 0 | 17 | 0 |  | 7917 | 3306 | 11223 | 4105 | 710 | 2238 | 0 | 3206 | 598 | 163 | 40 | 17 | 146 | 0 | 0 | 104.6
22:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 337 | 322 |  | 0 | 250 | 275 | 0 | 0 | 40 | 0 | 0 | 155 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 23 | 33 | 33 | 0 | 0 | 88 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 0 | 105 | 0 | 0 | 290 | 275 | 142 | 26 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 25 | 21 | 142 | 170 | 8 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 111 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 2 | 0 | 180 | 0 | 0 | 80 | 0 | 133 | 0 | 90 | 120 | 132 | 322 | 115 | 52 | 105 | 0 | 304 | 17 | 110 | 17 | 96 | 100 | 320 | 95 | 0 | 108 | 108 | 0 | 17 | 0 |  | 711 | 0 | 410 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 119 | 0 | 179 | 0 | 17 | 0 | 0 | 0 | 400 | 53 | 0 | 113 | 0 | 77 | 0 | 0 | 113 | 520 | 223 | 0 | 17 | 0 |  | 7418 | 3174 | 10592 | 4119 | 711 | 2253 | 0 | 2589 | 600 | 163 | 15 | 0 | 142 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 338 | 331 |  | 0 | 250 | 255 | 0 | 0 | 40 | 0 | 0 | 155 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 7 | 18 | 0 | 105 | 0 | 0 | 285 | 270 | 144 | 26 | 138 | 29 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 25 | 21 | 140 | 171 | 8 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 110 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 4 | 0 | 180 | 0 | 0 | 80 | 0 | 132 | 0 | 90 | 120 | 135 | 322 | 115 | 52 | 105 | 0 | 304 | 17 | 110 | 17 | 97 | 100 | 320 | 95 | 0 | 108 | 108 | 0 | 17 | 0 |  | 711 | 0 | 410 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 117 | 0 | 179 | 0 | 17 | 0 | 0 | 0 | 358 | 53 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 510 | 223 | 0 | 0 | 0 |  | 7422 | 3080 | 10502 | 4122 | 711 | 2190 | 0 | 2575 | 589 | 165 | 10 | 0 | 140 | 0 | 0 | 0
24:00 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 337 | 333 |  | 0 | 250 | 245 | 0 | 0 | 40 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 0 | 105 | 0 | 0 | 285 | 270 | 146 | 26 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 25 | 21 | 136 | 171 | 8 | 22 | 0 | 43 | 42 | 50 | 0 | 130 | 110 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 180 | 0 | 0 | 60 | 0 | 121 | 0 | 76 | 85 | 135 | 323 | 115 | 34 | 105 | 0 | 304 | 17 | 110 | 0 | 63 | 100 | 320 | 95 | 0 | 108 | 108 | 0 | 17 | 0 |  | 711 | 0 | 410 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 115 | 0 | 177 | 0 | 17 | 0 | 0 | 0 | 348 | 17 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 470 | 217 | 0 | 0 | 0 |  | 7239 | 2897 | 10136 | 4124 | 711 | 2151 | 0 | 2291 | 548 | 165 | 10 | 0 | 136 | 0 | 0 | 0
KWH | 0 | 0 | 0 | 3339000 | 0 | 1101909 | 0 | 8331270 | 7544000 |  | 0 | 6158300 | 6311535 | 0 | 0 | 1124612 | 0 | 0 | 4183000 | 0 | 570240 | 185760 | 127874 | 0 | 0 | 0 | 1290600 | 910360 | 813501 | 407520 | 600000 | 638820 | 826400 | 820000 | 356640 | 0 | 2046938 | 1532000 | 2800000 | 0 | 24710 | 0 | 0 | 0 | 0 |  | 84000 | 0 | 242646 | 353160 | 89280 | 330240 | 441456 | 551040 | 2372640 | 0 | 0 | 7232200 | 6758000 | 3494000 | 669090 | 3264800 | 598104 | 1302240 | 0 | 1200886 | 0 | 73976 | 247066 | 504972 | 173340 | 650200 | 485090 | 3121920 | 4180320 | 40320 | 504216 | 13000 | 1016000 | 1105680 | 1033200 | 0 | 3304472 | 2499000 | 1386720 | 1766440 | 0 | 4863060 | 393000 | 0 | 245880 | 7060000 | 518400 | 151728 | 30336 | 3342108 | 71755 | 33252 | 861600 | 54478 | 2581920 | 37260 | 1801920 | 2225280 | 2813527 | 7253000 | 2283600 | 519600 | 1451927 | 14160 | 5427164 | 432788 | 1461120 | 429780 | 1613640 | 2314560 | 7440400 | 1800000 | 280940 | 2606400 | 1726254 | 0 | 444240 | 212581 |  | 17138181 | 0 | 9225936 | 0 | 0 | 2119680 | 0 | 0 | 18240 | 0 | 0 | 1560000 | 528362 | 0 | 0 | 0 | 0 | 51312 | 43672 | 229792 | 46760 | 38121 | 56490 | 151680 | 0 | 490080 | 0 | 208836 | 1886836 | 0 | 0 | 0 | 0 | 2675900 | 0 | 4394873 | 0 | 421042 | 0 | 0 | 0 | 8467345 | 788169 | 0 | 1406400 | 0 | 8948544 | 0 | 22797 | 1339872 | 10970800 | 4880180 | 0 | 78000 | 19560 |  | 167932361 | 78207460 | 246139821 | 97297881 | 17138181 | 53036001 | 189821 | 55297577 | 12857636 | 3578938 | 2119680 | 901888 | 3121920 | 600298 | 0
Fuel Cost | 0 | 0 | 0 | 4908330 | 0 | 1454519.88 | 0 | 8414582.7 | 7770320 |  | 0 | 6712547 | 7005803.85 | 0 | 0 | 9514217.52 | 0 | 0 | 7236590 | 0 | 5200588.8 | 1827878.4 | 1178998.28 | 0 | 0 | 0 | 9421380 | 7037082.8 | 8021119.86 | 305640 | 450000 | 0 | 0 | 0 | 3448708.8 | 0 | 552673.26 | 413640 | 5068000 | 0 | 229555.9 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2353666.2 | 3372678 | 776736 | 2615500.8 | 556234.56 | 1636588.8 | 3511507.2 | 0 | 0 | 5351828 | 6758000 | 3214480 | 863126.1 | 3754520 | 675857.52 | 1823136 | 0 | 2053515.06 | 0 | 747157.6 | 2359480.3 | 641314.44 | 130005 | 1137850 | 363817.5 | 23414400 | 4431139.2 | 366105.6 | 640354.32 | 207220 | 1666240 | 1769088 | 1839096 | 0 | 3767098.08 | 2598960 | 2731838.4 | 3373900.4 | 0 | 8413093.8 | 860670 | 0 | 501595.2 | 7130600 | 388800 | 115313.28 | 516015.36 | 25266336.48 | 1218399.9 | 555973.44 | 4480320 | 910872.16 | 25406092.8 | 435569.4 | 14685648 | 24144288 | 19835365.35 | 6745290 | 20826432 | 4910220 | 12646284.17 | 0 | 41029359.84 | 3769583.48 | 12843244.8 | 4289204.4 | 13828894.8 | 15414969.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98715922.56 | 0 | 9687232.8 | 0 | 0 | 29378764.8 | 0 | 0 | 191337.6 | 0 | 0 | 1762800 | 818961.1 | 0 | 0 | 0 | 0 | 504910.08 | 443707.52 | 2033659.2 | 360052 | 515395.92 | 547388.1 | 1469779.2 | 0 | 940953.6 | 0 | 158088.852 | 11377621.08 | 0 | 0 | 0 | 0 | 3130803 | 0 | 5801232.36 | 0 | 631563 | 0 | 0 | 0 | 8382671.55 | 8228484.36 | 0 | 13346736 | 0 | 69440701.44 | 0 | 251906.85 | 9901654.08 | 48161812 | 0 | 0 | 0 | 0 |  | 458843052.39 | 326184139.052 | 785027191.442 | 103379500.932 | 98715922.56 | 56705995.62 | 3201260.86 | 400181199.38 | 59539433.08 | 966313.26 | 29378764.8 | 8649704.7 | 23414400 | 894696.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 105 | 0 | 97 | 0 | 368 | 292 |  | 0 | 250 | 280 | 0 | 0 | 50 | 0 | 0 | 200 | 0 | 32 | 0 | 10 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 33 | 33 | 25 | 0 | 90 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 18 | 12 | 135 | 0 | 0 | 285 | 285 | 140 | 26 | 137 | 26 | 51 | 0 | 51 | 0 | 0 | 10 | 22 | 7 | 16 | 16 | 134 | 165 | 0 | 22 | 2 | 43 | 42 | 45 | 0 | 110 | 110 | 60 | 80 | 0 | 218 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 135 | 0 | 0 | 32 | 0 | 132 | 4 | 76 | 80 | 125 | 80 | 98 | 17 | 99 | 2 | 304 | 17 | 107 | 17 | 55 | 100 | 365 | 93 | 46 | 108 | 105 | 0 | 17 | 15 |  | 710 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 96 | 0 | 152 | 0 | 18 | 0 | 0 | 0 | 346 | 35 | 0 | 100 | 0 | 35 | 0 | 2 | 100 | 370 | 222 | 0 | 0 | 0 |  | 9930 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 337 | 323 | 0 | 0 | 250 | 260 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 64 | 30 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 85 | 75 | 115 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 102 | 100 | 35 | 50 | 18 | 10 | 105 | 0 | 0 | 280 | 270 | 144 | 26 | 135 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 7 | 25 | 21 | 148 | 154 | 1 | 22 | 0 | 43 | 42 | 49 | 0 | 163 | 110 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 278 | 0 | 0 | 130 | 0 | 133 | 0 | 90 | 197 | 130 | 322 | 115 | 105 | 105 | 0 | 304 | 17 | 110 | 114 | 88 | 100 | 320 | 94 | 0 | 108 | 116 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 40 | 0 | 0 | 11 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 43 | 22 | 95 | 27 | 0 | 40 | 43 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 115 | 0 | 178 | 0 | 17 | 0 | 0 | 0 | 346 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 510 | 222 | 0 | 17 | 0 |  | 11874 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 0 | 100 | 0 | 390 | 330 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 185 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 90 | 50 | 18 | 25 | 105 | 0 | 0 | 330 | 0 | 146 | 26 | 138 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 200 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 727 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 33 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 42 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 126 | 0 | 210 | 0 | 42 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 170 | 0 | 100 | 0 | 390 | 300 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 155 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 18 | 21 | 105 | 0 | 0 | 330 | 0 | 146 | 26 | 138 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 138 | 200 | 8 | 21 | 1.6 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 100 | 100 | 190 | 50 | 149 | 20 | 90 | 200 | 135 | 321 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 727 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 42 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 126 | 0 | 210 | 0 | 42 | 50 | 0 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 337 | 337 | 0 | 0 | 250 | 250 | 0 | 0 | 30 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 25 | 28 | 33 |  | 0 | 0 | 88 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 105 | 0 | 0 | 270 | 0 | 148 | 26 | 136 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 18 | 14 | 94 | 208 | 8 | 22 | 1 | 43 | 42 | 13 | 0 | 110 | 110 | 40 | 10 | 0 | 166 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 9 | 30 | 17 | 10 | 323 | 45 | 0 | 0 | 1 | 70 | 17 | 0 | 0 | 58 | 30 | 320 | 0 | 22 | 17 | 17 | 0 | 17 | 10 | 0 | 714 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 95 | 0 | 166 | 0 | 17 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 360 | 150 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7981 | 6:00
| Highest Generation |  | 11874 | 19:00
| Day Peak Generation |  | 9930 | 12:00
| Evening Peak Generation |  | 11874 | 19:00
| HVDC Max Flow |  | 714 | 5:00
| HVDC EvPeak Flow |  | 710 | 19:00
| Load factor L.F |  | 86.37%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-22
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9930 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7573 | MW
Evening Peak Generation : |  | 11874 | MW Hour : | 19:00 | Available Max Generation : |  | 14404 | MW
E.P. Demand (at gen end) : |  | 11874 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 11874 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3404 | MW
Total Gen. (MKWH) : |  | 246.1398 | System Load Factor : | 86.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -84 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-22
Actual : | 104.7 | Ft.(MSL) , | Rule curve : | 108 | Ft.( MSL )
Gas Consumed : | Total = | 1197.66 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160085496.552
: |  | Coal : | 59539433.08 | Oil : | 441410929.74 | Total : | 661035859.372
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3891.3075 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1322.8493 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1185.156 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1070.8624 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 967.7372 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 780.9286 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 437.1852 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 201.0821 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 602.2884 |  |  | 0 | 0%
Total | 0 |  | 10459.3967 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2 ,3
2) Ghorasal-3,4,5,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sonargaon-Daudkandi 132 kV Ckt-1 was under shut down from 08:10 to 15:38 for A/M.
b) Thakurgaon 132/33 kV T2 transformer was under shutdown from 08:34 to 15:25 for A/M.
c) Sirajganj 132/33 kV T2 transformer was under shutdown from 08:14 to 15:25 for A/M.
d) Chapainawabganj 132/33 kV T3 transformer was under shutdown from 08:15 to 15:28 for A/M.
e) Mymensingh-Netrokona 132 kV Ckt-2 was shut down from 09:20 to 16:52 for A/M.
f) Jaldhaka 132/33 kV T1 transformer was under shutdown from 09:40 to 15:20 for A/M.
g) HVDC Bheramara-Jhenaidah(New) 230 kV Ckt-1 was under shut down from 09:25 to 15:31 for A/M.
h) Purbasadipur 132/33 kV T3 transformer tripped at 09:37 instantaneous E/F relay due to 33 kV |  |  |  |  | About 25 MW power interruption occurred under Purbasadipur
PBS feeder fault and was switched on at 09:52. |  |  |  |  | S/S area from 09:37 to 09:52.
i) Aminbazar-Agargaon 132 kV Ckt-1 was under shut down from 10:14 to 16:27 for A/M.
j) Kishoreganj 132/33 kV T3 transformer tripped at 09:46 showing O/C, E/F relay and was switched |  |  |  |  | About 30 MW power interruption occurred under Kishoreganj
on at 17:50. |  |  |  |  | S/S area from 09:46 to 17:50.
k) Tongi-Kabirpur 132 kV Ckt-1 tripped at 11:30 showing dist Z1,L3 B-phase, O/C relay and was
switched on at 11:44.
l) Madunaghat-Chandraghona 132 kV Ckt-1 was under shut down at 12:07 for A/M.
m) Bibiyana #03 ST tripped at 10:31 and was synchronized at 12:00.
n) HVDC filter 20DF23 was under shut down from 09:45 to 13:38 A/M.
o) Kaliakoir 400 kV bus CB was under shut down from 11:34 to 12:12 for A/M.
p) Khulna 225 MW ST was under shut down from 14:45 to 02:44(22-10-21) for auxiliary cooling water
line leakage maintenance.
q) Hasnabad 230/132 kV T02 was switched on at 20:06.
r) Pabna-Shajadpur 132 kV line was switched on by bus coupler breaker as main breaker is some problem.
s) Halishahar 132/33 kV T1,T2 & T3 transformer tripped at 21:45 due to 33 kV feeder fault and were |  |  |  |  | About 64 MW power interruption occurred under Halishahar
switched on at 22:00, Again T1 & T3 trip at 22:08 due to same case and were switched on at 22:19. |  |  |  |  | S/S area from 21:45 to 22:00.
t) Ashuganj (S) was shut sown since 05:05(22-10-21) for condenser cleaning.
u) Purbasadipur 132/33 kV T1 transformer was under shut down from 07:02 to 08:15(22-10-21) due |  |  |  |  | About 27 MW power interruption occurred under Purbasadipur
to red hot maint. |  |  |  |  | S/S area from 07:02 to 08:15.
v) Shahmirpur 132/33 kV T2 transformer was under shut down since 07:26 (22-10-21) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 3339000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 21 | 1101909 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 337 | 8331270 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 323 | 7544000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6158300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6311535 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1124612
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 30 | 127874 | Low demand.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 407520
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 4183000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 570240
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1290600
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 185760 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 910360
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 813501 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1238820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 826400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 820000
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 42 | 356640 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 3342108 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 71755 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 33252 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 54478 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 2581920 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 519600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 1800000 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 2606400 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 212581
| Dhaka area Total |  |  |  | 5560 | 2842 | 56863435
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 24710 | Low demand.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 37260
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 330240
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 160 | 3578938 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1451927
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 242646
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 353160
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1801920 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 441456 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 551040
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 35 | 89280 | Low demand.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 14160
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 5427164
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 432788 | Engine problem
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1461120
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2314560
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1726254
| Chattogram area Total |  |  |  | 2382 | 1448 | 23078623
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 105 | 2372640 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 144 | 3494000 | ST under maint
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7232200 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6758000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 598104 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1302240
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 669090 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1200886
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 2813527 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 73976 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3264800 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 197 | 2225280
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 504972
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 173340 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 3121920
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 650200 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 247066 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 485090 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 30336 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 429780
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 88 | 1613640 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1904 | 39705327
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 154 | 4180320 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 504216
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 1 | 40320 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13000
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 130 | 861600 | Low demand.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2283600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 280940
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 84000
| Mymensingh Area Total |  |  |  | 622 | 445 | 8247996
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1016000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1105680 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3304472
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2499000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1033200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 151728
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1386720
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1766440
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4863060
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 393000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 518400
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7060000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 322 | 7253000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245880
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7440400 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1744 | 40036980
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 710 | 17138181
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 11 | 18240 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 40 | 2119680 | Low demand.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9225936
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 788169
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1276 | 29290206
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 528362
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1560000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 17 | 421042 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 510 | 10970800
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 4880180
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 78000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 859 | 18438384
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 51312 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 22 | 43672 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 46760 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 38121 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 56490 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 115 | 2675900 | ST under maint & FGMO
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4394873 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Under maint.
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 346 | 8467345 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 490080
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 208836
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 151680 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 229792 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1406400
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1339872
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19560
| Rajshahi Area Total |  |  |  | 2179 | 1165 | 19620693
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 1886836
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 8948544
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22797
| Rangpur Area Total |  |  |  | 605 | 191 | 10858177
| Total |  |  |  | 20934 | 11874 | 246139821
| Eastern Grid Total |  |  |  | 13975 | 8383 | 167932361
| Western Grid Total |  |  |  | 6959 | 3491 | 78207460
| National Grid Total |  |  |  | 20934 | 11874 | 246139821
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-21
(a) ENTIRE EASTERN GRID : |  | 7965 | MW | (b) ENTIRE WESTERN GRID : |  | 3313 | MW
i) Dhaka area |  | 4236 | MW | i) Khulna area |  | 1302 | MW
ii) Chittagong area |  | 1295 | MW | ii) Rajshahi area |  | 1053 | MW
iii) Comilla area |  | 1056 | MW | iii) Barisal area |  | 314 | MW
iv) Mymensingh area |  | 892 | MW | iv) Rangpur area |  | 644 | MW
v) Sylhet area |  | 486 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11278 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 12:00 | Kishoreganj | 122 | 19:30 | Benapol | 48 | 18:30
Munsiganj | 86 | 20:00 | Netrokona | 102 | 19:30 | Jhenida(Old) | 96 | 18:30
Sonargaon | 68 | 10:00 | Jamalpur | 115 | 18:00 | Bottail | 110 | 18:00
Shyampur | 174 | 3:00 | Sherpur | 110 | 18:00 | G.K Project | 49 | 18:30
Bhulta | 182 | 10:00 | Srimongal | 51 | 17:00 | Faridpur | 123 | 18:30
Madanganj | 50 | 10:00 | Shahjibazar | 108 | 21:00 | Rajbari | 48 | 18:30
Shitalakhya | 110 | 18:30 | Fenchuganj | 41 | 17:00 | Madaripur | 83 | 19:30
Rahim steel | 16 | 7:00 | Kulawara | 44 | 18:00 | Sariatpur | 54 | 18:00
Matuail | 66 | 10:00 | Sylhet | 136 | 18:00 | Gopalganj | 80 | 18:30
Ghorasal | 71 | 14:00 | Chatak | 26 | 20:00 | Bagerhat | 90 | 18:30
Narsingdi | 160 | 19:30 | Sunamganj | 45 | 20:00 | Mongla | 32 | 9:00
Haripur (SBU) | 116 | 18:30 | Biani Bazar | 55 | 20:00 | Satkhira | 89 | 19:00
Sreenagar | 34 | 21:00 | Comilla (S) | 150 | 18:00 | Gallamari | 34 | 13:00
Ullon | 59 | 18:00 | Comilla(N) | 105 | 19:30 | Magura | 46 | 18:00
Hasnabad | 76 | 18:00 | Chandpur | 62 | 21:00 | Norail | 43 | 18:00
Magbazar | 98 | 11:00 | Feni | 102 | 18:00 | Chuadanga | 80 | 18:30
Maniknagar | 64 | 12:00 | Chowmuhani | 186 | 19:30 | Barisal(N) | 36 | 20:00
Bangabhaban | 11 | 10:00 | Ashuganj | 41 | 0:00 | Barisal (S) | 96 | 18:00
Motijheel | 28 | 13:00 | Daudkandi | 136 | 21:00 | Patuakhali | 97 | 21:00
Narinda | 54 | 18:00 | B.Baria | 150 | 19:00 | Bhandaria | 46 | 18:30
Kazla | 73 | 18:00 | Ramganj | 76 | 18:00 | Borguna | 16 | 21:00
Dhanmondi | 194 | 13:00 | Chaddagram | 42 | 18:00 | Borhan Uddin | 39 | 22:00
Lalbag | 83 | 13:00 | PHP | 10 | 0:00 | Ishurdi | 63 | 18:30
Madartek | 66 | 19:00 | Kochua | 58 | 19:30 | Ruppur Paromanobik | 4 | 10:00
Dhaka University | 34 | 13:00 | Madunaghat | 58 | 18:00 | Natore | 105 | 18:30
Aftabnagar | 14 | 11:00 | Hathazari | 92 | 19:30 | Bogra | 138 | 18:30
Fatullah | 60 | 10:00 | Khulshi | 180 | 20:00 | Noagaon | 94 | 18:30
Nawabganj | 43 | 21:00 | Halishahar | 92 | 11:00 | Rajshahi | 122 | 18:30
Keraniganj | 64 | 18:00 | Baraulia | 141 | 20:00 | Rajshahi New | 15 | 19:30
Banani | 30 | 13:00 | Sikalbaha | 42 | 18:00 | C.Nawabganj | 49 | 14:00
Mirpur | 113 | 18:00 | Dohazari | 90 | 18:30 | Amnura | 34 | 19:00
Kalyanpur | 90 | 18:00 | Cox'sbazar | 92 | 18:30 | Pabna | 89 | 18:30
Gulshan | 110 | 12:00 | Chandraghona | 26 | 18:00 | Shahjadpur | 81 | 18:30
Uttara | 86 | 18:00 | Kaptai | 4.2 | 18:30 | Serajganj | 80 | 19:00
Uttara New | 23 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 57 | 19:00
Kamrangirchar | 92 | 18:00 | Bakulia | 115 | 18:00 | Joypurhat | 41 | 18:30
Savar | 161 | 15:00 | Julda | 23 | 15:00 | Sherpur(Bogura) | 46 | 18:00
Bhasantec | 126 | 18:00 | TK chemical | 28.6 | 18:00 | Mohastangor | 52 | 20:00
Agargaon | 77 | 13:00 | Modern Steel | 5 | 9:00 | Bhangura | 26 | 18:00
Satmosjid | 99 | 13:00 | Shahmirpur | 31.5 | 18:30 | Rangpur | 109 | 18:00
Tongi | 119 | 11:00 | Khagrachhari | 22 | 18:00 | Lalmonirhat | 39 | 19:30
Kabirpur | 226 | 3288:00 | Matarbari | 41 | 17:00 | Saidpur | 88 | 18:00
Basundhara | 183 | 13:00 | Baroiar Hat | 50 | 18:00 | Purbasadipur | 91 | 18:30
Manikganj | 62 | 19:30 | Rangamati | 12 | 18:00 | Thakurgaon | 66 | 18:30
Joydevpur | 167 | 18:00 | Abul Khair 230 | 6 | 16:00 | Palashbari | 92 | 18:30
New Tongi | 85 | 11:00 | BSRM | 155 | 5:00 | Barapukuria | 46 | 18:30
Kodda | 253 | 15:00 | GPH Ispat | 87 | 18:30 | Panchagar | 47 | 18:00
Dhamrai | 94 | 11:00 | Agrabad | 65 | 18:00 | Joldhaka | 31 | 18:30
Rajendrapur | 94 | 18:30 | Goalpara | 24 | 18:00 | Kurigram | 55 | 18:00
Valuka | 110 | 19:00 | Central S/S | 90 | 18:30 | Mithapukur | 33 | 18:00
Tangail | 186 | 18:30 | Noapara | 41 | 18:30
Mymensing | 177 | 18:00 | Jessore | 97 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 2:00 | 403 | 15:00 | Kaliakoir | 398 | 0.29167 | 387 | 0.41667
| Bheramara | 397 | 24:00 | 393 | 18:00 | Bhulta | 387 | 0.083333 | 378 | 0.41667
| Ashuganj(N) | 394 | 22:00 | 387 | 10:00 | Gopalganj | 404 | 0.625 | 389 | 0.8125
| Payra | 410 | 2:00 | 399 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 235 | 7:00 | Hathazari | 235 | 18:30 | 219 | 9:00
| Ishurdi | 234 | 6:00 | 228 | 22:00 | Megnaghat | 236 | 18:30 | 228 | 19:30
| Ashuganj | 242 | 1:00 | 238 | 10:00 | Fenchuganj | 245 | 1:00 | 242 | 7:00
| Serajganj | 231 | 11:00 | 226 | 7:00 | Siddhirganj | 233 | 1:00 | 227 | 9:00
| Baghabari | 232 | 9:00 | 230 | 10:00 | Maniknagar | 231 | 1:00 | 225 | 16:00
| Barapukuria | 236 | 23:00 | 231 | 9:00 | Agargaon | 230 | 8:00 | 222 | 12:00
| Bogra | 227 | 7:00 | 222 | 10:00 | Barisal | 243 | 18:00 | 234 | 18:30
| Rajshahi | 229 | 17:00 | 221 | 22:00 | Bhola 225 MW | 246 | 7:00 | 239 | 18:00
| Khulna South | 232 | 6:00 | 219 | 15:00 | AKSML | 236 | 18:00 | 217 | 5:00
| Rampura | 231 | 24:00 | 224 | 10:00 | BSRM | 236 | 18:00 | 216 | 5:00
| Haripur | 230 | 1:00 | 224 | 16:00 | Bibiyana | 244 | 2:00 | 238 | 10:00
| Hasnabad | 230 | 1:00 | 225 | 10:00 | Bhulta | 233 | 2:00 | 226 | 10:00
| Shyampur | 229 | 2:00 | 223 | 12:00 | Ashuganj (S) | 238 | 1:00 | 234 | 10:00
| Aminbazar | 231 | 1:00 | 224 | 2:00 | Kaliakoir | 232 | 22:00 | 222 | 13:00
| Tongi | 230 | 21:00 | 220 | 10:00 | GPH | 238 | 18:00 | 216 | 5:00
| Comilla (N) | 233 | 18:00 | 227 | 9:00 | Jhenaidah | 228 | 6:00 | 216 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 132 | 9:00 | Madanhat | 139 | 0.75 | 128 | 0.33333
| Munsiganj | 136 | 18:30 | 132 | 10:00 | Hathazari | 138 | 0.79167 | 130 | 0.20833
| Sonargaon | 134 | 1:00 | 131 | 10:00 | Khulshi | 136 | 0.75 | 124 | 0.20833
| Shyampur | 137 | 1:00 | 133 | 12:00 | Halishahar | 138 | 0.75 | 125 | 0.20833
| Bhulta | 130 | 1:00 | 127 | 11:00 | Baraulia | 136 | 0.75 | 125 | 0.5
| Madanganj | 136 | 19:30 | 131 | 10:00 | Sikalbaha | 139 | 0.75 | 125 | 0.20833
| Shitalakhya | 137 | 20:00 | 131 | 16:00 | Dohazari | 133 | 0.75 | 123 | 0.16667
| Rahim steal | 135 | 1:00 | 132 | 7:00 | Cox'sbazar | 125 | 0.75 | 113 | 0.25
| Matuail | 135 | 1:00 | 132 | 9:00 | Chandraghona | 138 | 0.75 | 128 | 0.375
| Ghorasal | 140 | 1:00 | 139 | 23:00 | Kaptai | 137 | 0.75 | 130 | 0.041667
| Narsinghdi | 135 | 7:00 | 129 | 22:00 | A. Khaer Stl. | 136 | 0.77083 | 127 | 0.25
| Haripur (SBU) | 135 | 1:00 | 132 | 10:00 | Bakulia | 137 | 0.75 | 124 | 0.20833
| Sreenagar | 135 | 1:00 | 129 | 16:00 | Julda | 139 | 0.75 | 127 | 0.041667
| Ullon | 135 | 2:00 | 129 | 11:00 | TK Chemical | 138 | 0.75 | 128 | 0.25
| Hasnabad | 135 | 1:00 | 131 | 16:00 | Modern Steel | 137 | 0.77083 | 126 | 0.375
| Magbazar | 135 | 3:00 | 129 | 10:00 | Shahmirpur | 138 | 0.77083 | 126 | 0.16667
| Maniknagar | 135 | 1:00 | 131 | 11:00 | Khagrachhari | 136 | 0.75 | 127 | 0.20833
| Bangabhaban | 135 | 1:00 | 131 | 11:00 | Matarbari | 125 | 0.54167 | 118 | 0.041667
| Motijheel | 135 | 1:00 | 131 | 11:00 | Baroiar Hat | 134 | 0.66667 | 127 | 0.20833
| Narinda | 135 | 1:00 | 131 | 11:00 | Rangamati | 137 | 18:00 | 129 | 3:00
| Kazla | 135 | 1:00 | 131 | 11:00 | Agrabad | 137 | 18:00 | 126 | 4:00
| Dhanmondi | 135 | 1:00 | 131 | 11:00 | Goalpara S/S | 138 | 6:00 | 131 | 0.625
| Lalbag | 135 | 1:00 | 130 | 12:00 | Khulna Central S/S | 137 | 6:00 | 132 | 0.77083
| Madartek | 135 | 2:00 | 129 | 12:00 | Noapara | 137 | 5:00 | 129 | 0.625
| Dhaka University | 135 | 1:00 | 129 | 12:00 | Jessore | 134 | 8:00 | 127 | 0.625
| Aftabnagar | 135 | 1:00 | 129 | 11:00 | Benapol | 135 | 0.25 | 128 | 0.625
| Fatullah | 137 | 1:00 | 133 | 10:00 | Jhenida(Old) | 138 | 6:00 | 130 | 0.625
| Nawabganj | 135 | 1:00 | 130 | 10:00 | Bottail | 136 | 0.20833 | 132 | 0.58333
| Keraniganj | 136 | 2:00 | 130 | 15:00 | G.K Project | 139 | 0.25 | 135 | 0.91667
| Banani | 135 | 1:00 | 128 | 10:00 | Faridpur | 136 | 0.58333 | 129 | 0.91667
| Mirpur | 134 | 1:00 | 126 | 16:00 | Rajbari | 136 | 0.41667 | 129 | 0.91667
| Kalyanpur | 134 | 1:00 | 128 | 12:00 | Madaripur | 141 | 0.33333 | 136 | 0.75
| Gulshan | 134 | 1:00 | 129 | 10:00 | Shariyatpur S/S | 139 | 7:00 | 132 | 0.041667
| Uttara | 133 | 1:00 | 125 | 14:00 | Gopalganj | 142 | 0.33333 | 133 | 0.875
| Uttara New | 134 | 1:00 | 126 | 12:00 | Bagerhat | 135 | 6:00 | 127 | 0.625
| Kamrangirchar | 135 | 6:00 | 130 | 16:00 | Mongla | 134 | 11:00 | 127 | 0.625
| Savar | 135 | 1:00 | 128 | 12:00 | Satkhira | 136 | 6:00 | 127 | 18:30
| Bhasantec | 137 | 1:00 | 130 | 12:00 | Gallamari | 136 | 0.25 | 129 | 22:00
| Agargaon | 138 | 2:00 | 132 | 12:00 | Magura | 137 | 6:00 | 130 | 0.625
| Satmosjid | 138 | 2:00 | 131 | 12:00 | Narail | 135 | 0.25 | 127 | 0.75
| Tongi | 139 | 21:00 | 133 | 15:00 | Chuadanga | 134 | 6:00 | 125 | 0.77083
| Kabirpur | 137 | 4.00 | 132 | 18:29 | Barisal(N) | 141 | 8:00 | 132 | 0.91667
| Basundhara | 137 | 18:30 | 130 | 11:00 | Barisal (S) | 138 | 6:00 | 132 | 18:00
| Manikganj | 141 | 7.00 | 137 | 15:00 | Patuakhali(S) | 137 | 0.33333 | 128 | 0.95833
| Joydevpur | 139 | 18:30 | 132 | 10:00 | Bhandaria | 137 | 0.29167 | 127 | 0.875
| New Tongi | 137 | 3:00 | 132 | 10:00 | Borguna | 138 | 0.29167 | 131 | 0.875
| Kodda | 134 | 20:00 | 125 | 10:00 | Jhenaidah(230kV S/S)
| Dhamrai | 137 | 6.00 | 132 | 10:00 | Ishurdi | 136 | 6:00 | 133 | 1:00
| Rajendrapur | 131 | 14:00 | 124 | 11:00 | Ruppur Paromanobik | 136 | 6:00 | 134 | 1:00
| Valuka | 127 | 7:00 | 119 | 18:00 | Natore | 135 | 19:00 | 132 | 1:00
| Tangail | 133 | 5:00 | 129 | 15:00 | Bogra | 136 | 12:00 | 131 | 6:00
| Mymensing | 131 | 11:00 | 123 | 18:00 | Noagaon | 133 | 11:00 | 127 | 18:00
| Kishorganj | 133 | 11:00 | 126 | 18:00 | Rajshahi | 134 | 11:00 | 132 | 1:00
| Netrokona | 129 | 6:00 | 120 | 18:00 | Rajshahi New | 137 | 18:30 | 131 | 9:00
| Jamalpur | 139 | 19:00 | 124 | 18:00 | C.Nawabganj | 135 | 18:30 | 130 | 10:00
| Sherpur | 138 | 19:00 | 126 | 4:00 | Amnura | 136 | 18:00 | 129 | 1:00
| Srimongal | 138 | 9:00 | 135 | 23:00 | Pabna | 135 | 6:00 | 130 | 18:30
| Shahjibazar | 137 | 8:00 | 133 | 22:00 | Shahjadpur | 138 | 19:00 | 135 | 7:00
| Fenchuganj | 137 | 3:00 | 134 | 20:00 | Serajganj | 135 | 1:00 | 132 | 9:00
| Khulawara | 136 | 4:00 | 134 | 15:00 | Niyamatpur | 131 | 11:00 | 123 | 18:00
| Sylhet | 133 | 1:00 | 132 | 9:00 | Joypurhat | 134 | 10:00 | 129 | 18:30
| Chatak | 133 | 1:00 | 130 | 22:00 | Sherpur(Bogura) | 135 | 2:00 | 132 | 10:00
| Sunamganj | 131 | 6:00 | 127 | 19:00 | Mohastangor | 135 | 21:00 | 130 | 1:00
| Biani Bazar | 133 | 7:00 | 129 | 18:00 | Bangura | 136 | 11:00 | 134 | 7:00
| Comilla(s) | 128 | 23:00 | 124 | 16:00 | Rangpur | 132 | 20:00 | 126 | 8:00
| Comilla(n) | 139 | 18:00 | 135 | 7:00 | Lalmonirhat | 133 | 20:00 | 127 | 8:00
| Chandpur | 138 | 18:00 | 132 | 4:00 | Saidpur | 133 | 6:00 | 126 | 7:00
| Feni | 137 | 18:00 | 128 | 3:00 | Purbasadipur | 133 | 21:00 | 126 | 18:30
| Chowmuhani | 133 | 18:00 | 126 | 4:00 | Thakurgaon | 132 | 11:00 | 128 | 1:00
| Ashuganj | 140 | 11:00 | 137 | 23:00 | Palashbari | 133 | 2:00 | 128 | 9:00
| Daudkandi | 137 | 18:00 | 130 | 10:00 | Barapukuria | 135 | 12:00 | 131 | 9:00
| B.Baria | 135 | 17:00 | 130 | 22:00 | Panchagar | 134 | 0.875 | 128 | 0.375
| Ramganj | 137 | 18:00 | 130 | 0:00 | Joldhaka | 131 | 0.083333 | 125 | 0.375
| Chaddagram | 139 | 18:00 | 129 | 4:00 | Kurigram | 135 | 0.875 | 126 | 0.875
| PHP | 136 | 18:30 | 125 | 5:00 | Mithapukur | 136 | 0.875 | 130 | 0.33333
| Kochua | 138 | 17:00 | 131 | 4:00

## L-Curve
Date | 2021-10-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 38 | 7239 | 2897 | 10136 |  |  |  | QF-LDC-11
0:30 | 40 | 6983 | 2826.5 | 9809.5 | Date: | 2021-10-21
1:00 | 42 | 6727 | 2756 | 9483
1:30 | 38 | 6586.5 | 2681.5 | 9268
2:00 | 34 | 6446 | 2607 | 9053
2:30 | 74 | 6276.5 | 2621 | 8897.5 | [5 empty] | Gen. at Eve. Peak | 11874 | 11874 MW (19:00 )
3:00 | 114 | 6107 | 2635 | 8742 | [6 empty] | 19:00
3:30 | 126 | 5999.5 | 2585 | 8584.5 | [5 empty] | Gen. at Day Peak | 9930 | 9930 MW (12:00 )
4:00 | 138 | 5892 | 2535 | 8427 | [6 empty] | 12:00
4:30 | 179 | 5805.5 | 2557 | 8362.5 | [5 empty] | Highest Generation | 11874
5:00 | 220 | 5719 | 2579 | 8298 | [6 empty] | 19:00
5:30 | 254 | 5599.5 | 2540 | 8139.5
6:00 | 288 | 5480 | 2501 | 7981
6:30 | 223 | 5519 | 2504 | 8023
7:00 | 158 | 5558 | 2507 | 8065
7:30 | 185 | 5661.5 | 2496 | 8157.5
8:00 | 212 | 5765 | 2485 | 8250
8:30 | 259 | 5991 | 2497.5 | 8488.5
9:00 | 306 | 6217 | 2510 | 8727
9:30 | 330 | 6318 | 2561.5 | 8879.5
10:00 | 354 | 6419 | 2613 | 9032
10:30 | 348 | 6534.5 | 2677 | 9211.5
11:00 | 342 | 6650 | 2741 | 9391
11:30 | 317 | 6872 | 2788.5 | 9660.5
12:00 | 292 | 7094 | 2836 | 9930
12:30 | 243 | 7181.5 | 2901.5 | 10083
13:00 | 194 | 7269 | 2967 | 10236
13:30 | 170 | 7293.5 | 2887.5 | 10181
14:00 | 146 | 7318 | 2808 | 10126
14:30 | 226 | 7338.5 | 2836 | 10174.5
15:00 | 306 | 7359 | 2864 | 10223
15:30 | 327 | 7282 | 2833.5 | 10115.5
16:00 | 348 | 7205 | 2803 | 10008
16:30 | 289 | 7181 | 2731 | 9912
17:00 | 230 | 7157 | 2659 | 9816
17:30 | 137 | 7648.5 | 2981 | 10629.5
18:00 | 44 | 8140 | 3303 | 11443
18:30 | 30 | 8261.5 | 3397 | 11658.5
19:00 | 16 | 8383 | 3491 | 11874
19:30 | 48 | 8209 | 3398 | 11607
20:00 | 84 | 8167 | 3335 | 11502 |  |  |  | Executive Engineer
20:30 | 64 | 8042 | 3320.5 | 11362.5 |  |  |  | Network Operation Division
21:00 | 44 | 7917 | 3306 | 11223
21:30 | 53 | 7667.5 | 3240 | 10907.5
22:00 | 62 | 7418 | 3174 | 10592 |  |  |  |  | Page 6 of 7
22:30 | 71 | 7420 | 3127 | 10547
23:00 | 80 | 7422 | 3080 | 10502
23:30 | 59 | 7330.5 | 2988.5 | 10319
24:00 | 38 | 7239 | 2897 | 10136
11874 MW (19:00 )
9930 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-21 |  | Energy |  | 246139821
[13 empty] | 2021-10-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4124 | 711 | 2151 | 0 | 2291 | 548 | 165 | 10 | 0 | 136 | 0 | 0
0:30 | 4093 | 711 | 2197 | 0 | 1910 | 539 | 163.5 | 65 | 0 | 131 | 0 | 0 | Date: | 2021-10-21
1:00 | 4062 | 711 | 2243 | 0 | 1529 | 530 | 162 | 120 | 0 | 126 | 0 | 0
1:30 | 4030 | 712 | 2216.5 | 0 | 1385 | 520 | 160.5 | 120 | 0 | 124 | 0 | 0 | [8 empty] | Total Energy | 246.1398 | Total Energy Gen 246.140 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 246.140 MKWHr
2:00 | 3998 | 713 | 2190 | 0 | 1241 | 510 | 159 | 120 | 0 | 122 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3949.5 | 712.5 | 2215 | 0 | 1111 | 510 | 158.5 | 120 | 0 | 121 | 0 | 0 | [8 empty] | Energy Requirement | 246.1398
3:00 | 3901 | 712 | 2240 | 0 | 981 | 510 | 158 | 120 | 0 | 120 | 0 | 0
3:30 | 3896.5 | 712.5 | 2206.5 | 0 | 877.5 | 494.5 | 158 | 120 | 0 | 119 | 0 | 0 | [6 empty] | Shortage
4:00 | 3892 | 713 | 2173 | 0 | 774 | 479 | 158 | 120 | 0 | 118 | 0 | 0
4:30 | 3894.5 | 713.5 | 2190 | 0 | 690 | 479 | 158.5 | 120 | 0 | 117 | 0 | 0
5:00 | 3897 | 714 | 2207 | 0 | 606 | 479 | 159 | 120 | 0 | 116 | 0 | 0
5:30 | 3844 | 714 | 2090 | 0 | 629.5 | 469 | 160 | 120 | 0 | 113 | 0 | 0
6:00 | 3791 | 714 | 1973 | 0 | 653 | 459 | 161 | 120 | 0 | 110 | 0 | 0
6:30 | 3834 | 713.5 | 1981.5 | 0 | 662 | 459 | 143.5 | 120 | 0 | 106 | 3.5 | 0 |  |  |  |  | Coal
7:00 | 3877 | 713 | 1990 | 0 | 671 | 459 | 126 | 120 | 0 | 102 | 7 | 0
7:30 | 3873.5 | 713.5 | 1985 | 0 | 759.5 | 458.5 | 126.5 | 120 | 0 | 105 | 16 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3870 | 714 | 1980 | 0 | 848 | 458 | 127 | 120 | 0 | 108 | 25 | 0
8:30 | 3932.5 | 714 | 2019.5 | 0 | 975.5 | 449.5 | 127.5 | 120 | 0 | 111 | 39 | 0
9:00 | 3995 | 714 | 2059 | 0 | 1103 | 441 | 128 | 120 | 0 | 114 | 53 | 0
9:30 | 3985.5 | 714 | 2123 | 0 | 1180 | 440.5 | 128 | 120 | 0 | 119 | 69.5 | 0
10:00 | 3976 | 714 | 2187 | 0 | 1257 | 440 | 128 | 120 | 0 | 124 | 86 | 0
10:30 | 3920 | 714 | 2213 | 54 | 1404.5 | 445 | 129 | 120 | 0 | 125 | 87 | 0
11:00 | 3864 | 714 | 2239 | 108 | 1552 | 450 | 130 | 120 | 0 | 126 | 88 | 0
11:30 | 3842.5 | 712 | 2223.5 | 54 | 1919.5 | 449.5 | 130 | 120 | 0 | 130 | 79.5 | 0
12:00 | 3821 | 710 | 2208 | 0 | 2287 | 449 | 130 | 120 | 0 | 134 | 71 | 0
12:30 | 3952 | 710 | 2139.5 | 0 | 2367 | 449.5 | 130 | 120 | 0 | 131 | 84 | 0
13:00 | 4083 | 710 | 2071 | 0 | 2447 | 450 | 130 | 120 | 0 | 128 | 97 | 0
13:30 | 4083 | 710 | 2071 | 0 | 2447 | 450 | 130 | 120 | 0 | 128 | 97 | 0
14:00 | 4083 | 710 | 2071 | 0 | 2447 | 450 | 130 | 120 | 0 | 128 | 97 | 0
14:30 | 4065 | 709.5 | 2117 | 0 | 2453 | 445.5 | 145 | 80 | 0 | 134 | 80.5 | 0
15:00 | 4047 | 709 | 2163 | 0 | 2459 | 441 | 160 | 40 | 0 | 140 | 64 | 0
15:30 | 4060.5 | 709 | 2198.5 | 0 | 2313 | 446 | 160 | 40 | 2 | 139 | 47.5 | 0
16:00 | 4074 | 709 | 2234 | 0 | 2167 | 451 | 160 | 40 | 4 | 138 | 31 | 0
16:30 | 4009 | 709 | 2174 | 0 | 2199.5 | 450 | 160 | 40 | 17 | 135 | 18.5 | 0
17:00 | 3944 | 709 | 2114 | 0 | 2232 | 449 | 160 | 40 | 30 | 132 | 6 | 0
17:30 | 4007.5 | 709 | 2202 | 103.5 | 2576.5 | 463.5 | 160 | 40 | 223.5 | 141 | 3 | 0
18:00 | 4071 | 709 | 2290 | 207 | 2921 | 478 | 160 | 40 | 417 | 150 | 0 | 0
18:30 | 4097.5 | 709.5 | 2247 | 103.5 | 3222 | 533 | 160 | 40 | 397 | 149 | 0 | 0
19:00 | 4124 | 710 | 2204 | 0 | 3523 | 588 | 160 | 40 | 377 | 148 | 0 | 0
19:30 | 4106 | 710 | 2229 | 0 | 3440 | 598 | 160 | 40 | 176 | 148 | 0 | 0
20:00 | 4109 | 709 | 2190 | 0 | 3437 | 599 | 160 | 40 | 110 | 148 | 0 | 0
20:30 | 4107 | 709.5 | 2214 | 0 | 3321.5 | 598.5 | 161.5 | 40 | 63.5 | 147 | 0 | 0
21:00 | 4105 | 710 | 2238 | 0 | 3206 | 598 | 163 | 40 | 17 | 146 | 0 | 0
21:30 | 4112 | 710.5 | 2245.5 | 0 | 2897.5 | 599 | 163 | 27.5 | 8.5 | 144 | 0 | 0
22:00 | 4119 | 711 | 2253 | 0 | 2589 | 600 | 163 | 15 | 0 | 142 | 0 | 0
22:30 | 4120.5 | 711 | 2221.5 | 0 | 2582 | 594.5 | 164 | 12.5 | 0 | 141 | 0 | 0
23:00 | 4122 | 711 | 2190 | 0 | 2575 | 589 | 165 | 10 | 0 | 140 | 0 | 0
23:30 | 4123 | 711 | 2170.5 | 0 | 2433 | 568.5 | 165 | 10 | 0 | 138 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 32.3° C
24:00 | 4124 | 711 | 2151 | 0 | 2291 | 548 | 165 | 10 | 0 | 136 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 246.140 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 246.140 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 87 | 84 | 83 | 83 | 84 | 86 | 86 | 87 | 88 | 88 | 90 | 90 | 90 | 86 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 88 | 88 | 90 | 90 | 2046938
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1532000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 7 |  | 16 | [6 empty] | 24710
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 1 | 3 | 7 | 1 | 4 | 8 | 8 | 7 | 3 | 1 | [9 empty] | 37260
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 102 |  | 102 | 51 | 23 | 17 |  |  |  | 242646
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 |  |  |  |  | 5 | 16 | 17 | 17 | 24 | 39 | 99 | 105 | 105 | 105 | 51 | 51 | 70 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1451927
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 50 | [8 empty] | 30336
14 | Titas 50 MW Peaking PP | [17 empty] | 50 | [8 empty] | 73976
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 130 | 130 | 130 | 130 | 130 | 128 | 155 | 185 | 185 | 202 | 205 | 200 | 205 | 198 | 201 | 200 | 127 | 163 |  | 185 | 160 | 160 | 160 | 155 | 155 | 155 | 4183000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 1 | 15 | 15 | 15 | 135 | 215 | 270 | 270 | 276 | 281 | 278 |  | 278 | 285 | 300 | 296 | 180 | 180 | 180 | 3342108
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 669090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3339000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2372640
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 29 | 26 | 598104
33 | Ashuganj 225 MW CCPP | 146 | 147 | 145 | 146 | 144 | 146 | 144 | 146 | 143 | 142 | 145 | 140 | 143 | 140 | 139 | 139 | 142 | 141 |  | 144 | 143 | 144 | 144 | 142 | 144 | 146 | 3494000
34 | Ashuganj 450 MW CCPP(South) | 295 | 275 | 275 | 275 | 300 | 275 | 285 | 275 | 300 | 275 | 275 | 285 | 270 | 270 | 270 | 275 | 270 | 265 |  | 270 | 270 | 265 | 265 | 275 | 270 | 270 | 6758000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 310 | 280 | 300 | 270 | 355 | 280 | 310 | 285 | 265 | 270 | 280 | 285 | 280 | 280 |  | 280 | 280 | 285 | 280 | 290 | 285 | 285 | 7232200
35 | Ashuganj 55 MW PP (Precision) | 53 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 52 | 51 | 51 | 51 | 52 | 50 | 53 | 55 | 55 |  | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 1302240
36 | Chandpur 150 MW CCPP | 136 | 137 | 136 | 138 | 138 | 139 | 138 | 137 | 137 | 138 | 134 | 137 | 135 | 135 | 137 | 137 | 136 | 138 |  | 135 | 137 | 135 | 136 | 138 | 138 | 138 | 3264800
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 350 | 351 | 351 | 352 | 352 | 322 | 301 | 302 | 345 | 378 | 368 | 339 | 340 | 339 | 339 | 339 | 338 |  | 337 | 337 | 337 | 337 | 337 | 338 | 337 | 8331270
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6158300
41 | Haripur 360MW CCPP(HPL) | 332 | 331 | 332 | 332 | 332 | 302 | 301 | 302 | 303 | 293 | 304 | 292 | 287 | 287 | 288 | 323 | 329 | 328 |  | 323 | 323 | 323 | 322 | 322 | 331 | 333 | 7544000
42 | RPCL 210MW CCPP | 209 | 211 | 213 | 213 | 211 | 212 | 210 | 212 | 209 | 182 | 166 | 165 | 140 | 138 | 141 | 140 | 155 | 155 |  | 154 | 155 | 158 | 161 | 170 | 171 | 171 | 4180320
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 2 | 6 | 22 | 41 | 42 | 46 | 51 | 37 | 27 | 14 | 2 | [9 empty] | 280940
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1016000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1105680
46 | Shajibazar 330 MW CCPP | 111 | 112 | 110 | 110 | 111 | 110 | 111 | 112 | 110 | 110 | 111 | 110 | 110 | 109 | 110 | 110 | 110 | 109 |  | 110 | 111 | 110 | 110 | 111 | 110 | 110 | 2499000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 40 | 40 | 40 | 40 | 60 | 61 | 60 | 61 | 60 | 61 | 61 | 62 | 61 |  | 62 | 61 | 62 | 62 | 61 | 62 | 62 | 1386720
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 20 | 20 | 20 | 81 | 81 | 81 | 81 | 80 | 78 | 78 | 78 | 78 | 84 | 84 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1766440
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 166 | 140 | 205 | 218 | 218 | 218 | 218 | 218 | 206 | 167 | 166 | 166 | 166 | 205 |  | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 4863060
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 393000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245880
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 |  |  |  | 8 | 8 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 2 | 4 | 11 | 151728
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 14 | 14 | 14 | 14 | 44 | 44 | 45 | 45 | 49 | 46 | 44 | 47 | 49 |  | 49 | 49 | 49 | 49 | 50 | 50 | 50 | 1033200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 18 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 518400
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 270 | 270 | 265 | 290 | 290 | 295 | 300 | 290 | 300 | 280 | 280 | 270 | 270 | 300 | 300 | 300 | 290 |  | 270 | 290 | 280 | 280 | 290 | 290 | 275 | 7060000
| Bibiyana South 400 MW | 320 | 320 | 250 | 250 | 250 | 260 | 260 | 290 | 320 | 320 | 384 | 365 | 345 | 330 | 330 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7440400
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 813501
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 10 |  | 23 | 23 | 23 | 23 |  |  |  | 84000
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 441456
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 407520
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504216
63 | Impoprt (Tripura) | 126 | 122 | 120 | 118 | 116 | 110 | 102 | 108 | 114 | 124 | 126 | 134 | 128 | 138 | 140 | 138 | 132 | 150 |  | 148 | 148 | 148 | 146 | 142 | 140 | 136 | 3121920
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 37 | 4 | 4 | 4 | 10 | 12 | 25 | 25 | 10 | 5 | 6 | 12 |  | 10 | 10 | 17 | 30 | 0 | 0 | 0 | 551040
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504972
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 173340
67 | Jangalia 33MW PP (Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 650200
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 12 | 12 | 12 | 12 | 16 | 20 | 20 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 485090
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 29 | 28 | 28 | 29 | 29 | 29 | 28 | 29 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 17 |  | 29 | 29 | 29 | 26 | 23 | 29 | 29 | 638820
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820000
73 | Ghorashal 108MW PP (Regent) | 102 | 100 | 95 | 94 | 94 | 22 | 22 | 22 | 22 | 74 | 90 | 97 | 10 | 10 | 21 | 21 | 23 | 22 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 1101909
| Feni Lanka Power | [10 empty] | 8 | 17 | 17 |  |  |  | 17 | 86 |  | 114 | 114 | 95 | 52 | 17 | 17 |  | 429780
| Chowmuhani 113 MW | 59 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 49 | 55 | 59 | 57 | 58 | 59 | 58 | 85 |  | 88 | 97 | 96 | 98 | 96 | 97 | 63 | 1613640
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 150 | 108 | 54 | 54 | 54 | 62 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2606400
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 4 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 34 |  | 42 | 25 | 25 | 8 |  |  |  | 356640
79 | Kodda 150MW PP | [16 empty] | 16 | 98 |  | 64 | 32 | 32 |  |  |  |  | 185760
80 | Jamalpur 95 MW PP(Powerpac) | [19 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 40320
81 | Jangalia 52 MW PP (Lakdanavi) | [11 empty] | 10 | 8 | 8 | 8 | 8 | 8 | 10 |  | 43 | 43 | 43 | 43 | 8 | 8 |  | 247066
| Gazipur 100 MW PP | [10 empty] | 5 | 17 |  |  |  |  | 4 | 42 |  | 105 | 105 | 105 | 70 | 52 | 52 | 34 | 519600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 1 | 5 | 1 | 2 | 3 | 2 | 1 | 0 | 0 | [9 empty] | 14160
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432788
| Karnaphuli Power Ltd. | 17 | [6 empty] | 17 | 17 | 17 | 23 | 107 | 109 | 110 | 110 | 51 | 51 | 72 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1461120
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 10 |  |  |  |  | 5 | 20 |  | 30 | 24 | 27 | 14 |  |  |  | 127874
86 | Meghnaghat CCPP ( Summit) | 240 | 235 | 255 | 245 | 280 | 260 | 275 | 250 | 280 | 260 | 240 | 280 | 250 | 260 | 260 | 275 | 245 | 260 |  | 260 | 260 | 250 | 260 | 275 | 255 | 245 | 6311535
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 93 | 73 | 61 | 54 | 24 | 17 | 17 | 17 | 48 | 60 | 85 | 93 | 91 | 92 | 94 | 95 | 94 | 95 |  | 94 | 94 | 95 | 95 | 95 | 95 | 95 | 1800000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 7 | 10 | 10 |  |  |  | 10 | 72 |  | 100 | 100 | 100 | 50 | 10 | 10 |  | 353160
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 26 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1200886
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 5 | 32 | 32 | 32 | 32 | 32 | 32 | 70 |  | 102 | 102 | 102 | 64 | 7 | 7 |  | 570240
95 | Patenga 50MW PP (Baraka) | [11 empty] | 19 | 26 | 19 | 19 | 19 | 19 | 26 |  | 50 | 50 | 50 | 27 |  | 7 | 19 | 330240
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [5 empty] | 4 | 34 |  | 35 | 12 | 12 |  |  |  |  | 89280
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 40 | 15 | 15 | 15 | 15 | 30 | 55 | 55 | 45 | 50 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 1124612
100 | Manikganj 55 MW PP (Northern) | 55 | 35 | [5 empty] | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 910360
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 110 | 110 | 110 | 130 | 130 | 110 | 163 |  | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 3304472
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | [10 empty] | 13000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1290600
104 | Keranigonj 300 MW PP (APR) | [10 empty] | 108 | [6 empty] | 57 | [8 empty] | 71755
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 | [8 empty] | 33252
106 | Mymensingh 200 MW PP (United) | 24 | 8 | [8 empty] | 5 | 32 | 16 | 8 | 8 | 8 | 8 | 50 |  | 130 | 110 | 110 | 110 | 80 | 80 | 60 | 861600
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 0 | 0 |  |  |  |  | 50 | [8 empty] | 54478
114 | Kodda 149 MW PP Unit-1 (Summit) | 79 | 65 | 55 | 50 | 50 | 50 | 52 | 77 | 132 | 132 | 132 | 132 | 132 | 131 | 115 | 121 | 132 | 132 |  | 133 | 133 | 133 | 133 | 133 | 132 | 121 | 2581920
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 50 | 50 | 30 | 30 | 30 | 70 | 70 | 76 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 1801920
116 | Chandpur 200MW (Desh energy) | 36 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 37 | 80 | 125 | 155 | 155 | 85 | 85 | 105 |  | 197 | 200 | 200 | 200 | 120 | 120 | 85 | 2225280
117 | Ashuganj 150MW PP (Midland) | 125 | 122 | 122 | 80 | 50 | 50 | 50 | 65 | 115 | 115 | 128 | 125 | 125 | 128 | 133 | 128 | 130 | 130 |  | 130 | 130 | 128 | 130 | 132 | 135 | 135 | 2813527
118 | Bibiyana-III 400 MW CCPP | 322 | 322 | 321 | 321 | 321 | 321 | 321 | 322 | 323 | 323 | 15 | 80 | 319 | 322 | 323 | 322 | 322 | 322 |  | 322 | 322 | 322 | 322 | 322 | 322 | 323 | 7253000
| Jamalpur 115 MW PP (United) | 85 | 85 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 73 | 98 | 108 | 108 | 107 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2283600
| Anwara 300 MW PP (United) | 304 | 196 | 103 | 85 | 51 | 87 | 88 | 87 | 88 | 174 | 250 | 304 | 304 | 304 | 304 | 304 | 304 | 304 |  | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 5427164
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 70 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2314560
| Anlima Energy Ltd. | 53 | 35 |  |  |  | 13 | 17 | 17 | 17 | 35 | 59 | 105 | 108 | 108 | 108 | 108 | 108 | 108 |  | 116 | 116 | 116 | 116 | 108 | 108 | 108 | 1726254
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 14 | 23 | 24 | 35 | 15 | 31 | 28 | 20 | 9 | 1 | [9 empty] | 212581
120 | Eastern Zone Total | 6727 | 6446 | 6107 | 5892 | 5719 | 5480 | 5558 | 5765 | 6217 | 6419 | 6650 | 7094 | 7269 | 7318 | 7359 | 7205 | 7157 | 8140 |  | 8383 | 8209 | 8167 | 7917 | 7418 | 7422 | 7239 | 167932361
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 4 | 4 |  | 11 | [6 empty] | 18240
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 80 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 15 | 10 | 10 | 2119680
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 5 | 17 | 17 | 30 | 35 | 53 | 17 | 17 | 17 | 17 | 103 |  | 105 | 105 | 105 | 105 | 53 | 53 | 17 | 788169
130
131
132 | United Payra Power Ltd. | [17 empty] | 2 |  | 17 | 17 | 17 | 17 | 17 |  |  | 78000
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 207 | 225 | 184 | 180 | 180 | 151 | 151 | 151 | 151 | 222 | 222 | 212 | 220 | 222 | 222 | 218 | 223 |  | 222 | 222 | 222 | 222 | 223 | 223 | 217 | 4880180
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 421042
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1560000
140 | Bhola 33 MW PP (Venture) | 25 | 25 | 23 | 22 | 22 | 21 | 18 | 17 | 17 | 17 | 19 | 20 | 20 | 22 | 22 | 19 | 19 | 26 |  | 28 | 28 | 29 | 29 | 29 | 19 | 19 | 528362
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 711 | 713 | 712 | 713 | 714 | 714 | 713 | 714 | 714 | 714 | 714 | 710 | 710 | 709 | 709 | 709 | 709 | 709 |  | 710 | 710 | 709 | 710 | 711 | 711 | 711 | 17138181
147 | Bheramara 410 MW CCPP | 415 | 380 | 380 | 360 | 360 | 330 | 330 | 330 | 310 | 310 | 310 | 340 | 410 | 410 | 410 | 405 | 340 | 405 |  | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 9225936
148 | Payra 1320 MW | 450 | 430 | 430 | 400 | 400 | 380 | 380 | 380 | 360 | 360 | 370 | 370 | 370 | 320 | 360 | 370 | 370 | 400 |  | 510 | 520 | 520 | 520 | 520 | 510 | 470 | 10970800
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 80 | 79 | 79 | 79 | 79 | 78 | 81 | 80 | 80 | 79 | 80 | 81 | 81 | 81 | 79 | 78 |  | 78 | 78 | 79 | 78 | 80 | 79 | 78 | 1886836
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 17 |  | 43 | [6 empty] | 51312
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 5 | 5 | 0 | 0 | 0 | 3 | 1 | 0 | [9 empty] | 19560
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 109 | 92 | 88 | 89 | 92 | 95 | 97 | 99 | 94 | 123 | 130 | 96 | 107 | 80 | 97 | 118 | 117 | 122 |  | 115 | 115 | 116 | 117 | 119 | 117 | 115 | 2675900
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 160 | 163 | 163 | 163 | 165 | 169 | 171 | 175 | 193 | 196 | 197 | 152 | 172 | 159 | 167 | 180 | 178 | 179 |  | 178 | 180 | 180 | 179 | 179 | 179 | 177 | 4394873
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 314 | 285 | 302 | 293 | 335 | 301 | 336 | 302 | 337 | 407 | 362 | 346 | 339 | 337 | 363 | 390 | 303 | 402 |  | 346 | 383 | 356 | 382 | 400 | 358 | 348 | 8467345
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 22 |  | 22 | [6 empty] | 43672
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 18 | 20 | 19 | 19 | 20 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 490080
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 208836
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  | 27 | [6 empty] | 46760
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 24 | [8 empty] | 38121
167 | Katakhali 50 MW Peaking PP | [16 empty] | 5 | 34 |  | 40 | [6 empty] | 56490
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 16 |  | 43 | 43 | 43 | 43 |  |  |  | 151680
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 90 |  | 95 | 93 | 55 |  |  |  |  | 229792
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | [9 empty] | 10 | 100 | 110 | 113 | 113 | 50 | 50 | 63 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 1406400
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 50 | 100 | 113 | 113 | 113 | 50 | 50 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 1339872
173 | Rangpur 20 MW GTPP | [17 empty] | 0 |  | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [10 empty] | 10 | 35 | 39 | 34 | 34 | 34 | 34 | 92 |  | 113 | 113 | 113 | 113 | 77 | 70 | 70 | 8948544
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 3 | 2 | [9 empty] | 22797
178
178