## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-07-06 | Saturday
|  | Date (day): | 2019-07-06 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11969 | MW |  |  | (b) At Evening Peak Hour : |  | 14292 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-07-05 | 2019-07-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 124 | 124 | 124 | 124
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 375 | 340 | 350 | 350
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22
5 | Haripur GT PP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 375 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 334 | 348 | 350 | 350
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 430 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 38 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 287 | 280 | 290 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 70 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 34 | 34 | 34 |  |  | Test
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 85 | 90 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 48 | 48 | 48
21 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 110 | 140 | 140
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 32 | 39 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 55 | 56 | 56 |  | 24 | Engine problem
27 | Maona 33 MW (Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
28 | Rupganj 33 MW (Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 50 | 44 | 50
30 | Tongi 80 MW GT PP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 14 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300 |  |  | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100 |  |  | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100 |  |  | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 59 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 102 | 102 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2585 | 3094 | 3866 | 4529 | 470 | 242
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas Shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 5 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 46 | 40 | 45 |  |  | Engine problem
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 38 | 40 | 40 |  | 190 | Low water lavel
42 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 215 | 205 | 210 | 205
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 135 | 130 | 130 | 130
44 | Sikalbaha 51 MW PP(Engine) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 32 | 32 | 32 |  | 19 | Engine problem
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 84 | 0 | 84
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 0 | 68
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 80 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 90 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 24 | 42 | 33 | 35
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 97 | 80 | 100 |  |  | Engine problem
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | United Group | 300 MW | 300 | 300 | 165 | 215 | 230 | 250
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 835 | 1227 | 1167.4 | 1432 | 260 | 209
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 125 | 125 | 125
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 197 | 200 | 220
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 320 | 330 | 330
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 320 | 330 | 330
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 |  | 45 | Gas Line problem.
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 51 | 55 | 55
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 73 | 78 | 78 | 117 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 140 | 135 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 97 | 100 | 100
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 200 | 190 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 20 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 122 | 153 | 190
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 18 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1408 | 1814 | 1869 | 2201 | 380 | 61
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 96 | 151 | 152 | 150 |  | 52 | GT-1 Under maint.
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
76 | Jamalpur 95 MW PP |  | HFO | IPP | 12*8.924 | 95 | 95 | 45 | 84 | 84 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.8 | 0 | 1.6 | 0
78 | United Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 130 | 100 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 86 | 96 | 84 | 95 |  | 20 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 254.8 | 483 | 443.6 | 562 | 0 | 52
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 53 | 53 | 54 | 54
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 57 | 57 | 57 | 57
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 330 | 309 | 330 | 330
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 50 | 50
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 49 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 52 | 63 | 63 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 74 | 80 | 86
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 46 | 44 | 46
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 118 | 117 | 115 | 115
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 16 | 15 | 15
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 46 | 45 | 47
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 8 | 16 | 25
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 335 | 315 | 320
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 129 | 250 | 250 | 250
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1479 | 1613 | 1662 | 1686 | 0 | 0
97 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 32 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 931 | 942 | 942
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 99 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 10 | 40
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225 |  |  | Reserve.
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 10 | 65
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 87 | 87 | 90 | 90
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1051 | 1506 | 1296 | 1754 | 0 | 410
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 40 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 32
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 36 | 25 | 38
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 82 | 90 | 90 |  | 104 | GT-Under maint
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 201 | 307 | 250 | 365 | 0 | 104
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 0 | 33
115 | Amnura 50 MW PP |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 40 | 30 | 40 |  | 10 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 24 | 0 | 43 |  | 7 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 40
118 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 141 | 143 | 188 | 196 |  |  | FGMO
119 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 204 | 209 | 191 | 210 |  |  | FGMO
120 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 207 | 214 | 200 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 (Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  |  | Under maint.
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 41
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 12 | 14 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 8 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 24 | 52 | 45 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 24 | 86 | 50 | 95
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 108 | 108 | 108
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 706 | 1135 | 1116 | 1431 | 0 | 117
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 199 | 199
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 16
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 0 | 100 | 100
| Rangpur Area Total |  |  |  |  | 564 | 484 | 199 | 232 | 299 | 332 | 0 | 85
| Total |  |  |  |  | 18961 | 18438 | 8718.8 | 11411 | 11969 | 14292 | 1110 | 1280
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8294.7413 | 10856 | 11386.8604 | 13596.876
A. |  | 2019-07-05 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11710 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8326.3 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11411 | MW
3 | Day peak Generation : |  |  | 8718.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10856 | MW
4 | Evening peak Generation : |  |  | 11411 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 237.2782 | MKWHr | By Solar | 0.086695 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 147.46 | MKWHr |  | By Oil: | 59.1435 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.7862 | MKWHr |  | By Hydro: | 0.87462 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1110 | MW | Dhaka | 3779 | 3779 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1280 | MW | Chittagong | 1060 | 1060 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2390 | MW | Khulna | 1373 | 1373 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1312.09 | MMCFD |  |  | Rajshahi | 1170 | 1170 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 104763968.196 | ii) Oil : | Taka | 414800572.43 | Comilla | 1046 | 1046 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 18474732 | Total | Taka | 538039272.626 | Mymensingh | 905 | 905 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 6.2775 | MKWHr. | Sylhet | 513 | 513 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -590 | MW (E to W) at | 21:00 | hrs | Barisal | 317 | 317 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -640 | MW at | 1:00 | hrs | Rangpur | 693 | 693 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 10856 | 10856 |  | 0
B. |  | 2019-07-06 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14292 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 2492 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 239.1018 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8082.77 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2727 | MKWHr. | ii) HVDC Flow at Peak Time |  | 931 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6544 | MKWHr. | iii) Maximum HVDC Flow : |  | 933 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.11 |  | (b) Today: | 77.98 |  | (c) Rule Curve: |  | 84.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-07-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GT PP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Banco Energy 54MW | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW (Summit) | Rupganj 33 MW (Summit) | Gazipur 52 MW PP | Tongi 80 MW GT PP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Engine) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | United Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 124 | 0 | 190 | 300 | 12 | 0 | 330 | 355 |  | 0 | 350 | 255 | 100 | 47 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 125 | 50 | 71 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 42 | 0 | 100 | 0 | 25 | 205 | 0 | 130 | 0 |  | 33 | 49 | 51 | 50 | 97 | 46 | 15 | 37 | 125 | 0 | 0 | 310 | 92 | 217 | 152 | 100 | 0 | 56 | 0 | 38 | 0 | 0 | 52 | 8 | 11 | 33 | 0 | 130 | 101 | 93 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 308 | 56 | 77 | 46 | 109 | 16 | 46 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 149 | 0 | 100 | 198 | 143 | 296 | 87 | 102 | 35 | 0 | 215 |  | 913 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 34 | 60 | 33 | 82 | 36 | 110 | 12 | 0 | 60 | 50 | 32 | 85 | 40 | 34 | 37 | 42 | 27 | 22 | 12 | 11 | 0 | 0 | 199 | 17 | 18 | 144 | 0 | 187 | 0 | 94 | 100 | 199 | 0 | 0 | 105 | 0 | 35 | 87 | 109 |  | 8537 | 3173 | 11710 | 4240 | 913 | 1842 | 3715 | 199 | 42 | 629 | 130 | 0 | 0 | 78.13
2:00 | 70 | 124 | 0 | 190 | 300 | 13 | 0 | 326 | 305 |  | 0 | 320 | 281 | 65 | 30 | 30 | 0 | 0 | 0 | 0 | 60 | 101 | 125 | 50 | 71 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 41 | 0 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 32 | 8 | 51 | 50 | 97 | 46 | 18 | 37 | 125 | 0 | 0 | 310 | 80 | 216 | 185 | 100 | 0 | 57 | 0 | 38 | 0 | 0 | 52 | 8 | 11 | 33 | 20 | 130 | 102 | 93 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 312 | 50 | 77 | 46 | 110 | 16 | 46 | 10 | 280 | 24 | 11 | 0 | 150 | 0 | 0 | 190 | 0 | 148 | 0 | 100 | 197 | 142 | 296 | 87 | 102 | 35 | 0 | 215 |  | 925 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 34 | 60 | 33 | 82 | 34 | 110 | 12 | 0 | 60 | 50 | 32 | 85 | 40 | 34 | 37 | 42 | 0 | 22 | 12 | 11 | 0 | 0 | 199 | 17 | 18 | 147 | 0 | 182 | 0 | 95 | 99 | 189 | 0 | 0 | 105 | 0 | 53 | 87 | 109 |  | 8190 | 3162 | 11352 | 4233 | 925 | 1776 | 3487 | 199 | 41 | 561 | 130 | 0 | 0 | 78.13
3:00 | 70 | 124 | 0 | 190 | 300 | 13 | 0 | 350 | 307 |  | 0 | 350 | 287 | 65 | 30 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 45 | 0 | 71 | 0 | 6 | 53 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 40 | 0 | 100 | 0 | 25 | 217 | 0 | 135 | 0 |  | 33 | 8 | 51 | 50 | 97 | 46 | 18 | 39 | 125 | 0 | 0 | 340 | 92 | 215 | 185 | 100 | 0 | 56 | 0 | 38 | 0 | 0 | 52 | 10 | 11 | 33 | 20 | 128 | 100 | 93 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 316 | 50 | 77 | 46 | 123 | 0 | 46 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 84 | 0 | 100 | 199 | 142 | 293 | 87 | 102 | 35 | 0 | 215 |  | 924 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 34 | 55 | 32 | 82 | 31 | 110 | 0 | 0 | 60 | 50 | 32 | 85 | 12 | 34 | 35 | 42 | 0 | 22 | 12 | 8 | 0 | 0 | 199 | 17 | 18 | 144 | 0 | 199 | 0 | 95 | 70 | 193 | 0 | 0 | 105 | 0 | 72 | 86 | 109 |  | 7816 | 3082 | 10898 | 4329 | 924 | 1826 | 3022 | 199 | 40 | 430 | 128 | 0 | 0 | 78.12
4:00 | 70 | 124 | 0 | 190 | 300 | 13 | 0 | 340 | 305 |  | 0 | 350 | 280 | 65 | 30 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 45 | 0 | 71 | 0 | 6 | 53 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 39 | 0 | 100 | 0 | 25 | 206 | 0 | 130 | 0 |  | 32 | 0 | 51 | 10 | 97 | 46 | 18 | 40 | 125 | 0 | 0 | 325 | 103 | 216 | 185 | 100 | 0 | 57 | 0 | 38 | 0 | 0 | 52 | 10 | 11 | 33 | 20 | 124 | 100 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 309 | 63 | 77 | 46 | 115 | 0 | 46 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 59 | 0 | 100 | 199 | 142 | 293 | 87 | 102 | 0 | 0 | 215 |  | 925 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 46 | 32 | 82 | 31 | 110 | 0 | 0 | 60 | 50 | 32 | 85 | 12 | 34 | 34 | 42 | 0 | 22 | 12 | 8 | 0 | 0 | 199 | 17 | 18 | 145 | 0 | 195 | 0 | 95 | 0 | 202 | 0 | 0 | 105 | 0 | 35 | 87 | 109 |  | 7674 | 2972 | 10646 | 4304 | 925 | 1846 | 2798 | 199 | 39 | 411 | 124 | 0 | 0 | 78.12
5:00 | 70 | 125 | 0 | 190 | 300 | 13 | 0 | 345 | 305 |  | 0 | 350 | 250 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 45 | 0 | 71 | 0 | 6 | 53 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 37 | 0 | 100 | 0 | 25 | 204 | 0 | 131 | 0 |  | 33 | 0 | 51 | 10 | 44 | 42 | 18 | 40 | 125 | 0 | 0 | 310 | 150 | 218 | 185 | 100 | 0 | 56 | 0 | 38 | 0 | 0 | 52 | 8 | 11 | 33 | 20 | 118 | 101 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 308 | 63 | 78 | 46 | 109 | 0 | 46 | 10 | 335 | 24 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 53 | 0 | 100 | 199 | 143 | 296 | 87 | 102 | 0 | 0 | 215 |  | 924 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 46 | 32 | 82 | 30 | 80 | 0 | 0 | 60 | 50 | 0 | 85 | 12 | 34 | 0 | 42 | 0 | 22 | 12 | 8 | 0 | 0 | 199 | 0 | 0 | 145 | 0 | 195 | 0 | 94 | 0 | 200 | 0 | 0 | 105 | 0 | 35 | 86 | 109 |  | 7602 | 2835 | 10437 | 4336 | 924 | 1859 | 2654 | 199 | 37 | 310 | 118 | 0 | 0 | 78.11
6:00 | 70 | 125 | 0 | 190 | 300 | 13 | 0 | 330 | 304 |  | 0 | 350 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 6 | 53 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 8 | 0 | 37 | 0 | 100 | 0 | 25 | 217 | 0 | 110 | 0 |  | 33 | 0 | 0 | 10 | 10 | 40 | 18 | 38 | 100 | 0 | 0 | 285 | 235 | 200 | 73 | 100 | 0 | 56 | 0 | 38 | 0 | 0 | 36 | 14 | 8 | 33 | 20 | 108 | 100 | 84 | 22 | 0.1 | 53 | 57 | 50 | 46 | 100 | 322 | 63 | 77 | 46 | 124 | 0 | 46 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 10 | 140 | 100 | 250 | 87 | 102 | 0 | 0.12 | 215 |  | 924 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 28 | 41 | 0 | 82 | 24 | 16 | 0 | 0 | 60 | 0 | 0 | 40 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 0 | 0 | 199 | 0 | 0 | 146 | 0 | 189 | 0 | 97 | 0 | 200 | 0 | 0 | 105 | 0 | 35 | 17 | 109 |  | 6747.22 | 2409 | 9156.22 | 4299 | 924 | 1702 | 1778 | 199 | 37 | 109 | 108 | 0.22 | 0 | 78.11
7:00 | 70 | 124 | 0 | 190 | 300 | 14 | 0 | 342 | 306 |  | 0 | 350 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 53 | 17 | 17 | 0 | 25 | 31 | 33 | 33 | 6 | 0 | 37 | 0 | 100 | 0 | 25 | 209 | 0 | 100 | 0 |  | 32 | 0 | 0 | 10 | 12 | 40 | 18 | 37 | 100 | 0 | 0 | 270 | 264 | 190 | 73 | 100 | 0 | 56 | 0 | 38 | 0 | 0 | 8 | 14 | 8 | 33 | 0 | 98 | 100 | 84 | 22 | 0.2 | 53 | 57 | 50 | 46 | 100 | 311 | 63 | 77 | 46 | 113 | 0 | 44 | 10 | 325 | 24 | 10 | 0 | 2 | 0 | 0 | 50 | 0 | 0 | 1 | 10 | 105 | 10 | 250 | 87 | 0 | 0 | 1.5 | 215 |  | 924 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 36 | 0 | 82 | 25 | 16 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 0 | 0 | 199 | 0 | 0 | 145 | 0 | 196 | 0 | 95 | 0 | 201 | 0 | 0 | 105 | 0 | 35 | 17 | 109 |  | 6327.7 | 2383 | 8710.7 | 4249 | 924 | 1726 | 1387 | 199 | 37 | 88 | 98 | 2.7 | 0 | 78.1
8:00 | 70 | 124 | 0 | 190 | 300 | 12 | 0 | 328 | 274 |  | 0 | 330 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 53 | 55 | 17 | 0 | 25 | 31 | 28 | 33 | 25 | 0 | 37 | 0 | 100 | 0 | 25 | 205 | 0 | 100 | 0 |  | 32 | 0 | 0 | 10 | 12 | 40 | 18 | 33 | 100 | 0 | 0 | 275 | 280 | 198 | 73 | 100 | 0 | 56 | 0 | 35 | 0 | 0 | 0 | 16 | 8 | 33 | 20 | 88 | 100 | 40 | 22 | 1 | 53 | 57 | 50 | 46 | 100 | 317 | 62 | 77 | 46 | 85 | 0 | 44 | 10 | 300 | 24 | 11 | 0 | 11 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 17 | 10 | 200 | 87 | 0 | 0 | 3.3 | 163 |  | 930 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 5 | 4 | 16 | 86 | 20 | 16 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 0 | 0 | 200 | 0 | 0 | 146 | 0 | 170 | 0 | 94 | 0 | 180 | 0 | 0 | 53 | 0 | 35 | 88 | 92 |  | 6033.3 | 2293 | 8326.3 | 4163 | 930 | 1634 | 1237 | 200 | 37 | 33 | 88 | 4.3 | 0 | 78.1
9:00 | 70 | 124 | 0 | 190 | 350 | 12 | 0 | 345 | 276 |  | 0 | 330 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 53 | 55 | 17 | 22 | 25 | 24 | 28 | 33 | 45 | 0 | 40 | 0 | 100 | 0 | 25 | 204 | 0 | 100 | 0 |  | 32 | 0 | 0 | 10 | 12 | 39 | 18 | 33 | 100 | 0 | 0 | 260 | 320 | 183 | 73 | 100 | 0 | 56 | 0 | 35 | 0 | 0 | 0 | 16 | 11 | 33 | 17 | 94 | 99 | 44 | 20 | 1.6 | 52 | 57 | 50 | 46 | 100 | 311 | 63 | 76 | 46 | 74 | 0 | 44 | 10 | 325 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 1 | 10 | 17 | 10 | 200 | 87 | 80 | 0 | 0 | 108 |  | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 85 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 5 | 0 | 0 | 180 | 0 | 0 | 144 | 0 | 187 | 0 | 92 | 0 | 190 | 0 | 0 | 17 | 0 | 35 | 88 | 102 |  | 6168.6 | 2210 | 8378.6 | 4255 | 930 | 1659 | 1190 | 180 | 40 | 28 | 94 | 2.6 | 0 | 78.1
10:00 | 70 | 124 | 0 | 190 | 350 | 14 | 0 | 327 | 276 |  | 0 | 330 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 53 | 55 | 17 | 22 | 25 | 24 | 28 | 25 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 205 | 0 | 100 | 0 |  | 32 | 0 | 0 | 10 | 12 | 33 | 18 | 33 | 100 | 0 | 0 | 270 | 360 | 215 | 73 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 0 | 16 | 11 | 33 | 17 | 92 | 99 | 44 | 20 | 1.9 | 53 | 57 | 47 | 46 | 100 | 310 | 62 | 76 | 45 | 81 | 0 | 43 | 10 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 3 | 10 | 17 | 10 | 119 | 86 | 100 | 0 | 0 | 114 |  | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 85 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 5 | 0 | 0 | 170 | 0 | 0 | 144 | 0 | 186 | 0 | 90 | 0 | 195 | 0 | 0 | 17 | 0 | 35 | 87 | 1 |  | 6171.9 | 2103 | 8274.9 | 4233 | 931 | 1620 | 1156 | 170 | 40 | 28 | 92 | 4.9 | 0 | 78.09
11:00 | 70 | 124 | 0 | 190 | 350 | 14 | 0 | 348 | 335 |  | 0 | 330 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 53 | 55 | 17 | 22 | 25 | 24 | 28 | 25 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 215 | 0 | 100 | 0 |  | 32 | 0 | 0 | 10 | 12 | 36 | 18 | 16 | 100 | 0 | 0 | 305 | 360 | 202 | 73 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 0 | 16 | 11 | 33 | 17 | 98 | 97 | 45 | 20 | 2.6 | 53 | 57 | 47 | 46 | 100 | 318 | 62 | 76 | 45 | 86 | 0 | 40 | 10 | 320 | 16 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 17 | 10 | 130 | 86 | 102 | 0 | 0 | 114 |  | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 85 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 15 | 0 | 22 | 12 | 5 | 0 | 0 | 175 | 0 | 0 | 142 | 0 | 201 | 0 | 94 | 0 | 205 | 0 | 0 | 17 | 0 | 35 | 88 | 0 |  | 6331.6 | 2145 | 8476.6 | 4326 | 931 | 1693 | 1183 | 175 | 40 | 28 | 98 | 2.6 | 0 | 78.09
12:00 | 70 | 124 | 0 | 190 | 375 | 22 | 0 | 350 | 334 |  | 0 | 380 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 32 | 0 | 6 | 53 | 55 | 17 | 22 | 25 | 14 | 28 | 25 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 215 | 0 | 135 | 0 |  | 32 | 0 | 0 | 10 | 12 | 39 | 18 | 24 | 100 | 0 | 0 | 325 | 320 | 203 | 73 | 95 | 0 | 55 | 0 | 35 | 0 | 0 | 0 | 16 | 11 | 33 | 17 | 98 | 96 | 45 | 20 | 0.8 | 53 | 57 | 44 | 46 | 100 | 330 | 62 | 76 | 44 | 118 | 15 | 43 | 10 | 325 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | 10 | 17 | 10 | 129 | 86 | 102 | 0 | 0 | 165 |  | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 24 | 0 | 22 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 204 | 0 | 95 | 0 | 207 | 0 | 0 | 17 | 0 | 0 | 87 | 0 |  | 6561.8 | 2157 | 8718.8 | 4417 | 931 | 1759 | 1240 | 199 | 40 | 24 | 98 | 10.8 | 0 | 78.09
13:00 | 70 | 124 | 0 | 190 | 375 | 22 | 0 | 360 | 343 |  | 0 | 420 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 39 | 0 | 6 | 53 | 55 | 17 | 22 | 25 | 14 | 28 | 25 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 205 | 0 | 130 | 0 |  | 32 | 0 | 0 | 10 | 12 | 39 | 18 | 35 | 125 | 0 | 0 | 315 | 310 | 194 | 73 | 95 | 0 | 54 | 0 | 38 | 0 | 0 | 2 | 16 | 11 | 33 | 20 | 98 | 96 | 45 | 22 | 1.2 | 53 | 57 | 49 | 49 | 163 | 314 | 62 | 76 | 44 | 111 | 15 | 45 | 10 | 330 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 50 | 35 | 20 | 130 | 86 | 102 | 0 | 0 | 206 |  | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 28 | 0 | 22 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 140 | 0 | 206 | 0 | 95 | 0 | 210 | 0 | 0 | 35 | 0 | 0 | 87 | 0 |  | 6805.2 | 2184 | 8989.2 | 4403 | 931 | 1900 | 1373 | 199 | 40 | 24 | 98 | 21.2 | 0 | 78.08
14:00 | 70 | 124 | 0 | 190 | 375 | 22 | 0 | 342 | 340 |  | 0 | 420 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 39 | 0 | 6 | 53 | 55 | 17 | 0 | 25 | 16 | 33 | 25 | 49 | 0 | 40 | 0 | 100 | 0 | 25 | 218 | 0 | 130 | 0 |  | 32 | 0 | 0 | 10 | 12 | 38 | 18 | 29 | 125 | 0 | 0 | 342 | 350 | 207 | 73 | 95 | 0 | 53 | 0 | 10 | 0 | 0 | 25 | 16 | 11 | 33 | 20 | 100 | 96 | 45 | 22 | 1.8 | 53 | 57 | 10 | 10 | 130 | 326 | 58 | 50 | 10 | 95 | 15 | 12 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19 | 30 | 85 | 50 | 129 | 86 | 102 | 0 | 6.508 | 209 |  | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 84 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 40 | 0 | 22 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 203 | 0 | 92 | 0 | 200 | 0 | 0 | 35 | 0 | 0 | 88 | 0 |  | 6706.308 | 2181 | 8887.308 | 4439 | 931 | 1632 | 1495 | 199 | 40 | 24 | 100 | 27.308 | 0 | 0
15:00 | 70 | 124 | 0 | 190 | 375 | 22 | 0 | 365 | 343 |  | 0 | 450 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 38 | 0 | 6 | 53 | 55 | 17 | 0 | 25 | 14 | 33 | 25 | 49 | 0 | 40 | 0 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 32 | 0 | 0 | 10 | 12 | 38 | 18 | 28 | 125 | 0 | 0 | 312 | 305 | 193 | 73 | 96 | 0 | 52 | 0 | 17 | 0 | 0 | 42 | 20 | 11 | 33 | 20 | 108 | 97 | 48 | 22 | 1.7 | 52 | 57 | 46 | 44 | 163 | 308 | 58 | 75 | 45 | 115 | 16 | 45 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 2 | 30 | 125 | 61 | 129 | 86 | 102 | 0 | 1.78 | 209 |  | 930 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 2 | 16 | 85 | 25 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 33 | 0 | 21 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 139 | 0 | 205 | 0 | 95 | 0 | 209 | 0 | 0 | 70 | 0 | 0 | 87 | 0 |  | 6947.48 | 2233 | 9180.48 | 4376 | 930 | 1891 | 1589 | 199 | 40 | 42 | 108 | 5.48 | 0 | 78.08
16:00 | 70 | 124 | 0 | 190 | 320 | 22 | 0 | 328 | 303 |  | 0 | 450 | 260 | 16 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 40 | 30 | 0 | 38 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 14 | 33 | 22 | 49 | 0 | 36 | 0 | 100 | 0 | 0 | 204 | 0 | 130 | 0 |  | 32 | 0 | 0 | 10 | 11 | 38 | 18 | 22 | 125 | 0 | 0 | 310 | 305 | 182 | 73 | 98 | 0 | 52 | 0 | 40 | 0 | 0 | 52 | 20 | 11 | 33 | 20 | 104 | 97 | 84 | 22 | 1 | 52 | 57 | 49 | 48 | 130 | 314 | 59 | 74 | 46 | 112 | 16 | 46 | 9 | 310 | 24 | 11 | 0 | 14 | 0 | 0 | 32 | 0 | 0 | 7 | 30 | 198 | 127 | 130 | 86 | 85 | 0 | 1 | 212 |  | 931 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 16 | 19 | 84 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 43 | 0 | 21 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 188 | 0 | 96 | 0 | 191 | 0 | 0 | 70 | 0 | 0 | 87 | 0 |  | 7041 | 2266 | 9307 | 4262 | 931 | 1826 | 1870 | 199 | 36 | 70 | 104 | 9 | 0 | 78.07
17:00 | 70 | 124 | 0 | 190 | 300 | 22 | 0 | 327 | 276 |  | 0 | 370 | 260 | 13 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 30 | 0 | 38 | 0 | 6 | 53 | 55 | 35 | 22 | 25 | 14 | 33 | 33 | 49 | 0 | 38 | 0 | 100 | 0 | 0 | 205 | 0 | 130 | 0 |  | 32 | 0 | 0 | 10 | 11 | 38 | 18 | 38 | 125 | 0 | 0 | 310 | 295 | 182 | 73 | 97 | 0 | 54 | 0 | 40 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 104 | 98 | 84 | 22 | 0 | 52 | 57 | 50 | 48 | 130 | 310 | 40 | 40 | 46 | 109 | 15 | 45 | 0 | 290 | 24 | 11 | 0 | 14 | 0 | 0 | 32 | 0 | 0 | 1 | 30 | 197 | 140 | 130 | 86 | 103 | 0 | 1 | 215 |  | 931 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 8 | 83 | 17 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 43 | 0 | 21 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 142 | 0 | 171 | 0 | 97 | 0 | 179 | 0 | 0 | 17 | 0 | 0 | 17 | 0 |  | 6795 | 2084 | 8879 | 4186 | 931 | 1669 | 1661 | 199 | 38 | 89 | 104 | 2 | 0 | 78.07
18:00 | 70 | 124 | 0 | 190 | 280 | 22 | 0 | 327 | 273 |  | 0 | 320 | 238 | 7 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 32 | 0 | 38 | 0 | 6 | 53 | 55 | 35 | 22 | 25 | 14 | 28 | 30 | 50 | 0 | 35 | 0 | 100 | 0 | 25 | 165 | 0 | 130 | 0 |  | 32 | 0 | 0 | 10 | 11 | 46 | 18 | 41 | 125 | 0 | 0 | 250 | 280 | 182 | 73 | 98 | 0 | 25 | 0 | 40 | 0 | 0 | 25 | 18 | 11 | 33 | 20 | 90 | 120 | 70 | 22 | 0 | 52 | 57 | 13 | 10 | 100 | 301 | 50 | 20 | 20 | 72 | 15 | 13 | 10 | 280 | 8 | 11 | 0 | 14 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 160 | 142 | 129 | 86 | 102 | 0 | 0 | 215 |  | 931 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 32 | 55 | 8 | 82 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 0 | 0 | 24 | 0 | 22 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 100 | 0 | 145 | 0 | 52 | 0 | 156 | 0 | 0 | 17 | 0 | 34 | 17 | 0 |  | 6299 | 2020 | 8319 | 3925 | 931 | 1363 | 1633 | 199 | 35 | 143 | 90 | 0 | 0 | 78.06
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 124 | 0 | 190 | 250 | 22 | 0 | 340 | 281 |  | 0 | 350 | 300 | 7 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 32 | 0 | 38 | 0 | 7 | 53 | 55 | 35 | 22 | 25 | 17 | 28 | 33 | 50 | 0 | 35 | 0 | 100 | 0 | 25 | 167 | 0 | 110 | 0 |  | 32 | 67 | 65 | 10 | 22 | 46 | 18 | 42 | 125 | 0 | 0 | 335 | 300 | 211 | 73 | 98 | 0 | 25 | 0 | 40 | 0 | 0 | 28 | 19 | 11 | 33 | 18 | 122 | 151 | 68 | 22 | 0 | 53 | 57 | 14 | 15 | 100 | 321 | 61 | 20 | 20 | 123 | 16 | 45 | 10 | 300 | 8 | 11 | 0 | 14 | 0 | 0 | 45 | 0 | 7 | 0 | 80 | 144 | 140 | 130 | 96 | 102 | 16 | 0 | 215 |  | 931 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 42 | 55 | 24 | 82 | 30 | 100 | 0 | 0 | 60 | 40 | 10 | 70 | 12 | 8 | 35 | 25 | 30 | 22 | 12 | 5 | 0 | 0 | 199 | 16 | 0 | 100 | 0 | 146 | 0 | 55 | 5 | 165 | 0 | 0 | 70 | 0 | 108 | 80 | 0 |  | 6946 | 2588 | 9534 | 4155 | 931 | 1476 | 2154 | 199 | 35 | 462 | 122 | 0 | 0 | 78.06
19:30 | 70 | 124 | 0 | 190 | 320 | 22 | 0 | 360 | 324 |  | 0 | 380 | 300 | 25 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 32 | 42 | 0 | 38 | 0 | 24 | 53 | 55 | 35 | 22 | 25 | 17 | 0 | 33 | 50 | 0 | 38 | 0 | 100 | 0 | 25 | 218 | 0 | 140 | 0 |  | 32 | 83 | 68 | 10 | 70 | 46 | 18 | 42 | 125 | 0 | 0 | 346 | 300 | 203 | 73 | 98 | 0 | 52 | 0 | 40 | 0 | 0 | 52 | 19 | 11 | 33 | 18 | 112 | 153 | 74 | 22 | 0 | 53 | 57 | 35 | 44 | 130 | 323 | 58 | 76 | 40 | 123 | 16 | 46 | 10 | 340 | 8 | 11 | 0 | 14 | 0 | 0 | 65 | 0 | 24 | 0 | 90 | 200 | 140 | 130 | 96 | 103 | 17 | 0 | 215 |  | 931 | 16 | 0 | 0 | 92 | 0 | 0 | 0 | 42 | 65 | 24 | 82 | 32 | 110 | 0 | 0 | 60 | 43 | 32 | 90 | 40 | 8 | 46 | 52 | 33 | 22 | 12 | 11 | 0 | 0 | 199 | 16 | 17 | 138 | 0 | 200 | 0 | 98 | 90 | 203 | 0 | 0 | 88 | 0 | 108 | 87 | 0 |  | 7656 | 3087 | 10743 | 4438 | 931 | 1818 | 2614 | 199 | 38 | 593 | 112 | 0 | 0 | 0
20:00 | 70 | 124 | 0 | 190 | 320 | 22 | 0 | 367 | 323 |  | 0 | 400 | 300 | 23 | 15 | 15 | 14 | 0 | 0 | 0 | 0 | 64 | 75 | 0 | 39 | 0 | 43 | 53 | 55 | 50 | 22 | 25 | 17 | 33 | 33 | 50 | 0 | 38 | 0 | 100 | 0 | 25 | 218 | 0 | 138 | 0 |  | 32 | 84 | 68 | 10 | 95 | 46 | 18 | 42 | 125 | 0 | 0 | 345 | 350 | 204 | 73 | 98 | 0 | 51 | 0 | 35 | 0 | 0 | 52 | 20 | 11 | 33 | 18 | 118 | 151 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 130 | 332 | 61 | 74 | 46 | 125 | 16 | 46 | 10 | 335 | 8 | 11 | 0 | 14 | 0 | 0 | 72 | 0 | 33 | 0 | 100 | 200 | 140 | 130 | 96 | 102 | 17 | 0 | 215 |  | 931 | 32 | 0 | 0 | 99 | 0 | 0 | 0 | 41 | 55 | 32 | 82 | 34 | 110 | 12 | 0 | 60 | 43 | 32 | 90 | 40 | 8 | 47 | 52 | 36 | 22 | 12 | 11 | 0 | 0 | 199 | 16 | 17 | 140 | 0 | 203 | 0 | 95 | 91 | 207 | 0 | 0 | 90 | 0 | 108 | 87 | 0 |  | 7968 | 3134 | 11102 | 4562 | 931 | 1849 | 2757 | 199 | 38 | 648 | 118 | 0 | 0 | 78.05
21:00 | 70 | 124 | 0 | 190 | 340 | 22 | 0 | 375 | 348 |  | 0 | 430 | 280 | 38 | 15 | 15 | 34 | 0 | 0 | 0 | 0 | 85 | 110 | 0 | 39 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 38 | 0 | 100 | 0 | 25 | 205 | 0 | 130 | 0 |  | 32 | 84 | 68 | 10 | 97 | 46 | 18 | 42 | 125 | 0 | 0 | 320 | 320 | 197 | 73 | 97 | 0 | 51 | 0 | 35 | 0 | 0 | 52 | 20 | 11 | 33 | 18 | 122 | 151 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 130 | 309 | 52 | 74 | 46 | 117 | 16 | 46 | 10 | 335 | 8 | 11 | 0 | 14 | 0 | 0 | 130 | 0 | 59 | 0 | 100 | 200 | 140 | 250 | 96 | 102 | 17 | 0 | 215 |  | 931 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 55 | 40 | 82 | 36 | 80 | 12 | 0 | 60 | 43 | 31 | 86 | 40 | 24 | 44 | 52 | 36 | 22 | 12 | 11 | 0 | 0 | 199 | 16 | 17 | 143 | 0 | 209 | 0 | 97 | 100 | 214 | 0 | 0 | 105 | 0 | 108 | 87 | 0 |  | 8231 | 3180 | 11411 | 4635 | 931 | 1908 | 2903 | 199 | 38 | 675 | 122 | 0 | 0 | 78.05
22:00 | 70 | 124 | 0 | 190 | 340 | 22 | 0 | 340 | 350 |  | 0 | 430 | 280 | 50 | 15 | 15 | 34 | 0 | 0 | 0 | 0 | 101 | 112 | 0 | 39 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 32 | 84 | 51 | 10 | 97 | 46 | 18 | 42 | 125 | 0 | 0 | 320 | 320 | 195 | 73 | 100 | 0 | 53 | 0 | 35 | 0 | 0 | 52 | 20 | 11 | 33 | 18 | 122 | 151 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 163 | 308 | 29 | 76 | 46 | 118 | 16 | 46 | 10 | 325 | 16 | 7 | 0 | 14 | 0 | 0 | 142 | 0 | 104 | 0 | 100 | 198 | 140 | 249 | 96 | 102 | 17 | 0 | 215 |  | 930 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 45 | 40 | 82 | 36 | 96 | 12 | 0 | 60 | 43 | 31 | 86 | 40 | 43 | 40 | 52 | 35 | 22 | 9 | 11 | 0 | 0 | 195 | 17 | 17 | 144 | 0 | 220 | 0 | 97 | 100 | 218 | 0 | 0 | 105 | 0 | 108 | 87 | 0 |  | 8275 | 3209 | 11484 | 4596 | 930 | 1934 | 3021 | 195 | 40 | 646 | 122 | 0 | 0 | 78.04
23:00 | 70 | 124 | 0 | 190 | 340 | 22 | 0 | 331 | 351 |  | 0 | 430 | 280 | 50 | 25 | 15 | 34 | 0 | 0 | 0 | 0 | 101 | 112 | 0 | 39 | 0 | 15 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 206 | 0 | 130 | 0 |  | 33 | 84 | 51 | 10 | 97 | 46 | 18 | 42 | 125 | 0 | 0 | 310 | 315 | 190 | 73 | 100 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 20 | 11 | 33 | 20 | 118 | 152 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 163 | 310 | 29 | 76 | 46 | 110 | 16 | 46 | 10 | 325 | 16 | 11 | 0 | 14 | 0 | 0 | 163 | 0 | 100 | 0 | 100 | 199 | 142 | 249 | 86 | 102 | 19 | 0 | 215 |  | 933 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 33 | 40 | 82 | 38 | 96 | 12 | 0 | 60 | 43 | 31 | 86 | 40 | 43 | 37 | 51 | 35 | 22 | 9 | 11 | 0 | 0 | 195 | 17 | 17 | 145 | 0 | 215 | 0 | 97 | 100 | 218 | 0 | 0 | 105 | 0 | 108 | 86 | 0 |  | 8238 | 3193 | 11431 | 4567 | 933 | 1938 | 3009 | 195 | 40 | 631 | 118 | 0 | 0 | 78.04
24:00 | 70 | 124 | 0 | 190 | 300 | 22 | 0 | 332 | 304 |  | 0 | 430 | 280 | 50 | 40 | 15 | 34 | 0 | 0 | 0 | 0 | 101 | 112 | 0 | 39 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 204 | 0 | 130 | 0 |  | 32 | 84 | 34 | 10 | 85 | 46 | 18 | 42 | 125 | 0 | 0 | 305 | 315 | 187 | 73 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 118 | 151 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 130 | 312 | 29 | 76 | 46 | 112 | 16 | 46 | 10 | 310 | 16 | 11 | 0 | 14 | 0 | 0 | 180 | 0 | 100 | 0 | 100 | 198 | 142 | 249 | 87 | 103 | 33 | 0 | 214 |  | 933 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 9 | 40 | 82 | 34 | 99 | 12 | 0 | 60 | 43 | 31 | 86 | 40 | 43 | 37 | 45 | 35 | 22 | 12 | 11 | 0 | 0 | 200 | 17 | 18 | 145 | 0 | 215 | 0 | 98 | 99 | 218 | 0 | 0 | 105 | 0 | 108 | 86 | 0 |  | 8106 | 3155 | 11261 | 4522 | 933 | 1844 | 3029 | 200 | 40 | 575 | 118 | 0 | 0 | 78.04
KWH | 1610000 | 3150000 | 0 | 4473000 | 7955818 | 422363 | 0 | 8335360 | 7486000 |  | 0 | 8919375 | 6735069 | 718080 | 319536 | 255260 | 136327 | 0 | 0 | 0 | 177600 | 1039104 | 1121280 | 109360 | 889930 | 0 | 287088 | 1306440 | 1253203 | 857445 | 399060 | 600000 | 568620 | 733500 | 727300 | 1018716 | 0 | 874620 | 0 | 2400000 | 0 | 539177 | 4876877 | 0 | 2982432 | 0 |  | 785280 | 555984 | 579644 | 410520 | 1134720 | 1007040 | 418560 | 894000 | 2817510 | 0 | 0 | 7690100 | 6356500 | 4829000 | 2241454 | 2300590 | 0 | 1275360 | 0 | 832693 | 0 | 0 | 796574 | 371484 | 243900 | 812800 | 420150 | 2654400 | 2659920 | 1712640 | 482076 | 13900 | 1240000 | 1336200 | 1051200 | 1062144 | 3206241 | 7256000 | 1298400 | 1674240 | 991440 | 2642610 | 235920 | 986060 | 246780 | 7690500 | 454512 | 249936 | 0 | 822980 | 0 | 0 | 2145600 | 0 | 918720 | 55755 | 1343040 | 3366240 | 2298330 | 4814000 | 2089200 | 2179200 | 242544 | 17040 | 4769782 |  | 22272727 | 168300 | 0 | 0 | 1344000 | 0 | 0 | 0 | 486720 | 726144 | 466125 | 2014507 | 640035 | 1138560 | 83508 | 0 | 1400000 | 481112 | 293116 | 1216276 | 525820 | 321095 | 364450 | 747840 | 232145 | 509520 | 266256 | 161478 | 0 | 0 | 4786200 | 151000 | 160000 | 3495500 | 0 | 4827682 | 0 | 2220680 | 824640 | 4980318 | 0 | 85727 | 1679040 | 0 | 1093632 | 1826496 | 1028160 |  | 174259353 | 63018809 | 237278162 | 104757947 | 22272727 | 42702068 | 52523826 | 4786200 | 874620 | 6619679 | 2654400 | 86695 | 0
Fuel Cost | 1384600 | 2709000 | 0 | 3846780 | 5091723.52 | 342114.03 | 0 | 5084569.6 | 4566460 |  | 0 | 5975981.25 | 102305698.11 | 4509542.4 | 2134500.48 | 1559638.6 | 88612.55 | 0 | 0 | 0 | 1110000 | 6847695.36 | 10842777.6 | 696623.2 | 5330680.7 | 0 | 1914876.96 | 9314917.2 | 7832518.75 | 5376180.15 | 299295 | 450000 | 0 | 0 | 0 | 9637053.36 | 0 | 0 | 0 | 2640000 | 0 | 5106006.19 | 3218738.82 | 0 | 3429796.8 | 0 |  | 6902611.2 | 5987947.68 | 5639936.12 | 2541118.8 | 7330291.2 | 6586041.6 | 355776 | 0 | 2563934.1 | 0 | 0 | 4767862 | 4385985 | 3380300 | 1546603.26 | 2208566.4 | 0 | 1096809.6 | 0 | 682808.26 | 0 | 0 | 5910579.08 | 286042.68 | 182925 | 625856 | 315112.5 | 18156096 | 1994940 | 15739161.6 | 371198.52 | 0 | 1289600 | 1389648 | 1009152 | 955929.6 | 2500867.98 | 5079200 | 1480176 | 1791436.8 | 1090584 | 3012575.4 | 301977.6 | 917035.8 | 229505.4 | 4921920 | 340884 | 189951.36 | 0 | 5974834.8 | 0 | 0 | 15341040 | 0 | 0 | 0 | 0 | 31440681.6 | 21466402.2 | 4188180 | 0 | 0 | 0 | 0 | 0 |  | 113590907.7 | 4905945 | 0 | 0 | 11141760 | 0 | 0 | 0 | 5480467.2 | 8553976.32 | 3673065 | 1390009.83 | 633634.65 | 8425344 | 2812549.44 | 0 | 1470000 | 5508732.4 | 3142203.52 | 10897832.96 | 4548343 | 2857745.5 | 3881392.5 | 7418572.8 | 2732346.65 | 560472 | 250280.64 | 122238.846 | 0 | 0 | 18474732 | 4866730 | 4283200 | 2376940 | 0 | 3379377.4 | 0 | 0 | 14291011.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 418116465.77 | 251669810.556 | 669786276.326 | 75692372.926 | 113590907.7 | 29071595.27 | 335264535.04 | 18474732 | 0 | 79536037.39 | 18156096 | 0 | 0
Yesterday Day Peak | 70 | 124 | 0 | 190 | 375 | 22 | 0 | 350 | 334 |  | 0 | 380 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 32 | 0 | 6 | 53 | 55 | 17 | 22 | 25 | 14 | 28 | 25 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 215 | 0 | 135 | 0 |  | 32 | 0 | 0 | 10 | 12 | 39 | 18 | 24 | 100 | 0 | 0 | 325 | 320 | 203 | 73 | 95 | 0 | 55 | 0 | 35 | 0 | 0 | 0 | 16 | 11 | 33 | 17 | 98 | 96 | 45 | 20 | 0.8 | 53 | 57 | 44 | 46 | 100 | 330 | 62 | 76 | 44 | 118 | 15 | 43 | 10 | 325 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | 10 | 17 | 10 | 129 | 86 | 102 | 0 | 0 | 165 |  | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 0 | 0 | 24 | 0 | 22 | 12 | 5 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 204 | 0 | 95 | 0 | 207 | 0 | 0 | 17 | 0 | 0 | 87 | 0 |  | 8718.8 | DayPeak
Yesterday Evening Peak | 70 | 124 | 0 | 190 | 340 | 22 | 0 | 375 | 348 | 0 | 0 | 430 | 280 | 38 | 15 | 15 | 34 | 0 | 0 | 0 | 0 | 85 | 110 | 0 | 39 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 38 | 0 | 100 | 0 | 25 | 205 | 0 | 130 | 0 | 0 | 32 | 84 | 68 | 10 | 97 | 46 | 18 | 42 | 125 | 0 | 0 | 320 | 320 | 197 | 73 | 97 | 0 | 51 | 0 | 35 | 0 | 0 | 52 | 20 | 11 | 33 | 18 | 122 | 151 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 130 | 309 | 52 | 74 | 46 | 117 | 16 | 46 | 10 | 335 | 8 | 11 | 0 | 14 | 0 | 0 | 130 | 0 | 59 | 0 | 100 | 200 | 140 | 250 | 96 | 102 | 17 | 0 | 215 |  | 931 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 55 | 40 | 82 | 36 | 80 | 12 | 0 | 60 | 43 | 31 | 86 | 40 | 24 | 44 | 52 | 36 | 22 | 12 | 11 | 0 | 0 | 199 | 16 | 17 | 143 | 0 | 209 | 0 | 97 | 100 | 214 | 0 | 0 | 105 | 0 | 108 | 87 | 0 |  | 11411 | EvPeak
Forecast for Evening | 70 | 124 | 0 | 190 | 350 | 22 | 0 | 412 | 350 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 34 | 0 | 0 | 0 | 100 | 102 | 140 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 0 | 25 | 205 | 0 | 130 | 0 | 0 | 32 | 84 | 68 | 100 | 100 | 45 | 18 | 35 | 125 | 0 | 0 | 330 | 330 | 220 | 78 | 100 | 0 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 190 | 150 | 95 | 22 | 0 | 54 | 57 | 50 | 44 | 163 | 330 | 63 | 86 | 46 | 115 | 15 | 47 | 10 | 320 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 250 | 95 | 100 | 100 | 0 | 250 |  | 942 | 32 | 0 | 0 | 115 | 225 | 0 | 0 | 40 | 65 | 40 | 90 | 38 | 110 | 32 | 0 | 60 | 50 | 33 | 95 | 40 | 43 | 40 | 52 | 41 | 22 | 15 | 11 | 0 | 0 | 199 | 16 | 17 | 196 | 0 | 210 | 0 | 95 | 100 | 215 | 0 | 0 | 105 | 0 | 108 | 90 | 100
Forecast for Day | 70 | 124 | 0 | 190 | 350 | 22 | 0 | 412 | 350 | 0 | 0 | 450 | 290 | 100 | 100 | 55 | 34 | 0 | 0 | 0 | 100 | 90 | 140 | 70 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 44 | 0 | 40 | 0 | 100 | 0 | 25 | 210 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 80 | 80 | 40 | 18 | 33 | 125 | 0 | 0 | 330 | 330 | 200 | 78 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 153 | 152 | 84 | 22 | 1.6 | 54 | 57 | 50 | 44 | 163 | 330 | 63 | 80 | 44 | 115 | 15 | 45 | 10 | 315 | 16 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 5 | 90 | 190 | 135 | 250 | 84 | 100 | 50 | 4.4 | 230 |  | 942 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 10 | 10 | 40 | 90 | 25 | 40 | 0 | 0 | 60 | 0 | 0 | 50 | 30 | 0 | 0 | 45 | 0 | 22 | 14 | 8 | 0 | 0 | 199 | 0 | 0 | 188 | 0 | 191 | 0 | 95 | 0 | 200 | 0 | 0 | 105 | 0 | 108 | 90 | 100
Generation at 08:00(Today) | 70 | 124 | 0 | 190 | 250 | 22 | 0 | 331 | 273 | 0 | 0 | 340 | 290 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 39 | 0 | 6 | 53.97 | 36.5 | 0 | 0 | 25 | 31 | 33 | 33 | 25 | 0 | 38 | 0 | 100 | 0 | 0 | 212 | 0 | 100 | 0 | 0 | 32 | 0 | 0 | 10 | 12 | 30 | 18 | 12 | 100 | 0 | 0 | 270 | 275 | 173 | 16 | 0 | 0 | 53 | 0 | 35 | 0 | 0 | 8 | 21 | 8 | 33 | 12 | 90 | 151 | 8 | 22 | 0.6 | 53 | 57 | 50 | 46 | 100 | 321 | 29 | 77 | 44 | 97 | 16 | 44 | 10 | 300 | 16.3 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 90 | 10 | 201 | 87 | 103 | 0 | 0.4 | 70 | 0 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 82 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 30 | 12 | 8 | 0 | 0 | 0 | 22 | 9 | 8 | 0 | 0 | 199 | 0 | 0 | 147 | 0 | 161 | 0 | 96 | 0 | 167 | 0 | 0 | 17 | 0 | 90 | 87 | 0 | 0
199
| Minimum Generation |  | 8326.3 | 8:00
| Highest Generation |  | 11710 | 1:00
| Day Peak Generation |  | 8718.8 | 12:00
| Evening Peak Generation |  | 11411 | 21:00
| HVDC Max Flow |  | 933 | 23:00
| HVDC EvPeak Flow |  | 931 | 21:00
| Load factor L.F |  | 84.43%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-07-06
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-07-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8718.8 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8082.77 | MW
Evening Peak Generation : |  | 11411 | MW Hour : | 21:00 | Available Max Generation : |  | 14292 | MW
E.P. Demand (at gen end) : |  | 11411 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 11710 | MW Hour : | 1:00 | Reserve(Generation end) |  | 2492 | MW
Total Gen. (MKWH) : |  | 237.2782 | System Load Factor : | 84.43% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -640 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-07-06
Actual : | 77.98 | Ft.(MSL) , | Rule curve : | 84.8 | Ft.( MSL )
Gas Consumed : | Total = | 1312.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104763968.196
|  | Coal : | 18474732 | Oil : | 414800572.43 | Total : | 538039272.626
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4177.0792 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1422.0993 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1274.4499 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1151.6781 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1040.6969 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 839.8097 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 467.4425 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 216.1718 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 647.7132 |  |  | 0 | 0%
Total | 0 |  | 11237.1406 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 & 2. | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-4
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Sirajganj # 04
4) Bheramara 410 MW.
5) Siddhirganj ST
6) Ashuganj #4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mymenshing 132/33 kV T-2 & 33 kV Bus of T2 transformer were under shut down from 06:11 to 08:10 for C/M. |  |  |  |  | About 25 MW power interruption occurred under Mymenshing S/S
and were switched on at 10:34. |  |  |  |  | areas from 06:11 to 08:10.
b) Mymenshing 132/33 kV T-1 transformer was under shut down from 08:41 to 10:24 for C/M. |  |  |  |  | About 40 MW power interruption occurred under Mymenshing S/S
areas from 08:41 to 10:24.
c) Sikalbaha 230 kV Bus-2 was under shut down from 11:39 to 14:42 for D/W.
d) Nator 132/33 kV T1 transformer was shut down at 08:42 for D/W.
e) Saidpur-Joldhaka 132 kV Ckt-2 was under shut down from 10:15 to 18:10 for D/W.
f) Julda 132/33 kV T1 transformer was under shut down from 10:10 to 11:14 due to oil; leakage from radiator.
g) Shyampur 230/132 kV T1 transformer was under shut down from 11:13 to 17:02 due to project work.
h) Nator 33 kV Main Bus was under shut down from 09:31 to 09:52 for Changing loop of T1 bay. |  |  |  |  | About 35 MW power interruption occurred under Nator S/S
areas from 09:31 to 09:52.
i) Chandpur 150 MW CCPP GT tripped at 07:20(06/07/2019) due to GBC tripped and was synchronized
at 09:04(06/07/2019).
j) Patenga 50 MW RPP tripped at 06:47(06/07/2019) showing O/C relay and 33 kV feeder fault .
k) Hasnabad-Lalbagh 132 kV Ckt was shut down at 06:53(06/07/2019) for project work.
l) Hasnabad-Kamrangirchar 132 kV Ckt was shut down at 06:53(06/07/2019) for project work.
m) Narshingdi 132/33 kV T2 transformer was shut down at 07:05(06/07/2019) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-07-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1610000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 124 | 3150000 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4473000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 7955818 | Frequency control.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 422363 | Gas shortage
5 | Haripur GT PP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 375 | 8335360 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 7486000 | Frequency control.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 430 | 8919375 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 38 | 718080 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6735069 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 319536 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 255260 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 109360 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 399060
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 177600 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 34 | 136327 | Gas shortage
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 85 | 1039104
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 287088
21 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 53 | 1306440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 110 | 1121280 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1253203
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 857445
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 39 | 889930 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1168620 | Engine problem
27 | Maona 33 MW (Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 733500
28 | Rupganj 33 MW (Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 727300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 50 | 1018716
30 | Tongi 80 MW GT PP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 14 | 822980 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 59 | 918720 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 102 | 2179200
| Dhaka area Total |  |  |  | 5693 | 3094 | 65525734
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 539177
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 55755
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 1007040
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 38 | 874620 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 205 | 4876877 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2982432 | FGMO
44 | Sikalbaha 51 MW PP(Engine) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 32 | 785280 | Engine problem
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 242544 | Transformer overload.
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 84 | 555984
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 579644
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 410520 | Line overload
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1343040
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 418560
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 894000
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1134720
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 17040
53 | Anwara 300 MW PP (United) |  | United Group | 300 MW | 300 | 215 | 4769782 | Transformer overload.
| Chattogram area Total |  |  |  | 2053 | 1227 | 23887015
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 125 | 2817510
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 197 | 4829000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7690100 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 6356500 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Under maint.
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1275360
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 2241454 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 832693 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 2298330 | Engine problem
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 97 | 2300590 | ST under shut down.
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3366240
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 371484 | Engine problem
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243900
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 2654400 | Load restricted from India.
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 812800
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 796574
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 420150 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1814 | 39307085
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 151 | 2659920 | GT-1 under maint.
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 482076
76 | Jamalpur 95 MW PP |  | IPP | 12*8.924 | 95 | 84 | 1712640
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13900
78 | United Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 130 | 2145600 | Low demand
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 96 | 2089200 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 483 | 9103336
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 53 | 1240000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1336200
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3206241 | Frequency control.
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 309 | 7256000
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1051200
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1062144
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 249936
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 1298400
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1674240
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 46 | 991440
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 117 | 2642610 | FGMO
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 235920 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 46 | 986060
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 454512
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 335 | 7690500 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 250 | 4814000 | Frequency control.
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246780
| Sylhet Area Total |  |  |  | 1834 | 1613 | 36436183
97 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 32 | 168300
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 931 | 22272727
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1344000
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 486720
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 55 | 726144 | Machine problem
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 466125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 824640
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1679040
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 87 | 1826496 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1506 | 29794192
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 1138560
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 12 | 83508 | Engine problem
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 36 | 640035
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 82 | 2014507 | GT-1 under maint.
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 2220680
| Barisal Area Total |  |  |  | 462 | 307 | 6097290
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1400000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 481112
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 31 | 293116
115 | Amnura 50 MW PP |  | QRPP | 7*7.79 | 50 | 40 | 525820 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 24 | 321095 | Low demand
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 364450
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 143 | 3495500 | ST under maint.
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 209 | 4827682
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 214 | 4980318
121 | Sirajgonj 400 MW CCPP Unit-4 (Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 85727 | Under maint.
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 232145
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 509520
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 12 | 266256
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 161478
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 747840
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 1216276
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 108 | 1093632
| Rajshahi Area Total |  |  |  | 2070 | 1135 | 21001967
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4786200
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 151000
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 160000
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 0 | 1028160 | On test
| Rangpur Area Total |  |  |  | 484 | 232 | 6125360
| Total |  |  |  | 18438 | 11411 | 237278162
| Eastern Grid Total |  |  |  | 13108 | 8231 | 174259353
| Western Grid Total |  |  |  | 5330 | 3180 | 63018809
| National Grid Total |  |  |  | 18438 | 11411 | 237278162
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-07-05
| (a) ENTIRE EASTERN GRID : |  | 7303 | MW | (b) ENTIRE WESTERN GRID : |  | 3553 | MW
| i) Dhaka area |  | 3779 | MW | i) Khulna area |  | 1373 | MW
| ii) Chittagong area |  | 1060 | MW | ii) Rajshahi area |  | 1170 | MW
| iii) Comilla area |  | 1046 | MW | iii) Barisal area |  | 317 | MW
| iv) Mymensingh area |  | 905 | MW | iv) Rangpur area |  | 693 | MW
| v) Sylhet area |  | 513 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10856 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 110 | 100 | Jamalpur | 126 | 100 | Jessore | 107 | 2000
2 | Munsiganj | 136 | 2200 | Sherpur | 96 | 100 | Jhenida | 105 | 2100
3 | Sonargaon | 70 | 2000 | Srimongal | 38 | 2200 | Bottail | 116 | 2100
4 | Shyampur | 196 | 200 | Shahjibazar | 117 | 2100 | G.K Project | 57 | 100
5 | Bhulta | 186 | 100 | Fenchuganj | 57 | 2100 | Faridpur | 166 | 100
6 | Madanganj | 62 | 2100 | Kulawara | 44 | 1930 | Madaripur | 114 | 2200
7 | Shitalakhya | 100 | 100 | Sylhet | 142 | 2300 | Gopalganj | 86 | 2200
8 | Rahim steel | 9 | 1000 | Chatak | 34 | 2100 | Bagerhat | 81 | 2100
9 | Matuail | 92 | 100 | Sunamganj | 40 | 2000 | Mongla | 36 | 100
10 | Ghorasal | 86 | 2100 | Biani Bazar | 50 | 2100 | Satkhira | 100 | 100
11 | Narsingdi | 138 | 100 | Comilla (S) | 122 | 1900 | Gallamari | 46 | 100
12 | Haripur (SBU) | 95 | 200 | Comilla(N) | 157 | 2200 | Magura | 50 | 2000
13 | Ullon | 86 | 2000 | Chandpur | 99 | 2100 | Chuadanga | 83 | 100
14 | Hasnabad | 198 | 100 | Feni | 122 | 2100 | Barisal | 96 | 2300
15 | Magbazar | 114 | 1600 | Chowmuhani | 164 | 2000 | Patuakhali | 102 | 2200
16 | Maniknagar | 80 | 2100 | Ashuganj | 52 | 2300 | Bhandaria | 58 | 2000
17 | Bangabhaban | 16 | 2000 | Daudkandi | 118 | 2200 | Barisal (N) | 39 | 2100
18 | Narinda | 88 | 2300 | B.Baria | 146 | 2000 | Sariatpur | 35 | 2100
19 | Dhanmondi | 105 | 1900 | Ramganj | 92 | 2100 | Benapol | 40 | 2100
20 | Lalbag | 78 | 200 | Madunaghat | 57 | 100 | Borhan Uddin | 35 | 100
21 | Madartek | 55 | 2300 | Hathazari | 95 | 2100 | Ishurdi | 59 | 100
22 | Mirpur | 99 | 1930 | Khulshi | 186 | 2300 | Ruppur Paromanobik | 2 | 100
23 | Kalyanpur | 108 | 1900 | Halishahar | 124 | 2000 | Natore | 121 | 100
24 | Gulshan | 126 | 1500 | Baraulia | 168 | 100 | Bogra | 233 | 100
25 | Uttara | 81 | 1930 | Sikalbaha | 34 | 2000 | Noagaon | 122 | 100
26 | Uttara New | 14 | 1900 | Dohazari | 82 | 1900 | Rajshahi | 163 | 2200
27 | Kamrangirchar | 55 | 1930 | Cox'sbazar | 87 | 2000 | C.Nawabganj | 76 | 2100
28 | Savar | 117 | 1500 | Chandraghona | 28 | 2000 | Amnura | 36 | 2000
29 | Bhasantec | 144 | 1930 | Kaptai | 4 | 1930 | Pabna | 108 | 2100
30 | Agargaon | 52 | 1930 | A. Khaer Stl. | 5 | 1930 | Shahjadpur | 94 | 2100
31 | Satmosjid | 103 | 1930 | Bakulia | 89 | 2200 | Serajganj | 98 | 2000
32 | Tongi | 130 | 1100 | Julda | 16 | 100 | Niyamatpur | 63 | 2100
33 | Kabirpur | 171 | 100 | TK chemical | 3.2 | 1300 | Joypurhat | 45 | 100
34 | Basundhara | 118 | 2100 | Modern Steel | 14 | 300 | Mohastangor | 16 | 100
35 | Manikganj | 92 | 2100 | Shahmirpur | 31 | 100 | Rangpur | 137 | 200
36 | Joydevpur | 203 | 100 | Khagrachhari | 19 | 2100 | Lalmonirhat | 89 | 100
37 | New Tongi | 104 | 2300 | Matarbari | 25 | 2200 | Saidpur | 102 | 2300
38 | Korda | 210 | 100 | Baroiar Hat | 38 | 2100 | Purbasadipur | 99 | 2100
39 | Dhamrai | 56 | 2200 | Rangamati | 12 | 1900 | Thakurgaon | 73 | 100
40 | Valuka | 104 | 200 | Abul Khair 230 | 154 | 100 | Palashbari | 115 | 100
41 | Tangail | 188 | 2100 | BSRM | 145 | 100 | Barapukuria | 51 | 100
42 | Mymensing | 234 | 2100 | Goalpara | 24 | 2300 | Panchagar | 44 | 1930
43 | Kishorganj | 130 | 2100 | Central (S) | 90 | 2000 | Joldhaka | 18 | 2000
44 | Netrokona | 99 | 2100 | Noapara | 90 | 2000
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-07-05
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 391 | 18:00 | 384 | 12:00 | Kaliakoir | 373 | 18:00 | 360
2 | Bheramara | 393 | 6:00 | 385 | 1:00 | Bhulta | 388 | 1:00 | 380
3 | Ashuganj(N) | 392 | 18:00 | 385 | 11:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
1 | Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 223 | 18:00 | 218
2 | Ishurdi | 236 | 19:00 | 224 | 21:00 | Megnaghat | 224 | 8:00 | 220
3 | Ashuganj | 236 | 18:00 | 232 | 7:00 | Fenchuganj | 236 | 17:00 | 231
4 | Serajganj | 230 | 18:00 | 220 | 21:00 | Siddhirganj | 224 | 1:00 | 220
5 | Baghabari | 230 | 17:00 | 220 | 21:00 | Maniknagar | 222 | 1:00 | 218
6 | Barapukuria | 232 | 7:00 | 217 | 21:00 | Old Airport | 222 | 1:00 | 215
7 | Bogra | 224 | 19:00 | 205 | 21:00 | Barisal | 232 | 2:00 | 221
8 | Khulna South | 233 | 5:00 | 211 | 12:00 | AKSML | 220 | 18:00 | 213
9 | Rampura | 222 | 1:00 | 220 | 10:00 | BSRM | 223 | 18:30 | 216
10 | Haripur | 220 | 1:00 | 220 | 1:00 | Bibiyana | 232 | 16:00 | 228
11 | Hasnabad | 221 | 3:00 | 218 | 11:00 | Bhulta | 226 | 1:00 | 220
12 | Aminbazar | 224 | 1:00 | 212 | 10:00 | Ashuganj (S) | 237 | 18:00 | 231
13 | Tongi | 225 | 1:00 | 214 | 13:00 | Kaliakoir | 228 | 1:00 | 220
14 | Comilla (N) | 232 | 18:00 | 226 | 8:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 132 | 100 | 129 | 1200 | Hathazari | 132 | 100 | 130
2 | Munsiganj | 133 | 1830 | 129 | 1100 | Khulshi | 130 | 400 | 126
3 | Megnaghat | 131 | 100 | 128 | 900 | Halishahar | 134 | 300 | 130
4 | Shyampur | 136 | 1800 | 130 | 1300 | Baraulia | 136 | 2000 | 127
5 | Bhulta | 125 | 900 | 120 | 2100 | Sikalbaha | 135 | 100 | 130
6 | Madanganj | 1236 | 100 | 126 | 1200 | Dohazari | 133 | 1930 | 130
7 | Shitalakhya | 140 | 100 | 131 | 600 | Cox'sbazar | 128 | 2300 | 123
8 | Rahim steal | 132 | 1800 | 130 | 1200 | Chandraghona | 133 | 1930 | 129
9 | Matuail | 132 | 1800 | 128 | 1200 | Kaptai | 132 | 1900 | 130
10 | Ghorasal | 136 | 1900 | 135 | 100 | A. Khaer Stl. | 130 | 400 | 126
11 | Narsinghdi | 130 | 1100 | 124 | 2100 | Bakulia | 133 | 1930 | 129
12 | Haripur (SBU) | 132 | 100 | 130 | 900 | Julda | 133 | 100 | 130
13 | Ullon | 135 | 400 | 132 | 1200 | TK Chemical | 135 | 2300 | 131
14 | Hasnabad | 135 | 1800 | 132 | 1200 | Modern Steel | 134 | 1930 | 130
15 | Magbazar | 136 | 400 | 132 | 1200 | Shahmirpur | 134 | 200 | 130
16 | Maniknagar | 135 | 1800 | 132 | 1100 | Khagrachhari | 132 | 300 | 129
17 | Bangabhaban | 135 | 1800 | 132 | 1100 | Matarbari | 130 | 1100 | 125
18 | Narinda | 135 | 1800 | 132 | 1100 | Baroiar Hat | 129 | 1500 | 127
19 | Dhanmondi | 135 | 400 | 132 | 1200 | Rangamati | 132 | 1800 | 129
20 | Lalbag | 134 | 100 | 125 | 1200 | Goalpara | 138 | 300 | 124
21 | Madartek | 135 | 400 | 132 | 1200 | Central s/s | 137 | 200 | 124
22 | Mirpur | 135 | 200 | 126 | 1200 | Noapara | 134 | 1600 | 120
23 | Kalyanpur | 137 | 100 | 129 | 1200 | Jessore | 131 | 1800 | 118
24 | Gulshan | 135 | 100 | 131 | 1200 | Jhenida | 131 | 1800 | 115
25 | Uttara | 134 | 100 | 125 | 1100 | Bottail | 135 | 1700 | 122
26 | Uttara New | 135 | 100 | 128 | 1200 | G.K.Project | 140 | 1700 | 133
27 | Kamrangirchar | 135 | 100 | 123 | 1200 | Faridpur | 134 | 1800 | 121
28 | Savar | 134 | 200 | 127 | 1100 | Madaripur | 134 | 300 | 124
29 | Bhasantec | 138 | 100 | 132 | 1200 | Gopalganj | 139 | 500 | 131
30 | Agargaon | 138 | 100 | 133 | 1500 | Bagerhat | 136 | 300 | 120
31 | Satmosjid | 138 | 100 | 133 | 1100 | Mongla | 132 | 600 | 120
32 | Tongi | 137 | 100 | 130 | 1200 | Satkhira | 136 | 1500 | 122
33 | Kabirpur | 135 | 1800 | 128 | 2100 | Gallamari | 138 | 200 | 125
34 | Basundhara | 132 | 1800 | 127 | 1400 | Magura | 130 | 1600 | 114
35 | Manikganj | 137 | 2100 | 132 | 1500 | Chuadanga | 127 | 1800 | 110
36 | Joydevpur | 138 | 300 | 131 | 1600 | Barisal | 137 | 500 | 127
37 | New Tongi | 137 | 100 | 128 | 800 | Patuakhali | 134 | 300 | 125
38 | Kodda | 141 | 100 | 126 | 1500 | Bhandaria | 135 | 1800 | 125
39 | Dhamrai | 134 | 1800 | 127 | 2100 | Barisal (N) | 137 | 200 | 130
40 | Valuka | 132 | 1800 | 116 | 2100 | Sariatpur | 131 | 400 | 121
41 | Tangail | 135 | 1800 | 125 | 2100 | Benapol | 132 | 1800 | 118
42 | Mymensing | 133 | 1800 | 118 | 2100 | Ishurdi | 138 | 1800 | 129
43 | Kishorganj | 134 | 1800 | 122 | 2100 | Ruppur Paromanobik | 138 | 1500 | 128
44 | Netrokona | 135 | 1800 | 119 | 2100 | Natore | 134 | 1830 | 123
45 | Jamalpur | 139 | 1800 | 126 | 1300 | Bogra | 135 | 1900 | 121
46 | Sherpur | 135 | 1800 | 124 | 1400 | Noagaon | 129 | 1900 | 113
47 | Srimongal | 137 | 1700 | 132 | 2400 | Rajshahi | 129 | 100 | 122
48 | Shahjibazar | 135 | 600 | 130 | 2200 | C.Nawabganj | 129 | 1900 | 118
49 | Fenchuganj | 135 | 500 | 132 | 200 | Amnura | 130 | 1800 | 120
50 | Khulawara | 134 | 700 | 131 | 2000 | Pabna | 136 | 1800 | 127
51 | Sylhet | 135 | 700 | 131 | 2000 | Shahjadpur | 140 | 1800 | 130
52 | Chatak | 134 | 600 | 130 | 100 | Serajganj | 134 | 1830 | 125
53 | Sunamganj | 133 | 600 | 128 | 1900 | Niyamatpur | 128 | 1830 | 110
54 | Biani Bazar | 133 | 600 | 128 | 2100 | Joypurhat | 130 | 1830 | 111
55 | Comilla(s) | 127 | 700 | 120 | 1900 | Mohastangor | 132 | 1830 | 116
56 | Comilla(n) | 135 | 900 | 132 | 700 | Rangpur | 128 | 700 | 107
57 | Chandpur | 135 | 1800 | 128 | 1300 | Lalmonirhat | 123 | 800 | 102
58 | Feni | 130 | 1800 | 123 | 1100 | Saidpur | 127 | 700 | 106
59 | Chowmuhani | 127 | 1830 | 120 | 900 | Purbasadipur | 128 | 1800 | 108
60 | Ashuganj | 137 | 1800 | 132 | 2300 | Thakurgaon | 124 | 700 | 100
61 | Daudkandi | 131 | 1800 | 126 | 1100 | Palashbari | 130 | 700 | 110
62 | B.Baria | 134 | 1700 | 126 | 2200 | Barapukuria | 132 | 700 | 117

## L-Curve
Date | 2019-07-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 530 | 8106 | 3155 | 11261 |  |  |  | QF-LDC-12
0:30 | 585 | 8321.5 | 3164 | 11485.5 | Date: | 2019-07-05
1:00 | 640 | 8537 | 3173 | 11710
1:30 | 640 | 8363.5 | 3167.5 | 11531
2:00 | 640 | 8190 | 3162 | 11352
2:30 | 625 | 8003 | 3122 | 11125 | [5 empty] | Gen. at Eve. Peak | 11411 | 11411 MW (21:00 )
3:00 | 610 | 7816 | 3082 | 10898 | [6 empty] | 21:00
3:30 | 605 | 7745 | 3027 | 10772 | [5 empty] | Gen. at Day Peak | 8718.8 | 8718.8 MW (12:00 )
4:00 | 600 | 7674 | 2972 | 10646 | [6 empty] | 12:00
4:30 | 580 | 7638 | 2903.5 | 10541.5 | [5 empty] | Highest Generation | 11710
5:00 | 560 | 7602 | 2835 | 10437 | [6 empty] | 1:00
5:30 | 480 | 7174.61 | 2622 | 9796.61
6:00 | 400 | 6747.22 | 2409 | 9156.22
6:30 | 365 | 6537.46 | 2396 | 8933.46
7:00 | 330 | 6327.7 | 2383 | 8710.7
7:30 | 250 | 6180.5 | 2338 | 8518.5
8:00 | 170 | 6033.3 | 2293 | 8326.3
8:30 | 165 | 6100.95 | 2251.5 | 8352.45
9:00 | 160 | 6168.6 | 2210 | 8378.6
9:30 | 165 | 6170.25 | 2156.5 | 8326.75
10:00 | 170 | 6171.9 | 2103 | 8274.9
10:30 | 210 | 6251.75 | 2124 | 8375.75
11:00 | 250 | 6331.6 | 2145 | 8476.6
11:30 | 290 | 6446.7 | 2151 | 8597.7
12:00 | 330 | 6561.8 | 2157 | 8718.8
12:30 | 375 | 6683.5 | 2170.5 | 8854
13:00 | 420 | 6805.2 | 2184 | 8989.2
13:30 | 440 | 6755.754 | 2182.5 | 8938.254
14:00 | 460 | 6706.308 | 2181 | 8887.308
14:30 | 455 | 6826.894 | 2207 | 9033.894
15:00 | 450 | 6947.48 | 2233 | 9180.48
15:30 | 445 | 6994.24 | 2249.5 | 9243.74
16:00 | 440 | 7041 | 2266 | 9307
16:30 | 450 | 6918 | 2175 | 9093
17:00 | 460 | 6795 | 2084 | 8879
17:30 | 420 | 6547 | 2052 | 8599
18:00 | 380 | 6299 | 2020 | 8319
18:30 | 310 | 6622.5 | 2304 | 8926.5
19:00 | 240 | 6946 | 2588 | 9534
19:30 | 470 | 7656 | 3087 | 10743
20:00 | 620 | 7968 | 3134 | 11102 |  |  |  | Executive Engineer
20:30 | 605 | 8099.5 | 3157 | 11256.5 |  |  |  | Network Operation Division
21:00 | 590 | 8231 | 3180 | 11411
21:30 | 585 | 8253 | 3194.5 | 11447.5
22:00 | 580 | 8275 | 3209 | 11484 |  |  |  |  | Page 6 of 7
22:30 | 600 | 8256.5 | 3201 | 11457.5
23:00 | 620 | 8238 | 3193 | 11431
23:30 | 575 | 8172 | 3174 | 11346
24:00 | 530 | 8106 | 3155 | 11261
11411 MW (21:00 )
8718.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-07-05 |  | Energy | 237278162
[10 empty] | 2019-07-05 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4522 | 933 | 1844 | 3029 | 200 | 40 | 575 | 0 | 118
0:30 | 4381 | 923 | 1843 | 3372 | 199.5 | 41 | 602 | 0 | 124 | Date: | 2019-07-05
1:00 | 4240 | 913 | 1842 | 3715 | 199 | 42 | 629 | 0 | 130
1:30 | 4236.5 | 919 | 1809 | 3601 | 199 | 41.5 | 595 | 0 | 130 | [7 empty] | Total Energy | 237.2782 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 4233 | 925 | 1776 | 3487 | 199 | 41 | 561 | 0 | 130 | [7 empty] | Energy not Served | 0
2:30 | 4281 | 924.5 | 1801 | 3254.5 | 199 | 40.5 | 495.5 | 0 | 129 | [7 empty] | Energy Requirement | 237.2782
3:00 | 4329 | 924 | 1826 | 3022 | 199 | 40 | 430 | 0 | 128
3:30 | 4316.5 | 924.5 | 1836 | 2910 | 199 | 39.5 | 420.5 | 0 | 126 | [6 empty] | Shortage
4:00 | 4304 | 925 | 1846 | 2798 | 199 | 39 | 411 | 0 | 124
4:30 | 4320 | 924.5 | 1852.5 | 2726 | 199 | 38 | 360.5 | 0 | 121
5:00 | 4336 | 924 | 1859 | 2654 | 199 | 37 | 310 | 0 | 118
5:30 | 4317.5 | 924 | 1780.5 | 2216 | 199 | 37 | 209.5 | 0 | 113
6:00 | 4299 | 924 | 1702 | 1778 | 199 | 37 | 109 | 0 | 108
6:30 | 4274 | 924 | 1714 | 1582.5 | 199 | 37 | 98.5 | 0 | 103 |  |  |  |  | Coal
7:00 | 4249 | 924 | 1726 | 1387 | 199 | 37 | 88 | 0 | 98
7:30 | 4206 | 927 | 1680 | 1312 | 199.5 | 37 | 60.5 | 0 | 93 |  |  |  | Oil |  |  |  | ,
8:00 | 4163 | 930 | 1634 | 1237 | 200 | 37 | 33 | 0 | 88
8:30 | 4209 | 930 | 1646.5 | 1213.5 | 190 | 38.5 | 30.5 | 0 | 91
9:00 | 4255 | 930 | 1659 | 1190 | 180 | 40 | 28 | 0 | 94
9:30 | 4244 | 930.5 | 1639.5 | 1173 | 175 | 40 | 28 | 0 | 93
10:00 | 4233 | 931 | 1620 | 1156 | 170 | 40 | 28 | 0 | 92
10:30 | 4279.5 | 931 | 1656.5 | 1169.5 | 172.5 | 40 | 28 | 0 | 95
11:00 | 4326 | 931 | 1693 | 1183 | 175 | 40 | 28 | 0 | 98
11:30 | 4371.5 | 931 | 1726 | 1211.5 | 187 | 40 | 26 | 0 | 98
12:00 | 4417 | 931 | 1759 | 1240 | 199 | 40 | 24 | 0 | 98
12:30 | 4410 | 931 | 1829.5 | 1306.5 | 199 | 40 | 24 | 0 | 98
13:00 | 4403 | 931 | 1900 | 1373 | 199 | 40 | 24 | 0 | 98
13:30 | 4403 | 931 | 1900 | 1373 | 199 | 40 | 24 | 0 | 98
14:00 | 4403 | 931 | 1900 | 1373 | 199 | 40 | 24 | 0 | 98
14:30 | 4389.5 | 930.5 | 1895.5 | 1481 | 199 | 40 | 33 | 0 | 103
15:00 | 4376 | 930 | 1891 | 1589 | 199 | 40 | 42 | 0 | 108
15:30 | 4319 | 930.5 | 1858.5 | 1729.5 | 199 | 38 | 56 | 0 | 106
16:00 | 4262 | 931 | 1826 | 1870 | 199 | 36 | 70 | 0 | 104
16:30 | 4224 | 931 | 1747.5 | 1765.5 | 199 | 37 | 79.5 | 0 | 104
17:00 | 4186 | 931 | 1669 | 1661 | 199 | 38 | 89 | 0 | 104
17:30 | 4055.5 | 931 | 1516 | 1647 | 199 | 36.5 | 116 | 0 | 97
18:00 | 3925 | 931 | 1363 | 1633 | 199 | 35 | 143 | 0 | 90
18:30 | 4040 | 931 | 1419.5 | 1893.5 | 199 | 35 | 302.5 | 0 | 106
19:00 | 4155 | 931 | 1476 | 2154 | 199 | 35 | 462 | 0 | 122
19:30 | 4438 | 931 | 1818 | 2614 | 199 | 38 | 593 | 0 | 112
20:00 | 4562 | 931 | 1849 | 2757 | 199 | 38 | 648 | 0 | 118
20:30 | 4598.5 | 931 | 1878.5 | 2830 | 199 | 38 | 661.5 | 0 | 120
21:00 | 4635 | 931 | 1908 | 2903 | 199 | 38 | 675 | 0 | 122
21:30 | 4615.5 | 930.5 | 1921 | 2962 | 197 | 39 | 660.5 | 0 | 122
22:00 | 4596 | 930 | 1934 | 3021 | 195 | 40 | 646 | 0 | 122
22:30 | 4581.5 | 931.5 | 1936 | 3015 | 195 | 40 | 638.5 | 0 | 120
23:00 | 4567 | 933 | 1938 | 3009 | 195 | 40 | 631 | 0 | 118
23:30 | 4544.5 | 933 | 1891 | 3019 | 197.5 | 40 | 603 | 0 | 118 | Max Temp. in Dhaka |  | 34.5° C
24:00 | 4522 | 933 | 1844 | 3029 | 200 | 40 | 575 | 0 | 118
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-07-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 41 | 40 | 39 | 37 | 37 | 37 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 36 | 38 | 35 |  | 35 | 38 | 38 | 38 | 40 | 40 | 40 | 874620
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 539177
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 0 | 1 | 3 | 0 | 10 | 20 | 19 | 2 | 7 | 1 | 0 | [8 empty] | 55755
6 | Sikalbaha 225MW CCPP (Gas) | 205 | 204 | 217 | 206 | 204 | 217 | 209 | 205 | 204 | 205 | 215 | 215 | 205 | 218 | 205 | 204 | 205 | 165 |  | 167 | 218 | 218 | 205 | 204 | 206 | 204 | 4876877
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 135 | 130 | 131 | 110 | 100 | 100 | 100 | 100 | 100 | 135 | 130 | 130 | 130 | 130 | 130 | 130 |  | 110 | 140 | 138 | 130 | 130 | 130 | 130 | 2982432
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 0 | [11 empty] | 0 |  | 65 | 68 | 68 | 68 | 51 | 51 | 34 | 579644
12 | Hathazari 100 MW peaking PP | 49 | 8 | 8 | 0 | [13 empty] | 0 |  | 67 | 83 | 84 | 84 | 84 | 84 | 84 | 555984
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 35 | 35 | 35 | 0 | [15 empty] | 16 | 17 | 17 | 17 | 17 | 19 | 33 | 242544
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [20 empty] | 0 | 14 | 34 | 34 | 34 | 34 | 136327
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 150 | 0 |  |  | 0 | 2 | 11 | 15 | 15 | 15 | 0 | 0 |  | 0 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 822980
19 | Ashuganj 195MW PP (APSCL-United) | 152 | 185 | 185 | 185 | 185 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 2241454
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1610000
21 | Ghorasal Repowered CCPP Unit-3 | 124 | 124 | 124 | 124 | 125 | 125 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 |  | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 3150000
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4473000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 350 | 350 | 375 | 375 | 375 | 375 | 320 | 300 | 280 |  | 250 | 320 | 320 | 340 | 340 | 340 | 300 | 7955818
26
28 | Ashuganj TPP Unit- 3 | 125 | 125 | 125 | 125 | 125 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2817510
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 217 | 216 | 215 | 216 | 218 | 200 | 190 | 198 | 183 | 215 | 202 | 203 | 194 | 207 | 193 | 182 | 182 | 182 |  | 211 | 203 | 204 | 197 | 195 | 190 | 187 | 4829000
34 | Ashuganj 450 MW CCPP(South) | 92 | 80 | 92 | 103 | 150 | 235 | 264 | 280 | 320 | 360 | 360 | 320 | 310 | 350 | 305 | 305 | 295 | 280 |  | 300 | 300 | 350 | 320 | 320 | 315 | 315 | 6356500
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 340 | 325 | 310 | 285 | 270 | 275 | 260 | 270 | 305 | 325 | 315 | 342 | 312 | 310 | 310 | 250 |  | 335 | 346 | 345 | 320 | 320 | 310 | 305 | 7690100
35 | Ashuganj 55 MW PP (Precision) | 56 | 57 | 56 | 57 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 54 | 53 | 52 | 52 | 54 | 25 |  | 25 | 52 | 51 | 51 | 53 | 54 | 55 | 1275360
36 | Chandpur 150 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 | 96 | 98 | 97 | 98 |  | 98 | 98 | 98 | 97 | 100 | 100 | 100 | 2300590
37 | Tongi 80 MW GT PP
38 | Haripur GT PP
39 | Haripur 412 MW CCPP | 330 | 326 | 350 | 340 | 345 | 330 | 342 | 328 | 345 | 327 | 348 | 350 | 360 | 342 | 365 | 328 | 327 | 327 |  | 340 | 360 | 367 | 375 | 340 | 331 | 332 | 8335360
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 320 | 350 | 350 | 350 | 350 | 350 | 330 | 330 | 330 | 330 | 380 | 420 | 420 | 450 | 450 | 370 | 320 |  | 350 | 380 | 400 | 430 | 430 | 430 | 430 | 8919375
41 | Haripur 360MW CCPP(HPL) | 355 | 305 | 307 | 305 | 305 | 304 | 306 | 274 | 276 | 276 | 335 | 334 | 343 | 340 | 343 | 303 | 276 | 273 |  | 281 | 324 | 323 | 348 | 350 | 351 | 304 | 7486000
42 | RPCL 210MW CCPP | 101 | 102 | 100 | 100 | 101 | 100 | 100 | 100 | 99 | 99 | 97 | 96 | 96 | 96 | 97 | 97 | 98 | 120 |  | 151 | 153 | 151 | 151 | 151 | 152 | 151 | 2659920
43
44 | Fenchugonj CCPP Phase-1 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 53 | 53 | 53 | 53 | 53 | 52 | 52 | 52 | 52 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1240000
45 | Fenchugonj CCPP Phase-2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1336200
46 | Shajibazar 330 MW CCPP | 308 | 312 | 316 | 309 | 308 | 322 | 311 | 317 | 311 | 310 | 318 | 330 | 314 | 326 | 308 | 314 | 310 | 301 |  | 321 | 323 | 332 | 309 | 308 | 310 | 312 | 7256000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 50 | 50 | 63 | 63 | 63 | 63 | 62 | 63 | 62 | 62 | 62 | 62 | 58 | 58 | 59 | 40 | 50 |  | 61 | 58 | 61 | 52 | 29 | 29 | 29 | 1298400
48 | Shahjibazar 86MW PP (Shahjibazar) | 77 | 77 | 77 | 77 | 78 | 77 | 77 | 77 | 76 | 76 | 76 | 76 | 76 | 50 | 75 | 74 | 40 | 20 |  | 20 | 76 | 74 | 74 | 76 | 76 | 76 | 1674240
49 | Shahjibazar 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 44 | 44 | 10 | 45 | 46 | 46 | 20 |  | 20 | 40 | 46 | 46 | 46 | 46 | 46 | 991440
50 | Sylhet 150 MW CCPP | 109 | 110 | 123 | 115 | 109 | 124 | 113 | 85 | 74 | 81 | 86 | 118 | 111 | 95 | 115 | 112 | 109 | 72 |  | 123 | 123 | 125 | 117 | 118 | 110 | 112 | 2642610
51 | Sylhet 20 MW GTPP | 16 | 16 | 0 | [8 empty] | 15 | 15 | 15 | 16 | 16 | 15 | 15 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 235920
52 | Sylhet 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 43 | 40 | 43 | 45 | 12 | 45 | 46 | 45 | 13 |  | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 986060
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 0 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246780
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 0 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 7 | 11 | 11 | 249936
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 44 | 49 | 10 | 46 | 49 | 50 | 13 |  | 14 | 35 | 50 | 50 | 50 | 50 | 50 | 1051200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 8 |  | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 454512
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 280 | 300 | 320 | 335 | 300 | 325 | 300 | 325 | 290 | 320 | 325 | 330 | 305 | 325 | 310 | 290 | 280 |  | 300 | 340 | 335 | 335 | 325 | 325 | 310 | 7690500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 35 | 35 |  | 35 | 35 | 50 | 55 | 55 | 55 | 55 | 857445
59 | Sikalbaha 51 MW PP(Engine) | 33 | 32 | 33 | 32 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 33 | 32 | 785280
60 | Barabkunda 22 MW PP (Regent) | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418560
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 399060
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 482076
63 | Impoprt (Tripura) | 130 | 130 | 128 | 124 | 118 | 108 | 98 | 88 | 94 | 92 | 98 | 98 | 98 | 100 | 108 | 104 | 104 | 90 |  | 122 | 112 | 118 | 122 | 122 | 118 | 118 | 2654400
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 39 | 40 | 40 | 38 | 37 | 33 | 33 | 33 | 16 | 24 | 35 | 29 | 28 | 22 | 38 | 41 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 894000
65 | Feni 22MW PP (Doreen) | 8 | 8 | 10 | 10 | 8 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 19 | 18 |  | 19 | 19 | 20 | 20 | 20 | 20 | 21 | 371484
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243900
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 812800
68 | Cumilla 25 MW PP (Summit) | 0 | 20 | 20 | 20 | 20 | 20 | 0 | 20 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 420150
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 24 | 24 | 24 | 14 | 14 | 16 | 14 | 14 | 14 | 14 |  | 17 | 17 | 17 | 30 | 30 | 31 | 31 | 568620
71 | Maona 33 MW (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 28 |  | 28 | 0 | 33 | 33 | 33 | 33 | 33 | 733500
72 | Rupganj 33 MW (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 33 | 30 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 727300
73 | Ghorashal 108MW PP (Regent) | 12 | 13 | 13 | 13 | 13 | 13 | 14 | 12 | 12 | 14 | 14 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 422363
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 60 | 8 | 7 | [22 empty] | 177600
78 | Gazipur 52 MW PP | 42 | 42 | 25 | 25 | 25 | 8 | 6 | 25 | 45 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 49 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1018716
79 | Kodda 150MW PP | 125 | 125 | 45 | 45 | 45 | 0 | [8 empty] | 16 | 30 | 30 | 32 |  | 32 | 42 | 75 | 110 | 112 | 112 | 112 | 1121280
80 | Jamalpur 95 MW PP | 93 | 93 | 93 | 84 | 84 | 84 | 84 | 40 | 44 | 44 | 45 | 45 | 45 | 45 | 48 | 84 | 84 | 70 |  | 68 | 74 | 84 | 84 | 84 | 84 | 84 | 1712640
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 36 | 8 | 0 |  |  |  | 0 | 2 | 25 | 42 | 52 | 25 | 25 |  | 28 | 52 | 52 | 52 | 52 | 52 | 52 | 796574
| Gazipur 100 MW PP | 102 | 102 | 102 | 102 | 102 | 102 | 0 | 0 | 80 | 100 | 102 | 102 | 102 | 102 | 102 | 85 | 103 | 102 |  | 102 | 103 | 102 | 102 | 102 | 102 | 103 | 2179200
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0.12 | 1.5 | 3.3 | 0 |  |  |  |  | 6.508 | 1.78 | 1 | 1 | 0 |  | 0 | [6 empty] | 17040
82 | Madanganj 102 PP(Summit) | 47 | 30 | 30 | 30 | 15 | 0 | [10 empty] | 0 | 1 |  | 14 | 15 | 15 | 15 | 15 | 25 | 40 | 319536
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 50 | 50 | 0 | [23 empty] | 109360
86 | Meghnaghat CCPP(Summit) | 255 | 281 | 287 | 280 | 250 | 285 | 272 | 285 | 264 | 284 | 290 | 287 | 280 | 305 | 287 | 260 | 260 | 238 |  | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 6735069
87 | Meghnaghat 100 MW(IEL) | 100 | 65 | 65 | 65 | 65 | 16 | 0 | [8 empty] | 16 | 13 | 7 |  | 7 | 25 | 23 | 38 | 50 | 50 | 50 | 718080
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 410520
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 49 | 10 | 44 | 48 | 48 | 10 |  | 15 | 44 | 49 | 49 | 49 | 49 | 49 | 1062144
93 | Ashuganj 51 MW PP (Midland) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 35 | 35 | 35 | 35 | 35 | 38 | 10 | 17 | 40 | 40 | 40 |  | 40 | 40 | 35 | 35 | 35 | 35 | 35 | 832693
94 | Gagnagar 102 MW PP (Digital Power) | 101 | 101 | 50 | 50 | 50 | 0 |  |  | 0 | 24 | 24 | 24 | 24 | 24 | 50 | 40 | 7 | 7 |  | 7 | 32 | 64 | 85 | 101 | 101 | 101 | 1039104
95 | Patenga 50MW PP (Baraka) | 46 | 46 | 46 | 46 | 42 | 40 | 40 | 40 | 39 | 33 | 36 | 39 | 39 | 38 | 38 | 38 | 38 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1007040
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 97 | 44 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 |  | 22 | 70 | 95 | 97 | 97 | 97 | 85 | 1134720
97 | Katpotti 52 MW PP (Sinha) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 7 | 24 | 43 | 48 | 47 | 15 | 6 | 287088
98 | Bosila 108MW PP(CLC) | 71 | 71 | 71 | 71 | 71 | 47 | 0 |  |  |  | 0 | 32 | 39 | 39 | 38 | 38 | 38 | 38 |  | 38 | 38 | 39 | 39 | 39 | 39 | 39 | 889930
99 | Madanganj-55 MW PP(Summit) | 55 | 30 | 0 | [11 empty] | 0 | 7 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 255260
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1253203
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 130 | 163 | 130 | 130 | 100 |  | 100 | 130 | 130 | 130 | 163 | 163 | 130 | 3206241
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0.1 | 0.2 | 1 | 1.6 | 1.9 | 2.6 | 0.8 | 1.2 | 1.8 | 1.7 | 1 | 0 | 0 | [8 empty] | 13900
103 | Banco Energy 54MW | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 54 | 53 | 53 | 1306440
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | United Mymensingh 200 MW PP (United) | 190 | 190 | 190 | 190 | 190 | 100 | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 12 | 32 | 32 | 32 |  | 45 | 65 | 72 | 130 | 142 | 163 | 180 | 2145600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 148 | 84 | 59 | 53 | 0 | [11 empty] | 0 |  | 7 | 24 | 33 | 59 | 104 | 100 | 100 | 918720
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 30 | 30 | 30 | 30 | 30 |  | 80 | 90 | 100 | 100 | 100 | 100 | 100 | 1343040
116 | Chandpur 200MW (Desh energy) | 198 | 197 | 199 | 199 | 199 | 140 | 105 | 17 | 17 | 17 | 17 | 17 | 35 | 85 | 125 | 198 | 197 | 160 |  | 144 | 200 | 200 | 200 | 198 | 199 | 198 | 3366240
117 | Ashuganj 150MW PP (Midland) | 143 | 142 | 142 | 142 | 143 | 100 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 50 | 61 | 127 | 140 | 142 |  | 140 | 140 | 140 | 140 | 140 | 142 | 142 | 2298330
118 | Bibiyana-III 400 MW CCPP | 296 | 296 | 293 | 293 | 296 | 250 | 250 | 200 | 200 | 119 | 130 | 129 | 130 | 129 | 129 | 130 | 130 | 129 |  | 130 | 130 | 130 | 250 | 249 | 249 | 249 | 4814000
| Jamalpur 115 MW PP (United) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 96 | 96 | 96 | 96 | 96 | 86 | 87 | 2089200
| Anwara 300 MW PP (United) | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 163 | 108 | 114 | 114 | 165 | 206 | 209 | 209 | 212 | 215 | 215 |  | 215 | 215 | 215 | 215 | 215 | 215 | 214 | 4769782
120 | Eastern Zone Total | 8537 | 8190 | 7816 | 7674 | 7602 | 6747.22 | 6327.7 | 6033.3 | 6168.6 | 6171.9 | 6331.6 | 6561.8 | 6805.2 | 6706.308 | 6947.48 | 7041 | 6795 | 6299 |  | 6946 | 7656 | 7968 | 8231 | 8275 | 8238 | 8106 | 174259353
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 43 | 32 | 20 | 0 | [5 empty] | 9 | 49 | 16 | 16 |  | 51 | 92 | 99 | 115 | 115 | 115 | 115 | 1344000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 34 | 34 | 34 | 33 | 33 | 28 | 28 | 5 | 0 | [7 empty] | 0 | 32 |  | 42 | 42 | 41 | 41 | 41 | 41 | 41 | 486720
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 53 | 17 | 17 | 17 | 17 | 35 | 35 | 70 | 70 | 17 | 17 |  | 70 | 88 | 90 | 105 | 105 | 105 | 105 | 1679040
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 80 | 16 | 16 | 16 | 0 | [8 empty] | 0 |  | 100 | 110 | 110 | 80 | 96 | 96 | 99 | 1138560
136 | Barisal GT PP Unit-1& 2 | 12 | 12 | 0 | [18 empty] | 12 | 12 | 12 | 12 | 12 | 83508
137 | Bhola 95 MW PP (Aggreko) | 94 | 95 | 95 | 95 | 94 | 97 | 95 | 94 | 92 | 90 | 94 | 95 | 95 | 92 | 95 | 96 | 97 | 52 |  | 55 | 98 | 95 | 97 | 97 | 97 | 98 | 2220680
| Bhola 225 MW CCPP | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 86 | 85 | 85 | 85 | 87 | 87 | 84 | 85 | 84 | 83 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 2014507
140 | Bhola 33 MW PP (Venture) | 36 | 34 | 31 | 31 | 30 | 24 | 25 | 20 | 21 | 23 | 23 | 19 | 20 | 22 | 25 | 23 | 17 | 17 |  | 30 | 32 | 34 | 36 | 36 | 38 | 34 | 640035
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 99 | 70 | 0 | [15 empty] | 5 | 90 | 91 | 100 | 100 | 100 | 99 | 824640
142 | Noapara 40 MW PP (Khanjahan Ali) | 33 | 33 | 32 | 32 | 32 | 0 |  | 16 | 0 |  |  | 16 | 16 | 16 | 16 | 19 | 8 | 8 |  | 24 | 24 | 32 | 40 | 40 | 40 | 40 | 466125
143 | Gopalganj 100 MW Peaking PP | 60 | 60 | 55 | 46 | 46 | 41 | 36 | 4 | 4 | 4 | 4 | 0 |  |  | 2 | 16 | 35 | 55 |  | 55 | 65 | 55 | 55 | 45 | 33 | 9 | 726144
144 | Bheramara GT-1,2,3 | 32 | 32 | 0 | [16 empty] | 0 | 16 | 32 | 32 | 32 | 32 | 16 | 168300
145 | Madhumati 100 MW PP | 87 | 87 | 86 | 87 | 86 | 17 | 17 | 88 | 88 | 87 | 88 | 87 | 87 | 88 | 87 | 87 | 17 | 17 |  | 80 | 87 | 87 | 87 | 87 | 86 | 86 | 1826496
146 | Bheramara HVDC | 913 | 925 | 924 | 925 | 924 | 924 | 924 | 930 | 930 | 931 | 931 | 931 | 931 | 931 | 930 | 931 | 931 | 931 |  | 931 | 931 | 931 | 931 | 930 | 933 | 933 | 22272727
147 | Bheramara 360 MW CCPP
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 180 | 170 | 175 | 199 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 195 | 195 | 200 | 4786200
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1400000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | 0 | [13 empty] | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 481112
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 144 | 147 | 144 | 145 | 145 | 146 | 145 | 146 | 144 | 144 | 142 | 141 | 140 | 141 | 139 | 141 | 142 | 100 |  | 100 | 138 | 140 | 143 | 144 | 145 | 145 | 3495500
158 | Sirajgonj 225MW CCPP Unit-1(Oil) | [21 empty] | 0
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 187 | 182 | 199 | 195 | 195 | 189 | 196 | 170 | 187 | 186 | 201 | 204 | 206 | 203 | 205 | 188 | 171 | 145 |  | 146 | 200 | 203 | 209 | 220 | 215 | 215 | 4827682
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 199 | 189 | 193 | 202 | 200 | 200 | 201 | 180 | 190 | 195 | 205 | 207 | 210 | 200 | 209 | 191 | 179 | 156 |  | 165 | 203 | 207 | 214 | 218 | 218 | 218 | 4980318
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 (Gas) | [26 empty] | 85727
161 | Bera 70 MW Peaking PP | 32 | 32 | 32 | 32 | 0 | [14 empty] | 10 | 32 | 32 | 31 | 31 | 31 | 31 | 293116
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509520
163 | Bogura 20 MW PP (Energyprima) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 9 | 9 | 12 | 266256
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 161478
165 | Amnura 50 MW PP | 40 | 40 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 40 | 40 | 40 | 40 | 40 | 40 | 525820
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 0 | [13 empty] | 8 | 8 | 8 | 24 | 43 | 43 | 43 | 321095
167 | Katakhali 50 MW Peaking PP | 37 | 37 | 35 | 34 | 0 | [14 empty] | 35 | 46 | 47 | 44 | 40 | 37 | 37 | 364450
168 | Santahar 50 MW Peaking PP | 27 | 0 | [15 empty] | 0 |  | 30 | 33 | 36 | 36 | 35 | 35 | 35 | 232145
169 | Natore 52 MW PP (Rajlanka) | 42 | 42 | 42 | 42 | 42 | 0 |  |  |  |  | 15 | 24 | 28 | 40 | 33 | 43 | 43 | 24 |  | 25 | 52 | 52 | 52 | 52 | 51 | 45 | 747840
170 | Chapainawabganj 100 MW Peaking PP | 85 | 85 | 85 | 85 | 85 | 40 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 70 | 90 | 90 | 86 | 86 | 86 | 86 | 1216276
171 | Baghabari 200 MW PP (Paramount) | [21 empty] | 0
172 | Bagura 113 MW PP (Confidence) | 35 | 53 | 72 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 |  |  |  |  | 0 | 34 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 1093632
173 | Rangpur 20 MW GTPP | 17 | 17 | 17 | 17 | 0 | [14 empty] | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 151000
175 | Saidpur 20 MW GTPP | 18 | 18 | 18 | 18 | 0 | [14 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 18 | 160000
176 | Rangpur 113 MW PP (Confidence) | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 92 | 102 | 1 | 0 | [15 empty] | 1028160
177
178
178 | Western Zone Total | 3173 | 3162 | 3082 | 2972 | 2835 | 2409 | 2383 | 2293 | 2210 | 2103 | 2145 | 2157 | 2184 | 2181 | 2233 | 2266 | 2084 | 2020 |  | 2588 | 3087 | 3134 | 3180 | 3209 | 3193 | 3155 | 63018809