## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-24 | Sunday
|  |  | Date (day): | 2021-10-24 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13577.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14773 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-23 | 2021-10-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180 | 10 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 358 | 401 | 350 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 302 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 260 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 24 | 23 | 50 | 50 |  | 50 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 21 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 316 | 250 | 335 | 0
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 300 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 80 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 60 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 108 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2065 | 3034 | 3493 | 3940 | 450 | 1120
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 47 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 161 | 160 | 165 | 165 | 65 |  | Unit 2 & 5 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 51 | 100
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 76 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 10 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 65 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 157 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 108 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 90 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 673 | 1327 | 1481 | 1553 | 130 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 135 | 135 | 135 | 0 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 141 | 143 | 145 | 145 |  | 75 | ST under maint
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 335 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 19 | 29 | 30 | 30 |  | 15 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 78 | 78 | 78 | 117 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 125 | 130 | 130 |  | 20 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 138 | 138 | 138 |  | 25 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 139 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 7 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 142 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 20 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 21 | 18 | 18 |  | 7 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 62 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 58 | 96 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1193 | 1617 | 1815 | 2073 | 380 | 552
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 186 | 185 | 200 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 120 | 190 | 190 |  |  | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 55 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 9 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 300 | 451 | 608.6 | 557 | 0 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 110 | 110 | 110 | 110 |  | 220 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 41 | 41 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 60 | 65
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 78 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 275 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 322 | 323 | 321 | 321 | 79 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1765 | 1707 | 1817 | 1822 | 142 | 395
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 714 | 715 | 727 | 727
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 33 |  | 21 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 410 | 400 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 86 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1154 | 1331 | 1507 | 1730 | 0 | 90
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 27 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 67 | 67 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 23 | 23 | 42 | 42 | 53 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 430 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 222 | 223 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 651 | 770 | 1092 | 1242 | 53 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 198 | 166 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 170 | 220 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 422 | 308 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 90 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 110 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 100 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 827 | 1033 | 1576 | 1676 | 310 | 81
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 82 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 107 | 100 | 100 |  | 13 | Engine problem
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 82 | 187 | 188 | 180 | 0 | 412
|  | Total |  |  |  |  | 22031 | 20934 | 8710 | 11457 | 13577.6 | 14773 | 1465 | 3464
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8429.4737 | 11088 | 13140.301 | 14297.2003
| A. |  | 2021-10-23 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 11457 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7677 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11457 | MW
| 3 | Day peak Generation : |  |  | 8710 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11088 | MW
| 4 | Evening peak Generation : |  |  | 11457 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 217.085 | MKWHr | By Solar | 0.52853 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 143.0395 | MKWHr |  | By Oil: | 37.8907 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 11.6264 | MKWHr |  | By Hydro: | 3.8105 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1465 | MW | Dhaka | 4143 | 4143 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3464 | MW | Chittagong | 1281 | 1281 |  | 0 |  | 18:00 |  | 146
|  |  |  | Total = |  |  | 4929 | MW | Khulna | 1283 | 1283 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1161.08 | MMCFD |  |  | Rajshahi | 1063 | 1063 |  | 0 |  | 19:00 |  | 142
| 8 | Fuel Cost : | i) Gas : | Taka | 155813165.152 | ii) Oil : | Taka | 294178940.51 | Comilla | 1058 | 1058 |  | 0 |  | 19:30 |  | 142
|  |  | iii) Coal : |  | 54216684.54 | Total | Taka | 504208790.202 | Mymensingh | 857 | 857 |  | 0 |  | 20:00 |  | 136
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.2425 | MKWHr. | Sylhet | 447 | 447 |  | 0 |  | 21:00 |  | 136
|  | ii) During Peak Demand : |  |  | -96 | MW (E to W) at | 19:00 | hrs | Barisal | 310 | 310 |  | 0 |  | 22:00 |  | 134
|  | iii) Maximum : |  |  | -100 | MW at | 21:00 | hrs | Rangpur | 646 | 646 |  | 0 |  | 23:00 |  | 130
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.8° C |  |  | Total | 11088 | 11088 |  | 0
| B. |  | 2021-10-24 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14773 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2173 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 238.7423 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7831 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2604 | MKWHr. | ii) HVDC Flow at Peak Time |  | 715 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.929 | MKWHr. | iii) Maximum HVDC Flow : |  | 715 | MW at | 17:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.9 |  | (b) Today: | 104.92 |  | (c) Rule Curve: |  | 108.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 394 | 338 |  | 0 | 250 | 260 | 0 | 0 | 15 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 135 | 0 | 0 | 310 | 0 | 34 | 73 | 138 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 120 | 212 | 8 | 22 | 0 | 43 | 42 | 41 | 0 | 163 | 110 | 62 | 78 | 0 | 219 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 90 | 0 | 130 | 323 | 85 | 0 | 17 | 0 | 305 | 17 | 17 | 0 | 63 | 100 | 320 | 17 | 0 | 108 | 53 | 0 | 17 | 0 |  | 713 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 112 | 0 | 177 | 0 | 17 | 0 | 49 | 0 | 380 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 390 | 224 | 0 | 0 | 0 |  | 6135 | 2809 | 8944 | 3814 | 713 | 2330 | 0 | 1213 | 469 | 165 | 120 | 0 | 120 | 0 | 0 | 104.88
2:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 394 | 336 |  | 0 | 250 | 270 | 0 | 0 | 15 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 135 | 0 | 0 | 310 | 0 | 34 | 73 | 139 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 116 | 215 | 8 | 22 | 0 | 43 | 42 | 41 | 0 | 163 | 109 | 62 | 78 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 90 | 0 | 100 | 322 | 35 | 0 | 0 | 0 | 197 | 17 | 0 | 0 | 60 | 100 | 320 | 0 | 0 | 54 | 0 | 0 | 17 | 0 |  | 714 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 113 | 0 | 177 | 0 | 17 | 0 | 83 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 223 | 0 | 0 | 0 |  | 5754 | 2803 | 8557 | 3823 | 714 | 2378 | 0 | 782 | 460 | 164 | 120 | 0 | 116 | 0 | 0 | 104.88
3:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 395 | 336 |  | 0 | 250 | 270 | 0 | 0 | 15 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 135 | 0 | 0 | 310 | 0 | 35 | 73 | 139 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 114 | 213 | 8 | 22 | 0 | 43 | 42 | 41 | 0 | 163 | 110 | 62 | 78 | 0 | 219 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 90 | 0 | 50 | 322 | 35 | 0 | 0 | 0 | 105 | 17 | 0 | 0 | 63 | 100 | 320 | 0 | 0 | 17 | 0 | 0 | 17 | 0 |  | 714 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 115 | 0 | 178 | 0 | 17 | 0 | 94 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 223 | 0 | 0 | 0 |  | 5564 | 2702 | 8266 | 3818 | 714 | 2313 | 0 | 597 | 430 | 160 | 120 | 0 | 114 | 0 | 0 | 104.89
4:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 388 | 336 |  | 0 | 250 | 265 | 0 | 0 | 15 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 135 | 0 | 0 | 310 | 0 | 149 | 73 | 136 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 110 | 215 | 8 | 22 | 0 | 43 | 42 | 41 | 0 | 130 | 110 | 62 | 77 | 0 | 219 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 70 | 0 | 24 | 322 | 16 | 0 | 0 | 0 | 70 | 17 | 0 | 0 | 60 | 100 | 320 | 0 | 0 | 17 | 0 | 0 | 17 | 0 |  | 713 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 97 | 0 | 165 | 0 | 17 | 0 | 113 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 223 | 0 | 0 | 0 |  | 5479 | 2641 | 8120 | 3877 | 713 | 2251 | 0 | 489 | 400 | 160 | 120 | 0 | 110 | 0 | 0 | 104.89
5:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 350 | 337 |  | 0 | 250 | 280 | 0 | 0 | 15 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 135 | 0 | 0 | 260 | 0 | 148 | 73 | 136 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 112 | 215 | 8 | 22 | 0 | 43 | 42 | 14 | 0 | 130 | 110 | 62 | 30 | 0 | 193 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 70 | 0 | 10 | 322 | 16 | 0 | 0 | 0 | 70 | 17 | 0 | 0 | 58 | 100 | 320 | 0 | 0 | 17 | 0 | 0 | 17 | 0 |  | 713 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 94 | 0 | 163 | 0 | 17 | 0 | 143 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 180 | 0 | 0 | 0 |  | 5292 | 2611 | 7903 | 3787 | 713 | 2138 | 0 | 473 | 400 | 160 | 120 | 0 | 112 | 0 | 0 | 104.9
6:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 350 | 307 |  | 0 | 250 | 250 | 0 | 0 | 15 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 135 | 0 | 0 | 260 | 0 | 114 | 73 | 136 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 18 | 102 | 217 | 8 | 22 | 0 | 43 | 42 | 14 | 0 | 110 | 111 | 62 | 30 | 0 | 189 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 70 | 0 | 10 | 322 | 16 | 0 | 0 | 0 | 69 | 17 | 0 | 0 | 58 | 100 | 320 | 0 | 0 | 17 | 0 | 0 | 17 | 0 |  | 714 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 115 | 0 | 166 | 0 | 17 | 0 | 182 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 142 | 0 | 0 | 0 |  | 5170 | 2562 | 7732 | 3780 | 714 | 1979 | 0 | 476 | 401 | 160 | 120 | 0 | 102 | 0 | 0 | 104.9
7:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 350 | 271 |  | 0 | 250 | 285 | 0 | 0 | 15 | 0 | 0 | 60 | 0 | 3 | 0 | 6 | 0 | 0 | 0 | 54 | 0 | 20 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 37 | 135 | 0 | 0 | 280 | 0 | 111 | 73 | 139 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 15 | 92 | 212 | 8 | 22 | 0 | 43 | 42 | 14 | 0 | 110 | 109 | 51 | 30 | 0 | 178 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 70 | 0 | 10 | 322 | 16 | 0 | 0 | 1 | 70 | 17 | 0 | 0 | 58 | 100 | 320 | 0 | 7 | 17 | 0 | 0 | 17 | 4 |  | 714 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 17 | 0 | 176 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 142 | 0 | 0 | 0 |  | 5194 | 2483 | 7677 | 3644 | 714 | 2036 | 0 | 496 | 401 | 160 | 120 | 0 | 92 | 14 | 0 | 104.91
8:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 343 | 271 |  | 0 | 250 | 240 | 0 | 0 | 44 | 0 | 0 | 57 | 0 | 48 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 28 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 135 | 0 | 0 | 260 | 0 | 111 | 73 | 137 | 20 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 7 | 8 | 10 | 104 | 216 | 8 | 22 | 1 | 43 | 42 | 14 | 0 | 110 | 110 | 52 | 30 | 0 | 179 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1 | 70 | 0 | 10 | 324 | 48 | 0 | 0 | 2 | 70 | 17 | 0 | 0 | 58 | 100 | 320 | 0 | 22 | 17 | 0 | 0 | 11 | 11 |  | 714 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 17 | 0 | 174 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 320 | 139 | 0 | 0 | 1 |  | 5260 | 2428 | 7688 | 3608 | 714 | 1887 | 0 | 654 | 401 | 161 | 120 | 0 | 104 | 39 | 0 | 104.91
9:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 301 | 273 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 57 | 0 | 72 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 290 | 0 | 111 | 73 | 137 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 2 | 8 | 10 | 108 | 211 | 8 | 22 | 1 | 43 | 42 | 14 | 0 | 110 | 112 | 51 | 10 | 0 | 179 | 18 | 0 | 9 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 3 | 70 | 0 | 10 | 323 | 55 | 0 | 0 | 2 | 70 | 17 | 0 | 0 | 58 | 100 | 320 | 1 | 35 | 20 | 0 | 0 | 17 | 0 |  | 714 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 17 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 320 | 141 | 0 | 0 | 3 |  | 5366 | 2316 | 7682 | 3504 | 714 | 1874 | 0 | 754 | 400 | 162 | 120 | 0 | 108 | 46 | 0 | 104.92
10:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 302 | 303 |  | 0 | 250 | 275 | 0 | 0 | 55 | 0 | 0 | 60 | 0 | 102 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 14 | 33 | 33 | 0 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 270 | 0 | 111 | 73 | 139 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 8 | 10 | 108 | 208 | 8 | 22 | 2 | 43 | 42 | 14 | 0 | 110 | 111 | 51 | 78 | 0 | 199 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 20 | 70 | 0 | 28 | 240 | 55 | 0 | 0 | 4 | 88 | 17 | 0 | 0 | 58 | 90 | 385 | 16 | 45 | 52 | 0 | 0 | 17 | 0 |  | 713 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 17 | 0 | 153 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 320 | 142 | 0 | 0 | 4 |  | 5577 | 2429 | 8006 | 3502 | 713 | 2064 | 0 | 857 | 401 | 162 | 120 | 0 | 108 | 79 | 0 | 104.92
11:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 302 | 332 |  | 0 | 250 | 290 | 0 | 0 | 55 | 0 | 0 | 60 | 0 | 102 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 14 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 325 | 0 | 117 | 73 | 139 | 19 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 8 | 10 | 120 | 186 | 0 | 22 | 2 | 43 | 42 | 35 | 0 | 130 | 110 | 60 | 75 | 0 | 206 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 20 | 76 | 0 | 50 | 318 | 55 | 0 | 0 | 3 | 124 | 17 | 0 | 0 | 58 | 90 | 320 | 17 | 51 | 54 | 15 | 0 | 17 | 0 |  | 713 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 23 | 0 | 158 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 320 | 162 | 0 | 0 | 5 |  | 5802 | 2517 | 8319 | 3599 | 713 | 2189 | 0 | 931 | 401 | 161 | 120 | 0 | 120 | 85 | 0 | 104.92
12:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 358 | 332 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 97 | 0 | 102 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 14 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 280 | 0 | 141 | 78 | 140 | 19 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 8 | 16 | 124 | 186 | 0 | 22 | 2 | 43 | 42 | 41 | 0 | 163 | 110 | 60 | 75 | 0 | 220 | 18 | 0 | 10 | 320 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 76 | 0 | 50 | 322 | 55 | 0 | 0 | 4 | 157 | 17 | 0 | 0 | 58 | 90 | 320 | 17 | 35 | 54 | 17 | 0 | 17 | 0 |  | 714 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 23 | 0 | 173 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 222 | 0 | 0 | 5 |  | 5996 | 2714 | 8710 | 3763 | 714 | 2386 | 0 | 978 | 402 | 161 | 120 | 0 | 124 | 62 | 0 | 104.93
13:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 398 | 331 |  | 0 | 250 | 285 | 0 | 0 | 55 | 7 | 0 | 98 | 0 | 102 | 0 | 23 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 14 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 135 | 0 | 0 | 295 | 0 | 141 | 78 | 138 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 8 | 16 | 122 | 183 | 0 | 22 | 1 | 43 | 42 | 39 | 0 | 163 | 110 | 61 | 75 | 0 | 219 | 18 | 0 | 10 | 310 | 18 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 13 | 76 | 1 | 61 | 238 | 55 | 0 | 5 | 4 | 211 | 17 | 5 | 0 | 58 | 90 | 320 | 20 | 40 | 106 | 22 | 0 | 17 | 0 |  | 714 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 23 | 0 | 190 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 320 | 221 | 0 | 0 | 4 |  | 6163 | 2730 | 8893 | 3784 | 714 | 2372 | 0 | 1150 | 402 | 161 | 120 | 0 | 122 | 68 | 0 | 104.93
14:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 390 | 281 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 95 | 0 | 102 | 0 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 14 | 33 | 33 | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 135 | 0 | 0 | 310 | 0 | 141 | 78 | 138 | 25 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 8 | 16 | 136 | 169 | 0 | 22 | 2 | 43 | 42 | 39 | 0 | 130 | 110 | 60 | 75 | 0 | 220 | 18 | 0 | 10 | 280 | 18 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 100 | 16 | 90 | 12 | 95 | 402 | 55 | 0 | 34 | 3 | 213 | 17 | 27 | 0 | 52 | 90 | 320 | 53 | 38 | 108 | 53 | 0 | 17 | 0 |  | 713 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 23 | 0 | 179 | 0 | 348 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 320 | 221 | 0 | 0 | 2 |  | 6388 | 2656 | 9044 | 3914 | 713 | 2177 | 0 | 1357 | 402 | 164 | 120 | 0 | 136 | 61 | 0 | 104.93
15:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 365 | 302 |  | 0 | 250 | 285 | 0 | 0 | 55 | 0 | 0 | 95 | 0 | 102 | 0 | 18 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 14 | 33 | 33 | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 350 | 0 | 140 | 78 | 139 | 29 | 53 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 25 | 20 | 134 | 169 | 0 | 22 | 0 | 44 | 42 | 39 | 0 | 130 | 108 | 60 | 75 | 0 | 220 | 18 | 0 | 10 | 310 | 18 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 100 | 11 | 90 | 17 | 115 | 322 | 55 | 0 | 34 | 1 | 213 | 17 | 34 | 0 | 49 | 90 | 320 | 53 | 25 | 108 | 53 | 0 | 17 | 0 |  | 714 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 23 | 0 | 195 | 0 | 419 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 0 | 320 | 220 | 0 | 0 | 3 |  | 6425 | 2770 | 9195 | 3890 | 714 | 2310 | 0 | 1414 | 404 | 164 | 120 | 0 | 134 | 45 | 0 | 104.93
16:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 363 | 302 |  | 0 | 250 | 285 | 0 | 0 | 55 | 0 | 0 | 95 | 0 | 102 | 0 | 23 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 14 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 355 | 0 | 139 | 78 | 139 | 23 | 54 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 25 | 21 | 126 | 182 | 0 | 22 | 0 | 43 | 42 | 39 | 0 | 130 | 107 | 60 | 78 | 0 | 220 | 18 | 0 | 10 | 300 | 18 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 100 | 6 | 90 | 17 | 115 | 323 | 55 | 0 | 17 | 1 | 176 | 17 | 17 | 0 | 53 | 90 | 320 | 50 | 13 | 108 | 35 | 0 | 17 | 0 |  | 714 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 66 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 23 | 0 | 195 | 0 | 419 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 320 | 220 | 0 | 0 | 1 |  | 6316 | 2756 | 9072 | 3891 | 714 | 2302 | 0 | 1331 | 404 | 160 | 120 | 0 | 126 | 24 | 0 | 104.93
17:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 388 | 326 |  | 0 | 250 | 270 | 0 | 0 | 55 | 65 | 0 | 35 | 0 | 102 | 10 | 24 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 14 | 33 | 33 | 21 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 135 | 0 | 0 | 330 | 0 | 142 | 78 | 136 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 25 | 21 | 122 | 185 | 0 | 22 | 0 | 43 | 42 | 39 | 0 | 163 | 109 | 61 | 78 | 0 | 220 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 100 | 1 | 90 | 17 | 113 | 322 | 55 | 0 | 17 | 0 | 253 | 17 | 17 | 0 | 59 | 90 | 320 | 18 | 2 | 108 | 35 | 0 | 17 | 0 |  | 715 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 198 | 0 | 358 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 320 | 221 | 0 | 0 | 0 |  | 6430 | 2702 | 9132 | 3905 | 715 | 2296 | 0 | 1384 | 402 | 160 | 120 | 24 | 122 | 4 | 0 | 104.93
18:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 367 | 333 |  | 0 | 250 | 245 | 0 | 0 | 55 | 338 | 0 | 0 | 0 | 102 | 32 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 10 | 33 | 33 | 27 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 102 | 77 | 38 | 14 | 18 | 7 | 135 | 0 | 0 | 330 | 0 | 143 | 78 | 137 | 29 | 55 | 0 | 51 | 0 | 50 | 0 | 19 | 2 | 25 | 21 | 146 | 186 | 0 | 22 | 0 | 43 | 42 | 39 | 0 | 163 | 112 | 62 | 78 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 216 | 0 | 0 | 62 | 0 | 107 | 0 | 90 | 65 | 123 | 324 | 90 | 25 | 55 | 0 | 303 | 17 | 57 | 60 | 96 | 90 | 320 | 59 | 0 | 108 | 80 | 0 | 17 | 0 |  | 715 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 62 | 25 | 0 | 0 | 0 | 0 | 28 | 5 | 95 | 27 | 24 | 28 | 6 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 23 | 0 | 173 | 0 | 365 | 53 | 0 | 52 | 0 | 90 | 0 | 0 | 70 | 360 | 220 | 0 | 14 | 0 |  | 7677 | 3247 | 10924 | 4188 | 715 | 2276 | 0 | 2539 | 440 | 160 | 120 | 340 | 146 | 0 | 0 | 104.93
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 401 | 302 |  | 0 | 250 | 260 | 0 | 0 | 55 | 316 | 0 | 0 | 0 | 102 | 48 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 9 | 0 | 68 | 20 | 65 | 47 | 18 | 10 | 135 | 0 | 0 | 335 | 0 | 143 | 78 | 138 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 7 | 25 | 21 | 142 | 185 | 0 | 22 | 0 | 43 | 42 | 41 | 0 | 130 | 110 | 62 | 78 | 0 | 220 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 300 | 0 | 0 | 120 | 0 | 149 | 0 | 76 | 139 | 125 | 323 | 115 | 60 | 105 | 0 | 304 | 17 | 108 | 62 | 96 | 90 | 320 | 104 | 0 | 108 | 116 | 0 | 17 | 0 |  | 715 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 27 | 0 | 0 | 0 | 0 | 43 | 0 | 95 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 23 | 0 | 170 | 0 | 308 | 86 | 0 | 110 | 0 | 107 | 0 | 0 | 100 | 430 | 223 | 0 | 0 | 0 |  | 8136 | 3321 | 11457 | 4225 | 715 | 2165 | 0 | 3166 | 510 | 160 | 120 | 254 | 142 | 0 | 0 | 104.93
19:30 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 401 | 301 |  | 0 | 250 | 280 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 10 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 34 | 10 | 0 | 46 | 18 | 11 | 135 | 0 | 0 | 335 | 0 | 141 | 78 | 138 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 7 | 25 | 22 | 142 | 181 | 0 | 22 | 0 | 43 | 42 | 44 | 0 | 130 | 109 | 62 | 78 | 0 | 220 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 100 | 0 | 149 | 0 | 76 | 140 | 125 | 323 | 115 | 90 | 105 | 0 | 304 | 17 | 110 | 31 | 97 | 90 | 320 | 104 | 0 | 108 | 116 | 0 | 17 | 0 |  | 715 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 23 | 0 | 166 | 0 | 341 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 470 | 223 | 0 | 0 | 0 |  | 8055 | 3302 | 11357 | 4231 | 715 | 2248 | 0 | 3077 | 550 | 160 | 120 | 114 | 142 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 401 | 333 |  | 0 | 250 | 260 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 87 | 75 | 115 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 34 | 0 | 0 | 19 | 18 | 15 | 135 | 0 | 0 | 335 | 0 | 143 | 78 | 138 | 29 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 25 | 22 | 136 | 184 | 0 | 22 | 0 | 43 | 42 | 44 | 0 | 163 | 110 | 62 | 78 | 0 | 220 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 240 | 0 | 0 | 80 | 0 | 144 | 0 | 76 | 100 | 125 | 323 | 115 | 70 | 105 | 0 | 305 | 17 | 68 | 0 | 97 | 90 | 320 | 104 | 0 | 108 | 116 | 0 | 17 | 0 |  | 714 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 23 | 0 | 167 | 0 | 409 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 480 | 223 | 0 | 0 | 0 |  | 7836 | 3289 | 11125 | 4242 | 714 | 2356 | 0 | 2781 | 560 | 162 | 120 | 54 | 136 | 0 | 0 | 104.93
21:00 | 0 | 0 | 0 | 180 | 0 | 21 | 0 | 401 | 337 |  | 0 | 250 | 260 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 0 | 32 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 16 | 0 | 0 | 0 | 0 |  | 23 | 0 | 34 | 0 | 0 | 19 | 18 | 25 | 135 | 0 | 0 | 335 | 0 | 144 | 78 | 138 | 29 | 56 | 0 | 51 | 0 | 0 | 4 | 19 | 9 | 25 | 22 | 136 | 186 | 2 | 22 | 0 | 43 | 42 | 44 | 0 | 163 | 110 | 62 | 78 | 0 | 217 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 140 | 0 | 0 | 80 | 0 | 120 | 0 | 76 | 100 | 128 | 323 | 115 | 50 | 105 | 0 | 305 | 17 | 68 | 0 | 97 | 90 | 320 | 104 | 0 | 108 | 116 | 0 | 17 | 0 |  | 714 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 22 | 0 | 182 | 0 | 308 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 500 | 222 | 0 | 0 | 0 |  | 7724 | 3144 | 10868 | 4270 | 714 | 2271 | 0 | 2582 | 581 | 160 | 120 | 34 | 136 | 0 | 0 | 104.93
22:00 | 0 | 0 | 0 | 180 | 0 | 21 | 0 | 400 | 337 |  | 0 | 250 | 275 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 0 | 33 | 0 | 0 | 0 | 54 | 55 | 55 | 12 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 18 | 28 | 135 | 0 | 0 | 340 | 0 | 142 | 78 | 137 | 29 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 25 | 22 | 134 | 189 | 8 | 22 | 0 | 43 | 42 | 44 | 0 | 163 | 108 | 62 | 78 | 0 | 217 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 100 | 0 | 90 | 100 | 130 | 323 | 115 | 35 | 105 | 0 | 305 | 17 | 68 | 0 | 97 | 78 | 320 | 104 | 0 | 108 | 116 | 0 | 17 | 0 |  | 715 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 68 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 17 | 0 | 187 | 0 | 341 | 17 | 0 | 113 | 0 | 74 | 0 | 0 | 35 | 490 | 223 | 0 | 0 | 0 |  | 7535 | 3132 | 10667 | 4273 | 715 | 2312 | 0 | 2348 | 571 | 160 | 120 | 34 | 134 | 0 | 0 | 104.93
23:00 | 0 | 0 | 0 | 180 | 0 | 21 | 0 | 400 | 337 |  | 0 | 250 | 270 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 8 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 18 | 28 | 135 | 0 | 0 | 335 | 0 | 143 | 78 | 139 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 25 | 22 | 130 | 187 | 8 | 22 | 0 | 43 | 42 | 44 | 0 | 163 | 109 | 62 | 78 | 0 | 217 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 85 | 0 | 90 | 17 | 130 | 324 | 109 | 0 | 85 | 0 | 305 | 17 | 0 | 0 | 92 | 78 | 320 | 104 | 0 | 108 | 116 | 0 | 17 | 0 |  | 714 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 69 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 17 | 0 | 183 | 0 | 340 | 0 | 0 | 113 | 0 | 38 | 0 | 0 | 0 | 470 | 223 | 0 | 0 | 0 |  | 7172 | 3015 | 10187 | 4271 | 714 | 2305 | 0 | 1901 | 551 | 161 | 120 | 34 | 130 | 0 | 0 | 104.93
24:00 | 0 | 0 | 0 | 180 | 0 | 21 | 0 | 399 | 337 |  | 0 | 250 | 260 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 18 | 29 | 135 | 0 | 0 | 335 | 0 | 144 | 78 | 139 | 29 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 25 | 21 | 126 | 187 | 8 | 22 | 0 | 43 | 42 | 44 | 0 | 163 | 110 | 62 | 78 | 0 | 217 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 85 | 0 | 90 | 0 | 133 | 323 | 109 | 0 | 17 | 0 | 305 | 17 | 0 | 0 | 62 | 78 | 320 | 104 | 0 | 108 | 72 | 0 | 17 | 0 |  | 715 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 69 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 17 | 0 | 183 | 0 | 314 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 430 | 207 | 0 | 0 | 0 |  | 6917 | 2870 | 9787 | 4269 | 715 | 2243 | 0 | 1604 | 511 | 165 | 120 | 34 | 126 | 0 | 0 | 104.93
KWH | 0 | 0 | 0 | 4252500 | 0 | 532136 | 0 | 9023480 | 7574000 |  | 0 | 6161750 | 6485498 | 0 | 0 | 1046023 | 2289965 | 0 | 1372000 | 0 | 1648368 | 70080 | 407294 | 0 | 0 | 0 | 1291320 | 566688 | 924402 | 411984 | 600000 | 546840 | 790300 | 824900 | 289920 | 0 | 2006476 | 1804000 | 2800000 | 0 | 67163 | 0 | 0 | 0 | 0 |  | 62640 | 0 | 334899 | 90360 | 104640 | 122360 | 418704 | 527040 | 3262380 | 0 | 0 | 7813500 | 0 | 2906000 | 1873454 | 2145990 | 572256 | 1325280 | 0 | 1254820 | 0 | 52272 | 15379 | 467316 | 138960 | 365900 | 453350 | 2928960 | 4600880 | 106560 | 496404 | 12050 | 1023000 | 1005120 | 814200 | 0 | 3539700 | 2481000 | 1425504 | 1621440 | 0 | 5009600 | 398000 | 0 | 245520 | 7139500 | 504937 | 195360 | 0 | 1146654 | 0 | 0 | 590400 | 0 | 1837010 | 98145 | 1926720 | 704640 | 1970472 | 7663000 | 1614000 | 336000 | 838032 | 25320 | 4591636 | 432701 | 651524 | 159600 | 1633800 | 2231040 | 7704000 | 1006080 | 323090 | 1788480 | 1150418 | 0 | 437040 | 11735 |  | 17260363 | 0 | 8659008 | 0 | 0 | 3005760 | 0 | 0 | 0 | 0 | 0 | 1577000 | 508403 | 0 | 0 | 0 | 0 | 61480 | 7371 | 228472 | 38480 | 51065 | 39744 | 50880 | 0 | 503760 | 0 | 195786 | 1937018 | 0 | 0 | 0 | 0 | 713800 | 0 | 4330527 | 0 | 478425 | 0 | 4109269 | 0 | 8423018 | 270720 | 0 | 918720 | 0 | 549945 | 0 | 26935 | 395040 | 9689400 | 483063 | 0 | 26400 | 31260 |  | 152513859 | 64571112 | 217084971 | 93548520 | 17260363 | 49491007 | 0 | 34090614 | 11626418 | 3810476 | 3005760 | 794318 | 2928960 | 528535 | 0
Fuel Cost | 0 | 0 | 0 | 6251175 | 0 | 702419.52 | 0 | 9113714.8 | 7801220 |  | 0 | 6716307.5 | 7198902.78 | 0 | 0 | 8849354.58 | 2381563.6 | 0 | 2373560 | 0 | 15033116.16 | 689587.2 | 3755250.68 | 0 | 0 | 0 | 9426636 | 4380498.24 | 9114603.72 | 308988 | 450000 | 0 | 0 | 0 | 2803526.4 | 0 | 541748.52 | 487080 | 5068000 | 0 | 623944.27 | 0 | 0 | 0 | 0 |  | 0 | 0 | 3248520.3 | 862938 | 910368 | 969091.2 | 527567.04 | 1565308.8 | 4828322.4 | 0 | 0 | 5781990 | 0 | 2673520 | 2416755.66 | 2467888.5 | 646649.28 | 1855392 | 0 | 2145742.2 | 0 | 527947.2 | 146869.45 | 593491.32 | 104220 | 640325 | 340012.5 | 21967200 | 4876932.8 | 967564.8 | 630433.08 | 192077 | 1677720 | 1608192 | 1449276 | 0 | 4035258 | 2580240 | 2808242.88 | 3096950.4 | 0 | 8666608 | 871620 | 0 | 500860.8 | 7210895 | 378702.75 | 148473.6 | 0 | 8668704.24 | 0 | 0 | 3070080 | 0 | 18076178.4 | 1147315.05 | 15702768 | 7645344 | 13891827.6 | 7126590 | 14719680 | 3175200 | 7299258.72 | 0 | 34712768.16 | 3768825.71 | 5726895.96 | 1592808 | 14001666 | 14858726.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99419690.88 | 0 | 9091958.4 | 0 | 0 | 41659833.6 | 0 | 0 | 0 | 0 | 0 | 1782010 | 788024.65 | 0 | 0 | 0 | 0 | 604963.2 | 74889.36 | 2021977.2 | 296296 | 690398.8 | 385119.36 | 493027.2 | 0 | 967219.2 | 0 | 148210.002 | 11680218.54 | 0 | 0 | 0 | 0 | 835146 | 0 | 5716295.64 | 0 | 717637.5 | 0 | 4807844.73 | 0 | 8338787.82 | 2826316.8 | 0 | 8718652.8 | 0 | 4267573.2 | 0 | 297631.75 | 2919345.6 | 42536466 | 0 | 0 | 0 | 0 |  | 376175999.17 | 252085534.232 | 628261533.402 | 98306207.322 | 99419690.88 | 57506957.83 | 0 | 244966103.09 | 54216684.54 | 1028828.52 | 41659833.6 | 7553003.82 | 21967200 | 1637023.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 358 | 332 |  | 0 | 250 | 280 | 0 | 0 | 55 | 0 | 0 | 97 | 0 | 102 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 14 | 33 | 33 | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 0 | 0 | 280 | 0 | 141 | 78 | 140 | 19 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 8 | 16 | 124 | 186 | 0 | 22 | 2 | 43 | 42 | 41 | 0 | 163 | 110 | 60 | 75 | 0 | 220 | 18 | 0 | 10 | 320 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 76 | 0 | 50 | 322 | 55 | 0 | 0 | 4 | 157 | 17 | 0 | 0 | 58 | 90 | 320 | 17 | 35 | 54 | 17 | 0 | 17 | 0 |  | 714 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 23 | 0 | 173 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 222 | 0 | 0 | 5 |  | 8710 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 401 | 302 | 0 | 0 | 250 | 260 | 0 | 0 | 55 | 316 | 0 | 0 | 0 | 102 | 48 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 85 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 68 | 20 | 65 | 47 | 18 | 10 | 135 | 0 | 0 | 335 | 0 | 143 | 78 | 138 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 7 | 25 | 21 | 142 | 185 | 0 | 22 | 0 | 43 | 42 | 41 | 0 | 130 | 110 | 62 | 78 | 0 | 220 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 300 | 0 | 0 | 120 | 0 | 149 | 0 | 76 | 139 | 125 | 323 | 115 | 60 | 105 | 0 | 304 | 17 | 108 | 62 | 96 | 90 | 320 | 104 | 0 | 108 | 116 | 0 | 17 | 0 |  | 715 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 27 | 0 | 0 | 0 | 0 | 43 | 0 | 95 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 23 | 0 | 170 | 0 | 308 | 86 | 0 | 110 | 0 | 107 | 0 | 0 | 100 | 430 | 223 | 0 | 0 | 0 |  | 11457 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 412 | 330 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 90 | 50 | 18 | 15 | 135 | 0 | 0 | 330 | 0 | 145 | 78 | 138 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 18 | 164 | 200 | 8 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 65 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 130 | 321 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 727 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 33 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 42 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 42 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 100 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 350 | 300 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 90 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 18 | 5 | 135 | 0 | 0 | 330 | 0 | 145 | 78 | 138 | 30 | 55 | 0 | 51 | 0 | 50 | 20 | 22 | 11 | 33 | 18 | 138 | 200 | 8 | 22 | 1.6 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 100 | 100 | 190 | 50 | 149 | 20 | 90 | 200 | 130 | 321 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 727 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 42 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 42 | 50 | 220 | 0 | 400 | 105 | 0 | 113 | 0 | 100 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 21 | 0 | 321 | 253 | 0 | 0 | 250 | 255 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 29 | 33 |  | 0 | 0 | 86 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 135 | 0 | 0 | 260 | 0 | 30 | 78 | 137 | 29 | 52 | 0 | 35 | 0 | 0 | 0 | 19 | 0 | 25 | 15 | 92 | 197 | 8 | 22 | 1 | 43 | 42 | 28 | 0 | 110 | 112 | 62 | 75 | 0 | 190 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 2 | 0 | 0 | 8 | 0 | 74 | 10 | 76 | 0 | 8 | 324 | 65 | 0 | 34 | 2 | 159 | 17 | 34 | 0 | 58 | 90 | 320 | 0 | 22 | 4 | 35 | 0 | 17 | 13 | 0 | 715 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 17 | 0 | 140 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 300 | 141 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 7677 | 7:00
| Highest Generation |  | 11457 | 19:00
| Day Peak Generation |  | 8710 | 12:00
| Evening Peak Generation |  | 11457 | 19:00
| HVDC Max Flow |  | 715 | 17:00
| HVDC EvPeak Flow |  | 715 | 19:00
| Load factor L.F |  | 78.95%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-24
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8710 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7831 | MW
Evening Peak Generation : |  | 11457 | MW Hour : | 19:00 | Available Max Generation : |  | 14773 | MW
E.P. Demand (at gen end) : |  | 11457 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12600 | MW
Maximum Generation : |  | 11457 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2173 | MW
Total Gen. (MKWH) : |  | 217.085 | System Load Factor : | 78.95% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -100 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-24
Actual : | 104.92 | Ft.(MSL) , | Rule curve : | 108.2 | Ft.( MSL )
Gas Consumed : | Total = | 1161.08 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155813165.152
: |  | Coal : | 54216684.54 | Oil : | 294178940.51 | Total : | 504208790.202
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4531.2525 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1545.1057 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1385.117 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1251.8376 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1131.12 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 912.7845 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 504.9421 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 234.8734 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 704.0107 |  |  | 0 | 0%
Total | 0 |  | 12201.0436 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barguna 132/33 kV T-1 transformer was under shut down from 08:13 to 17:51 for A/M.
b) Barguna 132/33 kV T-3 transformer was under shut down from 08:21 to 15:02 for A/M.
c) Chapainawabganj 132/33 kV T-3 transformer was under shut down from 11:28 to 12:26 for A/M.
d) Goalpara 132/33 kV T-5 transformer was under shut down from 12:21 to 13:45 due to C/M.
e) GPH ispat 230/132 kV T-1 & T2 transformer were under shut down from 08:28 to 12:38 for C/M.
f) Hathazari-Rampur 230 kV bay-1 was under shut down from 10:05 to 14:27 for D/W.
g) Bheramara HVDC-Rajshahi 230 kV Ckt-1 was under shut down from 08:46 to 17:25 for A/M.
h) Jaldhaka 132/33 kV T-2 transformer was under shut down from 08:56 to 16:34 for A/M.
i) Kishoreganj 132/33 kV T-3 transformer was under shut down from 09:42 to 17:38 due to 33 kV
end L/A installation.
j) Mohastanghor 132/33 kV T-2 transformer was under shut down from 09:32 to 15:01 for C/M.
k) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:05 to 17:21 for A/M.
l) Noapara 132/33 kV T-1 transformer was under shut down from 08:25 to 14:22 for A/M.
m) Sirajganj 132/33 kV T-3 transformer was under shut down from 08:30 to 13:44 for A/M.
n) Shyampur-APR 230 kV Ckt was shut down at 08:30 for D/W.
o) Shyampur-Hasnabad 230 kV Ckt was shut down at 08:29 for D/W.
p) Siddirganj-335 MW CCPP GT was synchronized at 12:55.
q) Sonargaon-Daudkandi 132 kV Ckt-2 was under shut down from 08:27 to 15:35 for A/M.
r) Siddirganj-335 MW CCPP ST was synchronized at 16:05.
s) Siddirganj 210 MW GT-2 was shut down at 17:37 for gas shortage.
u) Mohastanghor 132/33 kV T-1 transformer was under shut down from 15:02 to 16:57 for A/M.
v) Hathazari-Rampur 230 kV Ckt-2 bay was under shut down from 14:29 to 15:51 for D/W.
w) Norsingdi 132/33 kV T-3 transformer was under shut down from 20:28 to 21:08 for C/M.
x) Cumilla(S) 132/33 kV T-1 transformer is under shut down since 01:30(24/10/21) for C/M.
y) Norsingdi 132/33 kV T-1 transformer is under shut down since 07:58(24/10/21) for C/M.
z) Bheramara HVDC-Rajshahi 230 kV Ckt-1 is under shut down since 07:58 to 17:25 for A/M.
aa) Mirpur-Aminbazar 132 kV Ckt-1 is under shut down since 07:22(24/10/21) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4252500 | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 532136 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 401 | 9023480
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 302 | 7574000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6161750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6485498 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1046023
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 23 | 407294 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 411984
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1372000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 316 | 2289965
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1648368
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1291320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 70080 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 566688
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 924402
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1146840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 790300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 824900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 289920
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 1146654
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1837010
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 60 | 336000 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1006080
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1788480 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 11735
| Dhaka area Total |  |  |  | 5560 | 3034 | 53235407
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 67163 | Low demand.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 98145
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 47 | 122360
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 160 | 3810476 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 838032
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 334899 | Red hot
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 90360 | Low demand.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 76 | 1926720 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 418704 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 527040
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 65 | 104640 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25320
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 4591636
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 432701 | Engine problem
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 108 | 651524
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 2231040
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1150418
| Chattogram area Total |  |  |  | 2382 | 1327 | 20221178
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 3262380 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 143 | 2906000 | ST under maint
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7813500 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 572256 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1325280
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 78 | 1873454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1254820
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 1970472 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 52272 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 2145990 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 139 | 704640 | Low demand.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 467316
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 138960 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 142 | 2928960
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 365900 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 15379 | Reserve.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 453350
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 62 | 159600 | Low demand.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1633800 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 437040 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1617 | 30481369
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 185 | 4600880
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 496404
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 106560 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12050
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 120 | 590400 | Low demand.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1614000
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 323090
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 9 | 62640
| Mymensingh Area Total |  |  |  | 622 | 451 | 7806024
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1023000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1005120 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3539700 | Frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2481000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 41 | 814200 | Engine problem
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 195360
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1425504
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1621440 | Engine problem
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5009600
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 398000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 504937
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7139500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 323 | 7663000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245520
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7704000 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1707 | 40769881
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 715 | 17260363
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3005760 | Low demand.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8659008
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 86 | 270720 | Engine problem
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1331 | 29195851
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 508403 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1577000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 23 | 478425 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 9689400 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 223 | 483063
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 26400 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 770 | 12762691
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 61480
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 7371 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 38480 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 51065 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 39744 | Reserve.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 713800 | ST under maint & FGMO
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 166 | 4330527 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 170 | 4109269 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 308 | 8423018 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 503760
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 195786
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 50880 | Low demand.
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 228472
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 110 | 918720
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 395040
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31260
| Rajshahi Area Total |  |  |  | 2179 | 1033 | 20098672
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1937018
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 549945
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26935
| Rangpur Area Total |  |  |  | 605 | 187 | 2513898
| Total |  |  |  | 20934 | 11457 | 217084971
| Eastern Grid Total |  |  |  | 13975 | 8136 | 152513859
| Western Grid Total |  |  |  | 6959 | 3321 | 64571112
| National Grid Total |  |  |  | 20934 | 11457 | 217084971
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-23
(a) ENTIRE EASTERN GRID : |  | 7786 | MW | (b) ENTIRE WESTERN GRID : |  | 3302 | MW
i) Dhaka area |  | 4143 | MW | i) Khulna area |  | 1283 | MW
ii) Chittagong area |  | 1281 | MW | ii) Rajshahi area |  | 1063 | MW
iii) Comilla area |  | 1058 | MW | iii) Barisal area |  | 310 | MW
iv) Mymensingh area |  | 857 | MW | iv) Rangpur area |  | 646 | MW
v) Sylhet area |  | 447 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11088 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 15:00 | Kishoreganj | 120 | 18:30 | Benapol | 52 | 18:00
Munsiganj | 86 | 15:00 | Netrokona | 93 | 18:00 | Jhenida(Old) | 94 | 18:00
Sonargaon | 66 | 10:00 | Jamalpur | 107 | 21:00 | Bottail | 106 | 18:00
Shyampur | 166 | 2:00 | Sherpur | 102 | 18:00 | G.K Project | 48 | 18:30
Bhulta | 188 | 20:00 | Srimongal | 45 | 18:00 | Faridpur | 123 | 18:30
Madanganj | 36 | 13:00 | Shahjibazar | 100 | 19:00 | Rajbari | 46 | 18:30
Shitalakhya | 102 | 15:00 | Fenchuganj | 42 | 17:00 | Madaripur | 74 | 22:00
Rahim steel | 18 | 11:00 | Kulawara | 40 | 20:00 | Sariatpur | 52 | 18:30
Matuail | 60 | 10:00 | Sylhet | 126 | 18:00 | Gopalganj | 80 | 18:30
Ghorasal | 70 | 18:30 | Chatak | 22 | 18:30 | Bagerhat | 96 | 18:00
Narsingdi | 153 | 19:30 | Sunamganj | 40 | 20:00 | Mongla | 44 | 11:00
Haripur (SBU) | 111 | 19:00 | Biani Bazar | 52 | 18:00 | Satkhira | 92 | 20:00
Sreenagar | 38 | 20:00 | Comilla (S) | 146 | 18:00 | Gallamari | 43 | 18:00
Ullon | 59 | 20:00 | Comilla(N) | 105 | 18:00 | Magura | 46 | 18:00
Hasnabad | 71 | 18:30 | Chandpur | 61 | 19:30 | Norail | 44 | 18:00
Magbazar | 89 | 12:00 | Feni | 103 | 18:30 | Chuadanga | 84 | 18:30
Maniknagar | 54 | 18:00 | Chowmuhani | 182 | 19:30 | Barisal(N) | 35 | 18:30
Bangabhaban | 6 | 11:00 | Ashuganj | 38 | 23:00 | Barisal (S) | 96 | 18:00
Motijheel | 22 | 12:00 | Daudkandi | 134 | 18:00 | Patuakhali | 93 | 19:00
Narinda | 62 | 13:00 | B.Baria | 143 | 18:00 | Bhandaria | 44 | 20:00
Kazla | 80 | 12:00 | Ramganj | 76 | 18:00 | Borguna | 14 | 18:00
Dhanmondi | 164 | 13:00 | Chaddagram | 41 | 19:30 | Borhan Uddin | 38 | 21:00
Lalbag | 78 | 12:00 | PHP | 11 | 18:00 | Ishurdi | 62 | 19:30
Madartek | 68 | 21:00 | Kochua | 54 | 18:30 | Ruppur Paromanobik | 3 | 1:00
Dhaka University | 29 | 12:00 | Madunaghat | 58 | 19:00 | Natore | 104 | 18:00
Aftabnagar | 13 | 18:00 | Hathazari | 93 | 18:00 | Bogra | 141 | 19:30
Fatullah | 55 | 23:00 | Khulshi | 187 | 18:00 | Noagaon | 91 | 20:00
Nawabganj | 42 | 22:00 | Halishahar | 90 | 17:00 | Rajshahi | 123 | 20:00
Keraniganj | 68 | 18:30 | Baraulia | 135 | 16:00 | Rajshahi New | 16 | 19:30
Banani | 25 | 13:00 | Sikalbaha | 38 | 19:00 | C.Nawabganj | 47 | 18:30
Mirpur | 107 | 12:00 | Dohazari | 80 | 19:00 | Amnura | 37 | 18:30
Kalyanpur | 87 | 13:00 | Cox'sbazar | 105 | 18:00 | Pabna | 88 | 19:00
Gulshan | 88 | 12:00 | Chandraghona | 28 | 18:00 | Shahjadpur | 84 | 19:00
Uttara | 72 | 18:00 | Kaptai | 4.2 | 18:00 | Serajganj | 77 | 18:30
Uttara New | 22 | 19:30 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 52 | 18:30
Kamrangirchar | 83 | 19:30 | Bakulia | 113 | 18:30 | Joypurhat | 43 | 18:30
Savar | 151 | 18:00 | Julda | 23 | 1:00 | Sherpur(Bogura) | 50 | 18:00
Bhasantec | 115 | 14:00 | TK chemical | 28.3 | 18:30 | Mohastangor | 50 | 18:00
Agargaon | 71 | 13:00 | Modern Steel | 4.5 | 10:00 | Bhangura | 26 | 18:00
Satmosjid | 99 | 13:00 | Shahmirpur | 33 | 18:00 | Rangpur | 112 | 18:30
Tongi | 112 | 18:00 | Khagrachhari | 26 | 18:30 | Lalmonirhat | 48 | 18:30
Kabirpur | 242 | 18:00 | Matarbari | 38.5 | 17:00 | Saidpur | 85 | 18:30
Basundhara | 172 | 18:00 | Baroiar Hat | 52 | 18:00 | Purbasadipur | 91 | 18:30
Manikganj | 66 | 18:30 | Rangamati | 13 | 18:00 | Thakurgaon | 63 | 18:30
Joydevpur | 166 | 18:00 | Abul Khair 230 | 6 | 2:00 | Palashbari | 91 | 18:30
New Tongi | 82 | 14:00 | BSRM | 158 | 7:00 | Barapukuria | 43 | 19:00
Kodda | 249 | 18:30 | GPH Ispat | 90 | 0:00 | Panchagar | 48 | 18:30
Dhamrai | 98 | 18:30 | Agrabad | 63 | 18:00 | Joldhaka | 28 | 18:00
Rajendrapur | 96 | 19:00 | Goalpara | 25 | 13:00 | Kurigram | 49 | 18:00
Valuka | 112 | 19:00 | Central S/S | 87 | 18:30 | Mithapukur | 25 | 18:00
Tangail | 186 | 19:00 | Noapara | 43 | 18:00
Mymensing | 173 | 18:30 | Jessore | 99 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 22:00 | 402 | 13:00 | Kaliakoir | 396 | 0.33333 | 385 | 0.45833
| Bheramara | 397 | 8:00 | 391 | 18:30 | Bhulta | 387 | 0.875 | 371 | 0.5
| Ashuganj(N) | 393 | 6:00 | 379 | 12:00 | Gopalganj | 409 | 0.625 | 388 | 0.875
| Payra | 413 | 8:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 13:00 | Hathazari | 236 | 18:00 | 215 | 10:00
| Ishurdi | 235 | 6:00 | 227 | 20:00 | Megnaghat | 234 | 8:00 | 226 | 4:00
| Ashuganj | 240 | 19:30 | 230 | 12:00 | Fenchuganj | 245 | 19:30 | 239 | 16:00
| Serajganj | 230 | 4:00 | 225 | 12:00 | Siddhirganj | 232 | 21:00 | 225 | 11:00
| Baghabari | 232 | 6:00 | 228 | 12:00 | Maniknagar | 231 | 21:00 | 222 | 12:00
| Barapukuria | 238 | 4:00 | 230 | 13:00 | Agargaon | 228 | 8:00 | 217 | 12:00
| Bogra | 227 | 5:00 | 219 | 13:00 | Barisal | 244 | 18:00 | 232 | 20:00
| Rajshahi | 231 | 18:00 | 218 | 13:00 | Bhola 225 MW | 247 | 6:00 | 239 | 21:00
| Khulna South | 2528 | 1:00 | 221 | 20:00 | AKSML | 234 | 18:00 | 217 | 4:00
| Rampura | 230 | 1:00 | 222 | 12:00 | BSRM | 234 | 18:30 | 218 | 11:00
| Haripur | 230 | 7:00 | 221 | 12:00 | Bibiyana | 244 | 8:00 | 237 | 16:00
| Hasnabad | 230 | 1:00 | 220 | 11:00 | Bhulta | 233 | 18:00 | 223 | 12:00
| Shyampur | 229 | 8:00 | 221 | 12:00 | Ashuganj (S) | 236 | 20:00 | 228 | 12:00
| Aminbazar | 229 | 1:00 | 25 | 2:00 | Kaliakoir | 229 | 20:00 | 218 | 13:00
| Tongi | 232 | 18:00 | 216 | 11:00 | GPH | 235 | 18:00 | 217 | 4:00
| Comilla (N) | 232 | 21:00 | 223 | 11:00 | Jhenaidah | 231 | 6:00 | 220 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 8:00 | 130 | 11:00 | Madanhat | 137 | 0.70833 | 126 | 0.625
| Munsiganj | 137 | 23:00 | 131 | 12:00 | Hathazari | 138 | 0.75 | 128 | 0.5
| Sonargaon | 135 | 18:00 | 129 | 12:00 | Khulshi | 136 | 0.75 | 123 | 0.45833
| Shyampur | 137 | 8:00 | 132 | 11:00 | Halishahar | 137 | 0.77083 | 124 | 0.41667
| Bhulta | 132 | 4:00 | 128 | 11:00 | Baraulia | 137 | 0.75 | 125 | 0.125
| Madanganj | 137 | 8:00 | 131 | 11:00 | Sikalbaha | 139 | 0.77083 | 125 | 0.41667
| Shitalakhya | 138 | 8:00 | 131 | 12:00 | Dohazari | 134 | 0.75 | 121 | 0.66667
| Rahim steal | 135 | 21:00 | 130 | 12:00 | Cox'sbazar | 121 | 0.75 | 111 | 0.5
| Matuail | 135 | 8:00 | 130 | 11:00 | Chandraghona | 136 | 0.75 | 129 | 0.16667
| Ghorasal | 140 | 1:00 | 136 | 10:00 | Kaptai | 136 | 0.75 | 130 | 0.45833
| Narsinghdi | 135 | 8:00 | 129 | 10:00 | A. Khaer Stl. | 135 | 0.75 | 125 | 0.41667
| Haripur (SBU) | 135 | 1:00 | 130 | 12:00 | Bakulia | 137 | 0.77083 | 124 | 0.41667
| Sreenagar | 134 | 1:00 | 129 | 12:00 | Julda | 137 | 0.75 | 126 | 0.375
| Ullon | 134 | 1:00 | 128 | 12:00 | TK Chemical | 138 | 0.75 | 125 | 0.45833
| Hasnabad | 135 | 1:00 | 131 | 15:00 | Modern Steel | 136 | 0.75 | 124 | 0.66667
| Magbazar | 135 | 1:00 | 128 | 12:00 | Shahmirpur | 138 | 0.77083 | 125 | 0.41667
| Maniknagar | 135 | 8:00 | 129 | 13:00 | Khagrachhari | 135 | 0.77083 | 127 | 0.45833
| Bangabhaban | 135 | 8:00 | 129 | 13:00 | Matarbari | 125 | 0.41667 | 115 | 0.125
| Motijheel | 135 | 8:00 | 129 | 13:00 | Baroiar Hat | 136 | 0.77083 | 126 | 0.125
| Narinda | 135 | 8:00 | 129 | 13:00 | Rangamati | 136 | 18:30 | 128 | 10:00
| Kazla | 144 | 7:00 | 129 | 13:00 | Agrabad | 135 | 18:00 | 124 | 11:00
| Dhanmondi | 134 | 5:00 | 129 | 12:00 | Goalpara S/S | 139 | 8:00 | 133 | 0.95833
| Lalbag | 134 | 1:00 | 121 | 12:00 | Khulna Central S/S | 138 | 7:00 | 133 | 0.8125
| Madartek | 135 | 6:00 | 127 | 12:00 | Noapara | 138 | 5:00 | 130 | 0.91667
| Dhaka University | 135 | 7:00 | 128 | 11:00 | Jessore | 137 | 8:00 | 128 | 0.8125
| Aftabnagar | 134 | 1:00 | 127 | 12:00 | Benapol | 137 | 0.33333 | 127 | 0.83333
| Fatullah | 137 | 8:00 | 131 | 12:00 | Jhenida(Old) | 139 | 8:00 | 130 | 0.83333
| Nawabganj | 136 | 8:00 | 128 | 12:00 | Bottail | 138 | 0.25 | 131 | 0.83333
| Keraniganj | 136 | 8:00 | 128 | 11:00 | G.K Project | 140 | 0.29167 | 136 | 0.8125
| Banani | 135 | 6:00 | 128 | 11:00 | Faridpur | 137 | 0.25 | 130 | 0.8125
| Mirpur | 131 | 1:00 | 123 | 11:00 | Rajbari | 138 | 0.25 | 129 | 0.8125
| Kalyanpur | 131 | 1:00 | 123 | 12:00 | Madaripur | 142 | 0.33333 | 133 | 0.8125
| Gulshan | 133 | 1:00 | 127 | 12:00 | Shariyatpur S/S | 141 | 6:00 | 131 | 0.83333
| Uttara | 131 | 1:00 | 123 | 10:00 | Gopalganj | 144 | 0.33333 | 132 | 0.83333
| Uttara New | 132 | 1:00 | 122 | 11:00 | Bagerhat | 137 | 6:00 | 128 | 0.83333
| Kamrangirchar | 135 | 7:00 | 128 | 11:00 | Mongla | 135 | 9:00 | 128 | 0.91667
| Savar | 132 | 1:00 | 122 | 11:00 | Satkhira | 137 | 5:00 | 129 | 20:00
| Bhasantec | 136 | 8:00 | 128 | 11:00 | Gallamari | 139 | 0.20833 | 128 | 20:00
| Agargaon | 137 | 3:00 | 128 | 12:00 | Magura | 140 | 8:00 | 130 | 0.8125
| Satmosjid | 136 | 1:00 | 129 | 11:00 | Narail | 137 | 0.25 | 128 | 0.83333
| Tongi | 138 | 19:30 | 130 | 11:00 | Chuadanga | 136 | 6:00 | 124 | 0.83333
| Kabirpur | 136 | 8:00 | 130 | 18:00 | Barisal(N) | 142 | 6:00 | 133 | 0.8125
| Basundhara | 136 | 19:00 | 126 | 11:00 | Barisal (S) | 140 | 7:00 | 131 | 20:00
| Manikganj | 141 | 5:00 | 134 | 18:00 | Patuakhali(S) | 139 | 0.16667 | 126 | 0.83333
| Joydevpur | 140 | 18:00 | 131 | 13:00 | Bhandaria | 140 | 0.25 | 127 | 0.83333
| New Tongi | 137 | 18:30 | 128 | 11:00 | Borguna | 141 | 0.33333 | 129 | 0.8125
| Kodda | 134 | 20:00 | 121 | 11:00 | Jhenaidah(230kV S/S) | 138 | 6:00 | 131 | 21:00
| Dhamrai | 137 | 6:00 | 129 | 16:00 | Ishurdi | 137 | 5:00 | 132 | 21:00
| Rajendrapur | 133 | 19:30 | 120 | 12:00 | Ruppur Paromanobik | 137 | 6:00 | 132 | 19:00
| Valuka | 130 | 8:00 | 119 | 18:00 | Natore | 136 | 6:00 | 130 | 12:00
| Tangail | 136 | 8:00 | 125 | 18:00 | Bogra | 135 | 6:00 | 130 | 13:00
| Mymensing | 133 | 8:00 | 124 | 17:00 | Noagaon | 132 | 6:00 | 125 | 13:00
| Kishorganj | 134 | 7:00 | 125 | 18:00 | Rajshahi | 135 | 7:00 | 129 | 12:00
| Netrokona | 132 | 7:00 | 121 | 16:00 | Rajshahi New | 137 | 18:00 | 129 | 20:00
| Jamalpur | 140 | 18:30 | 122 | 13:00 | C.Nawabganj | 134 | 6:00 | 127 | 13:00
| Sherpur | 138 | 18:30 | 119 | 2:00 | Amnura | 137 | 18:00 | 128 | 12:00
| Srimongal | 138 | 7:00 | 136 | 1:00 | Pabna | 136 | 6:00 | 131 | 13:00
| Shahjibazar | 137 | 10:00 | 133 | 18:00 | Shahjadpur | 138 | 1:00 | 134 | 16:00
| Fenchuganj | 137 | 8:00 | 133 | 16:00 | Serajganj | 135 | 1:00 | 130 | 15:00
| Khulawara | 136 | 9:00 | 133 | 3:00 | Niyamatpur | 131 | 6:00 | 121 | 1:00
| Sylhet | 133 | 1:00 | 131 | 18:00 | Joypurhat | 134 | 6:00 | 127 | 13:00
| Chatak | 134 | 10:00 | 131 | 18:00 | Sherpur(Bogura) | 135 | 5:00 | 129 | 13:00
| Sunamganj | 132 | 7:00 | 128 | 18:00 | Mohastangor | 134 | 6:00 | 128 | 13:00
| Biani Bazar | 133 | 6:00 | 130 | 16:00 | Bangura | 135 | 9:00 | 132 | 13:00
| Comilla(s) | 130 | 6:00 | 124 | 14:00 | Rangpur | 131 | 4:00 | 125 | 13:00
| Comilla(n) | 138 | 18:00 | 133 | 11:00 | Lalmonirhat | 133 | 6:00 | 123 | 18:00
| Chandpur | 137 | 19:00 | 131 | 1:00 | Saidpur | 134 | 6:00 | 125 | 13:00
| Feni | 138 | 18:30 | 126 | 16:00 | Purbasadipur | 134 | 4:00 | 122 | 18:00
| Chowmuhani | 134 | 6:00 | 127 | 16:00 | Thakurgaon | 134 | 4:00 | 125 | 18:00
| Ashuganj | 140 | 6:00 | 136 | 16:00 | Palashbari | 134 | 6:00 | 125 | 13:00
| Daudkandi | 134 | 18:00 | 128 | 11:00 | Barapukuria | 138 | 4:00 | 130 | 13:00
| B.Baria | 136 | 7:00 | 130 | 16:00 | Panchagar | 137 | 0.16667 | 124 | 0.75
| Ramganj | 136 | 18:30 | 126 | 3:00 | Joldhaka | 134 | 0.20833 | 122 | 0.75
| Chaddagram | 139 | 18:30 | 129 | 1:00 | Kurigram | 135 | 0.20833 | 126 | 0.75
| PHP | 137 | 18:30 | 126 | 2:00 | Mithapukur | 135 | 0.25 | 124 | 0.75
| Kochua | 137 | 18:00 | 130 | 2:00

## L-Curve
Date | 2021-10-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 52 | 6917 | 2870 | 9787 |  |  |  | QF-LDC-11
0:30 | 152 | 6526 | 2839.5 | 9365.5 | Date: | 2021-10-23
1:00 | 252 | 6135 | 2809 | 8944
1:30 | 294 | 5944.5 | 2806 | 8750.5
2:00 | 336 | 5754 | 2803 | 8557
2:30 | 341 | 5659 | 2752.5 | 8411.5 | [5 empty] | Gen. at Eve. Peak | 11457 | 11457 MW (19:00 )
3:00 | 346 | 5564 | 2702 | 8266 | [6 empty] | 19:00
3:30 | 378 | 5521.5 | 2671.5 | 8193 | [5 empty] | Gen. at Day Peak | 8710 | 8710 MW (12:00 )
4:00 | 410 | 5479 | 2641 | 8120 | [6 empty] | 12:00
4:30 | 435 | 5385.5 | 2626 | 8011.5 | [5 empty] | Highest Generation | 11457
5:00 | 460 | 5292 | 2611 | 7903 | [6 empty] | 19:00
5:30 | 462 | 5231 | 2586.5 | 7817.5
6:00 | 464 | 5170 | 2562 | 7732
6:30 | 350 | 5182 | 2522.5 | 7704.5
7:00 | 236 | 5194 | 2483 | 7677
7:30 | 256 | 5227 | 2455.5 | 7682.5
8:00 | 276 | 5260 | 2428 | 7688
8:30 | 322 | 5313 | 2372 | 7685
9:00 | 368 | 5366 | 2316 | 7682
9:30 | 411 | 5471.5 | 2372.5 | 7844
10:00 | 454 | 5577 | 2429 | 8006
10:30 | 467 | 5689.5 | 2473 | 8162.5
11:00 | 480 | 5802 | 2517 | 8319
11:30 | 438 | 5899 | 2615.5 | 8514.5
12:00 | 396 | 5996 | 2714 | 8710
12:30 | 356 | 6079.5 | 2722 | 8801.5
13:00 | 316 | 6163 | 2730 | 8893
13:30 | 278 | 6275.5 | 2693 | 8968.5
14:00 | 240 | 6388 | 2656 | 9044
14:30 | 320 | 6406.5 | 2713 | 9119.5
15:00 | 400 | 6425 | 2770 | 9195
15:30 | 440 | 6370.5 | 2763 | 9133.5
16:00 | 480 | 6316 | 2756 | 9072
16:30 | 390 | 6373 | 2729 | 9102
17:00 | 300 | 6430 | 2702 | 9132
17:30 | 156 | 7053.5 | 2974.5 | 10028
18:00 | 12 | 7677 | 3247 | 10924
18:30 | 54 | 7906.5 | 3284 | 11190.5
19:00 | 96 | 8136 | 3321 | 11457
19:30 | 74 | 8055 | 3302 | 11357
20:00 | 64 | 7836 | 3289 | 11125 |  |  |  | Executive Engineer
20:30 | 82 | 7780 | 3216.5 | 10996.5 |  |  |  | Network Operation Division
21:00 | 100 | 7724 | 3144 | 10868
21:30 | 57 | 7629.5 | 3138 | 10767.5
22:00 | 14 | 7535 | 3132 | 10667 |  |  |  |  | Page 6 of 7
22:30 | 30 | 7353.5 | 3073.5 | 10427
23:00 | 46 | 7172 | 3015 | 10187
23:30 | 49 | 7044.5 | 2942.5 | 9987
24:00 | 52 | 6917 | 2870 | 9787
11457 MW (19:00 )
8710 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-23 |  | Energy |  | 217084971
[13 empty] | 2021-10-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4269 | 715 | 2243 | 0 | 1604 | 511 | 165 | 120 | 34 | 126 | 0 | 0
0:30 | 4041.5 | 714 | 2286.5 | 0 | 1408.5 | 490 | 165 | 120 | 17 | 123 | 0 | 0 | Date: | 2021-10-23
1:00 | 3814 | 713 | 2330 | 0 | 1213 | 469 | 165 | 120 | 0 | 120 | 0 | 0
1:30 | 3818.5 | 713.5 | 2354 | 0 | 997.5 | 464.5 | 164.5 | 120 | 0 | 118 | 0 | 0 | [8 empty] | Total Energy | 217.085 | Total Energy Gen 217.085 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 217.085 MKWHr
2:00 | 3823 | 714 | 2378 | 0 | 782 | 460 | 164 | 120 | 0 | 116 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3820.5 | 714 | 2345.5 | 0 | 689.5 | 445 | 162 | 120 | 0 | 115 | 0 | 0 | [8 empty] | Energy Requirement | 217.085
3:00 | 3818 | 714 | 2313 | 0 | 597 | 430 | 160 | 120 | 0 | 114 | 0 | 0
3:30 | 3847.5 | 713.5 | 2282 | 0 | 543 | 415 | 160 | 120 | 0 | 112 | 0 | 0 | [6 empty] | Shortage
4:00 | 3877 | 713 | 2251 | 0 | 489 | 400 | 160 | 120 | 0 | 110 | 0 | 0
4:30 | 3832 | 713 | 2194.5 | 0 | 481 | 400 | 160 | 120 | 0 | 111 | 0 | 0
5:00 | 3787 | 713 | 2138 | 0 | 473 | 400 | 160 | 120 | 0 | 112 | 0 | 0
5:30 | 3783.5 | 713.5 | 2058.5 | 0 | 474.5 | 400.5 | 160 | 120 | 0 | 107 | 0 | 0
6:00 | 3780 | 714 | 1979 | 0 | 476 | 401 | 160 | 120 | 0 | 102 | 0 | 0
6:30 | 3712 | 714 | 2007.5 | 0 | 486 | 401 | 160 | 120 | 0 | 97 | 7 | 0 |  |  |  |  | Coal
7:00 | 3644 | 714 | 2036 | 0 | 496 | 401 | 160 | 120 | 0 | 92 | 14 | 0
7:30 | 3626 | 714 | 1961.5 | 0 | 575 | 401 | 160.5 | 120 | 0 | 98 | 26.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3608 | 714 | 1887 | 0 | 654 | 401 | 161 | 120 | 0 | 104 | 39 | 0
8:30 | 3556 | 714 | 1880.5 | 0 | 704 | 400.5 | 161.5 | 120 | 0 | 106 | 42.5 | 0
9:00 | 3504 | 714 | 1874 | 0 | 754 | 400 | 162 | 120 | 0 | 108 | 46 | 0
9:30 | 3503 | 713.5 | 1969 | 0 | 805.5 | 400.5 | 162 | 120 | 0 | 108 | 62.5 | 0
10:00 | 3502 | 713 | 2064 | 0 | 857 | 401 | 162 | 120 | 0 | 108 | 79 | 0
10:30 | 3550.5 | 713 | 2126.5 | 0 | 894 | 401 | 161.5 | 120 | 0 | 114 | 82 | 0
11:00 | 3599 | 713 | 2189 | 0 | 931 | 401 | 161 | 120 | 0 | 120 | 85 | 0
11:30 | 3681 | 713.5 | 2287.5 | 0 | 954.5 | 401.5 | 161 | 120 | 0 | 122 | 73.5 | 0
12:00 | 3763 | 714 | 2386 | 0 | 978 | 402 | 161 | 120 | 0 | 124 | 62 | 0
12:30 | 3773.5 | 714 | 2379 | 0 | 1064 | 402 | 161 | 120 | 0 | 123 | 65 | 0
13:00 | 3784 | 714 | 2372 | 0 | 1150 | 402 | 161 | 120 | 0 | 122 | 68 | 0
13:30 | 3784 | 714 | 2372 | 0 | 1150 | 402 | 161 | 120 | 0 | 122 | 68 | 0
14:00 | 3784 | 714 | 2372 | 0 | 1150 | 402 | 161 | 120 | 0 | 122 | 68 | 0
14:30 | 3837 | 714 | 2341 | 0 | 1282 | 403 | 162.5 | 120 | 0 | 128 | 56.5 | 0
15:00 | 3890 | 714 | 2310 | 0 | 1414 | 404 | 164 | 120 | 0 | 134 | 45 | 0
15:30 | 3890.5 | 714 | 2306 | 0 | 1372.5 | 404 | 162 | 120 | 0 | 130 | 34.5 | 0
16:00 | 3891 | 714 | 2302 | 0 | 1331 | 404 | 160 | 120 | 0 | 126 | 24 | 0
16:30 | 3898 | 714.5 | 2299 | 0 | 1357.5 | 403 | 160 | 120 | 12 | 124 | 14 | 0
17:00 | 3905 | 715 | 2296 | 0 | 1384 | 402 | 160 | 120 | 24 | 122 | 4 | 0
17:30 | 4046.5 | 715 | 2286 | 0 | 1961.5 | 421 | 160 | 120 | 182 | 134 | 2 | 0
18:00 | 4188 | 715 | 2276 | 0 | 2539 | 440 | 160 | 120 | 340 | 146 | 0 | 0
18:30 | 4206.5 | 715 | 2220.5 | 0 | 2852.5 | 475 | 160 | 120 | 297 | 144 | 0 | 0
19:00 | 4225 | 715 | 2165 | 0 | 3166 | 510 | 160 | 120 | 254 | 142 | 0 | 0
19:30 | 4231 | 715 | 2248 | 0 | 3077 | 550 | 160 | 120 | 114 | 142 | 0 | 0
20:00 | 4242 | 714 | 2356 | 0 | 2781 | 560 | 162 | 120 | 54 | 136 | 0 | 0
20:30 | 4256 | 714 | 2313.5 | 0 | 2681.5 | 570.5 | 161 | 120 | 44 | 136 | 0 | 0
21:00 | 4270 | 714 | 2271 | 0 | 2582 | 581 | 160 | 120 | 34 | 136 | 0 | 0
21:30 | 4271.5 | 714.5 | 2291.5 | 0 | 2465 | 576 | 160 | 120 | 34 | 135 | 0 | 0
22:00 | 4273 | 715 | 2312 | 0 | 2348 | 571 | 160 | 120 | 34 | 134 | 0 | 0
22:30 | 4272 | 714.5 | 2308.5 | 0 | 2124.5 | 561 | 160.5 | 120 | 34 | 132 | 0 | 0
23:00 | 4271 | 714 | 2305 | 0 | 1901 | 551 | 161 | 120 | 34 | 130 | 0 | 0
23:30 | 4270 | 714.5 | 2274 | 0 | 1752.5 | 531 | 163 | 120 | 34 | 128 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.8° C
24:00 | 4269 | 715 | 2243 | 0 | 1604 | 511 | 165 | 120 | 34 | 126 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 217.085 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 217.085 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 89 | 85 | 85 | 85 | 85 | 85 | 86 | 87 | 87 | 86 | 86 | 86 | 89 | 89 | 85 | 85 | 85 |  | 85 | 85 | 87 | 85 | 85 | 86 | 90 | 2006476
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1804000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 8 | 16 | 16 | 16 | 16 |  | 0 | 67163
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 1 | 3 | 20 | 20 | 16 | 13 | 16 | 11 | 6 | 1 | [9 empty] | 98145
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 102 |  | 68 | 34 | 34 | 34 | 34 | 34 | 34 | 334899
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | [11 empty] | 5 | 34 | 34 | 17 | 17 | 55 |  | 105 | 105 | 105 | 105 | 105 | 85 | 17 | 838032
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 50 | [7 empty] | 0 | 52272
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 92 | 92 | 92 | 60 | 60 | 57 | 60 | 57 | 57 | 60 | 60 | 97 | 98 | 95 | 95 | 95 | 35 | [8 empty] | 0 | 1372000
17 | Siddhirganj 335 MW CCPP | [12 empty] | 7 | 0 | 0 | 0 | 65 | 338 |  | 316 | 335 | 335 | 335 | 335 | 335 | 335 | 2289965
18 | Kodda 300 MW PP Unit-2 (Summit) | [13 empty] | 10 | 15 | 15 | 17 | 216 |  | 300 | 300 | 240 | 140 | 15 |  | 0 | 1146654
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1873454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4252500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3262380
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 20 | 23 | 23 | 19 | 19 | 26 | 25 | 29 | 23 | 26 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 572256
33 | Ashuganj 225 MW CCPP | 34 | 34 | 35 | 149 | 148 | 114 | 111 | 111 | 111 | 111 | 117 | 141 | 141 | 141 | 140 | 139 | 142 | 143 |  | 143 | 141 | 143 | 144 | 142 | 143 | 144 | 2906000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 260 | 260 | 280 | 260 | 290 | 270 | 325 | 280 | 295 | 310 | 350 | 355 | 330 | 330 |  | 335 | 335 | 335 | 335 | 340 | 335 | 335 | 7813500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 54 | 55 | 53 | 54 | 54 | 55 |  | 55 | 55 | 56 | 56 | 56 | 55 | 56 | 1325280
36 | Chandpur 150 MW CCPP | 138 | 139 | 139 | 136 | 136 | 136 | 139 | 137 | 137 | 139 | 139 | 140 | 138 | 138 | 139 | 139 | 136 | 137 |  | 138 | 138 | 138 | 138 | 137 | 139 | 139 | 2145990
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 394 | 394 | 395 | 388 | 350 | 350 | 350 | 343 | 301 | 302 | 302 | 358 | 398 | 390 | 365 | 363 | 388 | 367 |  | 401 | 401 | 401 | 401 | 400 | 400 | 399 | 9023480
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6161750
41 | Haripur 360MW CCPP(HPL) | 338 | 336 | 336 | 336 | 337 | 307 | 271 | 271 | 273 | 303 | 332 | 332 | 331 | 281 | 302 | 302 | 326 | 333 |  | 302 | 301 | 333 | 337 | 337 | 337 | 337 | 7574000
42 | RPCL 210MW CCPP | 212 | 215 | 213 | 215 | 215 | 217 | 212 | 216 | 211 | 208 | 186 | 186 | 183 | 169 | 169 | 182 | 185 | 186 |  | 185 | 181 | 184 | 186 | 189 | 187 | 187 | 4600880
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 22 | 35 | 45 | 51 | 35 | 40 | 38 | 25 | 13 | 2 | [9 empty] | 323090
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1005120
46 | Shajibazar 330 MW CCPP | 110 | 109 | 110 | 110 | 110 | 111 | 109 | 110 | 112 | 111 | 110 | 110 | 110 | 110 | 108 | 107 | 109 | 112 |  | 110 | 109 | 110 | 110 | 108 | 109 | 110 | 2481000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 51 | 52 | 51 | 51 | 60 | 60 | 61 | 60 | 60 | 60 | 61 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1425504
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 77 | 30 | 30 | 30 | 30 | 10 | 78 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1621440
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 193 | 189 | 178 | 179 | 179 | 199 | 206 | 220 | 219 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 217 | 217 | 217 | 217 | 5009600
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 398000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245520
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 195360
55 | Fenchugonj 51 MW PP (Barakatullah) | 41 | 41 | 41 | 41 | 14 | 14 | 14 | 14 | 14 | 14 | 35 | 41 | 39 | 39 | 39 | 39 | 39 | 39 |  | 41 | 44 | 44 | 44 | 44 | 44 | 44 | 814200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 504937
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 290 | 285 | 285 | 270 | 290 | 270 | 270 | 290 | 300 | 320 | 310 | 280 | 310 | 300 | 310 | 290 |  | 275 | 300 | 290 | 295 | 290 | 290 | 280 | 7139500
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 385 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7704000
58 | Nababganj 55 MW PP (Southern power ) | 17 | [5 empty] | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 924402
59 | Tangail Palli Power Gen 22 MW | [17 empty] | 2 |  | 9 | 23 | 23 | 23 |  |  | 0 | 62640
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418704
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 12 | 19 | 19 | 411984
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496404
63 | Impoprt (Tripura) | 120 | 116 | 114 | 110 | 112 | 102 | 92 | 104 | 108 | 108 | 120 | 124 | 122 | 136 | 134 | 126 | 122 | 146 |  | 142 | 142 | 136 | 136 | 134 | 130 | 126 | 2928960
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 37 | 10 | 2 | 2 | 2 | 2 | 5 | 3 | 2 | 2 | 3 | 7 |  | 10 | 11 | 15 | 25 | 28 | 28 | 29 | 527040
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 467316
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 7 | 7 | 9 | 9 | 9 | 9 | 9 | 138960
67 | Jangalia 33MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 365900
68 | Cumilla 25 MW PP (Summit) | [5 empty] | 18 | 15 | 10 | 10 | 10 | 10 | 16 | 16 | 16 | 20 | 21 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 453350
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 20 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 546840
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 824900
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 532136
| Feni Lanka Power | [17 empty] | 60 |  | 62 | 31 |  |  |  |  | 0 | 159600
| Chowmuhani 113 MW | 63 | 60 | 63 | 60 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 52 | 49 | 53 | 59 | 96 |  | 96 | 97 | 97 | 97 | 97 | 92 | 62 | 1633800
| Manikgonj 162MW PP(MPGL) | 108 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 52 | 54 | 54 | 106 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 1788480
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [16 empty] | 21 | 27 |  | 51 | 51 | 51 | 51 | 51 | 8 | 0 | 289920
79 | Kodda 150MW PP | [16 empty] | 10 | 32 |  | 48 | 10 |  |  |  |  | 0 | 70080
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [12 empty] | 2 | 8 | 8 | 8 | 106560
81 | Jangalia 52 MW PP (Lakdanavi) | [22 empty] | 4 |  |  |  | 15379
| Gazipur 100 MW PP | [17 empty] | 25 |  | 60 | 90 | 70 | 50 | 35 |  | 0 | 336000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 3 | 4 | 4 | 3 | 1 | 1 | 0 | [9 empty] | 25320
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432701
| Karnaphuli Power Ltd. | 17 | [11 empty] | 5 | 27 | 34 | 17 | 17 | 57 |  | 108 | 110 | 68 | 68 | 68 |  | 0 | 651524
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [6 empty] | 6 | 24 | 24 | 24 | 24 | 24 | 23 | 13 | 18 | 23 | 24 | 24 |  | 23 | 24 | 25 | 32 | 33 | 25 | 0 | 407294
86 | Meghnaghat CCPP ( Summit) | 260 | 270 | 270 | 265 | 280 | 250 | 285 | 240 | 290 | 275 | 290 | 280 | 285 | 270 | 285 | 285 | 270 | 245 |  | 260 | 280 | 260 | 260 | 275 | 270 | 260 | 6485498
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | [7 empty] | 1 | 16 | 17 | 17 | 20 | 53 | 53 | 50 | 18 | 59 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1006080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 77 |  | 20 | 10 |  |  |  |  | 0 | 90360
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1254820
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 3 | 48 | 72 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1648368
95 | Patenga 50MW PP (Baraka) | [17 empty] | 14 |  | 47 | 46 | 19 | 19 |  |  | 0 | 122360
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [6 empty] | 38 |  | 65 | [5 empty] | 0 | 104640
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 44 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1046023
100 | Manikganj 55 MW PP (Northern) | 17 | [11 empty] | 17 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 566688
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 130 | 163 | 163 | 130 | 130 | 130 | 163 | 163 |  | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 3539700
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 0 | 0 | 0 | [9 empty] | 12050
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1291320
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 62 |  | 120 | 100 | 80 | 80 | 80 | 35 | 8 | 590400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 48 | 35 | 26 | 21 | 21 | 25 | 15 | 20 | 68 | 68 | 68 | 80 | 100 | 100 | 100 | 100 | 100 | 107 |  | 149 | 149 | 144 | 120 | 100 | 85 | 85 | 1837010
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 |  | 76 | 76 | 76 | 76 | 90 | 90 | 90 | 1926720
116 | Chandpur 200MW (Desh energy) | [12 empty] | 1 | 12 | 17 | 17 | 17 | 65 |  | 139 | 140 | 100 | 100 | 100 | 17 | 0 | 704640
117 | Ashuganj 150MW PP (Midland) | 130 | 100 | 50 | 24 | 10 | 10 | 10 | 10 | 10 | 28 | 50 | 50 | 61 | 95 | 115 | 115 | 113 | 123 |  | 125 | 125 | 125 | 128 | 130 | 130 | 133 | 1970472
118 | Bibiyana-III 400 MW CCPP | 323 | 322 | 322 | 322 | 322 | 322 | 322 | 324 | 323 | 240 | 318 | 322 | 238 | 402 | 322 | 323 | 322 | 324 |  | 323 | 323 | 323 | 323 | 323 | 324 | 323 | 7663000
| Jamalpur 115 MW PP (United) | 85 | 35 | 35 | 16 | 16 | 16 | 16 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 90 |  | 115 | 115 | 115 | 115 | 115 | 109 | 109 | 1614000
| Anwara 300 MW PP (United) | 305 | 197 | 105 | 70 | 70 | 69 | 70 | 70 | 70 | 88 | 124 | 157 | 211 | 213 | 213 | 176 | 253 | 303 |  | 304 | 304 | 305 | 305 | 305 | 305 | 305 | 4591636
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 78 | 78 | 78 | 2231040
| Anlima Energy Ltd. | 53 | [9 empty] | 15 | 17 | 22 | 53 | 53 | 35 | 35 | 80 |  | 116 | 116 | 116 | 116 | 116 | 116 | 72 | 1150418
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 437040
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 11 | [18 empty] | 11735
120 | Eastern Zone Total | 6135 | 5754 | 5564 | 5479 | 5292 | 5170 | 5194 | 5260 | 5366 | 5577 | 5802 | 5996 | 6163 | 6388 | 6425 | 6316 | 6430 | 7677 |  | 8136 | 8055 | 7836 | 7724 | 7535 | 7172 | 6917 | 152513859
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3005760
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 53 |  | 86 | 53 | 53 | 17 | 17 |  | 0 | 270720
130
131
132 | United Payra Power Ltd. | [17 empty] | 14 | [7 empty] | 0 | 26400
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 223 | 223 | 223 | 180 | 142 | 142 | 139 | 141 | 142 | 162 | 222 | 221 | 221 | 220 | 220 | 221 | 220 |  | 223 | 223 | 223 | 222 | 223 | 223 | 207 | 483063
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 22 | 17 | 17 | 17 | 478425
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 67 | 66 | 66 | 66 | 66 | 67 | 62 |  | 67 | 68 | 68 | 68 | 68 | 69 | 69 | 1577000
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 20 | 20 | 18 | 16 | 15 | 15 | 16 | 18 | 19 | 19 | 20 | 20 | 18 | 19 | 25 |  | 27 | 29 | 29 | 29 | 28 | 28 | 26 | 508403
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 713 | 714 | 714 | 713 | 713 | 714 | 714 | 714 | 714 | 713 | 713 | 714 | 714 | 713 | 714 | 714 | 715 | 715 |  | 715 | 715 | 714 | 714 | 715 | 714 | 715 | 17260363
147 | Bheramara 410 MW CCPP | 395 | 370 | 350 | 350 | 350 | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 340 | 340 | 340 | 340 | 320 | 410 |  | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 8659008
148 | Payra 1320 MW | 390 | 380 | 350 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 360 |  | 430 | 470 | 480 | 500 | 490 | 470 | 430 | 9689400
149
150 | Barapukuria TPP Unit-1 | 79 | 80 | 80 | 80 | 80 | 81 | 81 | 81 | 80 | 81 | 81 | 82 | 82 | 82 | 84 | 84 | 82 | 80 |  | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 1937018
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 28 |  | 43 | [6 empty] | 61480
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 2 | 3 | 1 | 0 | [9 empty] | 31260
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 112 | 113 | 115 | 97 | 94 | 115 | [19 empty] | 0 | 713800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 177 | 177 | 178 | 165 | 163 | 166 | 165 | 164 | 130 | 130 | 178 | 198 | 181 | 176 | 177 | 169 | 180 | 169 |  | 166 | 162 | 164 | 177 | 180 | 176 | 178 | 4330527
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 49 | 83 | 94 | 113 | 143 | 182 | 176 | 174 | 130 | 153 | 158 | 173 | 190 | 179 | 195 | 195 | 198 | 173 |  | 170 | 166 | 167 | 182 | 187 | 183 | 183 | 4109269
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 412 | 348 | 331 | 319 | 295 | 340 | 287 | 250 | 335 | 341 | 422 | 415 | 348 | 419 | 419 | 358 | 365 |  | 308 | 341 | 409 | 308 | 341 | 340 | 314 | 8423018
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 | [8 empty] | 7371
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 503760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 195786
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 | [8 empty] | 38480
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 24 | [8 empty] | 51065
167 | Katakhali 50 MW Peaking PP | [17 empty] | 28 | [8 empty] | 39744
168 | Santahar 50 MW Peaking PP | [25 empty] | 0 | 0
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 6 |  | 8 | [5 empty] | 0 | 50880
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 14 | 95 |  | 95 | 70 | 20 |  |  |  |  | 228472
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | [12 empty] | 17 | 35 | 35 | 35 | 52 |  | 110 | 113 | 113 | 113 | 113 | 113 | 90 | 918720
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 70 |  | 100 | 113 | 70 | 35 | 35 |  | 0 | 395040
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 90 |  | 107 | 113 | 113 | 113 | 74 | 38 | 0 | 549945
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 4 |  | 6 |  | 5 | 3 | 1 | [9 empty] | 26935
178
178