## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-10-30 | Saturday
|  |  | Date (day): | 2021-10-30 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13594.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14749 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-29 | 2021-10-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22 | 86 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 334 | 346 | 360 | 360 | 52 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 256 | 280 | 315 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 240 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 24 | 40 | 40 |  | 60 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 213 | 82 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 48 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 25 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 17 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 25 | 185 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 78 | 80 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2019 | 2316 | 3343 | 3718 | 668 | 1130
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 158 | 158 | 158 | 158 | 72 |  | Unit 2 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 55 | 51 | 100
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 50 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 28 | 36 | 40 | 40
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 159 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 21 | 35 | 36 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 76 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 53 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 733 | 1286 | 1509 | 1571 | 137 | 685
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 130 | 110 | 110 | 110 | 25 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 217 | 200 | 215
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 285 | 320 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 365 | 265 | 320 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 51 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 21 | 118 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 139 | 136 | 138 | 138 |  | 25 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 22 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 120 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 41 | 96 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1528 | 1877 | 2114 | 2375 | 475 | 111
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 179 | 180 | 180 | 22 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 8 | 8 | 8 |  |  | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 94 | 181 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 45 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 324 | 450 | 598.6 | 547 | 22 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 31 | 42 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 130 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 70 | 90 | 110 | 110 |  | 220 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 28 | 44 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 62 | 60 | 65
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 81 | 81 | 81
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 202 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 240 | 270 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 242 | 322 | 324 | 324 | 76 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 220 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1252 | 1668 | 1817 | 1822 | 139 | 395
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 701 | 701 | 716 | 716
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 220 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 300 | 300
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 22 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 32 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 843 | 958 | 1391 | 1611 | 0 | 93
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 27 | 28 | 28
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 21 | 22 | 22 | 58 | 37 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 430 | 530 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 201 | 207 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 737 | 886 | 1065 | 1251 | 37 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 178 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 180 | 210 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 387 | 345 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52 |  | 9 | Engine problem
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 95 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 43 | 94 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 904 | 1145 | 1556 | 1661 | 310 | 105
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 79 | 81 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 12 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 98 | 194 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 8438 | 10780 | 13594.6 | 14749 | 1788 | 3047
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8091.2436 | 10337 | 13035.9351 | 14142.8955
| A. |  | 2021-10-29 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 10780 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7690 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10780 | MW
| 3 | Day peak Generation : |  |  | 8438 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10337 | MW
| 4 | Evening peak Generation : |  |  | 10780 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 222.6569 | MKWHr | By Solar | 0.8313 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 136.3925 | MKWHr |  | By Oil: | 48.3765 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.6963 | MKWHr |  | By Hydro: | 3.7767 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1788 | MW | Dhaka | 3597 | 3597 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3047 | MW | Chittagong | 1208 | 1208 |  | 0 |  | 18:00 |  | 128
|  |  |  | Total = |  |  | 4835 | MW | Khulna | 1243 | 1243 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1065.8 | MMCFD |  |  | Rajshahi | 985 | 985 |  | 0 |  | 19:00 |  | 120
| 8 | Fuel Cost : | i) Gas : | Taka | 142660788.072 | ii) Oil : | Taka | 365888375.33 | Comilla | 1077 | 1077 |  | 0 |  | 19:30 |  | 120
|  |  | iii) Coal : |  | 63188091.92 | Total | Taka | 571737255.322 | Mymensingh | 853 | 853 |  | 0 |  | 20:00 |  | 120
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.101 | MKWHr. | Sylhet | 473 | 473 |  | 0 |  | 21:00 |  | 120
|  | ii) During Peak Demand : |  |  | -102 | MW (E to W) at | 19:00 | hrs | Barisal | 309 | 309 |  | 0 |  | 22:00 |  | 122
|  | iii) Maximum : |  |  | -102 | MW at | 19:00 | hrs | Rangpur | 592 | 592 |  | 0 |  | 23:00 |  | 114
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.2° C |  |  | Total | 10337 | 10337 |  | 0
| B. |  | 2021-10-30 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 31.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14749 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3049 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 241.6592 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7764 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.9687 | MKWHr. | ii) HVDC Flow at Peak Time |  | 701 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.615 | MKWHr. | iii) Maximum HVDC Flow : |  | 714 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.2 |  | (b) Today: | 104.04 |  | (c) Rule Curve: |  | 108.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 346 | 251 |  | 0 | 250 | 250 | 0 | 0 | 45 | 227 | 0 | 0 | 0 | 64 | 0 | 25 | 0 | 0 | 0 | 54 | 0 | 55 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 91 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 33 | 18 | 38 | 80 | 0 | 0 | 300 | 300 | 218 | 8 | 136 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 120 | 150 | 0 | 22 | 0 | 43 | 42 | 44 | 0 | 120 | 71 | 40 | 81 | 0 | 192 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 0 | 76 | 120 | 135 | 322 | 0 | 0 | 105 | 0 | 302 | 35 | 110 | 0 | 50 | 100 | 320 | 104 | 0 | 162 | 35 | 0 | 17 | 0 |  | 714 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 23 | 0 | 185 | 0 | 371 | 105 | 0 | 113 | 0 | 0 | 0 | 0 | 70 | 500 | 200 | 0 | 0 | 0 |  | 6969 | 2853 | 9822 | 3781 | 714 | 2086 | 0 | 2165 | 578 | 161 | 200 | 17 | 120 | 0 | 0 | 104.22
2:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 345 | 271 |  | 0 | 250 | 255 | 0 | 0 | 55 | 227 | 0 | 0 | 0 | 64 | 0 | 25 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 91 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 33 | 18 | 38 | 80 | 0 | 0 | 300 | 300 | 217 | 8 | 136 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 118 | 158 | 0 | 22 | 0 | 43 | 42 | 44 | 0 | 120 | 70 | 40 | 81 | 0 | 179 | 18 | 0 | 10 | 240 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 0 | 76 | 85 | 80 | 240 | 0 | 0 | 105 | 0 | 302 | 35 | 110 | 0 | 51 | 70 | 270 | 104 | 0 | 162 | 0 | 0 | 17 | 0 |  | 713 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 23 | 0 | 187 | 0 | 410 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 470 | 202 | 0 | 0 | 0 |  | 6620 | 2716 | 9336 | 3644 | 713 | 2101 | 0 | 1835 | 547 | 161 | 200 | 17 | 118 | 0 | 0 | 104.21
3:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 345 | 293 |  | 0 | 250 | 270 | 0 | 0 | 55 | 227 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 92 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 38 | 80 | 0 | 0 | 300 | 300 | 217 | 8 | 137 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 114 | 160 | 0 | 22 | 0 | 43 | 42 | 44 | 0 | 130 | 71 | 40 | 81 | 0 | 179 | 18 | 0 | 10 | 240 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 100 | 0 | 90 | 51 | 20 | 240 | 0 | 0 | 105 | 0 | 304 | 35 | 110 | 0 | 49 | 70 | 270 | 104 | 0 | 162 | 0 | 0 | 17 | 0 |  | 701 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 187 | 0 | 389 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 470 | 202 | 0 | 0 | 0 |  | 6500 | 2586 | 9086 | 3634 | 701 | 2126 | 0 | 1630 | 549 | 162 | 170 | 0 | 114 | 0 | 0 | 104.2
4:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 344 | 306 |  | 0 | 250 | 250 | 0 | 0 | 55 | 225 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 92 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 18 | 38 | 80 | 0 | 0 | 300 | 305 | 216 | 8 | 138 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 110 | 160 | 0 | 22 | 0 | 43 | 42 | 44 | 0 | 130 | 70 | 40 | 81 | 0 | 179 | 18 | 0 | 10 | 240 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 90 | 34 | 20 | 240 | 0 | 0 | 68 | 0 | 307 | 35 | 110 | 0 | 48 | 20 | 220 | 67 | 0 | 162 | 0 | 0 | 17 | 0 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 23 | 0 | 188 | 0 | 419 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 440 | 202 | 0 | 0 | 0 |  | 6252 | 2525 | 8777 | 3608 | 702 | 2148 | 0 | 1408 | 519 | 162 | 120 | 0 | 110 | 0 | 0 | 104.22
5:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 350 | 318 |  | 0 | 250 | 255 | 0 | 0 | 55 | 200 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 91 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 38 | 80 | 0 | 0 | 330 | 325 | 216 | 8 | 138 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 108 | 160 | 0 | 22 | 0 | 31 | 32 | 28 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 95 | 0 | 90 | 34 | 20 | 240 | 0 | 0 | 68 | 0 | 302 | 35 | 110 | 0 | 50 | 20 | 220 | 53 | 0 | 162 | 0 | 0 | 17 | 0 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 23 | 0 | 185 | 0 | 335 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 440 | 202 | 0 | 0 | 0 |  | 6118 | 2424 | 8542 | 3564 | 702 | 2003 | 0 | 1365 | 519 | 161 | 120 | 0 | 108 | 0 | 0 | 104.21
6:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 353 | 331 |  | 0 | 250 | 245 | 0 | 0 | 55 | 150 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 89 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 40 | 80 | 0 | 0 | 300 | 300 | 218 | 8 | 136 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 100 | 163 | 0 | 22 | 0 | 31 | 32 | 28 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 23 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 77 | 0 | 90 | 17 | 10 | 240 | 0 | 0 | 68 | 0 | 305 | 35 | 110 | 0 | 48 | 20 | 220 | 53 | 0 | 162 | 0 | 0 | 17 | 0 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 23 | 0 | 168 | 0 | 295 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 410 | 182 | 0 | 0 | 0 |  | 5936 | 2300 | 8236 | 3447 | 702 | 1948 | 0 | 1271 | 489 | 159 | 120 | 0 | 100 | 0 | 0 | 104.2
7:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 334 | 316 |  | 0 | 250 | 255 | 0 | 0 | 55 | 150 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 290 | 310 | 190 | 8 | 138 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 25 | 20 | 90 | 162 | 0 | 22 | 0 | 30 | 32 | 28 | 0 | 110 | 72 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 23 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 70 | 2 | 10 | 0 | 10 | 240 | 0 | 0 | 17 | 1 | 304 | 35 | 73 | 0 | 48 | 10 | 220 | 0 | 7 | 108 | 0 | 0 | 17 | 3 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 22 | 0 | 158 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 182 | 0 | 0 | 0 |  | 5543 | 2243 | 7786 | 3376 | 702 | 1979 | 0 | 900 | 448 | 158 | 120 | 0 | 90 | 13 | 0 | 104.19
8:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 335 | 314 |  | 0 | 250 | 250 | 0 | 0 | 55 | 150 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 27 | 33 | 33 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 80 | 0 | 0 | 280 | 290 | 171 | 8 | 138 | 23 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 25 | 20 | 86 | 160 | 0 | 22 | 1 | 30 | 32 | 28 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 23 | 8 | 0 | 0 | 0 | 0 | 63 | 0 | 70 | 11 | 10 | 0 | 10 | 240 | 0 | 0 | 17 | 2 | 304 | 35 | 34 | 0 | 49 | 10 | 220 | 0 | 24 | 108 | 0 | 0 | 17 | 11 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 22 | 0 | 166 | 0 | 339 | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 0 | 370 | 182 | 0 | 0 | 2 |  | 5485 | 2272 | 7757 | 3328 | 702 | 1972 | 0 | 890 | 448 | 158 | 120 | 0 | 86 | 53 | 0 | 104.18
9:00 | 0 | 0 | 0 | 110 | 0 | 21 | 0 | 336 | 315 |  | 0 | 250 | 250 | 0 | 0 | 55 | 150 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 23 | 33 | 33 | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 29 | 80 | 0 | 0 | 270 | 275 | 172 | 8 | 135 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 88 | 157 | 0 | 22 | 2 | 31 | 32 | 28 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 23 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 74 | 16 | 10 | 0 | 10 | 240 | 0 | 0 | 17 | 3 | 268 | 35 | 34 | 0 | 49 | 10 | 220 | 0 | 38 | 72 | 0 | 0 | 17 | 24 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 22 | 0 | 166 | 0 | 313 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 0 | 370 | 182 | 0 | 0 | 4 |  | 5419 | 2271 | 7690 | 3302 | 702 | 1935 | 0 | 844 | 450 | 158 | 120 | 0 | 88 | 91 | 0 | 104.17
10:00 | 0 | 0 | 0 | 110 | 0 | 21 | 0 | 336 | 290 |  | 0 | 250 | 290 | 0 | 0 | 55 | 150 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 23 | 33 | 33 | 0 | 0 | 87 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 80 | 0 | 0 | 290 | 300 | 209 | 8 | 139 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 78 | 154 | 0 | 22 | 2 | 31 | 42 | 28 | 0 | 110 | 71 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 16 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 78 | 18 | 12 | 0 | 10 | 240 | 0 | 0 | 17 | 4 | 187 | 35 | 17 | 0 | 49 | 10 | 220 | 2 | 47 | 72 | 0 | 0 | 17 | 29 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 22 | 0 | 170 | 0 | 420 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 0 | 380 | 182 | 0 | 0 | 5 |  | 5410 | 2398 | 7808 | 3390 | 701 | 2039 | 0 | 754 | 459 | 157 | 120 | 0 | 78 | 110 | 0 | 104.16
11:00 | 0 | 0 | 0 | 110 | 0 | 21 | 0 | 336 | 270 |  | 0 | 250 | 260 | 0 | 0 | 55 | 190 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 20 | 33 | 33 | 0 | 0 | 87 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 11 | 18 | 14 | 80 | 0 | 0 | 290 | 335 | 186 | 8 | 138 | 29 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 96 | 154 | 0 | 22 | 3 | 31 | 42 | 28 | 0 | 110 | 72 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 16 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 78 | 20 | 90 | 3 | 10 | 241 | 0 | 0 | 17 | 4 | 161 | 35 | 17 | 0 | 42 | 64 | 220 | 36 | 52 | 72 | 0 | 0 | 17 | 27 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 22 | 0 | 206 | 0 | 415 | 2 | 0 | 35 | 0 | 0 | 0 | 6 | 20 | 420 | 181 | 0 | 0 | 5 |  | 5582 | 2518 | 8100 | 3500 | 702 | 1975 | 0 | 933 | 500 | 157 | 120 | 0 | 96 | 117 | 0 | 104.15
12:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 334 | 256 |  | 0 | 250 | 290 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 25 | 17 | 16 | 25 | 18 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 18 | 28 | 130 | 0 | 0 | 310 | 365 | 184 | 8 | 139 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 108 | 154 | 0 | 22 | 2 | 31 | 42 | 28 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 16 | 5 | 0 | 25 | 0 | 0 | 94 | 0 | 78 | 20 | 76 | 22 | 21 | 242 | 0 | 0 | 17 | 4 | 159 | 21 | 17 | 0 | 41 | 76 | 220 | 53 | 52 | 72 | 0 | 0 | 17 | 33 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 21 | 0 | 200 | 0 | 387 | 22 | 0 | 43 | 0 | 12 | 0 | 7 | 50 | 430 | 201 | 0 | 0 | 5 |  | 5856 | 2582 | 8438 | 3606 | 701 | 2010 | 0 | 1103 | 509 | 158 | 120 | 0 | 108 | 123 | 0 | 104.14
13:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 343 | 243 |  | 0 | 250 | 240 | 0 | 0 | 55 | 218 | 0 | 0 | 0 | 32 | 0 | 8 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 18 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 23 | 18 | 36 | 135 | 0 | 0 | 310 | 300 | 182 | 8 | 135 | 29 | 30 | 0 | 51 | 0 | 0 | 2 | 22 | 11 | 25 | 19 | 114 | 153 | 0 | 20 | 2 | 31 | 42 | 29 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 23 | 5 | 0 | 45 | 0 | 0 | 110 | 0 | 91 | 19 | 90 | 100 | 51 | 242 | 0 | 0 | 24 | 4 | 213 | 25 | 24 | 0 | 48 | 76 | 220 | 84 | 50 | 156 | 0 | 0 | 17 | 30 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 18 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 21 | 0 | 189 | 0 | 363 | 80 | 0 | 84 | 0 | 34 | 0 | 7 | 100 | 430 | 213 | 0 | 0 | 5 |  | 6232 | 2727 | 8959 | 3542 | 701 | 1944 | 0 | 1753 | 510 | 158 | 120 | 0 | 114 | 117 | 0 | 104.14
14:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 341 | 243 |  | 0 | 250 | 275 | 0 | 0 | 55 | 150 | 0 | 0 | 0 | 32 | 0 | 12 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 13 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 25 | 18 | 31 | 135 | 0 | 0 | 310 | 300 | 182 | 8 | 140 | 29 | 48 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 20 | 110 | 152 | 0 | 20 | 2 | 31 | 42 | 31 | 0 | 110 | 70 | 40 | 40 | 0 | 141 | 18 | 0 | 10 | 240 | 23 | 8 | 0 | 15 | 0 | 0 | 110 | 0 | 80 | 15 | 90 | 100 | 70 | 242 | 0 | 0 | 34 | 3 | 213 | 35 | 34 | 0 | 48 | 76 | 220 | 104 | 42 | 162 | 0 | 0 | 17 | 26 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 22 | 0 | 184 | 0 | 400 | 53 | 0 | 70 | 0 | 34 | 0 | 6 | 50 | 380 | 218 | 0 | 0 | 4 |  | 6183 | 2607 | 8790 | 3452 | 702 | 2037 | 0 | 1653 | 460 | 158 | 120 | 0 | 110 | 98 | 0 | 104.13
15:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 335 | 245 |  | 0 | 250 | 240 | 0 | 0 | 55 | 180 | 0 | 0 | 0 | 32 | 0 | 13 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 13 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 60 | 0 | 25 | 18 | 29 | 135 | 0 | 0 | 330 | 295 | 187 | 8 | 136 | 29 | 49 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 21 | 112 | 152 | 0 | 20 | 1 | 31 | 42 | 31 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 24 | 8 | 0 | 15 | 0 | 0 | 125 | 0 | 80 | 12 | 76 | 106 | 78 | 241 | 0 | 0 | 42 | 2 | 51 | 35 | 44 | 0 | 49 | 76 | 220 | 104 | 29 | 162 | 0 | 0 | 17 | 18 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 22 | 0 | 188 | 0 | 400 | 53 | 0 | 95 | 0 | 64 | 0 | 4 | 100 | 410 | 195 | 0 | 0 | 3 |  | 6068 | 2737 | 8805 | 3516 | 701 | 1979 | 0 | 1661 | 489 | 158 | 120 | 0 | 112 | 69 | 0 | 104.13
16:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 341 | 254 |  | 0 | 250 | 250 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 16 | 0 | 13 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 13 | 0 | 17 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 60 | 0 | 21 | 18 | 18 | 135 | 0 | 0 | 295 | 275 | 190 | 8 | 137 | 29 | 49 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 18 | 106 | 152 | 0 | 19 | 0 | 31 | 42 | 31 | 0 | 130 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 0 | 240 | 24 | 8 | 0 | 15 | 0 | 0 | 160 | 0 | 80 | 6 | 76 | 135 | 92 | 241 | 0 | 0 | 68 | 1 | 103 | 35 | 68 | 0 | 82 | 50 | 220 | 55 | 15 | 108 | 0 | 0 | 17 | 8 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 22 | 0 | 169 | 0 | 386 | 35 | 0 | 50 | 0 | 70 | 0 | 2 | 50 | 420 | 181 | 0 | 0 | 1 |  | 5974 | 2594 | 8568 | 3364 | 701 | 1968 | 0 | 1618 | 500 | 158 | 120 | 0 | 106 | 33 | 0 | 104.12
17:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 342 | 272 |  | 0 | 250 | 240 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 16 | 0 | 12 | 0 | 0 | 0 | 54 | 17 | 17 | 16 | 25 | 17 | 33 | 17 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 38 | 18 | 25 | 135 | 0 | 0 | 285 | 265 | 195 | 8 | 138 | 29 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 18 | 102 | 152 | 0 | 19 | 0 | 31 | 42 | 31 | 0 | 110 | 70 | 40 | 40 | 0 | 164 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 15 | 0 | 0 | 120 | 0 | 80 | 0 | 90 | 100 | 103 | 241 | 2 | 0 | 68 | 0 | 105 | 35 | 68 | 5 | 87 | 50 | 220 | 34 | 1 | 108 | 0 | 0 | 17 | 1 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 5 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 22 | 0 | 166 | 0 | 310 | 35 | 0 | 50 | 0 | 38 | 0 | 1 | 50 | 420 | 142 | 0 | 0 | 0 |  | 5945 | 2437 | 8382 | 3400 | 702 | 1890 | 0 | 1505 | 502 | 158 | 120 | 0 | 102 | 3 | 0 | 104.12
18:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 347 | 280 |  | 0 | 250 | 260 | 0 | 0 | 55 | 135 | 0 | 0 | 0 | 48 | 64 | 22 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 17 | 33 | 17 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 68 | 50 | 13 | 49 | 18 | 36 | 125 | 0 | 0 | 285 | 265 | 207 | 8 | 137 | 29 | 50 | 0 | 51 | 0 | 0 | 18 | 22 | 11 | 25 | 20 | 128 | 154 | 0 | 19 | 0 | 43 | 42 | 40 | 0 | 163 | 70 | 61 | 81 | 0 | 212 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 82 | 0 | 0 | 146 | 0 | 80 | 0 | 90 | 126 | 110 | 320 | 28 | 17 | 86 | 0 | 260 | 35 | 90 | 52 | 97 | 100 | 290 | 60 | 0 | 140 | 17 | 0 | 17 | 0 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 50 | 0 | 80 | 27 | 0 | 0 | 22 | 16 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 23 | 0 | 168 | 0 | 392 | 70 | 0 | 75 | 32 | 100 | 0 | 0 | 100 | 470 | 223 | 0 | 15 | 0 |  | 7196 | 3066 | 10262 | 3637 | 701 | 2228 | 0 | 2460 | 552 | 158 | 120 | 278 | 128 | 0 | 0 | 104.11
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.11
19:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 346 | 280 |  | 0 | 250 | 240 | 0 | 0 | 55 | 82 | 0 | 0 | 0 | 48 | 64 | 24 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 30 | 33 | 17 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 55 | 50 | 12 | 50 | 18 | 36 | 110 | 0 | 0 | 285 | 265 | 217 | 8 | 136 | 29 | 51 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 120 | 179 | 8 | 19 | 0 | 42 | 42 | 44 | 0 | 130 | 90 | 62 | 81 | 0 | 202 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 185 | 0 | 0 | 181 | 0 | 80 | 0 | 90 | 200 | 118 | 322 | 45 | 17 | 105 | 0 | 304 | 35 | 110 | 52 | 96 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 27 | 0 | 0 | 52 | 28 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 22 | 0 | 180 | 0 | 345 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 530 | 207 | 0 | 35 | 0 |  | 7597 | 3183 | 10780 | 3673 | 701 | 2095 | 0 | 3059 | 611 | 158 | 120 | 243 | 120 | 0 | 0 | 104.1
19:30 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 304 | 280 |  | 0 | 250 | 270 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 48 | 64 | 25 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 50 | 12 | 50 | 18 | 36 | 110 | 0 | 0 | 290 | 275 | 214 | 8 | 138 | 29 | 51 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 120 | 185 | 8 | 19 | 0 | 42 | 42 | 44 | 0 | 130 | 110 | 61 | 81 | 0 | 165 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 185 | 0 | 0 | 190 | 0 | 80 | 0 | 90 | 200 | 120 | 322 | 25 | 0 | 105 | 0 | 304 | 35 | 110 | 52 | 97 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 12 | 0 | 0 | 52 | 28 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 22 | 0 | 186 | 0 | 398 | 105 | 0 | 100 | 32 | 113 | 0 | 0 | 113 | 530 | 223 | 0 | 35 | 0 |  | 7539 | 3212 | 10751 | 3582 | 701 | 2235 | 0 | 3032 | 611 | 158 | 120 | 192 | 120 | 0 | 0 | 104.1
20:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 321 | 280 |  | 0 | 250 | 262 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 48 | 48 | 25 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 50 | 12 | 50 | 18 | 36 | 110 | 0 | 0 | 285 | 265 | 215 | 8 | 138 | 29 | 51 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 120 | 185 | 8 | 19 | 0 | 43 | 42 | 44 | 0 | 130 | 109 | 61 | 81 | 0 | 165 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 185 | 0 | 0 | 200 | 0 | 80 | 0 | 90 | 200 | 120 | 322 | 8 | 0 | 105 | 0 | 306 | 35 | 110 | 34 | 97 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 12 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 22 | 0 | 187 | 0 | 385 | 105 | 0 | 108 | 32 | 113 | 0 | 0 | 113 | 530 | 225 | 0 | 35 | 0 |  | 7503 | 3187 | 10690 | 3591 | 702 | 2206 | 0 | 3035 | 610 | 158 | 120 | 148 | 120 | 0 | 0 | 0
21:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 302 | 291 |  | 0 | 250 | 260 | 0 | 0 | 55 | 6 | 0 | 0 | 0 | 48 | 16 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 50 | 12 | 50 | 18 | 42 | 110 | 0 | 0 | 290 | 275 | 214 | 8 | 138 | 29 | 52 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 120 | 182 | 8 | 22 | 0 | 42 | 42 | 43 | 0 | 163 | 110 | 61 | 81 | 0 | 165 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 185 | 0 | 0 | 200 | 0 | 63 | 0 | 90 | 200 | 130 | 322 | 8 | 0 | 105 | 0 | 305 | 35 | 110 | 17 | 97 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 22 | 0 | 193 | 0 | 398 | 105 | 0 | 113 | 32 | 113 | 0 | 0 | 113 | 530 | 224 | 0 | 35 | 0 |  | 7494 | 3159 | 10653 | 3608 | 701 | 2266 | 0 | 3002 | 611 | 158 | 120 | 67 | 120 | 0 | 0 | 104.1
22:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 302 | 336 |  | 0 | 250 | 235 | 0 | 0 | 55 | 5 | 0 | 0 | 0 | 24 | 0 | 26 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 48 | 50 | 12 | 25 | 18 | 42 | 110 | 0 | 0 | 285 | 270 | 214 | 8 | 138 | 29 | 52 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 122 | 182 | 8 | 22 | 0 | 42 | 42 | 50 | 0 | 163 | 110 | 61 | 81 | 0 | 165 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 120 | 0 | 0 | 160 | 0 | 60 | 0 | 90 | 200 | 135 | 322 | 8 | 0 | 105 | 0 | 305 | 35 | 110 | 17 | 97 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 22 | 0 | 186 | 0 | 380 | 105 | 0 | 113 | 32 | 113 | 0 | 0 | 113 | 530 | 224 | 0 | 35 | 0 |  | 7350 | 3118 | 10468 | 3572 | 702 | 2266 | 0 | 2872 | 611 | 155 | 120 | 48 | 122 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 302 | 337 |  | 0 | 250 | 235 | 0 | 0 | 40 | 1 | 0 | 0 | 0 | 24 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 10 | 0 | 25 | 18 | 42 | 110 | 0 | 0 | 285 | 270 | 216 | 8 | 138 | 29 | 49 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 114 | 178 | 8 | 22 | 0 | 42 | 42 | 46 | 0 | 163 | 110 | 62 | 81 | 0 | 165 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 30 | 0 | 0 | 140 | 0 | 60 | 0 | 90 | 200 | 137 | 321 | 0 | 0 | 105 | 0 | 304 | 35 | 110 | 0 | 91 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 22 | 0 | 185 | 0 | 390 | 105 | 0 | 113 | 32 | 68 | 0 | 0 | 113 | 530 | 224 | 0 | 0 | 0 |  | 7049 | 2990 | 10039 | 3562 | 701 | 2259 | 0 | 2465 | 611 | 156 | 120 | 51 | 114 | 0 | 0 | 104.1
24:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 302 | 337 |  | 0 | 250 | 242 | 0 | 0 | 55 | 1 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 42 | 100 | 0 | 0 | 275 | 250 | 213 | 8 | 138 | 29 | 49 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 114 | 182 | 0 | 22 | 0 | 42 | 42 | 50 | 0 | 163 | 110 | 62 | 81 | 0 | 165 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 90 | 0 | 60 | 0 | 90 | 155 | 130 | 322 | 0 | 0 | 105 | 0 | 305 | 35 | 110 | 0 | 57 | 100 | 320 | 104 | 0 | 162 | 45 | 0 | 17 | 0 |  | 702 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 22 | 0 | 182 | 0 | 378 | 105 | 0 | 113 | 32 | 0 | 0 | 0 | 70 | 530 | 223 | 0 | 0 | 0 |  | 6861 | 2867 | 9728 | 3529 | 702 | 2267 | 0 | 2177 | 611 | 157 | 120 | 51 | 114 | 0 | 0 | 104.09
KWH | 0 | 0 | 0 | 2709000 | 0 | 534227 | 0 | 8138750 | 6866000 |  | 0 | 6167250 | 6187753 | 0 | 0 | 1322671 | 3537402 | 0 | 0 | 0 | 824832 | 183360 | 291913 | 0 | 0 | 0 | 1303920 | 561417 | 610273 | 363528 | 600000 | 571500 | 805000 | 757900 | 0 | 0 | 2076687 | 1700000 | 2700000 | 0 | 0 | 0 | 0 | 0 | 0 |  | 112080 | 0 | 400438 | 502680 | 66240 | 600000 | 439344 | 840000 | 2511044 | 0 | 0 | 7512500 | 7126000 | 4909000 | 217454 | 3286950 | 666288 | 962880 | 0 | 1240128 | 0 | 2296 | 268392 | 516096 | 212040 | 609600 | 503780 | 2615040 | 3783840 | 36480 | 467316 | 14450 | 862000 | 943800 | 865800 | 0 | 3165218 | 1856000 | 1100064 | 1469760 | 0 | 3779160 | 392000 | 0 | 227700 | 6376000 | 545568 | 219168 | 0 | 1083937 | 0 | 0 | 3062400 | 0 | 1951776 | 135270 | 1754880 | 2360640 | 1742981 | 6405000 | 138000 | 32088 | 1643454 | 30721 | 5866255 | 842719 | 1916100 | 182400 | 1531320 | 1553280 | 6077700 | 1772160 | 358930 | 3402720 | 383891 | 0 | 443160 | 213765 |  | 16968727 | 0 | 0 | 0 | 0 | 3262080 | 0 | 0 | 0 | 0 | 0 | 1555000 | 515227 | 0 | 0 | 0 | 0 | 64896 | 0 | 197464 | 67170 | 0 | 0 | 316800 | 58795 | 474720 | 0 | 167166 | 1866764 | 0 | 0 | 0 | 0 | 0 | 0 | 4578327 | 0 | 539011 | 0 | 4613391 | 0 | 9127236 | 1351200 | 0 | 1677312 | 233568 | 899625 | 0 | 40840 | 1310400 | 11829500 | 4794870 | 0 | 186000 | 37320 |  | 155923524 | 66733409 | 222656933 | 85821222 | 16968727 | 50571234 | 0 | 44207134 | 13696264 | 3776687 | 3262080 | 907249 | 2615040 | 831296 | 0
Fuel Cost | 0 | 0 | 0 | 3982230 | 0 | 705179.64 | 0 | 8220137.5 | 7071980 |  | 0 | 6722302.5 | 6868405.83 | 0 | 0 | 11189796.66 | 3678898.08 | 0 | 0 | 0 | 7522467.84 | 1804262.4 | 2691437.86 | 0 | 0 | 0 | 9518616 | 4339753.41 | 6017291.78 | 272646 | 450000 | 0 | 0 | 0 | 0 | 0 | 560705.49 | 459000 | 4887000 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 3884248.6 | 4800594 | 576288 | 4752000 | 553573.44 | 2494800 | 3716345.12 | 0 | 0 | 5559250 | 7126000 | 4516280 | 280515.66 | 3779992.5 | 752905.44 | 1348032 | 0 | 2120618.88 | 0 | 23189.6 | 2563143.6 | 655441.92 | 159030 | 1066800 | 377835 | 19612800 | 4010870.4 | 331238.4 | 593491.32 | 230333 | 1413680 | 1510080 | 1541124 | 0 | 3608348.52 | 1930240 | 2167126.08 | 2807241.6 | 0 | 6537946.8 | 858480 | 0 | 464508 | 6439760 | 409176 | 166567.68 | 0 | 8194563.72 | 0 | 0 | 15924480 | 0 | 19205475.84 | 1581306.3 | 14302272 | 25612944 | 12288016.05 | 5956650 | 1258560 | 303231.6 | 14314484.34 | 0 | 44348887.8 | 7340082.49 | 16842519 | 1820352 | 13123412.4 | 10344844.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97739867.52 | 0 | 0 | 0 | 0 | 45212428.8 | 0 | 0 | 0 | 0 | 0 | 1757150 | 798601.85 | 0 | 0 | 0 | 0 | 638576.64 | 0 | 1747556.4 | 517209 | 0 | 0 | 3069792 | 570311.5 | 911462.4 | 0 | 126544.662 | 11256586.92 | 0 | 0 | 0 | 0 | 0 | 0 | 6043391.64 | 0 | 808516.5 | 0 | 5397667.47 | 0 | 9035963.64 | 14106528 | 0 | 15917690.88 | 2204881.92 | 6981090 | 0 | 451282 | 9683856 | 51931505 | 0 | 0 | 0 | 0 |  | 405464088.89 | 286908460.742 | 692372549.632 | 88633427.052 | 97739867.52 | 54027361.02 | 0 | 312007801.39 | 63188091.92 | 1019705.49 | 45212428.8 | 8668145.14 | 19612800 | 2262921.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 334 | 256 |  | 0 | 250 | 290 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 25 | 17 | 16 | 25 | 18 | 33 | 33 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 18 | 28 | 130 | 0 | 0 | 310 | 365 | 184 | 8 | 139 | 29 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 108 | 154 | 0 | 22 | 2 | 31 | 42 | 28 | 0 | 110 | 70 | 40 | 40 | 0 | 140 | 18 | 0 | 10 | 240 | 16 | 5 | 0 | 25 | 0 | 0 | 94 | 0 | 78 | 20 | 76 | 22 | 21 | 242 | 0 | 0 | 17 | 4 | 159 | 21 | 17 | 0 | 41 | 76 | 220 | 53 | 52 | 72 | 0 | 0 | 17 | 33 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 21 | 0 | 200 | 0 | 387 | 22 | 0 | 43 | 0 | 12 | 0 | 7 | 50 | 430 | 201 | 0 | 0 | 5 |  | 8438 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 346 | 280 | 0 | 0 | 250 | 240 | 0 | 0 | 55 | 82 | 0 | 0 | 0 | 48 | 64 | 24 | 0 | 0 | 0 | 54 | 55 | 17 | 16 | 25 | 30 | 33 | 17 | 0 | 0 | 88 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 55 | 50 | 12 | 50 | 18 | 36 | 110 | 0 | 0 | 285 | 265 | 217 | 8 | 136 | 29 | 51 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 120 | 179 | 8 | 19 | 0 | 42 | 42 | 44 | 0 | 130 | 90 | 62 | 81 | 0 | 202 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 185 | 0 | 0 | 181 | 0 | 80 | 0 | 90 | 200 | 118 | 322 | 45 | 17 | 105 | 0 | 304 | 35 | 110 | 52 | 96 | 100 | 320 | 104 | 0 | 162 | 53 | 0 | 17 | 0 |  | 701 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 27 | 0 | 0 | 52 | 28 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 22 | 0 | 180 | 0 | 345 | 105 | 0 | 94 | 32 | 113 | 0 | 0 | 113 | 530 | 207 | 0 | 35 | 0 |  | 10780 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 360 | 320 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 90 | 50 | 18 | 40 | 110 | 0 | 0 | 330 | 330 | 215 | 8 | 138 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 164 | 180 | 8 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 65 | 81 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 135 | 324 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 716 | 0 | 300 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 65 | 28 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 58 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 360 | 315 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 88 | 70 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 18 | 40 | 110 | 0 | 0 | 320 | 320 | 200 | 8 | 138 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 138 | 180 | 8 | 22 | 1.6 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 81 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 0 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 135 | 324 | 115 | 105 | 105 | 5 | 300 | 36 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 716 | 0 | 300 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 22 | 50 | 210 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 307 | 281 | 0 | 0 | 250 | 250 | 0 | 0 | 15 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 16 | 25 | 28 | 33 |  | 0 | 0 | 88 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 80 | 0 | 0 | 290 | 305 | 181 | 8 | 137 | 26 | 51 | 0 | 20 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 60 | 202 | 0 | 22 | 1 | 42 | 42 | 45 | 0 | 110 | 110 | 61 | 78 | 0 | 165 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 41 | 10 | 30 | 0 | 0 | 322 | 6 | 0 | 0 | 1 | 211 | 35 | 34 | 0 | 8 | 0 | 320 | 17 | 12 | 4 | 0 | 0 | 17 | 16 | 0 | 708 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 17 | 0 | 165 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 170 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 7690 | 9:00
| Highest Generation |  | 10780 | 19:00
| Day Peak Generation |  | 8438 | 12:00
| Evening Peak Generation |  | 10780 | 19:00
| HVDC Max Flow |  | 714 | 1:00
| HVDC EvPeak Flow |  | 701 | 19:00
| Load factor L.F |  | 86.06%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-10-30
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8438 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7764 | MW
Evening Peak Generation : |  | 10780 | MW Hour : | 19:00 | Available Max Generation : |  | 14749 | MW
E.P. Demand (at gen end) : |  | 10780 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11700 | MW
Maximum Generation : |  | 10780 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3049 | MW
Total Gen. (MKWH) : |  | 222.6569 | System Load Factor : | 86.06% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -102 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-10-30
Actual : | 104.04 | Ft.(MSL) , | Rule curve : | 108.8 | Ft.( MSL )
Gas Consumed : | Total = | 1065.8 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142660788.072
: |  | Coal : | 63188091.92 | Oil : | 365888375.33 | Total : | 571737255.322
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4173.856 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1420.9799 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1273.4428 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1150.7666 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1039.874 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 839.1456 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 467.1013 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 216.0017 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 647.2008 |  |  | 0 | 0%
Total | 0 |  | 11228.3687 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Benapol 132/33 kV T-1 transformer was under shut down from 09:32 to 16:06 for A/M.
b) Bogura(New)-Sherpur 132 kV Ckt-1 was under shut down from 08:35 to 17:25 for A/M.
c) Daudkandi 132/33 kV T-2 & T-3 transformers were under shut down from 08:20 to 11:52 due to |  |  |  |  | About 20 MW power interruption occurred under Daudkandi S/S
PBS work at 33 kV side. |  |  |  |  | area from 08:20 to 11:52.
d) Kurigram 132/33 kV T-1 transformer was under shut down from 08:34 to 15:07 for A/M.
e) Sikalbaha 230/132 kV T-01 transformer was under shut down from 10:13 to 13:47 for D/W.
f) Madunaghat-Chandraghona 132 kV Ckt-2 was shutdown at 09:06 for D/W.
g) Sonargaon 132/33 kV T-1 transformer was under shut down from 09:41 to 11:55 for C/M.
h) Sikalbaha 230/132 kV T-02 transformer was under shut down from 14:21 to 17:03 for D/W.
i) Bagherhat 132/33 kV T-3 transformer was under shut down from 22:48 to 00:06(30/10/2021) to |  |  |  |  | About 45 MW power interruption occurred under Bagherhat S/S
attend R/H at 33 kV Fakir Hat feeder. |  |  |  |  | area from 22:48 to 00:06(30/10/2021).
j) Sylhet-Chatak 132 kV Ckt-2 was shut down at 06:22(30/10/2021) to attend CT oil leakage at Sylhet end.
k) Halishahar 132/33 kV T-1 transformer was shutdown at 07:17(30/10/2021) for A/M.
l) Madaripur 132/33 kV T-1 transformer was shutdown at 07:18(30/10/2021) for A/M.
m) After maintenance Siddhirganj 335 MW ST was synchronized at 00:47(30/10/2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2709000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 534227 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8138750 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 280 | 6866000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6167250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 6187753 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1322671
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 24 | 291913 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 363528
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 82 | 3537402 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 48 | 824832 | Low demand.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1303920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 183360 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 561417
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 610273 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1171500 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 805000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 757900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 185 | 1083937
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 80 | 1951776 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 32088 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1772160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3402720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 213765
| Dhaka area Total |  |  |  | 5560 | 2316 | 50793142
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 135270
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 600000
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3776687 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1643454
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 55 | 400438 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 502680 | Low demand.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1754880 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 439344 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 36 | 840000
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 66240 | Low demand.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30721
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 5866255
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 842719 | Engine problem
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1916100
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1553280
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 383891 | Low demand.
| Chattogram area Total |  |  |  | 2382 | 1286 | 23451959
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 110 | 2511044 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 4909000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7512500 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 7126000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 666288 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 962880
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1240128
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 118 | 1742981 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 2296 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3286950 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2360640
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 516096
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212040
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2615040
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 609600 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 268392 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 503780
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 182400 | Low demand.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1531320 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443160 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1877 | 39419989
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 179 | 3783840 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 467316
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 8 | 36480
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14450
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 181 | 3062400 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 45 | 138000 | Low demand.
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 358930
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 112080
| Mymensingh Area Total |  |  |  | 622 | 450 | 7973496
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 862000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 943800 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3165218 | frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 90 | 1856000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 44 | 865800 | Engine problem
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 219168
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1100064
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1469760
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 202 | 3779160
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 392000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 545568
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6376000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 322 | 6405000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 227700
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 6077700 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1668 | 34284938
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 701 | 16968727
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3262080
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1351200
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 32 | 233568 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 958 | 21815575
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 515227 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1555000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 539011 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 11829500
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 207 | 4794870
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 186000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 886 | 19419608
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 64896
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 67170 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4578327 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4613391 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 345 | 9127236 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 58795 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 474720
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 167166
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 316800
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 197464 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1677312 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1310400
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37320
| Rajshahi Area Total |  |  |  | 2179 | 1145 | 22690997
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1866764
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 899625
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40840
| Rangpur Area Total |  |  |  | 605 | 194 | 2807229
| Total |  |  |  | 20934 | 10780 | 222656933
| Eastern Grid Total |  |  |  | 13975 | 7597 | 155923524
| Western Grid Total |  |  |  | 6959 | 3183 | 66733409
| National Grid Total |  |  |  | 20934 | 10780 | 222656933
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-29
(a) ENTIRE EASTERN GRID : |  | 7208 | MW | (b) ENTIRE WESTERN GRID : |  | 3129 | MW
i) Dhaka area |  | 3597 | MW | i) Khulna area |  | 1243 | MW
ii) Chittagong area |  | 1208 | MW | ii) Rajshahi area |  | 985 | MW
iii) Comilla area |  | 1077 | MW | iii) Barisal area |  | 309 | MW
iv) Mymensingh area |  | 853 | MW | iv) Rangpur area |  | 592 | MW
v) Sylhet area |  | 473 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10337 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 1:00 | Kishoreganj | 118 | 19:30 | Benapol | 42 | 18:30
Munsiganj | 90 | 21:00 | Netrokona | 94 | 18:00 | Jhenida(Old) | 94 | 18:30
Sonargaon | 68 | 1:00 | Jamalpur | 117 | 18:00 | Bottail | 90 | 18:00
Shyampur | 176 | 3:00 | Sherpur | 102 | 18:00 | G.K Project | 45 | 18:30
Bhulta | 170 | 1:00 | Srimongal | 52 | 18:00 | Faridpur | 112 | 18:30
Madanganj | 40 | 21:00 | Shahjibazar | 104 | 19:30 | Rajbari | 44 | 18:30
Shitalakhya | 93 | 1:00 | Fenchuganj | 43 | 18:00 | Madaripur | 82 | 19:00
Rahim steel | 10 | 1:00 | Kulawara | 44 | 18:00 | Sariatpur | 58 | 21:00
Matuail | 54 | 2:00 | Sylhet | 116 | 18:00 | Gopalganj | 81 | 20:00
Ghorasal | 71 | 3:00 | Chatak | 24 | 18:00 | Bagerhat | 84 | 18:00
Narsingdi | 150 | 21:00 | Sunamganj | 42 | 19:00 | Mongla | 31 | 1:00
Haripur (SBU) | 107 | 8:00 | Biani Bazar | 55 | 18:30 | Satkhira | 93 | 19:30
Sreenagar | 36 | 21:00 | Comilla (S) | 128 | 18:00 | Gallamari | 29 | 12:00
Ullon | 60 | 18:30 | Comilla(N) | 107 | 18:30 | Magura | 46 | 18:00
Hasnabad | 72 | 22:00 | Chandpur | 63 | 19:30 | Norail | 40 | 18:00
Magbazar | 72 | 15:00 | Feni | 114 | 18:30 | Chuadanga | 78 | 18:30
Maniknagar | 52 | 22:00 | Chowmuhani | 184 | 21:00 | Barisal(N) | 35 | 18:00
Bangabhaban | 4 | 1:00 | Ashuganj | 41 | 0:00 | Barisal (S) | 92 | 18:00
Motijheel | 15 | 18:00 | Daudkandi | 132 | 21:00 | Patuakhali | 18 | 20:00
Narinda | 48 | 13:00 | B.Baria | 145 | 18:30 | Bhandaria | 45 | 21:00
Kazla | 74 | 18:00 | Ramganj | 80 | 22:00 | Borguna | 14 | 18:30
Dhanmondi | 137 | 19:30 | Chaddagram | 56 | 21:00 | Borhan Uddin | 38 | 22:00
Lalbag | 60 | 1:00 | PHP | 10 | 21:00 | Ishurdi | 53 | 18:30
Madartek | 70 | 18:00 | Kochua | 64 | 18:00 | Ruppur Paromanobik | 4 | 18:00
Dhaka University | 16 | 12:00 | Madunaghat | 50 | 1:00 | Natore | 106 | 19:00
Aftabnagar | 14 | 18:00 | Hathazari | 88 | 18:30 | Bogra | 121 | 18:00
Fatullah | 51 | 2:00 | Khulshi | 171 | 18:00 | Noagaon | 86 | 18:00
Nawabganj | 45 | 21:00 | Halishahar | 81 | 18:00 | Rajshahi | 101 | 20:00
Keraniganj | 55 | 22:00 | Baraulia | 134 | 1:00 | Rajshahi New | 14 | 18:30
Banani | 23 | 16:00 | Sikalbaha | 34 | 0:00 | C.Nawabganj | 42 | 18:30
Mirpur | 105 | 18:00 | Dohazari | 76 | 18:00 | Amnura | 32 | 18:00
Kalyanpur | 87 | 13:00 | Cox'sbazar | 106 | 18:00 | Pabna | 80 | 18:30
Gulshan | 84 | 18:00 | Chandraghona | 26 | 18:00 | Shahjadpur | 75 | 18:30
Uttara | 72 | 18:00 | Kaptai | 4.2 | 18:00 | Serajganj | 72 | 18:00
Uttara New | 16 | 1:00 | A. Khaer Stl. | 15 | 1:00 | Niyamatpur | 49 | 18:30
Kamrangirchar | 78 | 1:00 | Bakulia | 103 | 19:30 | Joypurhat | 43 | 18:30
Savar | 128 | 12:00 | Julda | 24 | 11:00 | Sherpur(Bogura) | 48 | 18:00
Bhasantec | 116 | 18:30 | TK chemical | 29.4 | 19:00 | Mohastangor | 50 | 18:30
Agargaon | 63 | 18:00 | Modern Steel | 0 | 1:00 | Bhangura | 25 | 18:30
Satmosjid | 95 | 18:00 | Shahmirpur | 23.8 | 19:30 | Rangpur | 106 | 18:30
Tongi | 101 | 21:00 | Khagrachhari | 28 | 18:30 | Lalmonirhat | 41 | 18:00
Kabirpur | 163 | 19:00 | Matarbari | 39 | 21:00 | Saidpur | 64 | 19:30
Basundhara | 170 | 18:00 | Baroiar Hat | 44 | 18:00 | Purbasadipur | 83 | 18:30
Manikganj | 64 | 18:30 | Rangamati | 14 | 18:30 | Thakurgaon | 62 | 18:30
Joydevpur | 136 | 1:00 | Abul Khair 230 | 126 | 8:00 | Palashbari | 90 | 18:00
New Tongi | 65 | 1:00 | BSRM | 148 | 3:00 | Barapukuria | 38 | 18:00
Kodda | 188 | 1:00 | GPH Ispat | 92 | 6:00 | Panchagar | 44 | 18:30
Dhamrai | 78 | 19:00 | Agrabad | 57 | 19:00 | Joldhaka | 28 | 18:30
Rajendrapur | 84 | 1:00 | Goalpara | 23 | 22:00 | Kurigram | 48 | 18:00
Valuka | 94 | 19:00 | Central S/S | 84 | 18:30 | Mithapukur | 23 | 18:00
Tangail | 178 | 18:30 | Noapara | 30 | 21:00
Mymensing | 166 | 18:30 | Jessore | 99 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 13:00 | 404 | 15:00 | Kaliakoir | 399 | 0.375 | 393 | 0.041667
| Bheramara | 403 | 5:00 | 397 | 18:00 | Bhulta | 391 | 0.25 | 382 | 0.45833
| Ashuganj(N) | 396 | 6:00 | 390 | 10:00 | Gopalganj | 405 | 0.625 | 392 | 0.875
| Payra | 410 | 6:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 234 | 18:30 | 215 | 10:00
| Ishurdi | 234 | 6:00 | 227 | 21:00 | Megnaghat | 236 | 9:00 | 233 | 1:00
| Ashuganj | 242 | 4:00 | 237 | 10:00 | Fenchuganj | 245 | 6:00 | 242 | 10:00
| Serajganj | 234 | 6:00 | 232 | 2:00 | Siddhirganj | 234 | 5:00 | 230 | 24:00
| Baghabari | 232 | 14:00 | 230 | 1:00 | Maniknagar | 232 | 5:00 | 229 | 10:00
| Barapukuria | 237 | 6:00 | 232 | 18:00 | Agargaon | 231 | 8:00 | 225 | 10:00
| Bogra | 228 | 13:00 | 223 | 11:00 | Barisal | 242 | 19:00 | 235 | 20:00
| Rajshahi | 228 | 6:00 | 222 | 21:00 | Bhola 225 MW | 246 | 9:00 | 239 | 24:00
| Khulna South | 233 | 6:00 | 225 | 19:30 | AKSML | 234 | 19:00 | 220 | 10:00
| Rampura | 231 | 8:00 | 229 | 1:00 | BSRM | 234 | 19:00 | 222 | 10:00
| Haripur | 232 | 3:00 | 228 | 10:00 | Bibiyana | 244 | 6:00 | 239 | 22:00
| Hasnabad | 230 | 3:00 | 225 | 1:00 | Bhulta | 235 | 6:00 | 230 | 23:00
| Shyampur | 232 | 6:00 | 228 | 10:00 | Ashuganj (S) | 239 | 4:00 | 234 | 11:00
| Aminbazar | 232 | 1:00 | 226 | 2:00 | Kaliakoir | 226 | 5:00 | 219 | 14:00
| Tongi | 230 | 18:00 | 223 | 9:00 | GPH | 235 | 19:00 | 220 | 10:00
| Comilla (N) | 234 | 18:00 | 229 | 15:00 | Jhenaidah | 230 | 6:00 | 220 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 5:00 | 134 | 10:00 | Madanhat | 139 | 0.70833 | 129 | 0.375
| Munsiganj | 138 | 18:00 | 135 | 1:00 | Hathazari | 137 | 0.77083 | 130 | 0.5
| Sonargaon | 134 | 3:00 | 132 | 7:00 | Khulshi | 135 | 0.79167 | 126 | 0.41667
| Shyampur | 139 | 6:00 | 136 | 10:00 | Halishahar | 137 | 0.77083 | 123 | 0.41667
| Bhulta | 131 | 5:00 | 129 | 1:00 | Baraulia | 137 | 0.77083 | 127 | 0.41667
| Madanganj | 137 | 4:00 | 134 | 10:00 | Sikalbaha | 137 | 0.79167 | 125 | 0.41667
| Shitalakhya | 138 | 6:00 | 135 | 10:00 | Dohazari | 132 | 0.77083 | 124 | 0.5
| Rahim steal | 136 | 3:00 | 134 | 10:00 | Cox'sbazar | 122 | 0.375 | 114 | 0.41667
| Matuail | 136 | 5:00 | 134 | 10:00 | Chandraghona | 136 | 0.75 | 130 | 0.41667
| Ghorasal | 140 | 18:00 | 138 | 1:00 | Kaptai | 136 | 0.91667 | 131 | 0.45833
| Narsinghdi | 134 | 7:00 | 130 | 1:00 | A. Khaer Stl. | 135 | 0.77083 | 127 | 0.5
| Haripur (SBU) | 137 | 6:00 | 134 | 1:00 | Bakulia | 136 | 0.77083 | 125 | 0.41667
| Sreenagar | 136 | 19:30 | 132 | 11:00 | Julda | 138 | 0.77083 | 123 | 0.41667
| Ullon | 135 | 7:00 | 132 | 11:00 | TK Chemical | 136 | 0.75 | 124 | 0.41667
| Hasnabad | 136 | 3:00 | 133 | 10:00 | Modern Steel | 136 | 0.75 | 126 | 0.45833
| Magbazar | 135 | 1:00 | 133 | 10:00 | Shahmirpur | 137 | 0.75 | 124 | 0.41667
| Maniknagar | 136 | 5:00 | 133 | 11:00 | Khagrachhari | 134 | 0.77083 | 127 | 0.41667
| Bangabhaban | 136 | 5:00 | 133 | 11:00 | Matarbari | 124 | 0.375 | 115 | 0.625
| Motijheel | 136 | 5:00 | 133 | 11:00 | Baroiar Hat | 134 | 0.75 | 129 | 0.5
| Narinda | 136 | 5:00 | 133 | 11:00 | Rangamati | 135 | 18:00 | 130 | 12:00
| Kazla | 136 | 5:00 | 133 | 11:00 | Agrabad | 136 | 18:00 | 123 | 10:00
| Dhanmondi | 136 | 6:00 | 133 | 1:00 | Goalpara S/S | 139 | 9:00 | 136 | 0.041667
| Lalbag | 133 | 6:00 | 128 | 10:00 | Khulna Central S/S | 138 | 17:00 | 135 | 0.75
| Madartek | 136 | 6:00 | 132 | 16:00 | Noapara | 138 | 6:00 | 133 | 0.8125
| Dhaka University | 137 | 6:00 | 132 | 10:00 | Jessore | 136 | 6:00 | 130 | 0.75
| Aftabnagar | 136 | 5:00 | 132 | 10:00 | Benapol | 136 | 0.25 | 130 | 0.75
| Fatullah | 139 | 6:00 | 136 | 10:00 | Jhenida(Old) | 136 | 5:00 | 130 | 0.75
| Nawabganj | 136 | 6:00 | 133 | 2:00 | Bottail | 136 | 0.25 | 130 | 0.041667
| Keraniganj | 136 | 6:00 | 132 | 11:00 | G.K Project | 136 | 0.25 | 132 | 0.041667
| Banani | 135 | 4:00 | 132 | 10:00 | Faridpur | 136 | 0.25 | 131 | 0.8125
| Mirpur | 132 | 3:00 | 127 | 11:00 | Rajbari | 136 | 0.33333 | 131 | 0.8125
| Kalyanpur | 132 | 6:00 | 129 | 10:00 | Madaripur | 141 | 0.375 | 134 | 0.8125
| Gulshan | 136 | 6:00 | 132 | 10:00 | Shariyatpur S/S | 141 | 6:00 | 133 | 0.77083
| Uttara | 133 | 7:00 | 128 | 9:00 | Gopalganj | 142 | 0.70833 | 135 | 0.77083
| Uttara New | 134 | 6:00 | 128 | 10:00 | Bagerhat | 136 | 12:00 | 131 | 0.8125
| Kamrangirchar | 135 | 5:00 | 133 | 10:00 | Mongla | 135 | 9:00 | 131 | 0.041667
| Savar | 134 | 5:00 | 127 | 10:00 | Satkhira | 137 | 6:00 | 130 | 18:00
| Bhasantec | 138 | 6:00 | 133 | 10:00 | Gallamari | 138 | 0.25 | 134 | 18:00
| Agargaon | 138 | 6:00 | 134 | 10:00 | Magura | 137 | 6:00 | 130 | 0.75
| Satmosjid | 138 | 6:00 | 134 | 10:00 | Narail | 136 | 0.375 | 130 | 0.75
| Tongi | 137 | 21:00 | 135 | 23:00 | Chuadanga | 136 | 6:00 | 127 | 0.75
| Kabirpur | 137 | 13:00 | 135 | 18:00 | Barisal(N) | 140 | 6:00 | 135 | 0.875
| Basundhara | 136 | 18:00 | 132 | 10:00 | Barisal (S) | 139 | 7:00 | 132 | 23:00
| Manikganj | 141 | 13:00 | 138 | 18:00 | Patuakhali(S) | 138 | 0.29167 | 128 | 0.95833
| Joydevpur | 139 | 18:00 | 135 | 1:00 | Bhandaria | 138 | 0.29167 | 130 | 0.875
| New Tongi | 138 | 18:00 | 133 | 10:00 | Borguna | 140 | 0.25 | 133 | 0.95833
| Kodda | 134 | 18:30 | 128 | 11:00 | Jhenaidah(New) | 138 | 6:00 | 132 | 18:00
| Dhamrai | 139 | 1:00 | 135 | 10:00 | Ishurdi | 136 | 6:00 | 132 | 19:30
| Rajendrapur | 132 | 14:00 | 126 | 12:00 | Ruppur Paromanobik | 135 | 6:00 | 132 | 18:30
| Valuka | 127 | 10:00 | 118 | 18:00 | Natore | 135 | 6:00 | 132 | 11:00
| Tangail | 142 | 23:00 | 130 | 15:00 | Bogra | 138 | 15:00 | 133 | 8:00
| Mymensing | 130 | 6:00 | 121 | 18:00 | Noagaon | 135 | 15:00 | 129 | 18:00
| Kishorganj | 133 | 5:00 | 126 | 18:00 | Rajshahi | 134 | 17:00 | 131 | 3:00
| Netrokona | 129 | 8:00 | 119 | 18:00 | Rajshahi New | 135 | 18:30 | 130 | 12:00
| Jamalpur | 139 | 19:00 | 127 | 7:00 | C.Nawabganj | 135 | 18:30 | 130 | 3:00
| Sherpur | 135 | 19:00 | 120 | 7:00 | Amnura | 136 | 18:30 | 130 | 3:00
| Srimongal | 138 | 5:00 | 136 | 1:00 | Pabna | 135 | 17:00 | 131 | 18:00
| Shahjibazar | 137 | 7:00 | 134 | 18:00 | Shahjadpur | 139 | 7:00 | 135 | 12:00
| Fenchuganj | 137 | 6:00 | 134 | 18:30 | Serajganj | 135 | 17:00 | 133 | 7:00
| Khulawara | 136 | 6:00 | 134 | 1:00 | Niyamatpur | 132 | 13:00 | 126 | 3:00
| Sylhet | 134 | 4:00 | 132 | 1:00 | Joypurhat | 135 | 12:00 | 130 | 7:00
| Chatak | 135 | 5:00 | 131 | 19:00 | Sherpur(Bogura) | 136 | 6:00 | 133 | 7:00
| Sunamganj | 132 | 6:00 | 128 | 19:00 | Mohastangor | 137 | 15:00 | 132 | 8:00
| Biani Bazar | 134 | 8:00 | 130 | 18:00 | Bangura | 136 | 13:00 | 133 | 7:00
| Comilla(s) | 129 | 5:00 | 124 | 18:00 | Rangpur | 135 | 16:00 | 128 | 7:00
| Comilla(n) | 139 | 17:00 | 135 | 10:00 | Lalmonirhat | 132 | 2:00 | 126 | 12:00
| Chandpur | 138 | 1:00 | 133 | 10:00 | Saidpur | 136 | 15:00 | 128 | 18:30
| Feni | 135 | 18:00 | 129 | 0:00 | Purbasadipur | 134 | 15:00 | 124 | 18:00
| Chowmuhani | 133 | 23:00 | 128 | 0:00 | Thakurgaon | 137 | 6:00 | 125 | 18:00
| Ashuganj | 140 | 17:00 | 138 | 23:00 | Palashbari | 136 | 15:00 | 130 | 7:00
| Daudkandi | 137 | 8:00 | 132 | 23:00 | Barapukuria | 137 | 6:00 | 132 | 18:00
| B.Baria | 135 | 17:00 | 132 | 18:00 | Panchagar | 139 | 0.25 | 122 | 0.75
| Ramganj | 134 | 8:00 | 128 | 10:00 | Joldhaka | 134 | 0.25 | 126 | 0.75
| Chaddagram | 136 | 17:00 | 130 | 10:00 | Kurigram | 134 | 0.625 | 126 | 0.75
| PHP | 134 | 18:00 | 128 | 10:00 | Mithapukur | 137 | 0.625 | 131 | 0.75
| Kochua | 137 | 17:00 | 132 | 10:00

## L-Curve
Date | 2021-10-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 270 | 6861 | 2867 | 9728 |  |  |  | QF-LDC-11
0:30 | 218 | 6915 | 2860 | 9775 | Date: | 2021-10-29
1:00 | 166 | 6969 | 2853 | 9822
1:30 | 167 | 6794.5 | 2784.5 | 9579
2:00 | 168 | 6620 | 2716 | 9336
2:30 | 188 | 6560 | 2651 | 9211 | [5 empty] | Gen. at Eve. Peak | 10780 | 10780 MW (19:00 )
3:00 | 208 | 6500 | 2586 | 9086 | [6 empty] | 19:00
3:30 | 214 | 6376 | 2555.5 | 8931.5 | [5 empty] | Gen. at Day Peak | 8438 | 8438 MW (12:00 )
4:00 | 220 | 6252 | 2525 | 8777 | [6 empty] | 12:00
4:30 | 195 | 6185 | 2474.5 | 8659.5 | [5 empty] | Highest Generation | 10780
5:00 | 170 | 6118 | 2424 | 8542 | [6 empty] | 19:00
5:30 | 177 | 6027 | 2362 | 8389
6:00 | 184 | 5936 | 2300 | 8236
6:30 | 147 | 5739.5 | 2271.5 | 8011
7:00 | 110 | 5543 | 2243 | 7786
7:30 | 113 | 5514 | 2257.5 | 7771.5
8:00 | 116 | 5485 | 2272 | 7757
8:30 | 173 | 5452 | 2271.5 | 7723.5
9:00 | 230 | 5419 | 2271 | 7690
9:30 | 334 | 5414.5 | 2334.5 | 7749
10:00 | 438 | 5410 | 2398 | 7808
10:30 | 441 | 5496 | 2458 | 7954
11:00 | 444 | 5582 | 2518 | 8100
11:30 | 389 | 5719 | 2550 | 8269
12:00 | 334 | 5856 | 2582 | 8438
12:30 | 269 | 6044 | 2654.5 | 8698.5
13:00 | 204 | 6232 | 2727 | 8959
13:30 | 222 | 6207.5 | 2667 | 8874.5
14:00 | 240 | 6183 | 2607 | 8790
14:30 | 351 | 6125.5 | 2672 | 8797.5
15:00 | 462 | 6068 | 2737 | 8805
15:30 | 440 | 6021 | 2665.5 | 8686.5
16:00 | 418 | 5974 | 2594 | 8568
16:30 | 352 | 5959.5 | 2515.5 | 8475
17:00 | 286 | 5945 | 2437 | 8382
17:30 | 174 | 6570.5 | 2751.5 | 9322
18:00 | 62 | 7196 | 3066 | 10262
18:30 | 82 | 7396.5 | 3124.5 | 10521
19:00 | 102 | 7597 | 3183 | 10780
19:30 | 20 | 7539 | 3212 | 10751
20:00 | 4 | 7503 | 3187 | 10690 |  |  |  | Executive Engineer
20:30 | 6 | 7498.5 | 3173 | 10671.5 |  |  |  | Network Operation Division
21:00 | 8 | 7494 | 3159 | 10653
21:30 | 74 | 7422 | 3138.5 | 10560.5
22:00 | 140 | 7350 | 3118 | 10468 |  |  |  |  | Page 6 of 7
22:30 | 190 | 7199.5 | 3054 | 10253.5
23:00 | 240 | 7049 | 2990 | 10039
23:30 | 255 | 6955 | 2928.5 | 9883.5
24:00 | 270 | 6861 | 2867 | 9728
10780 MW (19:00 )
8438 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-29 |  | Energy |  | 222656933
[13 empty] | 2021-10-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3529 | 702 | 2267 | 0 | 2177 | 611 | 157 | 120 | 51 | 114 | 0 | 0
0:30 | 3655 | 708 | 2176.5 | 0 | 2171 | 594.5 | 159 | 160 | 34 | 117 | 0 | 0 | Date: | 2021-10-29
1:00 | 3781 | 714 | 2086 | 0 | 2165 | 578 | 161 | 200 | 17 | 120 | 0 | 0
1:30 | 3712.5 | 713.5 | 2093.5 | 0 | 2000 | 562.5 | 161 | 200 | 17 | 119 | 0 | 0 | [8 empty] | Total Energy | 222.6569 | Total Energy Gen 222.657 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 222.657 MKWHr
2:00 | 3644 | 713 | 2101 | 0 | 1835 | 547 | 161 | 200 | 17 | 118 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3639 | 707 | 2113.5 | 0 | 1732.5 | 548 | 161.5 | 185 | 8.5 | 116 | 0 | 0 | [8 empty] | Energy Requirement | 222.6569
3:00 | 3634 | 701 | 2126 | 0 | 1630 | 549 | 162 | 170 | 0 | 114 | 0 | 0
3:30 | 3621 | 701.5 | 2137 | 0 | 1519 | 534 | 162 | 145 | 0 | 112 | 0 | 0 | [6 empty] | Shortage
4:00 | 3608 | 702 | 2148 | 0 | 1408 | 519 | 162 | 120 | 0 | 110 | 0 | 0
4:30 | 3586 | 702 | 2075.5 | 0 | 1386.5 | 519 | 161.5 | 120 | 0 | 109 | 0 | 0
5:00 | 3564 | 702 | 2003 | 0 | 1365 | 519 | 161 | 120 | 0 | 108 | 0 | 0
5:30 | 3505.5 | 702 | 1975.5 | 0 | 1318 | 504 | 160 | 120 | 0 | 104 | 0 | 0
6:00 | 3447 | 702 | 1948 | 0 | 1271 | 489 | 159 | 120 | 0 | 100 | 0 | 0
6:30 | 3411.5 | 702 | 1963.5 | 0 | 1085.5 | 468.5 | 158.5 | 120 | 0 | 95 | 6.5 | 0 |  |  |  |  | Coal
7:00 | 3376 | 702 | 1979 | 0 | 900 | 448 | 158 | 120 | 0 | 90 | 13 | 0
7:30 | 3352 | 702 | 1975.5 | 0 | 895 | 448 | 158 | 120 | 0 | 88 | 33 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3328 | 702 | 1972 | 0 | 890 | 448 | 158 | 120 | 0 | 86 | 53 | 0
8:30 | 3315 | 702 | 1953.5 | 0 | 867 | 449 | 158 | 120 | 0 | 87 | 72 | 0
9:00 | 3302 | 702 | 1935 | 0 | 844 | 450 | 158 | 120 | 0 | 88 | 91 | 0
9:30 | 3346 | 701.5 | 1987 | 0 | 799 | 454.5 | 157.5 | 120 | 0 | 83 | 100.5 | 0
10:00 | 3390 | 701 | 2039 | 0 | 754 | 459 | 157 | 120 | 0 | 78 | 110 | 0
10:30 | 3445 | 701.5 | 2007 | 0 | 843.5 | 479.5 | 157 | 120 | 0 | 87 | 113.5 | 0
11:00 | 3500 | 702 | 1975 | 0 | 933 | 500 | 157 | 120 | 0 | 96 | 117 | 0
11:30 | 3553 | 701.5 | 1992.5 | 0 | 1018 | 504.5 | 157.5 | 120 | 0 | 102 | 120 | 0
12:00 | 3606 | 701 | 2010 | 0 | 1103 | 509 | 158 | 120 | 0 | 108 | 123 | 0
12:30 | 3574 | 701 | 1977 | 0 | 1428 | 509.5 | 158 | 120 | 0 | 111 | 120 | 0
13:00 | 3542 | 701 | 1944 | 0 | 1753 | 510 | 158 | 120 | 0 | 114 | 117 | 0
13:30 | 3542 | 701 | 1944 | 0 | 1753 | 510 | 158 | 120 | 0 | 114 | 117 | 0
14:00 | 3542 | 701 | 1944 | 0 | 1753 | 510 | 158 | 120 | 0 | 114 | 117 | 0
14:30 | 3529 | 701 | 1961.5 | 0 | 1707 | 499.5 | 158 | 120 | 0 | 113 | 93 | 0
15:00 | 3516 | 701 | 1979 | 0 | 1661 | 489 | 158 | 120 | 0 | 112 | 69 | 0
15:30 | 3440 | 701 | 1973.5 | 0 | 1639.5 | 494.5 | 158 | 120 | 0 | 109 | 51 | 0
16:00 | 3364 | 701 | 1968 | 0 | 1618 | 500 | 158 | 120 | 0 | 106 | 33 | 0
16:30 | 3382 | 701.5 | 1929 | 0 | 1561.5 | 501 | 158 | 120 | 0 | 104 | 18 | 0
17:00 | 3400 | 702 | 1890 | 0 | 1505 | 502 | 158 | 120 | 0 | 102 | 3 | 0
17:30 | 3518.5 | 701.5 | 2059 | 0 | 1982.5 | 527 | 158 | 120 | 139 | 115 | 1.5 | 0
18:00 | 3637 | 701 | 2228 | 0 | 2460 | 552 | 158 | 120 | 278 | 128 | 0 | 0
18:30 | 3655 | 701 | 2161.5 | 0 | 2759.5 | 581.5 | 158 | 120 | 260.5 | 124 | 0 | 0
19:00 | 3673 | 701 | 2095 | 0 | 3059 | 611 | 158 | 120 | 243 | 120 | 0 | 0
19:30 | 3582 | 701 | 2235 | 0 | 3032 | 611 | 158 | 120 | 192 | 120 | 0 | 0
20:00 | 3591 | 702 | 2206 | 0 | 3035 | 610 | 158 | 120 | 148 | 120 | 0 | 0
20:30 | 3599.5 | 701.5 | 2236 | 0 | 3018.5 | 610.5 | 158 | 120 | 107.5 | 120 | 0 | 0
21:00 | 3608 | 701 | 2266 | 0 | 3002 | 611 | 158 | 120 | 67 | 120 | 0 | 0
21:30 | 3590 | 701.5 | 2266 | 0 | 2937 | 611 | 156.5 | 120 | 57.5 | 121 | 0 | 0
22:00 | 3572 | 702 | 2266 | 0 | 2872 | 611 | 155 | 120 | 48 | 122 | 0 | 0
22:30 | 3567 | 701.5 | 2262.5 | 0 | 2668.5 | 611 | 155.5 | 120 | 49.5 | 118 | 0 | 0
23:00 | 3562 | 701 | 2259 | 0 | 2465 | 611 | 156 | 120 | 51 | 114 | 0 | 0
23:30 | 3545.5 | 701.5 | 2263 | 0 | 2321 | 611 | 156.5 | 120 | 51 | 114 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.2° C
24:00 | 3529 | 702 | 2267 | 0 | 2177 | 611 | 157 | 120 | 51 | 114 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 222.657 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 222.657 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 91 | 91 | 92 | 92 | 91 | 89 | 88 | 88 | 88 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 85 | 86 | 87 | 2076687
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1700000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 11 | 16 | 18 | 20 | 20 | 19 | 15 | 12 | 6 | 0 | [9 empty] | 135270
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | [15 empty] | 68 |  | 55 | 51 | 51 | 51 | 48 | 51 | 51 | 400438
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 68 | 68 | 68 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 34 | 42 | 68 | 68 | 86 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1643454
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [26 empty] | 2296
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 227 | 227 | 227 | 225 | 200 | 150 | 150 | 150 | 150 | 150 | 190 | 213 | 218 | 150 | 180 | 140 | 140 | 135 |  | 82 |  |  | 6 | 5 | 1 | 1 | 3537402
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 25 | 45 | 15 | 15 | 15 | 15 | 82 |  | 185 | 185 | 185 | 185 | 120 | 30 |  | 1083937
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2709000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 135 | 135 | 135 | 135 | 135 | 125 |  | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 2511044
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 23 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 666288
33 | Ashuganj 225 MW CCPP | 218 | 217 | 217 | 216 | 216 | 218 | 190 | 171 | 172 | 209 | 186 | 184 | 182 | 182 | 187 | 190 | 195 | 207 |  | 217 | 214 | 215 | 214 | 214 | 216 | 213 | 4909000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 305 | 325 | 300 | 310 | 290 | 275 | 300 | 335 | 365 | 300 | 300 | 295 | 275 | 265 | 265 |  | 265 | 275 | 265 | 275 | 270 | 270 | 250 | 7126000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 330 | 300 | 290 | 280 | 270 | 290 | 290 | 310 | 310 | 310 | 330 | 295 | 285 | 285 |  | 285 | 290 | 285 | 290 | 285 | 285 | 275 | 7512500
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 48 | 49 | 49 | 50 | 50 |  | 51 | 51 | 51 | 52 | 52 | 49 | 49 | 962880
36 | Chandpur 150 MW CCPP | 136 | 136 | 137 | 138 | 138 | 136 | 138 | 138 | 135 | 139 | 138 | 139 | 135 | 140 | 136 | 137 | 138 | 137 |  | 136 | 138 | 138 | 138 | 138 | 138 | 138 | 3286950
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 346 | 345 | 345 | 344 | 350 | 353 | 334 | 335 | 336 | 336 | 336 | 334 | 343 | 341 | 335 | 341 | 342 | 347 |  | 346 | 304 | 321 | 302 | 302 | 302 | 302 | 8138750
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6167250
41 | Haripur 360MW CCPP(HPL) | 251 | 271 | 293 | 306 | 318 | 331 | 316 | 314 | 315 | 290 | 270 | 256 | 243 | 243 | 245 | 254 | 272 | 280 |  | 280 | 280 | 280 | 291 | 336 | 337 | 337 | 6866000
42 | RPCL 210MW CCPP | 150 | 158 | 160 | 160 | 160 | 163 | 162 | 160 | 157 | 154 | 154 | 154 | 153 | 152 | 152 | 152 | 152 | 154 |  | 179 | 185 | 185 | 182 | 182 | 178 | 182 | 3783840
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 24 | 38 | 47 | 52 | 52 | 50 | 42 | 29 | 15 | 1 | [9 empty] | 358930
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 31 | 31 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 43 |  | 42 | 42 | 43 | 42 | 42 | 42 | 42 | 862000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 32 | 32 | 32 | 32 | 32 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 943800
46 | Shajibazar 330 MW CCPP | 71 | 70 | 71 | 70 | 70 | 70 | 72 | 70 | 70 | 71 | 72 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 90 | 110 | 109 | 110 | 110 | 110 | 110 | 1856000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 61 |  | 62 | 61 | 61 | 61 | 61 | 62 | 62 | 1100064
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1469760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 192 | 179 | 179 | 179 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 141 | 140 | 140 | 164 | 212 |  | 202 | 165 | 165 | 165 | 165 | 165 | 165 | 3779160
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 392000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 227700
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219168
55 | Fenchugonj 51 MW PP (Barakatullah) | 44 | 44 | 44 | 44 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 31 | 31 | 31 | 31 | 40 |  | 44 | 44 | 44 | 43 | 50 | 46 | 50 | 865800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 16 | 16 | 16 | 23 | 23 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 545568
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 280 | 290 |  | 270 | 310 | 300 | 300 | 290 | 280 | 290 | 6376000
| Bibiyana South 400 MW | 320 | 270 | 270 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 290 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 6077700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 35 | 35 | 55 | 55 | 55 | 610273
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 0 | 5 |  | 18 | 24 | 24 | 24 | 24 |  |  | 112080
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 439344
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 |  | 16 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 363528
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 19 | 19 | 19 |  | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 467316
63 | Impoprt (Tripura) | 120 | 118 | 114 | 110 | 108 | 100 | 90 | 86 | 88 | 78 | 96 | 108 | 114 | 110 | 112 | 106 | 102 | 128 |  | 120 | 120 | 120 | 120 | 122 | 114 | 114 | 2615040
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 40 | 42 | 38 | 29 | 10 | 14 | 28 | 36 | 31 | 29 | 18 | 25 | 36 |  | 36 | 36 | 36 | 42 | 42 | 42 | 42 | 840000
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 516096
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 212040
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 609600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 19 | 20 | 21 | 18 | 18 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 503780
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 23 | 23 | 20 | 18 | 18 | 13 | 13 | 13 | 17 | 17 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 571500
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 |  | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 757900
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 534227
| Feni Lanka Power | [16 empty] | 5 | 52 |  | 52 | 52 | 34 | 17 | 17 |  |  | 182400
| Chowmuhani 113 MW | 50 | 51 | 49 | 48 | 50 | 48 | 48 | 49 | 49 | 49 | 42 | 41 | 48 | 48 | 49 | 82 | 87 | 97 |  | 96 | 97 | 97 | 97 | 97 | 91 | 57 | 1531320
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 108 | 108 | 72 | 72 | 72 | 72 | 156 | 162 | 162 | 108 | 108 | 140 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3402720
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [17 empty] | 64 |  | 64 | 64 | 48 | 16 |  |  |  | 183360
80 | Jamalpur 95 MW PP(Powerpac) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 36480
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 2 | 8 | 8 | 8 | 8 | 18 |  | 43 | 43 | 43 | 43 | 43 |  |  | 268392
| Gazipur 100 MW PP | [17 empty] | 17 |  | 17 | [6 empty] | 32088
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 30721
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 21 | 25 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 842719
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 73 | 34 | 34 | 17 | 17 | 17 | 24 | 34 | 44 | 68 | 68 | 90 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1916100
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 25 | 25 | [10 empty] | 8 | 12 | 13 | 13 | 12 | 22 |  | 24 | 25 | 25 | 24 | 26 | 25 | 24 | 291913
86 | Meghnaghat CCPP ( Summit) | 250 | 255 | 270 | 250 | 255 | 245 | 255 | 250 | 250 | 290 | 260 | 290 | 240 | 275 | 240 | 250 | 240 | 260 |  | 240 | 270 | 262 | 260 | 235 | 235 | 242 | 6187753
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 67 | 53 | 53 |  |  |  | 2 | 36 | 53 | 84 | 104 | 104 | 55 | 34 | 60 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1772160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 10 | 10 | 50 | 30 | 60 | 60 | 20 | 50 |  | 50 | 50 | 50 | 50 | 50 | 10 |  | 502680
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1240128
94 | Gagnagar 102 MW PP (Digital Power) | 64 | 64 | 64 | 32 | 32 | 32 | 32 | 32 | 7 | 7 | 7 | 7 | 32 | 32 | 32 | 16 | 16 | 48 |  | 48 | 48 | 48 | 48 | 24 | 24 | 24 | 824832
95 | Patenga 50MW PP (Baraka) | 33 | 33 | 33 | 20 | 19 | 6 |  |  |  |  | 11 | 19 | 23 | 25 | 25 | 21 | 38 | 49 |  | 50 | 50 | 50 | 50 | 25 | 25 | 25 | 600000
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 13 |  | 12 | 12 | 12 | 12 | 12 |  |  | 66240
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 40 | 55 | 1322671
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 25 | 55 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 561417
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 110 | 163 |  | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 3165218
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 3 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 14450
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1303920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 150 | 150 | 120 | 100 | 80 | 60 | 40 | 63 | 80 | 80 | 80 | 94 | 110 | 110 | 125 | 160 | 120 | 146 |  | 181 | 190 | 200 | 200 | 160 | 140 | 90 | 3062400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 100 | 100 | 100 | 100 | 95 | 77 | 70 | 70 | 74 | 78 | 78 | 78 | 91 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 63 | 60 | 60 | 60 | 1951776
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 76 | 90 | 90 | 90 | 90 | 10 | 10 | 10 | 12 | 90 | 76 | 90 | 90 | 76 | 76 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1754880
116 | Chandpur 200MW (Desh energy) | 120 | 85 | 51 | 34 | 34 | 17 |  |  |  |  | 3 | 22 | 100 | 100 | 106 | 135 | 100 | 126 |  | 200 | 200 | 200 | 200 | 200 | 200 | 155 | 2360640
117 | Ashuganj 150MW PP (Midland) | 135 | 80 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 21 | 51 | 70 | 78 | 92 | 103 | 110 |  | 118 | 120 | 120 | 130 | 135 | 137 | 130 | 1742981
118 | Bibiyana-III 400 MW CCPP | 322 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 241 | 242 | 242 | 242 | 241 | 241 | 241 | 320 |  | 322 | 322 | 322 | 322 | 322 | 321 | 322 | 6405000
| Jamalpur 115 MW PP (United) | [16 empty] | 2 | 28 |  | 45 | 25 | 8 | 8 | 8 |  |  | 138000
| Anwara 300 MW PP (United) | 302 | 302 | 304 | 307 | 302 | 305 | 304 | 304 | 268 | 187 | 161 | 159 | 213 | 213 | 51 | 103 | 105 | 260 |  | 304 | 304 | 306 | 305 | 305 | 304 | 305 | 5866255
| Juldah unit-2 (Acorn) | 100 | 70 | 70 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 64 | 76 | 76 | 76 | 76 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1553280
| Anlima Energy Ltd. | 35 | [15 empty] | 0 | 17 |  | 53 | 53 | 53 | 53 | 53 | 53 | 45 | 383891
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443160
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 11 | 24 | 29 | 27 | 33 | 30 | 26 | 18 | 8 | 1 | [9 empty] | 213765
120 | Eastern Zone Total | 6969 | 6620 | 6500 | 6252 | 6118 | 5936 | 5543 | 5485 | 5419 | 5410 | 5582 | 5856 | 6232 | 6183 | 6068 | 5974 | 5945 | 7196 |  | 7597 | 7539 | 7503 | 7494 | 7350 | 7049 | 6861 | 155923524
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 200 | 200 | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3262080
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 70 | 35 | 17 | 17 | [5 empty] | 2 | 22 | 80 | 53 | 53 | 35 | 35 | 70 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1351200
130
131
132 | United Payra Power Ltd. | [17 empty] | 15 |  | 35 | 35 | 35 | 35 | 35 |  |  | 186000
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 202 | 202 | 202 | 202 | 182 | 182 | 182 | 182 | 182 | 181 | 201 | 213 | 218 | 195 | 181 | 142 | 223 |  | 207 | 223 | 225 | 224 | 224 | 224 | 223 | 4794870
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 22 | 22 | 22 | 22 | 23 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 539011
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1555000
140 | Bhola 33 MW PP (Venture) | 25 | 24 | 23 | 22 | 21 | 21 | 17 | 16 | 15 | 16 | 14 | 20 | 20 | 20 | 20 | 18 | 18 | 28 |  | 27 | 28 | 28 | 28 | 29 | 28 | 28 | 515227
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 233568
146 | Bheramara HVDC | 714 | 713 | 701 | 702 | 702 | 702 | 702 | 702 | 702 | 701 | 702 | 701 | 701 | 702 | 701 | 701 | 702 | 701 |  | 701 | 701 | 702 | 701 | 702 | 701 | 702 | 16968727
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 500 | 470 | 470 | 440 | 440 | 410 | 370 | 370 | 370 | 380 | 420 | 430 | 430 | 380 | 410 | 420 | 420 | 470 |  | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 11829500
149
150 | Barapukuria TPP Unit-1 | 78 | 77 | 79 | 79 | 79 | 79 | 78 | 78 | 80 | 79 | 80 | 79 | 80 | 80 | 79 | 80 | 82 | 82 |  | 81 | 81 | 80 | 81 | 81 | 81 | 81 | 1866764
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 | [8 empty] | 64896
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 37320
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 174 | 178 | 180 | 186 | 173 | 173 | 168 | 173 | 164 | 169 | 201 | 196 | 187 | 168 | 188 | 193 | 184 | 178 |  | 178 | 187 | 192 | 202 | 184 | 184 | 187 | 4578327
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 187 | 187 | 188 | 185 | 168 | 158 | 166 | 166 | 170 | 206 | 200 | 189 | 184 | 188 | 169 | 166 | 168 |  | 180 | 186 | 187 | 193 | 186 | 185 | 182 | 4613391
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 371 | 410 | 389 | 419 | 335 | 295 | 334 | 339 | 313 | 420 | 415 | 387 | 363 | 400 | 400 | 386 | 310 | 392 |  | 345 | 398 | 385 | 398 | 380 | 390 | 378 | 9127236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 19 | 18 | 18 | 18 | 17 | 18 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 474720
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 167166
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 |  | 27 | 12 | 12 |  |  |  |  | 67170
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 16 |  | 28 | 28 | [5 empty] | 58795
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 5 | 8 | 8 | 8 | 8 | 22 |  | 52 | 52 | 52 | 52 | 52 |  |  | 316800
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 80 |  | 96 | 49 | 49 |  |  |  |  | 197464
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | 35 | 35 | 35 | 35 |  | 5 | 35 | 35 | 35 | 43 | 84 | 70 | 95 | 50 | 50 | 75 |  | 94 | 100 | 108 | 113 | 113 | 113 | 113 | 1677312
172 | Confidence Power Bogura Unit-1 113 MW | 70 | [9 empty] | 20 | 50 | 100 | 50 | 100 | 50 | 50 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 1310400
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [11 empty] | 12 | 34 | 34 | 64 | 70 | 38 | 100 |  | 113 | 113 | 113 | 113 | 113 | 68 |  | 899625
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 4 | 5 | 6 | 7 | 7 | 6 | 4 | 2 | 1 | [9 empty] | 40840
178
178