## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-11-01 | Monday
|  |  | Date (day): | 2021-11-01 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13528.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14872 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-10-31 | 2021-11-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 98 | 102 | 90 | 102 | 6 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 403 | 360 | 412 | 0
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 172 | 206 | 270 | 270 | 90 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 250 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 42 | 42 | 45 | 45
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 25 | 24 | 35 | 35 |  | 65 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 333 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 64 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 38 | 35 | 35 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 22 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 0 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 145 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 106 | 105 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 52 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2367 | 2625 | 3333 | 3786 | 586 | 1135
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 21 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 114 | 80 | 120 | 110 |  | Unit 2 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 90 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 51 | 100
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 30 | 40 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21 |  | 1 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 9 | 5 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 9 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 285 | 303 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 35 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 48 | 108 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 978 | 1304 | 1398 | 1506 | 175 | 682
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 110 | 110 | 25 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 180 | 200 | 215
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 290 | 320 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 300 | 320 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 36 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 58 | 120 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 136 | 138 | 138 |  | 25 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 13 | 195 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 130 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 0 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 2 | 25 | 43 | 43 |  |  | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 22 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 4 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 48 | 92 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1573 | 1815 | 2114 | 2375 | 475 | 111
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 126 | 140 | 170 | 170 | 32 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 8 | 8 | 8 |  |  | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 120 | 182 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 16 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 331 | 391 | 588.6 | 537 | 32 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 41 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 110 | 111 | 110 | 110 |  | 220 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 47 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 62 | 60 | 65
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 84 | 81 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 192 | 192 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 275 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 322 | 322 | 324 | 324 | 76 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1707 | 1677 | 1817 | 1825 | 139 | 395
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 718 | 718 | 738 | 738
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 220 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 30 | 340 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 20 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 50 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 858 | 1023 | 1453 | 1743 | 0 | 24
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 30 | 28 | 30
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 18 | 18 | 22 | 58 | 37 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 290 | 390 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 191 | 220 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 585 | 740 | 1065 | 1253 | 37 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 188 | 174 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 184 | 210 | 210 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 400 | 362 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 16 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 15 | 95 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 60 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 80 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 959 | 1009 | 1556 | 1651 | 310 | 96
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 82 | 83 | 83
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 87 | 195 | 204 | 196 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 9445 | 10779 | 13528.6 | 14872 | 1754 | 2971
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9097.1324 | 10382 | 13030.3298 | 14324.2512
| A. |  | 2021-10-31 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 10779 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7775 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10779 | MW
| 3 | Day peak Generation : |  |  | 9445 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10382 | MW
| 4 | Evening peak Generation : |  |  | 10779 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 220.3073 | MKWHr | By Solar | 0.77364 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 142.211 | MKWHr |  | By Oil: | 45.0455 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 10.9153 | MKWHr |  | By Hydro: | 1.2215 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1754 | MW | Dhaka | 4007 | 4007 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2971 | MW | Chittagong | 1311 | 1311 |  | 0 |  | 18:00 |  | 138
|  |  |  | Total = |  |  | 4725 | MW | Khulna | 1154 | 1154 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1110.07 | MMCFD |  |  | Rajshahi | 917 | 917 |  | 0 |  | 19:00 |  | 130
| 8 | Fuel Cost : | i) Gas : | Taka | 151696960.7 | ii) Oil : | Taka | 342474503.89 | Comilla | 945 | 945 |  | 0 |  | 19:30 |  | 130
|  |  | iii) Coal : |  | 51094955.54 | Total | Taka | 545266420.13 | Mymensingh | 755 | 755 |  | 0 |  | 20:00 |  | 128
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.14 | MKWHr. | Sylhet | 431 | 431 |  | 0 |  | 21:00 |  | 126
|  | ii) During Peak Demand : |  |  | -6 | MW (E to W) at | 19:00 | hrs | Barisal | 274 | 274 |  | 0 |  | 22:00 |  | 118
|  | iii) Maximum : |  |  | -150 | MW at | 20:00 | hrs | Rangpur | 588 | 588 |  | 0 |  | 23:00 |  | 118
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.7° C |  |  | Total | 10382 | 10382 |  | 0
| B. |  | 2021-11-01 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 28.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14872 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
| 4 | Reserve(Generation end) |  |  |  | 3872 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 224.8242 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7312 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3476 | MKWHr. | ii) HVDC Flow at Peak Time |  | 718 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7926 | MKWHr. | iii) Maximum HVDC Flow : |  | 721 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.98 |  | (b) Today: | 103.93 |  | (c) Rule Curve: |  | 109
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-10-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 97 | 0 | 389 | 312 |  | 0 | 250 | 255 | 0 | 0 | 42 | 300 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 32 | 20 | 23 | 100 | 0 | 0 | 280 | 305 | 180 | 36 | 138 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 21 | 122 | 139 | 0 | 22 | 0 | 40 | 30 | 47 | 0 | 130 | 110 | 62 | 81 | 0 | 192 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 90 | 100 | 68 | 322 | 0 | 0 | 105 | 0 | 302 | 35 | 110 | 0 | 59 | 60 | 0 | 95 | 0 | 162 | 0 | 0 | 17 | 0 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 18 | 0 | 142 | 0 | 367 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 420 | 222 | 0 | 0 | 0 |  | 6503 | 2472 | 8975 | 3519 | 718 | 2273 | 0 | 1666 | 500 | 40 | 120 | 17 | 122 | 0 | 0 | 103.98
2:00 | 0 | 0 | 0 | 110 | 0 | 96 | 0 | 380 | 336 |  | 0 | 250 | 245 | 0 | 0 | 42 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 23 | 100 | 0 | 0 | 280 | 305 | 180 | 36 | 138 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 118 | 157 | 0 | 22 | 0 | 40 | 30 | 47 | 0 | 130 | 109 | 62 | 81 | 0 | 192 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 70 | 0 | 70 | 51 | 0 | 322 | 0 | 0 | 68 | 0 | 250 | 35 | 68 | 0 | 58 | 60 | 320 | 73 | 0 | 108 | 0 | 0 | 17 | 0 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 18 | 0 | 142 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 218 | 0 | 0 | 0 |  | 6431 | 2314 | 8745 | 3847 | 718 | 2273 | 0 | 1159 | 470 | 40 | 120 | 0 | 118 | 0 | 0 | 103.98
3:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 379 | 342 |  | 0 | 250 | 240 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 29 | 100 | 0 | 0 | 280 | 305 | 180 | 36 | 137 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 114 | 163 | 0 | 22 | 0 | 40 | 30 | 47 | 0 | 130 | 110 | 62 | 81 | 0 | 192 | 18 | 0 | 10 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 65 | 0 | 70 | 0 | 0 | 322 | 0 | 0 | 34 | 0 | 250 | 35 | 51 | 0 | 59 | 10 | 320 | 45 | 0 | 54 | 0 | 0 | 17 | 0 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 17 | 0 | 142 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 210 | 0 | 0 | 0 |  | 6118 | 2289 | 8407 | 3852 | 718 | 2252 | 0 | 851 | 460 | 40 | 120 | 0 | 114 | 0 | 0 | 103.98
4:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 379 | 342 |  | 0 | 250 | 230 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 280 | 305 | 180 | 36 | 136 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 112 | 163 | 0 | 22 | 0 | 40 | 30 | 47 | 0 | 130 | 111 | 52 | 10 | 0 | 192 | 18 | 0 | 0 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 52 | 0 | 70 | 0 | 0 | 322 | 0 | 0 | 34 | 0 | 217 | 35 | 51 | 0 | 58 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 17 | 0 | 142 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 219 | 0 | 0 | 0 |  | 5819 | 2297 | 8116 | 3822 | 718 | 2186 | 0 | 668 | 450 | 40 | 120 | 0 | 112 | 0 | 0 | 103.98
5:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 371 | 342 |  | 0 | 250 | 260 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 17 | 33 | 25 | 0 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 280 | 305 | 180 | 36 | 138 | 26 | 30 | 0 | 7 | 0 | 0 | 0 | 22 | 11 | 10 | 21 | 106 | 163 | 0 | 22 | 0 | 40 | 30 | 8 | 0 | 130 | 111 | 40 | 10 | 0 | 192 | 18 | 0 | 0 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 52 | 0 | 50 | 0 | 0 | 322 | 0 | 0 | 34 | 0 | 214 | 35 | 34 | 0 | 59 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 17 | 0 | 142 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 223 | 0 | 0 | 0 |  | 5629 | 2237 | 7866 | 3776 | 718 | 2112 | 0 | 614 | 380 | 40 | 120 | 0 | 106 | 0 | 0 | 103.98
6:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 353 | 329 |  | 0 | 250 | 235 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 26 | 33 | 25 | 0 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 23 | 100 | 0 | 0 | 280 | 305 | 180 | 36 | 136 | 26 | 30 | 0 | 7 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 98 | 163 | 0 | 22 | 0 | 40 | 30 | 8 | 0 | 130 | 111 | 40 | 10 | 0 | 192 | 18 | 0 | 0 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 52 | 0 | 50 | 0 | 0 | 322 | 0 | 0 | 36 | 0 | 251 | 35 | 35 | 0 | 58 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 17 | 0 | 144 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 224 | 0 | 0 | 0 |  | 5619 | 2179 | 7798 | 3759 | 718 | 2030 | 0 | 653 | 380 | 40 | 120 | 0 | 98 | 0 | 0 | 103.98
7:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 311 | 272 |  | 0 | 250 | 270 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 26 | 33 | 25 | 0 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 27 | 100 | 0 | 0 | 285 | 305 | 182 | 36 | 138 | 26 | 30 | 0 | 7 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 94 | 163 | 0 | 22 | 0 | 41 | 30 | 8 | 0 | 110 | 110 | 40 | 10 | 0 | 192 | 18 | 0 | 0 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 52 | 3 | 50 | 0 | 0 | 322 | 0 | 0 | 68 | 1 | 251 | 35 | 68 | 0 | 58 | 10 | 320 | 0 | 7 | 0 | 0 | 0 | 17 | 5 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 18 | 0 | 147 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 180 | 0 | 0 | 0 |  | 5605 | 2170 | 7775 | 3731 | 718 | 1968 | 0 | 718 | 370 | 40 | 120 | 0 | 94 | 16 | 0 | 103.97
8:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 305 | 267 |  | 0 | 250 | 265 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 26 | 33 | 25 | 4 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 10 | 100 | 0 | 0 | 280 | 305 | 180 | 36 | 138 | 23 | 30 | 0 | 14 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 96 | 163 | 0 | 22 | 1 | 41 | 30 | 8 | 0 | 110 | 110 | 40 | 10 | 0 | 192 | 18 | 0 | 0 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 72 | 10 | 50 | 0 | 2 | 321 | 0 | 0 | 68 | 2 | 252 | 35 | 68 | 0 | 58 | 40 | 320 | 5 | 24 | 16 | 0 | 0 | 17 | 15 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 18 | 0 | 156 | 0 | 336 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 300 | 152 | 0 | 0 | 2 |  | 5741 | 2166 | 7907 | 3730 | 718 | 1933 | 0 | 835 | 380 | 40 | 120 | 0 | 96 | 55 | 0 | 103.97
9:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 307 | 230 |  | 0 | 250 | 270 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 26 | 33 | 25 | 25 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 20 | 5 | 100 | 0 | 0 | 300 | 305 | 183 | 36 | 139 | 20 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 24 | 15 | 100 | 153 | 0 | 22 | 1 | 41 | 30 | 43 | 0 | 110 | 110 | 61 | 78 | 0 | 192 | 18 | 0 | 0 | 300 | 24 | 2 | 0 | 0 | 0 | 0 | 70 | 0 | 80 | 15 | 90 | 0 | 10 | 323 | 0 | 0 | 75 | 2 | 252 | 35 | 77 | 0 | 58 | 40 | 320 | 17 | 39 | 43 | 0 | 0 | 17 | 19 |  | 719 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 17 | 0 | 162 | 0 | 340 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 300 | 151 | 0 | 0 | 3 |  | 6052 | 2218 | 8270 | 3771 | 719 | 2043 | 0 | 1014 | 381 | 40 | 120 | 0 | 100 | 82 | 0 | 103.97
10:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 352 | 203 |  | 0 | 250 | 265 | 0 | 0 | 30 | 333 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 54 | 0 | 15 | 21 | 25 | 26 | 33 | 25 | 25 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 21 | 4 | 100 | 0 | 0 | 330 | 350 | 180 | 36 | 136 | 23 | 54 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 102 | 147 | 0 | 22 | 2 | 41 | 30 | 44 | 0 | 130 | 110 | 61 | 81 | 0 | 192 | 18 | 0 | 7 | 290 | 24 | 2 | 0 | 0 | 0 | 0 | 103 | 0 | 102 | 18 | 76 | 0 | 16 | 321 | 2 | 0 | 89 | 4 | 285 | 35 | 100 | 0 | 59 | 65 | 320 | 17 | 49 | 75 | 0 | 0 | 17 | 24 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 17 | 0 | 156 | 0 | 414 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 0 | 300 | 151 | 0 | 0 | 4 |  | 6470 | 2301 | 8771 | 3966 | 718 | 2131 | 0 | 1207 | 381 | 40 | 120 | 0 | 102 | 106 | 0 | 103.97
11:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 401 | 182 |  | 0 | 250 | 275 | 0 | 0 | 41 | 335 | 0 | 0 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 40 | 0 | 50 | 21 | 25 | 22 | 33 | 25 | 33 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 21 | 3 | 100 | 0 | 0 | 310 | 350 | 181 | 36 | 136 | 20 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 112 | 140 | 0 | 22 | 2 | 41 | 30 | 44 | 0 | 130 | 110 | 61 | 83 | 0 | 192 | 18 | 0 | 9 | 290 | 23 | 5 | 0 | 7 | 0 | 0 | 120 | 0 | 102 | 18 | 90 | 0 | 35 | 322 | 8 | 0 | 90 | 4 | 285 | 35 | 110 | 0 | 51 | 90 | 320 | 50 | 52 | 158 | 15 | 0 | 17 | 27 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 17 | 0 | 169 | 0 | 392 | 17 | 0 | 40 | 0 | 0 | 0 | 6 | 0 | 290 | 151 | 0 | 0 | 5 |  | 6788 | 2291 | 9079 | 3981 | 718 | 2102 | 0 | 1519 | 373 | 40 | 120 | 0 | 112 | 114 | 0 | 103.97
12:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 398 | 172 |  | 0 | 250 | 270 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 24 | 0 | 25 | 0 | 0 | 0 | 38 | 22 | 0 | 19 | 25 | 30 | 33 | 25 | 51 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 21 | 21 | 2 | 100 | 0 | 0 | 310 | 350 | 181 | 36 | 138 | 26 | 49 | 0 | 51 | 0 | 0 | 2 | 22 | 11 | 25 | 20 | 116 | 126 | 0 | 22 | 2 | 41 | 30 | 42 | 0 | 163 | 110 | 61 | 80 | 0 | 192 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 15 | 0 | 0 | 120 | 0 | 106 | 14 | 76 | 13 | 58 | 322 | 8 | 0 | 90 | 1 | 285 | 35 | 110 | 0 | 48 | 90 | 320 | 90 | 53 | 162 | 48 | 0 | 17 | 27 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | 0 | 200 | 0 | 400 | 20 | 0 | 60 | 0 | 0 | 0 | 6 | 80 | 290 | 191 | 0 | 0 | 5 |  | 6956 | 2489 | 9445 | 4026 | 718 | 2160 | 0 | 1786 | 371 | 40 | 120 | 0 | 116 | 108 | 0 | 103.97
13:00 | 0 | 0 | 0 | 110 | 0 | 100 | 0 | 398 | 156 |  | 0 | 250 | 260 | 0 | 0 | 42 | 333 | 0 | 0 | 0 | 58 | 0 | 24 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 27 | 33 | 25 | 51 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 45 | 21 | 2 | 80 | 0 | 0 | 265 | 305 | 181 | 36 | 136 | 26 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 20 | 118 | 118 | 0 | 22 | 2 | 41 | 30 | 47 | 0 | 110 | 111 | 61 | 83 | 0 | 192 | 18 | 0 | 10 | 280 | 24 | 5 | 0 | 60 | 0 | 0 | 120 | 0 | 117 | 18 | 90 | 88 | 80 | 323 | 8 | 0 | 90 | 1 | 288 | 35 | 110 | 0 | 48 | 90 | 320 | 92 | 49 | 162 | 107 | 0 | 17 | 25 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 18 | 0 | 186 | 0 | 330 | 105 | 0 | 105 | 0 | 50 | 0 | 7 | 112 | 290 | 214 | 0 | 0 | 4 |  | 7116 | 2640 | 9756 | 3888 | 718 | 2038 | 0 | 2357 | 371 | 40 | 120 | 0 | 118 | 106 | 0 | 103.96
14:00 | 0 | 0 | 0 | 110 | 0 | 100 | 0 | 359 | 156 |  | 0 | 250 | 265 | 0 | 0 | 42 | 280 | 0 | 0 | 0 | 58 | 0 | 25 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 27 | 33 | 25 | 25 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 46 | 21 | 4 | 80 | 0 | 0 | 260 | 265 | 181 | 36 | 138 | 25 | 52 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 20 | 128 | 117 | 0 | 22 | 2 | 41 | 30 | 47 | 0 | 110 | 109 | 40 | 82 | 0 | 192 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 60 | 0 | 0 | 140 | 0 | 116 | 14 | 90 | 85 | 117 | 323 | 8 | 0 | 90 | 3 | 289 | 53 | 110 | 0 | 56 | 90 | 320 | 93 | 40 | 162 | 108 | 0 | 17 | 20 |  | 717 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 18 | 0 | 170 | 0 | 312 | 105 | 0 | 113 | 0 | 40 | 0 | 7 | 112 | 290 | 219 | 0 | 0 | 4 |  | 7029 | 2596 | 9625 | 3703 | 717 | 2043 | 0 | 2413 | 371 | 40 | 120 | 0 | 128 | 90 | 0 | 103.96
15:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 353 | 166 |  | 0 | 250 | 250 | 0 | 0 | 42 | 280 | 0 | 0 | 0 | 58 | 0 | 25 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 27 | 33 | 8 | 25 | 0 | 36 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 46 | 21 | 4 | 80 | 0 | 0 | 290 | 290 | 181 | 36 | 135 | 26 | 52 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 20 | 126 | 117 | 0 | 22 | 1 | 42 | 30 | 44 | 0 | 130 | 110 | 61 | 82 | 0 | 191 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 65 | 0 | 0 | 120 | 0 | 116 | 11 | 90 | 85 | 120 | 322 | 8 | 0 | 105 | 2 | 286 | 45 | 110 | 0 | 58 | 90 | 320 | 93 | 28 | 162 | 108 | 0 | 17 | 14 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 18 | 0 | 167 | 0 | 360 | 105 | 0 | 113 | 0 | 36 | 0 | 5 | 113 | 300 | 214 | 0 | 0 | 3 |  | 7095 | 2639 | 9734 | 3749 | 718 | 2097 | 0 | 2404 | 380 | 76 | 120 | 0 | 126 | 64 | 0 | 103.95
16:00 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 352 | 176 |  | 0 | 250 | 240 | 0 | 0 | 42 | 280 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 35 | 17 | 35 | 20 | 25 | 27 | 33 | 25 | 25 | 0 | 79 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 19 | 21 | 4 | 80 | 0 | 0 | 290 | 290 | 180 | 36 | 136 | 26 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 21 | 118 | 125 | 0 | 22 | 0 | 42 | 30 | 43 | 0 | 130 | 110 | 61 | 82 | 0 | 192 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 65 | 0 | 0 | 120 | 0 | 117 | 5 | 90 | 85 | 80 | 322 | 8 | 0 | 105 | 1 | 286 | 35 | 110 | 0 | 50 | 90 | 320 | 60 | 11 | 162 | 53 | 0 | 12 | 6 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 18 | 0 | 165 | 0 | 354 | 70 | 0 | 50 | 0 | 35 | 0 | 3 | 50 | 300 | 201 | 0 | 0 | 1 |  | 6867 | 2454 | 9321 | 3771 | 718 | 2077 | 0 | 1989 | 382 | 119 | 120 | 0 | 118 | 27 | 0 | 103.95
17:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 351 | 203 |  | 0 | 250 | 230 | 0 | 0 | 42 | 280 | 0 | 0 | 0 | 40 | 16 | 24 | 0 | 0 | 0 | 35 | 17 | 35 | 20 | 25 | 24 | 33 | 25 | 25 | 0 | 34 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 5 | 19 | 21 | 6 | 80 | 0 | 0 | 290 | 290 | 180 | 36 | 135 | 29 | 50 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 0 | 21 | 110 | 133 | 0 | 22 | 0 | 42 | 30 | 47 | 0 | 110 | 110 | 62 | 83 | 0 | 192 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 65 | 0 | 0 | 120 | 0 | 116 | 1 | 90 | 51 | 80 | 322 | 12 | 3 | 105 | 0 | 303 | 54 | 110 | 17 | 53 | 100 | 320 | 55 | 1 | 162 | 53 | 0 | 17 | 1 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 18 | 0 | 166 | 0 | 299 | 70 | 0 | 50 | 11 | 34 | 0 | 1 | 50 | 300 | 170 | 0 | 0 | 0 |  | 6837 | 2379 | 9216 | 3754 | 718 | 1995 | 0 | 2043 | 382 | 74 | 120 | 16 | 110 | 4 | 0 | 103.95
18:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 324 | 207 |  | 0 | 250 | 230 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 72 | 64 | 24 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 20 | 33 | 25 | 25 | 0 | 34 | 40 | 115 | 0 | 7 | 0 | 0 | 0 | 0 |  | 8 | 0 | 68 | 100 | 34 | 28 | 21 | 9 | 100 | 0 | 0 | 290 | 300 | 180 | 36 | 136 | 29 | 54 | 0 | 51 | 0 | 0 | 20 | 22 | 11 | 0 | 21 | 138 | 133 | 4 | 22 | 0 | 42 | 30 | 47 | 0 | 163 | 109 | 62 | 84 | 0 | 192 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 116 | 0 | 0 | 141 | 0 | 116 | 0 | 90 | 81 | 98 | 322 | 32 | 21 | 105 | 0 | 303 | 54 | 110 | 114 | 88 | 100 | 320 | 73 | 0 | 162 | 78 | 0 | 17 | 0 |  | 718 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 50 | 0 | 80 | 27 | 43 | 0 | 25 | 36 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 18 | 0 | 168 | 0 | 383 | 95 | 0 | 78 | 50 | 110 | 0 | 0 | 90 | 350 | 215 | 0 | 9 | 0 |  | 7667 | 3061 | 10728 | 3838 | 718 | 2197 | 0 | 2915 | 430 | 74 | 120 | 298 | 138 | 0 | 0 | 103.95
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 403 | 206 |  | 0 | 250 | 250 | 0 | 0 | 42 | 333 | 0 | 0 | 0 | 64 | 16 | 24 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 29 | 33 | 25 | 0 | 0 | 74 | 40 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 68 | 40 | 9 | 50 | 21 | 9 | 100 | 0 | 0 | 290 | 300 | 180 | 36 | 136 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 22 | 11 | 0 | 22 | 130 | 140 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 130 | 111 | 62 | 84 | 0 | 192 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 145 | 0 | 0 | 182 | 0 | 105 | 0 | 90 | 195 | 120 | 322 | 16 | 52 | 105 | 0 | 303 | 54 | 110 | 4 | 92 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 718 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 18 | 0 | 184 | 0 | 362 | 105 | 0 | 113 | 50 | 113 | 0 | 0 | 113 | 390 | 220 | 0 | 17 | 0 |  | 7812 | 2967 | 10779 | 3961 | 718 | 2156 | 0 | 3009 | 472 | 114 | 120 | 99 | 130 | 0 | 0 | 103.95
19:30 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 397 | 206 |  | 0 | 250 | 260 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 40 | 16 | 24 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 29 | 33 | 25 | 0 | 0 | 34 | 40 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 10 | 0 | 50 | 21 | 10 | 100 | 0 | 0 | 290 | 300 | 180 | 36 | 137 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 0 | 22 | 130 | 140 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 130 | 110 | 62 | 84 | 0 | 192 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 182 | 0 | 100 | 0 | 90 | 200 | 120 | 322 | 16 | 52 | 105 | 0 | 304 | 54 | 110 | 0 | 97 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 718 | 0 | 41 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 18 | 0 | 180 | 0 | 373 | 105 | 0 | 113 | 50 | 70 | 0 | 0 | 113 | 400 | 220 | 0 | 0 | 0 |  | 7724 | 2906 | 10630 | 3962 | 718 | 2204 | 0 | 2856 | 482 | 74 | 120 | 84 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 397 | 211 |  | 0 | 250 | 260 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 40 | 16 | 25 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 29 | 33 | 25 | 0 | 0 | 34 | 40 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 68 | 10 | 0 | 50 | 21 | 9 | 100 | 0 | 0 | 330 | 300 | 180 | 36 | 135 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 0 | 22 | 128 | 144 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 130 | 110 | 62 | 84 | 0 | 192 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 145 | 0 | 0 | 182 | 0 | 100 | 0 | 90 | 200 | 120 | 322 | 0 | 17 | 105 | 0 | 305 | 54 | 108 | 0 | 97 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 720 | 0 | 35 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 18 | 0 | 182 | 0 | 337 | 105 | 0 | 113 | 50 | 70 | 0 | 0 | 113 | 400 | 212 | 0 | 0 | 0 |  | 7710 | 2868 | 10578 | 4006 | 720 | 2160 | 0 | 2803 | 483 | 74 | 120 | 84 | 128 | 0 | 0 | 103.95
21:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 396 | 232 |  | 0 | 250 | 260 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 35 | 55 | 17 | 20 | 25 | 29 | 33 | 25 | 0 | 0 | 34 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | 51 | 0 | 0 | 50 | 21 | 27 | 100 | 0 | 0 | 335 | 300 | 180 | 36 | 135 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 0 | 22 | 126 | 148 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 130 | 105 | 62 | 84 | 0 | 192 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 100 | 0 | 90 | 100 | 123 | 322 | 0 | 0 | 105 | 0 | 303 | 54 | 92 | 0 | 97 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 720 | 0 | 75 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 18 | 0 | 182 | 0 | 349 | 105 | 0 | 113 | 50 | 34 | 0 | 0 | 50 | 410 | 221 | 0 | 0 | 0 |  | 7390 | 2845 | 10235 | 4058 | 720 | 2220 | 0 | 2374 | 492 | 74 | 120 | 51 | 126 | 0 | 0 | 103.95
22:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 395 | 262 |  | 0 | 250 | 255 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 20 | 25 | 29 | 33 | 25 | 0 | 0 | 34 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 21 | 34 | 100 | 0 | 0 | 340 | 300 | 180 | 36 | 135 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 0 | 22 | 118 | 154 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 130 | 117 | 63 | 84 | 0 | 192 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 100 | 0 | 90 | 17 | 30 | 322 | 0 | 0 | 105 | 0 | 303 | 54 | 95 | 0 | 97 | 100 | 320 | 90 | 0 | 162 | 53 | 0 | 17 | 0 |  | 721 | 0 | 165 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 18 | 0 | 182 | 0 | 340 | 105 | 0 | 113 | 50 | 0 | 0 | 0 | 50 | 410 | 211 | 0 | 0 | 0 |  | 7025 | 2880 | 9905 | 4168 | 721 | 2217 | 0 | 1960 | 493 | 74 | 120 | 34 | 118 | 0 | 0 | 103.95
23:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 394 | 269 |  | 0 | 250 | 240 | 0 | 0 | 42 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 21 | 25 | 29 | 33 | 25 | 0 | 0 | 34 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 40 | 100 | 0 | 0 | 340 | 300 | 180 | 36 | 137 | 29 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 118 | 153 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 110 | 116 | 40 | 84 | 0 | 192 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 90 | 0 | 90 | 0 | 0 | 322 | 0 | 0 | 105 | 0 | 303 | 54 | 95 | 0 | 96 | 30 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 721 | 0 | 360 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 18 | 0 | 178 | 0 | 380 | 105 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 390 | 220 | 0 | 0 | 0 |  | 6358 | 2931 | 9289 | 4284 | 721 | 2235 | 0 | 1264 | 473 | 74 | 120 | 0 | 118 | 0 | 0 | 103.95
24:00 | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 394 | 311 |  | 0 | 250 | 240 | 0 | 0 | 42 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 25 | 29 | 33 | 25 | 0 | 0 | 34 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 100 | 0 | 0 | 340 | 300 | 180 | 36 | 137 | 29 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 108 | 163 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 110 | 116 | 40 | 84 | 0 | 192 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 68 | 0 | 90 | 0 | 0 | 322 | 0 | 0 | 68 | 0 | 304 | 54 | 97 | 0 | 62 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 721 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 18 | 0 | 168 | 0 | 340 | 70 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 350 | 220 | 0 | 0 | 0 |  | 6228 | 2758 | 8986 | 4243 | 721 | 2236 | 0 | 1052 | 432 | 74 | 120 | 0 | 108 | 0 | 0 | 103.95
KWH | 0 | 0 | 0 | 2677500 | 0 | 2323000 | 0 | 8937480 | 5852000 |  | 0 | 6159500 | 6069324 | 0 | 0 | 887749 | 7420849 | 0 | 0 | 0 | 624528 | 100320 | 279188 | 0 | 0 | 0 | 1060560 | 467599 | 578416 | 424368 | 600000 | 651240 | 826300 | 587400 | 313440 | 0 | 249513 | 972000 | 2700000 | 0 | 25936 | 0 | 0 | 0 | 0 |  | 72480 | 0 | 316488 | 255600 | 49920 | 548640 | 483456 | 351600 | 2333096 | 0 | 0 | 7436000 | 7424000 | 4424000 | 886545 | 3426490 | 592848 | 1201440 | 0 | 1116618 | 0 | 0 | 123077 | 507744 | 243720 | 363900 | 525730 | 2792640 | 3412400 | 53760 | 500400 | 13950 | 984000 | 713280 | 937200 | 0 | 3238609 | 2613000 | 1314336 | 1600320 | 0 | 4596350 | 397000 | 0 | 188820 | 6992500 | 576576 | 233472 | 0 | 935890 | 0 | 0 | 2635200 | 0 | 2184192 | 129330 | 1941120 | 1316640 | 1291345 | 7775000 | 153600 | 129852 | 2097599 | 25201 | 6679200 | 1043652 | 2243125 | 99180 | 1594320 | 1564800 | 7649800 | 1344000 | 353570 | 2633760 | 1021200 | 0 | 438480 | 176345 |  | 17347636 | 0 | 960768 | 0 | 0 | 3014400 | 0 | 0 | 0 | 0 | 0 | 1557000 | 566749 | 0 | 0 | 0 | 0 | 56784 | 0 | 94720 | 35660 | 49145 | 0 | 96480 | 45620 | 477840 | 0 | 176940 | 1937018 | 0 | 0 | 0 | 0 | 0 | 0 | 4384309 | 0 | 437627 | 0 | 4206291 | 0 | 8692327 | 1312320 | 0 | 1357824 | 353088 | 539376 | 0 | 39848 | 956448 | 8978300 | 481934 | 0 | 28800 | 35400 |  | 162086616 | 58220652 | 220307268 | 94637043 | 17347636 | 47573953 | 0 | 41417189 | 10915318 | 1221513 | 3014400 | 613932 | 2792640 | 773644 | 0
Fuel Cost | 0 | 0 | 0 | 3935925 | 0 | 3066360 | 0 | 9026854.8 | 6027560 |  | 0 | 6713855 | 6736949.64 | 0 | 0 | 7510356.54 | 7717682.96 | 0 | 0 | 0 | 5695695.36 | 987148.8 | 2574113.36 | 0 | 0 | 0 | 7742088 | 3614540.27 | 5703181.76 | 318276 | 450000 | 0 | 0 | 0 | 3030964.8 | 0 | 67368.51 | 262440 | 4887000 | 0 | 240945.44 | 0 | 0 | 0 | 0 |  | 0 | 0 | 3069933.6 | 2440980 | 434304 | 4345228.8 | 609154.56 | 1044252 | 3452982.08 | 0 | 0 | 5502640 | 7424000 | 4070080 | 1143643.05 | 3940463.5 | 669918.24 | 1682016 | 0 | 1909416.78 | 0 | 0 | 1175385.35 | 644834.88 | 182790 | 636825 | 394297.5 | 20944800 | 3617144 | 488140.8 | 635508 | 222363 | 1613760 | 1141248 | 1668216 | 0 | 3692014.26 | 2717520 | 2589241.92 | 3056611.2 | 0 | 7951685.5 | 869430 | 0 | 385192.8 | 7062425 | 432432 | 177438.72 | 0 | 7075328.4 | 0 | 0 | 13703040 | 0 | 21492449.28 | 1511867.7 | 15820128 | 14285544 | 9103982.25 | 7230750 | 1400832 | 1227101.4 | 18270087.29 | 0 | 50494752 | 9090208.92 | 19717068.75 | 989816.4 | 13663322.4 | 10421568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99922383.36 | 0 | 1008806.4 | 0 | 0 | 41779584 | 0 | 0 | 0 | 0 | 0 | 1759410 | 878460.95 | 0 | 0 | 0 | 0 | 558754.56 | 0 | 838272 | 274582 | 664440.4 | 0 | 934891.2 | 442514 | 917452.8 | 0 | 133943.58 | 11680218.54 | 0 | 0 | 0 | 0 | 0 | 0 | 5787287.88 | 0 | 656440.5 | 0 | 4921360.47 | 0 | 8605403.73 | 13700620.8 | 0 | 12885749.76 | 3333150.72 | 4185557.76 | 0 | 440320.4 | 7068150.72 | 39414737 | 0 | 0 | 0 | 0 |  | 405845469.57 | 262792493.53 | 668637963.1 | 96450690.99 | 99922383.36 | 55246269.71 | 0 | 294798296.93 | 51094955.54 | 329808.51 | 41779584 | 5896622.96 | 20944800 | 2174551.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 398 | 172 |  | 0 | 250 | 270 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 24 | 0 | 25 | 0 | 0 | 0 | 38 | 22 | 0 | 19 | 25 | 30 | 33 | 25 | 51 | 0 | 0 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 21 | 21 | 2 | 100 | 0 | 0 | 310 | 350 | 181 | 36 | 138 | 26 | 49 | 0 | 51 | 0 | 0 | 2 | 22 | 11 | 25 | 20 | 116 | 126 | 0 | 22 | 2 | 41 | 30 | 42 | 0 | 163 | 110 | 61 | 80 | 0 | 192 | 18 | 0 | 9 | 290 | 24 | 5 | 0 | 15 | 0 | 0 | 120 | 0 | 106 | 14 | 76 | 13 | 58 | 322 | 8 | 0 | 90 | 1 | 285 | 35 | 110 | 0 | 48 | 90 | 320 | 90 | 53 | 162 | 48 | 0 | 17 | 27 |  | 718 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 18 | 0 | 200 | 0 | 400 | 20 | 0 | 60 | 0 | 0 | 0 | 6 | 80 | 290 | 191 | 0 | 0 | 5 |  | 9445 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 403 | 206 | 0 | 0 | 250 | 250 | 0 | 0 | 42 | 333 | 0 | 0 | 0 | 64 | 16 | 24 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 29 | 33 | 25 | 0 | 0 | 74 | 40 | 115 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 68 | 40 | 9 | 50 | 21 | 9 | 100 | 0 | 0 | 290 | 300 | 180 | 36 | 136 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 22 | 11 | 0 | 22 | 130 | 140 | 8 | 22 | 0 | 41 | 30 | 47 | 0 | 130 | 111 | 62 | 84 | 0 | 192 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 145 | 0 | 0 | 182 | 0 | 105 | 0 | 90 | 195 | 120 | 322 | 16 | 52 | 105 | 0 | 303 | 54 | 110 | 4 | 92 | 100 | 320 | 104 | 0 | 162 | 108 | 0 | 17 | 0 |  | 718 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 18 | 0 | 184 | 0 | 362 | 105 | 0 | 113 | 50 | 113 | 0 | 0 | 113 | 390 | 220 | 0 | 17 | 0 |  | 10779 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 110 | 0 | 102 | 0 | 412 | 270 | 0 | 0 | 250 | 300 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 149 | 35 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 51 | 0 | 80 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 90 | 50 | 21 | 10 | 110 | 0 | 0 | 330 | 330 | 215 | 8 | 138 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 164 | 170 | 8 | 22 | 0 | 43 | 42 | 50 | 0 | 163 | 110 | 65 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 135 | 324 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 738 | 0 | 410 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 65 | 30 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 58 | 100 | 210 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 110 | 0 | 90 | 0 | 360 | 270 | 0 | 0 | 250 | 300 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 149 | 35 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 51 | 0 | 40 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 21 | 5 | 110 | 0 | 0 | 320 | 320 | 200 | 8 | 138 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 138 | 170 | 8 | 22 | 1.6 | 43 | 42 | 50 | 0 | 163 | 110 | 60 | 81 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 0 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 135 | 324 | 115 | 105 | 105 | 5 | 300 | 35 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 738 | 0 | 340 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 22 | 50 | 210 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 47 | 0 | 352 | 272 | 0 | 0 | 250 | 230 | 0 | 0 | 18 | 250 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 30 |  | 0 | 0 | 35 | 40 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 80 | 0 | 0 | 270 | 265 | 180 | 8 | 135 | 26 | 10 | 0 | 23 | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 82 | 167 | 0 | 0 | 1 | 30 | 30 | 21 | 0 | 110 | 122 | 40 | 10 | 0 | 165 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 37 | 9 | 20 | 0 | 0 | 324 | 0 | 0 | 17 | 2 | 215 | 54 | 51 | 0 | 25 | 10 | 320 | 4 | 20 | 4 | 0 | 0 | 17 | 11 | 0 | 725 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 17 | 0 | 140 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 154 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 7775 | 7:00
| Highest Generation |  | 10779 | 19:00
| Day Peak Generation |  | 9445 | 12:00
| Evening Peak Generation |  | 10779 | 19:00
| HVDC Max Flow |  | 721 | 22:00
| HVDC EvPeak Flow |  | 718 | 19:00
| Load factor L.F |  | 85.16%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-11-01
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-10-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9445 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7312 | MW
Evening Peak Generation : |  | 10779 | MW Hour : | 19:00 | Available Max Generation : |  | 14872 | MW
E.P. Demand (at gen end) : |  | 10779 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10779 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3872 | MW
Total Gen. (MKWH) : |  | 220.3073 | System Load Factor : | 85.16% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -150 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-11-01
Actual : | 103.93 | Ft.(MSL) , | Rule curve : | 109 | Ft.( MSL )
Gas Consumed : | Total = | 1110.07 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151696960.7
: |  | Coal : | 51094955.54 | Oil : | 342474503.89 | Total : | 545266420.13
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3944.0846 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1341.1791 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1201.647 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1085.7877 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 981.2116 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 791.803 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 442.7732 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 203.8689 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 610.6776 |  |  | 0 | 0%
Total | 0 |  | 10603.0327 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj-Cumilla(N) 230 kV Ckt-1 was under shut down from 10:25 to 21:17 for C/M.
b) B.Baria 132/33 kV T-3 transformer was under shut down from 11:50 to 11:58 for C/M.
c) Baghabari-Ishwardi 132 kV Ckt was under shut down from 08:28 to 15:56 for A/M.
d) Bogura-Sherpur 132 kV Ckt-2 was under shut down from 08:47 to 16:10 for A/M.
e) Dohazari-Cox'sbazar 132 kV Ckt was under shut down from 10:08 to 11:56 for tree trimming.
f) Juldah-Shahmirpur 132 kV Ckt-2 was under shut down from 08:26 to 10:55 for C/M.
g) Fenchuganj 132/33 kV T-1 transformer was under shut down from 09:20 to 11:49 for A/M.
h) Fenchuganj 132/33 kV T-2 transformer was under shut down from 11:52 to 13:52 for A/M.
i) Kurigram 132/33 kV T-2 transformer was shut down from 09:12 to 16:17 for A/M.
j) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 08:58 to 17:24 for A/M.
k) Niamatpur 132/33 kV T-3 transformer was shut down from 08:14 to 17:26 for A/M.
l) Palashbari 132/33 kV T-2 transformer of 33 kV exit Bus was shut down from 10:10 to 15:30 for A/M.
m) Sherpur 132/33 kV T-3 transformer was shut down from 08:35 to 16:39 for A/M.
n) Ponchagarh 132/33 kV T-2 transformer was shut down from 08:13 to 16:01 for A/M.
o) Tongi S/S-Tongi P/P 132 kV Ckt was under shut down from 09:09 to 13:10 for C/M.
p) Kaptai-Chandraghona 132 kV Ckt was switched on at 19:53.
q) Bheramara 410 MW CCPP GT was synchronized at 17:01.
r) Tangail-Mymensing RPCL 132 kV Ckt-1 tripped at 18:04 from both showing Diff. E/F relays and
was switched on at 22:28.
s) Cantonment 132/33 kV T-1 transformer tripped at 16:19 showing buchholz relay at 33 kV end
and was switched on at 19:01
t) Shyampur(New)-Shyampur(Old) 132 kV Ckt-1 tripped at 06:25(01-11-2021) from both end showing
dist. Z1 Y-phase, O/C, E.F relays and was switched on at 07:06(01-11-2021).
u) Shyampur(New)-Shyampur(Old) 132 kV Ckt-2 tripped at 06:25(01-11-2021) from both end showing
dist. Z1 Y-phase, O/C, E.F relays and was switched on at 07:04(01-11-2021).
v) Mirpur-Aminbazar 230 kV Ckt-2 was shut down at 07:38(01-11-2021) for A/M.
w) Madaripur 132/33 kV T-2 transformer was shut down at 07:27(01/11/2021) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-10-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2677500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2323000
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 403 | 8937480
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 206 | 5852000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6159500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 250 | 6069324 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 42 | 887749 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 24 | 279188 | Low demand.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 424368 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7420849
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 624528 | Low demand.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 1060560 | Low demand.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 100320 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 467599
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 578416
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1251240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 826300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 587400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 313440 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 935890 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 105 | 2184192 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 129852 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1344000
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2633760
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 176345
| Dhaka area Total |  |  |  | 5560 | 2625 | 54244800
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 25936 | Low demand.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 129330
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 548640
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 114 | 1221513 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2097599
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 316488 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 255600 | Low demand.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1941120 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 483456 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 9 | 351600
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 9 | 49920 | Low demand.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25201
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 303 | 6679200
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1043652
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2243125
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1564800
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 1021200 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1304 | 22698380
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2333096 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4424000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7436000 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7424000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 592848 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1201440
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 886545 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1116618
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 120 | 1291345 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3426490 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 195 | 1316640
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507744
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243720
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 2792640
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 363900 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 123077 | Low demand.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 525730 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 4 | 99180 | Low demand.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 92 | 1594320 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 438480 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1815 | 38137813
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 140 | 3412400 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 500400
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 8 | 53760
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13950
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 182 | 2635200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 16 | 153600 | Line Shut down
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 353570
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 72480
| Mymensingh Area Total |  |  |  | 622 | 391 | 7195360
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 984000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 713280 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3238609
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 111 | 2613000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 937200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 233472
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1314336
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1600320
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 192 | 4596350 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 397000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 576576
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 6992500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 322 | 7775000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 188820
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7649800 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1677 | 39810263
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 718 | 17347636
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3014400 | Low demand.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 30 | 960768 | Machine problem
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1312320
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 50 | 353088 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1023 | 22988212
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 566749 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1557000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 18 | 437627 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 390 | 8978300
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 481934
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 28800 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 740 | 12050410
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 56784 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 35660 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 49145 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4384309 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 184 | 4206291 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 362 | 8692327 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 45620 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 477840
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 176940
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 96480 | Low demand.
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 15 | 94720 | Low demand.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1357824
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 956448
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35400
| Rajshahi Area Total |  |  |  | 2179 | 1009 | 20665788
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 82 | 1937018
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 539376
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39848
| Rangpur Area Total |  |  |  | 605 | 195 | 2516242
| Total |  |  |  | 20934 | 10779 | 220307268
| Eastern Grid Total |  |  |  | 13975 | 7812 | 162086616
| Western Grid Total |  |  |  | 6959 | 2967 | 58220652
| National Grid Total |  |  |  | 20934 | 10779 | 220307268
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-10-31
(a) ENTIRE EASTERN GRID : |  | 7449 | MW | (b) ENTIRE WESTERN GRID : |  | 2933 | MW
i) Dhaka area |  | 4007 | MW | i) Khulna area |  | 1154 | MW
ii) Chittagong area |  | 1311 | MW | ii) Rajshahi area |  | 917 | MW
iii) Comilla area |  | 945 | MW | iii) Barisal area |  | 274 | MW
iv) Mymensingh area |  | 755 | MW | iv) Rangpur area |  | 588 | MW
v) Sylhet area |  | 431 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10382 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 12:00 | Kishoreganj | 104 | 19:30 | Benapol | 38 | 18:00
Munsiganj | 78 | 20:00 | Netrokona | 83 | 18:00 | Jhenida(Old) | 88 | 18:00
Sonargaon | 71 | 21:00 | Jamalpur | 104 | 18:00 | Bottail | 94 | 18:00
Shyampur | 194 | 12:00 | Sherpur | 100 | 18:00 | G.K Project | 39 | 18:00
Bhulta | 175 | 1:00 | Srimongal | 41 | 19:00 | Faridpur | 110 | 18:00
Madanganj | 40 | 11:00 | Shahjibazar | 89 | 1:00 | Rajbari | 40 | 18:00
Shitalakhya | 110 | 15:00 | Fenchuganj | 39 | 17:00 | Madaripur | 68 | 18:30
Rahim steel | 21 | 11:00 | Kulawara | 38 | 18:00 | Sariatpur | 46 | 18:30
Matuail | 62 | 10:00 | Sylhet | 127 | 18:00 | Gopalganj | 76 | 18:00
Ghorasal | 64 | 16:00 | Chatak | 22 | 18:00 | Bagerhat | 84 | 18:00
Narsingdi | 144 | 19:30 | Sunamganj | 38 | 18:30 | Mongla | 47 | 1:00
Haripur (SBU) | 118 | 10:00 | Biani Bazar | 53 | 18:00 | Satkhira | 84 | 18:00
Sreenagar | 30 | 1:00 | Comilla (S) | 138 | 18:00 | Gallamari | 24 | 13:00
Ullon | 58 | 18:00 | Comilla(N) | 90 | 18:00 | Magura | 44 | 18:00
Hasnabad | 67 | 22:00 | Chandpur | 54 | 18:00 | Norail | 36 | 18:00
Magbazar | 91 | 15:00 | Feni | 109 | 18:00 | Chuadanga | 70 | 18:00
Maniknagar | 64 | 13:00 | Chowmuhani | 166 | 18:30 | Barisal(N) | 30 | 20:00
Bangabhaban | 10 | 10:00 | Ashuganj | 37 | 1:00 | Barisal (S) | 90 | 18:00
Motijheel | 25 | 11:00 | Daudkandi | 122 | 18:30 | Patuakhali | 89 | 19:30
Narinda | 62 | 13:00 | B.Baria | 125 | 18:00 | Bhandaria | 40 | 18:00
Kazla | 80 | 19:00 | Ramganj | 68 | 18:00 | Borguna | 12 | 1:00
Dhanmondi | 184 | 13:00 | Chaddagram | 35 | 18:00 | Borhan Uddin | 32 | 1:00
Lalbag | 71 | 13:00 | PHP | 11 | 13:00 | Ishurdi | 53 | 18:00
Madartek | 66 | 21:00 | Kochua | 48 | 18:00 | Ruppur Paromanobik | 3 | 18:00
Dhaka University | 30 | 11:00 | Madunaghat | 58 | 18:00 | Natore | 90 | 18:00
Aftabnagar | 14 | 13:00 | Hathazari | 87 | 19:30 | Bogra | 115 | 18:00
Fatullah | 57 | 10:00 | Khulshi | 179 | 12:00 | Noagaon | 78 | 19:00
Nawabganj | 38 | 18:00 | Halishahar | 110 | 11:00 | Rajshahi | 106 | 20:00
Keraniganj | 66 | 13:00 | Baraulia | 152 | 16:00 | Rajshahi New | 23 | 18:30
Banani | 30 | 15:00 | Sikalbaha | 38 | 10:00 | C.Nawabganj | 47 | 21:00
Mirpur | 107 | 18:00 | Dohazari | 78 | 18:00 | Amnura | 32 | 19:30
Kalyanpur | 87 | 18:00 | Cox'sbazar | 104 | 20:00 | Pabna | 79 | 18:00
Gulshan | 102 | 13:00 | Chandraghona | 28 | 18:00 | Shahjadpur | 67 | 18:00
Uttara | 72 | 18:00 | Kaptai | 4.2 | 18:30 | Serajganj | 68 | 18:30
Uttara New | 24 | 18:00 | A. Khaer Stl. | 15 | 3:00 | Niyamatpur | 46 | 18:30
Kamrangirchar | 89 | 18:00 | Bakulia | 120 | 19:00 | Joypurhat | 41 | 18:30
Savar | 147 | 18:00 | Julda | 23 | 11:00 | Sherpur(Bogura) | 48 | 18:00
Bhasantec | 115 | 13:00 | TK chemical | 28 | 18:30 | Mohastangor | 46 | 18:00
Agargaon | 79 | 18:00 | Modern Steel | 8 | 13:00 | Bhangura | 21 | 18:00
Satmosjid | 92 | 18:00 | Shahmirpur | 26.5 | 18:00 | Rangpur | 102 | 18:30
Tongi | 112 | 18:00 | Khagrachhari | 22 | 20:00 | Lalmonirhat | 45 | 18:00
Kabirpur | 221 | 15:00 | Matarbari | 37 | 20:00 | Saidpur | 79 | 18:00
Basundhara | 177 | 14:00 | Baroiar Hat | 44 | 18:00 | Purbasadipur | 81 | 18:30
Manikganj | 56 | 21:00 | Rangamati | 12 | 18:00 | Thakurgaon | 61 | 18:00
Joydevpur | 163 | 18:00 | Abul Khair 230 | 134 | 14:00 | Palashbari | 90 | 18:00
New Tongi | 82 | 12:00 | BSRM | 151 | 2:00 | Barapukuria | 38 | 18:30
Kodda | 247 | 18:00 | GPH Ispat | 92 | 18:30 | Panchagar | 45 | 18:00
Dhamrai | 86 | 18:00 | Agrabad | 68 | 18:00 | Joldhaka | 28 | 18:00
Rajendrapur | 100 | 18:00 | Goalpara | 24 | 13:00 | Kurigram | 46 | 18:00
Valuka | 104 | 18:00 | Central S/S | 93 | 18:00 | Mithapukur | 23 | 18:00
Tangail | 164 | 18:00 | Noapara | 32 | 18:30
Mymensing | 165 | 18:00 | Jessore | 98 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-10-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 20:00 | 402 | 10:00 | Kaliakoir | 399 | 0.33333 | 389 | 0.5
| Bheramara | 399 | 18:00 | 394 | 7:00 | Bhulta | 393 | 0.83333 | 380 | 0.66667
| Ashuganj(N) | 398 | 18:00 | 381 | 13:00 | Gopalganj | 409 | 0.625 | 401 | 0.041667
| Payra | 413 | 20:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 235 | 19:30 | 221 | 5:00
| Ishurdi | 235 | 6:00 | 228 | 12:00 | Megnaghat | 236 | 18:00 | 231 | 9:00
| Ashuganj | 245 | 18:00 | 239 | 23:00 | Fenchuganj | 246 | 19:30 | 241 | 4:00
| Serajganj | 235 | 18:00 | 232 | 7:00 | Siddhirganj | 234 | 20:00 | 228 | 10:00
| Baghabari | 234 | 21:00 | 229 | 10:00 | Maniknagar | 232 | 20:00 | 226 | 12:00
| Barapukuria | 238 | 6:00 | 232 | 7:00 | Agargaon | 229 | 8:00 | 222 | 10:00
| Bogra | 229 | 15:00 | 223 | 8:00 | Barisal | 244 | 20:00 | 238 | 21:00
| Rajshahi | 232 | 18:00 | 223 | 11:00 | Bhola 225 MW | 246 | 8:00 | 240 | 24:00
| Khulna South | 235 | 24:00 | 228 | 12:00 | AKSML | 236 | 20:00 | 217 | 5:00
| Rampura | 231 | 17:00 | 227 | 15:00 | BSRM | 234 | 18:00 | 219 | 5:00
| Haripur | 231 | 21:00 | 226 | 12:00 | Bibiyana | 245 | 20:00 | 240 | 5:00
| Hasnabad | 230 | 18:00 | 220 | 23:00 | Bhulta | 236 | 20:00 | 229 | 9:00
| Shyampur | 231 | 20:00 | 225 | 10:00 | Ashuganj (S) | 241 | 18:30 | 234 | 12:00
| Aminbazar | 230 | 1:00 | 224 | 2:00 | Kaliakoir | 231 | 18:00 | 224 | 12:00
| Tongi | 226 | 11:00 | 222 | 5:00 | GPH | 234 | 18:00 | 217 | 5:00
| Comilla (N) | 234 | 18:30 | 228 | 9:00 | Jhenaidah | 231 | 22:00 | 224 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 6:00 | 131 | 9:00 | Madanhat | 138 | 0.77083 | 129 | 0.20833
| Munsiganj | 136 | 1:00 | 132 | 10:00 | Hathazari | 137 | 0.70833 | 131 | 0.20833
| Sonargaon | 136 | 18:00 | 130 | 23:00 | Khulshi | 134 | 0.70833 | 124 | 0.125
| Shyampur | 138 | 20:00 | 134 | 10:00 | Halishahar | 136 | 0.75 | 126 | 0.20833
| Bhulta | 131 | 4:00 | 128 | 10:00 | Baraulia | 136 | 0.79167 | 126 | 0.20833
| Madanganj | 136 | 3:00 | 131 | 10:00 | Sikalbaha | 139 | 0.75 | 125 | 0.125
| Shitalakhya | 136 | 18:00 | 132 | 10:00 | Dohazari | 131 | 0.77083 | 119 | 0.125
| Rahim steal | 135 | 4:00 | 132 | 10:00 | Cox'sbazar | 121 | 0.70833 | 104 | 0.45833
| Matuail | 135 | 6:00 | 131 | 9:00 | Chandraghona | 137 | 0.75 | 124 | 0.16667
| Ghorasal | 140 | 14:00 | 137 | 15:00 | Kaptai | 135 | 0.75 | 125 | 0.041667
| Narsinghdi | 135 | 7:00 | 130 | 1:00 | A. Khaer Stl. | 136 | 0.75 | 126 | 0.20833
| Haripur (SBU) | 136 | 20:00 | 132 | 10:00 | Bakulia | 136 | 0.75 | 122 | 0.20833
| Sreenagar | 135 | 20:00 | 130 | 10:00 | Julda | 136 | 0.70833 | 124 | 0.125
| Ullon | 135 | 6:00 | 131 | 10:00 | TK Chemical | 136 | 0.8125 | 127 | 0.25
| Hasnabad | 135 | 1:00 | 130 | 11:00 | Modern Steel | 135 | 0.77083 | 125 | 0.16667
| Magbazar | 135 | 1:00 | 130 | 12:00 | Shahmirpur | 135 | 0.70833 | 123 | 0.20833
| Maniknagar | 135 | 1:00 | 131 | 11:00 | Khagrachhari | 136 | 0.83333 | 122 | 0.16667
| Bangabhaban | 135 | 1:00 | 131 | 11:00 | Matarbari | 122 | 0.45833 | 111 | 0
| Motijheel | 135 | 1:00 | 131 | 11:00 | Baroiar Hat | 137 | 0.75 | 127 | 0.16667
| Narinda | 135 | 1:00 | 131 | 11:00 | Rangamati | 136 | 20:00 | 123 | 4:00
| Kazla | 135 | 1:00 | 131 | 11:00 | Agrabad | 136 | 20:00 | 123 | 3:00
| Dhanmondi | 135 | 1:00 | 131 | 10:00 | Goalpara S/S | 139 | 6:00 | 137 | 0.041667
| Lalbag | 135 | 1:00 | 125 | 23:00 | Khulna Central S/S | 139 | 22:00 | 136 | 0.041667
| Madartek | 135 | 2:00 | 130 | 11:00 | Noapara | 138 | 4:00 | 135 | 0.5
| Dhaka University | 135 | 2:00 | 131 | 10:00 | Jessore | 137 | 5:00 | 133 | 0.5
| Aftabnagar | 135 | 1:00 | 130 | 11:00 | Benapol | 137 | 0.16667 | 133 | 0.5
| Fatullah | 138 | 20:00 | 133 | 10:00 | Jhenida(Old) | 139 | 6:00 | 134 | 0.5
| Nawabganj | 135 | 18:30 | 131 | 10:00 | Bottail | 138 | 0.91667 | 132 | 0.5
| Keraniganj | 135 | 2:00 | 130 | 10:00 | G.K Project | 140 | 0.95833 | 134 | 0.5
| Banani | 135 | 2:00 | 130 | 12:00 | Faridpur | 137 | 0.20833 | 134 | 0.5
| Mirpur | 132 | 2:00 | 125 | 22:00 | Rajbari | 138 | 0.20833 | 134 | 0.54167
| Kalyanpur | 132 | 18:00 | 126 | 9:00 | Madaripur | 141 | 0.29167 | 139 | 0.041667
| Gulshan | 135 | 3:00 | 130 | 11:00 | Shariyatpur S/S | 141 | 7:00 | 136 | 0.041667
| Uttara | 132 | 18:00 | 124 | 22:00 | Gopalganj | 145 | 0.95833 | 140 | 0.041667
| Uttara New | 132 | 1:00 | 130 | 18:00 | Bagerhat | 137 | 21:00 | 133 | 0.041667
| Kamrangirchar | 135 | 21:00 | 130 | 10:00 | Mongla | 136 | 17:00 | 131 | 0.083333
| Savar | 133 | 19:30 | 124 | 22:00 | Satkhira | 137 | 5:00 | 134 | 18:00
| Bhasantec | 136 | 2:00 | 131 | 9:00 | Gallamari | 139 | 0.20833 | 137 | 1:00
| Agargaon | 137 | 1:00 | 132 | 9:00 | Magura | 140 | 17:00 | 134 | 0.5
| Satmosjid | 136 | 1:00 | 132 | 9:00 | Narail | 137 | 0.91667 | 133 | 0.5
| Tongi | 138 | 19:30 | 132 | 15:00 | Chuadanga | 137 | 5:00 | 131 | 0.5
| Kabirpur | 137 | 18:00 | 133 | 18:29 | Barisal(N) | 142 | 6:00 | 138 | 0.77083
| Basundhara | 136 | 18:30 | 130 | 10:00 | Barisal (S) | 140 | 6:00 | 136 | 1:00
| Manikganj | 141 | 7.00 | 137 | 12:00 | Patuakhali(S) | 139 | 0.29167 | 132 | 0.041667
| Joydevpur | 139 | 18:00 | 134 | 11:00 | Bhandaria | 140 | 0.29167 | 134 | 0.041667
| New Tongi | 137 | 18:30 | 132 | 11:00 | Borguna | 140 | 0.41667 | 133 | 0.041667
| Kodda | 133 | 13:00 | 125 | 11:00 | Jhenaidah(New) | 140 | 24:00 | 134 | 13:00
| Dhamrai | 138 | 18:30 | 133 | 15:00 | Ishurdi | 138 | 6:00 | 132 | 12:00
| Rajendrapur | 131 | 14:00 | 124 | 12:00 | Ruppur Paromanobik | 137 | 21:00 | 133 | 10:00
| Valuka | 127 | 10:00 | 123 | 1:00 | Natore | 138 | 18:00 | 132 | 12:00
| Tangail | 135 | 3:00 | 129 | 13:00 | Bogra | 138 | 14:00 | 132 | 8:00
| Mymensing | 132 | 10:00 | 126 | 7:00 | Noagaon | 135 | 18:00 | 129 | 8:00
| Kishorganj | 134 | 8:00 | 130 | 18:30 | Rajshahi | 138 | 18:00 | 131 | 9:00
| Netrokona | 130 | 10:00 | 125 | 12:00 | Rajshahi New | 138 | 18:00 | 131 | 12:00
| Jamalpur | 138 | 18:00 | 124 | 7:00 | C.Nawabganj | 139 | 18:00 | 129 | 12:00
| Sherpur | 136 | 17:00 | 118 | 7:00 | Amnura | 138 | 18:00 | 129 | 10:00
| Srimongal | 139 | 17:00 | 136 | 1:00 | Pabna | 136 | 5:00 | 131 | 12:00
| Shahjibazar | 138 | 10:00 | 134 | 3:00 | Shahjadpur | 140 | 16:00 | 136 | 7:00
| Fenchuganj | 138 | 17:00 | 135 | 1:00 | Serajganj | 135 | 4:00 | 131 | 12:00
| Khulawara | 136 | 10:00 | 134 | 5:00 | Niyamatpur | 133 | 6:00 | 127 | 8:00
| Sylhet | 134 | 24:00 | 133 | 1:00 | Joypurhat | 135 | 15:00 | 130 | 8:00
| Chatak | 135 | 12:00 | 133 | 1:00 | Sherpur(Bogura) | 137 | 18:00 | 132 | 9:00
| Sunamganj | 132 | 7:00 | 129 | 1:00 | Mohastangor | 137 | 18:00 | 131 | 11:00
| Biani Bazar | 133 | 7:00 | 131 | 1:00 | Bangura | 138 | 18:00 | 133 | 12:00
| Comilla(s) | 129 | 5:00 | 125 | 18:00 | Rangpur | 133 | 15:00 | 127 | 12:00
| Comilla(n) | 140 | 18:00 | 136 | 1:00 | Lalmonirhat | 134 | 4:00 | 125 | 9:00
| Chandpur | 137 | 4:00 | 134 | 10:00 | Saidpur | 134 | 6:00 | 127 | 8:00
| Feni | 139 | 18:00 | 126 | 5:00 | Purbasadipur | 134 | 6:00 | 127 | 12:00
| Chowmuhani | 134 | 17:00 | 129 | 1:00 | Thakurgaon | 135 | 17:00 | 127 | 11:00
| Ashuganj | 140 | 6:00 | 139 | 1:00 | Palashbari | 135 | 18:30 | 129 | 11:00
| Daudkandi | 135 | 8:00 | 130 | 23:00 | Barapukuria | 138 | 6:00 | 132 | 11:00
| B.Baria | 136 | 9:00 | 133 | 1:00 | Panchagar | 136 | 0.625 | 125 | 0.5
| Ramganj | 138 | 18:00 | 128 | 1:00 | Joldhaka | 134 | 0.70833 | 127 | 0.41667
| Chaddagram | 138 | 18:00 | 129 | 3:00 | Kurigram | 132 | 0.625 | 126 | 0.5
| PHP | 137 | 18:00 | 126 | 5:00 | Mithapukur | 137 | 0.79167 | 129 | 0.5
| Kochua | 139 | 20:00 | 132 | 3:00

## L-Curve
Date | 2021-10-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 410 | 6228 | 2758 | 8986 |  |  |  | QF-LDC-11
0:30 | 251 | 6365.5 | 2615 | 8980.5 | Date: | 2021-10-31
1:00 | 92 | 6503 | 2472 | 8975
1:30 | 92 | 6467 | 2393 | 8860
2:00 | 92 | 6431 | 2314 | 8745
2:30 | 121 | 6274.5 | 2301.5 | 8576 | [5 empty] | Gen. at Eve. Peak | 10779 | 10779 MW (19:00 )
3:00 | 150 | 6118 | 2289 | 8407 | [6 empty] | 19:00
3:30 | 196 | 5968.5 | 2293 | 8261.5 | [5 empty] | Gen. at Day Peak | 9445 | 9445 MW (12:00 )
4:00 | 242 | 5819 | 2297 | 8116 | [6 empty] | 12:00
4:30 | 260 | 5724 | 2267 | 7991 | [5 empty] | Highest Generation | 10779
5:00 | 278 | 5629 | 2237 | 7866 | [6 empty] | 19:00
5:30 | 244 | 5624 | 2208 | 7832
6:00 | 210 | 5619 | 2179 | 7798
6:30 | 115 | 5612 | 2174.5 | 7786.5
7:00 | 20 | 5605 | 2170 | 7775
7:30 | 27 | 5673 | 2168 | 7841
8:00 | 34 | 5741 | 2166 | 7907
8:30 | 108 | 5896.5 | 2192 | 8088.5
9:00 | 182 | 6052 | 2218 | 8270
9:30 | 177 | 6261 | 2259.5 | 8520.5
10:00 | 172 | 6470 | 2301 | 8771
10:30 | 140 | 6629 | 2296 | 8925
11:00 | 108 | 6788 | 2291 | 9079
11:30 | 157 | 6872 | 2390 | 9262
12:00 | 206 | 6956 | 2489 | 9445
12:30 | 160 | 7036 | 2564.5 | 9600.5
13:00 | 114 | 7116 | 2640 | 9756
13:30 | 179 | 7072.5 | 2618 | 9690.5
14:00 | 244 | 7029 | 2596 | 9625
14:30 | 293 | 7062 | 2617.5 | 9679.5
15:00 | 342 | 7095 | 2639 | 9734
15:30 | 298 | 6981 | 2546.5 | 9527.5
16:00 | 254 | 6867 | 2454 | 9321
16:30 | 225 | 6852 | 2416.5 | 9268.5
17:00 | 196 | 6837 | 2379 | 9216
17:30 | 128 | 7252 | 2720 | 9972
18:00 | 60 | 7667 | 3061 | 10728
18:30 | 33 | 7739.5 | 3014 | 10753.5
19:00 | 6 | 7812 | 2967 | 10779
19:30 | 108 | 7724 | 2906 | 10630
20:00 | 150 | 7710 | 2868 | 10578 |  |  |  | Executive Engineer
20:30 | 85 | 7550 | 2856.5 | 10406.5 |  |  |  | Network Operation Division
21:00 | 20 | 7390 | 2845 | 10235
21:30 | 121 | 7207.5 | 2862.5 | 10070
22:00 | 222 | 7025 | 2880 | 9905 |  |  |  |  | Page 6 of 7
22:30 | 331 | 6691.5 | 2905.5 | 9597
23:00 | 440 | 6358 | 2931 | 9289
23:30 | 425 | 6293 | 2844.5 | 9137.5
24:00 | 410 | 6228 | 2758 | 8986
10779 MW (19:00 )
9445 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-10-31 |  | Energy |  | 220307268
[13 empty] | 2021-10-31 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4243 | 721 | 2236 | 0 | 1052 | 432 | 74 | 120 | 0 | 108 | 0 | 0
0:30 | 3881 | 719.5 | 2254.5 | 0 | 1359 | 466 | 57 | 120 | 8.5 | 115 | 0 | 0 | Date: | 2021-10-31
1:00 | 3519 | 718 | 2273 | 0 | 1666 | 500 | 40 | 120 | 17 | 122 | 0 | 0
1:30 | 3683 | 718 | 2273 | 0 | 1412.5 | 485 | 40 | 120 | 8.5 | 120 | 0 | 0 | [8 empty] | Total Energy | 220.3073 | Total Energy Gen 220.307 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 220.307 MKWHr
2:00 | 3847 | 718 | 2273 | 0 | 1159 | 470 | 40 | 120 | 0 | 118 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3849.5 | 718 | 2262.5 | 0 | 1005 | 465 | 40 | 120 | 0 | 116 | 0 | 0 | [8 empty] | Energy Requirement | 220.3073
3:00 | 3852 | 718 | 2252 | 0 | 851 | 460 | 40 | 120 | 0 | 114 | 0 | 0
3:30 | 3837 | 718 | 2219 | 0 | 759.5 | 455 | 40 | 120 | 0 | 113 | 0 | 0 | [6 empty] | Shortage
4:00 | 3822 | 718 | 2186 | 0 | 668 | 450 | 40 | 120 | 0 | 112 | 0 | 0
4:30 | 3799 | 718 | 2149 | 0 | 641 | 415 | 40 | 120 | 0 | 109 | 0 | 0
5:00 | 3776 | 718 | 2112 | 0 | 614 | 380 | 40 | 120 | 0 | 106 | 0 | 0
5:30 | 3767.5 | 718 | 2071 | 0 | 633.5 | 380 | 40 | 120 | 0 | 102 | 0 | 0
6:00 | 3759 | 718 | 2030 | 0 | 653 | 380 | 40 | 120 | 0 | 98 | 0 | 0
6:30 | 3745 | 718 | 1999 | 0 | 685.5 | 375 | 40 | 120 | 0 | 96 | 8 | 0 |  |  |  |  | Coal
7:00 | 3731 | 718 | 1968 | 0 | 718 | 370 | 40 | 120 | 0 | 94 | 16 | 0
7:30 | 3730.5 | 718 | 1950.5 | 0 | 776.5 | 375 | 40 | 120 | 0 | 95 | 35.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3730 | 718 | 1933 | 0 | 835 | 380 | 40 | 120 | 0 | 96 | 55 | 0
8:30 | 3750.5 | 718.5 | 1988 | 0 | 924.5 | 380.5 | 40 | 120 | 0 | 98 | 68.5 | 0
9:00 | 3771 | 719 | 2043 | 0 | 1014 | 381 | 40 | 120 | 0 | 100 | 82 | 0
9:30 | 3868.5 | 718.5 | 2087 | 0 | 1110.5 | 381 | 40 | 120 | 0 | 101 | 94 | 0
10:00 | 3966 | 718 | 2131 | 0 | 1207 | 381 | 40 | 120 | 0 | 102 | 106 | 0
10:30 | 3973.5 | 718 | 2116.5 | 0 | 1363 | 377 | 40 | 120 | 0 | 107 | 110 | 0
11:00 | 3981 | 718 | 2102 | 0 | 1519 | 373 | 40 | 120 | 0 | 112 | 114 | 0
11:30 | 4003.5 | 718 | 2131 | 0 | 1652.5 | 372 | 40 | 120 | 0 | 114 | 111 | 0
12:00 | 4026 | 718 | 2160 | 0 | 1786 | 371 | 40 | 120 | 0 | 116 | 108 | 0
12:30 | 3957 | 718 | 2099 | 0 | 2071.5 | 371 | 40 | 120 | 0 | 117 | 107 | 0
13:00 | 3888 | 718 | 2038 | 0 | 2357 | 371 | 40 | 120 | 0 | 118 | 106 | 0
13:30 | 3888 | 718 | 2038 | 0 | 2357 | 371 | 40 | 120 | 0 | 118 | 106 | 0
14:00 | 3888 | 718 | 2038 | 0 | 2357 | 371 | 40 | 120 | 0 | 118 | 106 | 0
14:30 | 3818.5 | 718 | 2067.5 | 0 | 2380.5 | 375.5 | 58 | 120 | 0 | 122 | 85 | 0
15:00 | 3749 | 718 | 2097 | 0 | 2404 | 380 | 76 | 120 | 0 | 126 | 64 | 0
15:30 | 3760 | 718 | 2087 | 0 | 2196.5 | 381 | 97.5 | 120 | 0 | 122 | 45.5 | 0
16:00 | 3771 | 718 | 2077 | 0 | 1989 | 382 | 119 | 120 | 0 | 118 | 27 | 0
16:30 | 3762.5 | 718 | 2036 | 0 | 2016 | 382 | 96.5 | 120 | 8 | 114 | 15.5 | 0
17:00 | 3754 | 718 | 1995 | 0 | 2043 | 382 | 74 | 120 | 16 | 110 | 4 | 0
17:30 | 3796 | 718 | 2096 | 0 | 2479 | 406 | 74 | 120 | 157 | 124 | 2 | 0
18:00 | 3838 | 718 | 2197 | 0 | 2915 | 430 | 74 | 120 | 298 | 138 | 0 | 0
18:30 | 3899.5 | 718 | 2176.5 | 0 | 2962 | 451 | 94 | 120 | 198.5 | 134 | 0 | 0
19:00 | 3961 | 718 | 2156 | 0 | 3009 | 472 | 114 | 120 | 99 | 130 | 0 | 0
19:30 | 3962 | 718 | 2204 | 0 | 2856 | 482 | 74 | 120 | 84 | 130 | 0 | 0
20:00 | 4006 | 720 | 2160 | 0 | 2803 | 483 | 74 | 120 | 84 | 128 | 0 | 0
20:30 | 4032 | 720 | 2190 | 0 | 2588.5 | 487.5 | 74 | 120 | 67.5 | 127 | 0 | 0
21:00 | 4058 | 720 | 2220 | 0 | 2374 | 492 | 74 | 120 | 51 | 126 | 0 | 0
21:30 | 4113 | 720.5 | 2218.5 | 0 | 2167 | 492.5 | 74 | 120 | 42.5 | 122 | 0 | 0
22:00 | 4168 | 721 | 2217 | 0 | 1960 | 493 | 74 | 120 | 34 | 118 | 0 | 0
22:30 | 4226 | 721 | 2226 | 0 | 1612 | 483 | 74 | 120 | 17 | 118 | 0 | 0
23:00 | 4284 | 721 | 2235 | 0 | 1264 | 473 | 74 | 120 | 0 | 118 | 0 | 0
23:30 | 4263.5 | 721 | 2235.5 | 0 | 1158 | 452.5 | 74 | 120 | 0 | 113 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 32.7° C
24:00 | 4243 | 721 | 2236 | 0 | 1052 | 432 | 74 | 120 | 0 | 108 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 220.307 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 220.307 MKWHr
Note on W13: Author:

## Generation
g | 2021-10-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  | 36 | 79 | 34 | 34 |  | 74 | 34 | 34 | 34 | 34 | 34 | 34 | 249513
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 7 |  | 8 | 8 | 8 |  |  |  |  | 25936
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 10 | 15 | 18 | 18 | 14 | 18 | 14 | 11 | 5 | 1 | [9 empty] | 129330
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 0 | [15 empty] | 68 |  | 68 | 68 | 68 | 51 | 34 |  |  | 316488
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 68 | 34 | 34 | 34 | 36 | 68 | 68 | 75 | 89 | 90 | 90 | 90 | 90 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 68 | 2097599
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 333 | 335 | 335 | 333 | 280 | 280 | 280 | 280 | 335 |  | 333 | 335 | 335 | 335 | 335 | 290 | 290 | 7420849
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 7 | 15 | 60 | 60 | 65 | 65 | 65 | 116 |  | 145 | 145 | 145 | 30 |  |  |  | 935890
19 | Ashuganj 195MW PP (APSCL-United) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 886545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2677500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2333096
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 20 | 23 | 20 | 26 | 26 | 25 | 26 | 26 | 29 | 29 |  | 29 | 26 | 26 | 29 | 29 | 29 | 29 | 592848
33 | Ashuganj 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 182 | 180 | 183 | 180 | 181 | 181 | 181 | 181 | 181 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4424000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 350 | 350 | 350 | 305 | 265 | 290 | 290 | 290 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7424000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 285 | 280 | 300 | 330 | 310 | 310 | 265 | 260 | 290 | 290 | 290 | 290 |  | 290 | 290 | 330 | 335 | 340 | 340 | 340 | 7436000
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 56 | 30 | 30 | 30 | 30 | 30 | 54 | 53 | 49 | 50 | 52 | 52 | 50 | 50 | 54 |  | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 1201440
36 | Chandpur 150 MW CCPP | 138 | 138 | 137 | 136 | 138 | 136 | 138 | 138 | 139 | 136 | 136 | 138 | 136 | 138 | 135 | 136 | 135 | 136 |  | 136 | 137 | 135 | 135 | 135 | 137 | 137 | 3426490
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 389 | 380 | 379 | 379 | 371 | 353 | 311 | 305 | 307 | 352 | 401 | 398 | 398 | 359 | 353 | 352 | 351 | 324 |  | 403 | 397 | 397 | 396 | 395 | 394 | 394 | 8937480
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6159500
41 | Haripur 360MW CCPP(HPL) | 312 | 336 | 342 | 342 | 342 | 329 | 272 | 267 | 230 | 203 | 182 | 172 | 156 | 156 | 166 | 176 | 203 | 207 |  | 206 | 206 | 211 | 232 | 262 | 269 | 311 | 5852000
42 | RPCL 210MW CCPP | 139 | 157 | 163 | 163 | 163 | 163 | 163 | 163 | 153 | 147 | 140 | 126 | 118 | 117 | 117 | 125 | 133 | 133 |  | 140 | 140 | 144 | 148 | 154 | 153 | 163 | 3412400
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 24 | 39 | 49 | 52 | 53 | 49 | 40 | 28 | 11 | 1 | [9 empty] | 353570
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 984000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 713280
46 | Shajibazar 330 MW CCPP | 110 | 109 | 110 | 111 | 111 | 111 | 110 | 110 | 110 | 110 | 110 | 110 | 111 | 109 | 110 | 110 | 110 | 109 |  | 111 | 110 | 110 | 105 | 117 | 116 | 116 | 2613000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 52 | 40 | 40 | 40 | 40 | 61 | 61 | 61 | 61 | 61 | 40 | 61 | 61 | 62 | 62 |  | 62 | 62 | 62 | 62 | 63 | 40 | 40 | 1314336
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 10 | 10 | 10 | 10 | 10 | 78 | 81 | 83 | 80 | 83 | 82 | 82 | 82 | 83 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1600320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 191 | 192 | 192 | 192 |  | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 4596350
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 397000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 0 | [5 empty] | 7 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 188820
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 2 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 233472
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 8 | 8 | 8 | 8 | 43 | 44 | 44 | 42 | 47 | 47 | 44 | 43 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 937200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576576
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 265 | 270 | 265 | 290 | 270 | 290 | 300 | 290 | 290 | 290 | 280 | 290 | 290 | 290 | 285 | 290 |  | 275 | 300 | 295 | 295 | 280 | 270 | 270 | 6992500
| Bibiyana South 400 MW |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7649800
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 0 | [5 empty] | 15 | 50 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 17 | 17 | 17 |  | 578416
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 0 | 8 |  | 23 | 24 | 22 | 15 |  |  |  | 72480
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 483456
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 21 | 21 | 19 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 424368
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500400
63 | Impoprt (Tripura) | 122 | 118 | 114 | 112 | 106 | 98 | 94 | 96 | 100 | 102 | 112 | 116 | 118 | 128 | 126 | 118 | 110 | 138 |  | 130 | 130 | 128 | 126 | 118 | 118 | 108 | 2792640
64 | Malancha, Ctg. EPZ (United) | 23 | 23 | 29 | 30 | 30 | 23 | 27 | 10 | 5 | 4 | 3 | 2 | 2 | 4 | 4 | 4 | 6 | 9 |  | 9 | 10 | 9 | 27 | 34 | 40 | 40 | 351600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507744
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243720
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 10 | 0 |  | 25 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [10 empty] | 363900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 525730
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 17 | 26 | 26 | 26 | 26 | 26 | 22 | 30 | 27 | 27 | 27 | 27 | 24 | 20 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 651240
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826300
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 587400
73 | Ghorashal 108MW PP (Regent) | 97 | 96 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 100 | 100 | 98 | 98 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2323000
| Feni Lanka Power | [16 empty] | 17 | 114 |  | 4 | [6 empty] | 99180
| Chowmuhani 113 MW | 59 | 58 | 59 | 58 | 59 | 58 | 58 | 58 | 58 | 59 | 51 | 48 | 48 | 56 | 58 | 50 | 53 | 88 |  | 92 | 97 | 97 | 97 | 97 | 96 | 62 | 1594320
| Manikgonj 162MW PP(MPGL) | 162 | 108 | 54 | 0 |  |  |  | 16 | 43 | 75 | 158 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 |  |  | 2633760
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 4 | 25 | 25 | 33 | 51 | 51 | 25 | 25 | 25 | 25 | 25 | [8 empty] | 313440
79 | Kodda 150MW PP | [16 empty] | 16 | 64 |  | 16 | 16 | 16 |  |  |  |  | 100320
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 4 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 53760
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 0 | [9 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 20 |  | 25 | 8 | 8 |  |  |  |  | 123077
| Gazipur 100 MW PP | [16 empty] | 3 | 21 |  | 52 | 52 | 17 |  |  |  |  | 129852
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 4 | 1 | 1 | 3 | 2 | 1 | 0 | [9 empty] | 25201
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 53 | 45 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1043652
| Karnaphuli Power Ltd. | 110 | 68 | 51 | 51 | 34 | 35 | 68 | 68 | 77 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 108 | 92 | 95 | 95 | 97 | 2243125
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [9 empty] | 1 | 24 | 25 | 24 | 25 | 25 | 25 | 24 | 24 |  | 24 | 24 | 25 | 25 |  |  |  | 279188
86 | Meghnaghat CCPP ( Summit) | 255 | 245 | 240 | 230 | 260 | 235 | 270 | 265 | 270 | 265 | 275 | 270 | 260 | 265 | 250 | 240 | 230 | 230 |  | 250 | 260 | 260 | 260 | 255 | 240 | 240 | 6069324
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 95 | 73 | 45 | 0 |  |  |  | 5 | 17 | 17 | 50 | 90 | 92 | 93 | 93 | 60 | 55 | 73 |  | 104 | 104 | 104 | 104 | 90 |  |  | 1344000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 30 | 30 | 30 | 30 | 10 | 10 | 100 |  | 40 | 10 | 10 |  |  |  |  | 255600
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 7 | 7 | 7 | 14 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1116618
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 0 | [8 empty] | 5 | 24 | 58 | 58 | 58 | 40 | 40 | 72 |  | 64 | 40 | 40 | 40 | 40 | 32 | 32 | 624528
95 | Patenga 50MW PP (Baraka) | 32 | 0 | [5 empty] | 1 | 6 | 6 | 6 | 21 | 45 | 46 | 46 | 19 | 19 | 28 |  | 50 | 50 | 50 | 50 | 50 | 25 |  | 548640
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 5 | 34 |  | 9 | [6 empty] | 49920
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 42 | 42 | 30 | 30 | 15 | 15 | 15 | 17 | 30 | 30 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 887749
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 22 | 55 | 55 | 55 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 17 |  |  | 467599
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 130 | 130 | 163 | 110 | 110 | 130 | 130 | 110 | 163 |  | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 3238609
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 13950
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 38 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1060560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 80 | 80 | 60 | 40 | 40 | 40 | 40 | 70 | 70 | 103 | 120 | 120 | 120 | 140 | 120 | 120 | 120 | 141 |  | 182 | 182 | 182 | 150 | 120 | 70 | 50 | 2635200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 80 | 70 | 65 | 52 | 52 | 52 | 52 | 72 | 80 | 102 | 102 | 106 | 117 | 116 | 116 | 117 | 116 | 116 |  | 105 | 100 | 100 | 100 | 100 | 90 | 68 | 2184192
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 70 | 70 | 70 | 50 | 50 | 50 | 50 | 90 | 76 | 90 | 76 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1941120
116 | Chandpur 200MW (Desh energy) | 100 | 51 | 0 | [8 empty] | 13 | 88 | 85 | 85 | 85 | 51 | 81 |  | 195 | 200 | 200 | 100 | 17 |  |  | 1316640
117 | Ashuganj 150MW PP (Midland) | 68 | 0 | [5 empty] | 2 | 10 | 16 | 35 | 58 | 80 | 117 | 120 | 80 | 80 | 98 |  | 120 | 120 | 120 | 123 | 30 |  |  | 1291345
118 | Bibiyana-III 400 MW CCPP | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 321 | 323 | 321 | 322 | 322 | 323 | 323 | 322 | 322 | 322 | 322 |  | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 7775000
| Jamalpur 115 MW PP (United) | [9 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 32 |  | 16 | 16 | [5 empty] | 153600
| Anwara 300 MW PP (United) | 302 | 250 | 250 | 217 | 214 | 251 | 251 | 252 | 252 | 285 | 285 | 285 | 288 | 289 | 286 | 286 | 303 | 303 |  | 303 | 304 | 305 | 303 | 303 | 303 | 304 | 6679200
| Juldah unit-2 (Acorn) | 60 | 60 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 65 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 30 | 10 | 1564800
| Anlima Energy Ltd. | [10 empty] | 15 | 48 | 107 | 108 | 108 | 53 | 53 | 78 |  | 108 | 108 | 108 | 108 | 53 |  |  | 1021200
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 12 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438480
| Spectra Solar Plant Ltd. | [6 empty] | 5 | 15 | 19 | 24 | 27 | 27 | 25 | 20 | 14 | 6 | 1 | [9 empty] | 176345
120 | Eastern Zone Total | 6503 | 6431 | 6118 | 5819 | 5629 | 5619 | 5605 | 5741 | 6052 | 6470 | 6788 | 6956 | 7116 | 7029 | 7095 | 6867 | 6837 | 7667 |  | 7812 | 7724 | 7710 | 7390 | 7025 | 6358 | 6228 | 162086616
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3014400
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 | [8 empty] | 17 | 20 | 105 | 105 | 105 | 70 | 70 | 95 |  | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 1312320
130
131
132 | United Payra Power Ltd. | [17 empty] | 9 |  | 17 | [6 empty] | 28800
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 218 | 210 | 219 | 223 | 224 | 180 | 152 | 151 | 151 | 151 | 191 | 214 | 219 | 214 | 201 | 170 | 215 |  | 220 | 220 | 212 | 221 | 211 | 220 | 220 | 481934
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 18 | 18 | 17 | 17 | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 437627
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1557000
140 | Bhola 33 MW PP (Venture) | 28 | 25 | 25 | 24 | 24 | 21 | 22 | 17 | 13 | 15 | 18 | 21 | 23 | 23 | 23 | 24 | 24 | 27 |  | 30 | 31 | 31 | 31 | 30 | 30 | 29 | 566749
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [16 empty] | 11 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 353088
146 | Bheramara HVDC | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 719 | 718 | 718 | 718 | 718 | 717 | 718 | 718 | 718 | 718 |  | 718 | 718 | 720 | 720 | 721 | 721 | 721 | 17347636
147 | Bheramara 410 MW CCPP | [17 empty] | 30 |  | 30 | 41 | 35 | 75 | 165 | 360 | 320 | 960768
148 | Payra 1320 MW | 420 | 390 | 380 | 370 | 300 | 300 | 290 | 300 | 300 | 300 | 290 | 290 | 290 | 290 | 300 | 300 | 300 | 350 |  | 390 | 400 | 400 | 410 | 410 | 390 | 350 | 8978300
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 83 | 81 | 81 | 81 | 80 | 82 | 82 | 80 |  | 82 | 82 | 83 | 82 | 83 | 83 | 82 | 1937018
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 | [8 empty] | 56784
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 35400
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 161 | 161 | 161 | 161 | 161 | 163 | 165 | 168 | 183 | 191 | 172 | 188 | 186 | 174 | 172 | 170 | 170 | 162 |  | 174 | 175 | 181 | 187 | 187 | 184 | 183 | 4384309
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 142 | 142 | 142 | 142 | 142 | 144 | 147 | 156 | 162 | 156 | 169 | 200 | 186 | 170 | 167 | 165 | 166 | 168 |  | 184 | 180 | 182 | 182 | 182 | 178 | 168 | 4206291
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 367 | 350 | 344 | 354 | 360 | 300 | 338 | 336 | 340 | 414 | 392 | 400 | 330 | 312 | 360 | 354 | 299 | 383 |  | 362 | 373 | 337 | 349 | 340 | 380 | 340 | 8692327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 18 | 18 | 18 | 19 | 20 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 477840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 8 | 5 | 5 | 176940
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 27 | [8 empty] | 35660
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 43 | [8 empty] | 49145
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 36 | [8 empty] | 45620
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 2 | 25 |  | 16 | [6 empty] | 96480
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 80 |  | 15 | [6 empty] | 94720
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 0 | [5 empty] | 6 | 35 | 35 | 40 | 60 | 105 | 113 | 113 | 50 | 50 | 78 |  | 113 | 113 | 113 | 113 | 113 |  |  | 1357824
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 80 | 112 | 112 | 113 | 50 | 50 | 90 |  | 113 | 113 | 113 | 50 | 50 |  |  | 956448
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [12 empty] | 50 | 40 | 36 | 35 | 34 | 110 |  | 113 | 70 | 70 | 34 |  |  |  | 539376
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 6 | 6 | 7 | 7 | 5 | 3 | 1 | 0 | [8 empty] | 39848
178
178