## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-11-03 | Wednesday
|  |  | Date (day): | 2021-11-03 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13259.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14571 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-11-02 | 2021-11-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 87 | 96 | 90 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 356 | 395 | 350 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 282 | 262 | 290 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 255 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 43 | 48 | 45 | 45 |  | 10 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 25 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 21
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 64 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 35 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 51 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 8 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 175 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 117 | 117 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 70 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 88 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2204 | 2683 | 3333 | 3865 | 490 | 1155
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 25 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 103 | 103 | 103 | 127 |  | Unit 2 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 68 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 51 | 100
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 30 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 40 | 90 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 10 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 303 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 35 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 108 | 68 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 80 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 52 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 813 | 1102 | 1426 | 1499 | 187 | 681
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 171 | 200 | 215
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 340 | 320 | 340 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 340 | 320 | 340 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 10 | 10 | 10 | 45 |  | Gas shortage
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 100 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 138 | 138 | 138 |  | 25 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 85 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 116 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 22 | 20 | 22
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 70 | 100 | 100 |  | 13 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1366 | 1677 | 2031 | 2314 | 550 | 115
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 156 | 147 | 170 | 170
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 8 | 8
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 70 | 170 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 8 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 301 | 369 | 588.6 | 537 | 0 | 0
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 117 | 132 | 131 | 132 |  | 198 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 40 | 60 | 65
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 80 | 81 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 205 | 218 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 275 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 322 | 322 | 324 | 324 | 76 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1703 | 1690 | 1813 | 1822 | 139 | 398
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 719 | 716 | 733 | 733
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 220 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 125 | 350 | 350 | 60 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 944 | 946 | 1458 | 1678 | 60 | 93
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 21 | 28 | 30
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 67 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 21 | 22 | 30 | 65 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 250 | 430 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 221 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 535 | 760 | 1065 | 1225 | 65 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 25 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 153 | 123 | 0 | 0 |  | 220 | Under maint.
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 130 | 210 | 210 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 390 | 363 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 17 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 20 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 70 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 803 | 855 | 1344 | 1438 | 310 | 319
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 79 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 88 | 192 | 201 | 193 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 8757 | 10274 | 13259.6 | 14571 | 1801 | 3289
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8364.0686 | 9813 | 12664.6345 | 13917.1913
| A. |  | 2021-11-02 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 10274 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6986 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10274 | MW
| 3 | Day peak Generation : |  |  | 8757 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9813 | MW
| 4 | Evening peak Generation : |  |  | 10274 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 206.7517 | MKWHr | By Solar | 0.68323 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 144.6814 | MKWHr |  | By Oil: | 29.5696 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 10.1956 | MKWHr |  | By Hydro: | 2.122 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1801 | MW | Dhaka | 3794 | 3794 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3289 | MW | Chittagong | 1245 | 1245 |  | 0 |  | 18:00 |  | 120
|  |  |  | Total = |  |  | 5090 | MW | Khulna | 1111 | 1111 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1091.12 | MMCFD |  |  | Rajshahi | 899 | 899 |  | 0 |  | 19:00 |  | 116
| 8 | Fuel Cost : | i) Gas : | Taka | 147537487.782 | ii) Oil : | Taka | 216539741.8 | Comilla | 839 | 839 |  | 0 |  | 19:30 |  | 118
|  |  | iii) Coal : |  | 47951650.62 | Total | Taka | 412028880.202 | Mymensingh | 727 | 727 |  | 0 |  | 20:00 |  | 116
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.48 | MKWHr. | Sylhet | 384 | 384 |  | 0 |  | 21:00 |  | 112
|  | ii) During Peak Demand : |  |  | -228 | MW (E to W) at | 19:00 | hrs | Barisal | 251 | 251 |  | 0 |  | 22:00 |  | 108
|  | iii) Maximum : |  |  | -334 | MW at | 18:30 | hrs | Rangpur | 563 | 563 |  | 0 |  | 23:00 |  | 102
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.4° C |  |  | Total | 9813 | 9813 |  | 0
| B. |  | 2021-11-03 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 29° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14571 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8800 | MW
| 4 | Reserve(Generation end) |  |  |  | 4071 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 211.2997 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7085 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3716 | MKWHr. | ii) HVDC Flow at Peak Time |  | 716 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1283 | MKWHr. | iii) Maximum HVDC Flow : |  | 723 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.85 |  | (b) Today: | 103.76 |  | (c) Rule Curve: |  | 108.8
.

## YesterdayGen
2021-11-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 55 | 0 | 351 | 303 |  | 0 | 250 | 225 | 0 | 0 | 42 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 40 | 135 | 0 | 0 | 275 | 265 | 180 | 8 | 136 | 29 | 24 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 80 | 179 | 8 | 20 | 0 | 30 | 30 | 22 | 0 | 130 | 135 | 64 | 20 | 0 | 179 | 0 | 0 | 0 | 275 | 0 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 0 | 70 | 0 | 0 | 323 | 0 | 0 | 17 | 0 | 304 | 54 | 17 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 723 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 18 | 0 | 162 | 0 | 340 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 190 | 0 | 0 | 0 |  | 5592 | 2502 | 8094 | 4146 | 723 | 1933 | 0 | 711 | 381 | 103 | 0 | 17 | 80 | 0 | 0 | 103.87
2:00 | 0 | 0 | 0 | 110 | 0 | 10 | 0 | 351 | 302 |  | 0 | 250 | 230 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 135 | 0 | 0 | 275 | 265 | 180 | 8 | 137 | 29 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 80 | 205 | 8 | 0 | 0 | 30 | 30 | 0 | 0 | 130 | 136 | 40 | 5 | 0 | 179 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 0 | 70 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 251 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 723 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 164 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 180 | 0 | 0 | 0 |  | 5240 | 2423 | 7663 | 4056 | 723 | 1803 | 0 | 527 | 371 | 103 | 0 | 0 | 80 | 0 | 0 | 103.87
3:00 | 0 | 0 | 0 | 110 | 0 | 11 | 0 | 350 | 252 |  | 0 | 250 | 240 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 135 | 0 | 0 | 275 | 265 | 180 | 8 | 136 | 29 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 80 | 204 | 8 | 0 | 0 | 30 | 30 | 0 | 0 | 110 | 134 | 40 | 5 | 0 | 165 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 0 | 70 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 250 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 723 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 166 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 155 | 0 | 0 | 0 |  | 5138 | 2273 | 7411 | 3957 | 723 | 1661 | 0 | 526 | 361 | 103 | 0 | 0 | 80 | 0 | 0 | 103.86
4:00 | 0 | 0 | 0 | 110 | 0 | 11 | 0 | 350 | 231 |  | 0 | 250 | 240 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 135 | 0 | 0 | 270 | 265 | 180 | 8 | 136 | 29 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 76 | 212 | 8 | 0 | 0 | 30 | 30 | 0 | 0 | 110 | 126 | 40 | 5 | 0 | 165 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 0 | 70 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 106 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 723 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 150 | 0 | 0 | 0 |  | 4956 | 2102 | 7058 | 3803 | 723 | 1654 | 0 | 367 | 332 | 103 | 0 | 0 | 76 | 0 | 0 | 103.86
5:00 | 0 | 0 | 0 | 110 | 0 | 11 | 0 | 350 | 231 |  | 0 | 250 | 230 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 80 | 0 | 0 | 270 | 265 | 180 | 8 | 137 | 29 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 74 | 219 | 8 | 0 | 0 | 30 | 30 | 0 | 0 | 110 | 138 | 40 | 5 | 0 | 165 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 0 | 70 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 105 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 723 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 150 | 0 | 0 | 0 |  | 4907 | 2079 | 6986 | 3767 | 723 | 1621 | 0 | 366 | 332 | 103 | 0 | 0 | 74 | 0 | 0 | 103.85
6:00 | 0 | 0 | 0 | 110 | 0 | 11 | 0 | 350 | 252 |  | 0 | 250 | 225 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 25 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 80 | 0 | 0 | 275 | 265 | 180 | 8 | 135 | 29 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 72 | 221 | 8 | 0 | 0 | 30 | 30 | 0 | 0 | 130 | 119 | 40 | 5 | 0 | 165 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 0 | 70 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 139 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 722 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 149 | 0 | 0 | 0 |  | 5005 | 2097 | 7102 | 3755 | 722 | 1719 | 0 | 400 | 331 | 103 | 0 | 0 | 72 | 0 | 0 | 103.85
7:00 | 0 | 0 | 0 | 110 | 0 | 11 | 0 | 350 | 283 |  | 0 | 250 | 240 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 25 | 33 | 25 | 0 | 0 | 34 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 80 | 0 | 0 | 270 | 265 | 180 | 8 | 137 | 26 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 0 | 18 | 64 | 219 | 8 | 0 | 0 | 30 | 30 | 0 | 0 | 130 | 136 | 40 | 5 | 0 | 165 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 35 | 4 | 70 | 0 | 0 | 322 | 0 | 0 | 0 | 1 | 139 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 6 | 0 | 0 | 0 | 17 | 3 |  | 722 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 158 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 150 | 0 | 0 | 0 |  | 5108 | 2200 | 7308 | 3874 | 722 | 1797 | 0 | 402 | 331 | 104 | 0 | 0 | 64 | 14 | 0 | 103.84
8:00 | 0 | 0 | 0 | 110 | 0 | 53 | 0 | 350 | 282 |  | 0 | 250 | 240 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 25 | 33 | 25 | 0 | 0 | 34 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 80 | 0 | 0 | 290 | 310 | 180 | 8 | 137 | 26 | 5 | 0 | 19 | 0 | 0 | 0 | 22 | 8 | 20 | 18 | 72 | 207 | 8 | 20 | 1 | 30 | 30 | 5 | 0 | 130 | 123 | 40 | 5 | 0 | 165 | 0 | 0 | 0 | 295 | 0 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 45 | 0 | 70 | 0 | 0 | 322 | 0 | 0 | 0 | 1 | 139 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 6 |  | 719 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 163 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 151 | 0 | 0 | 2 |  | 5289 | 2278 | 7567 | 4048 | 719 | 1828 | 0 | 455 | 330 | 104 | 0 | 0 | 72 | 11 | 0 | 103.84
9:00 | 0 | 0 | 0 | 110 | 0 | 53 | 0 | 350 | 281 |  | 0 | 250 | 235 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 25 | 33 | 25 | 0 | 0 | 34 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 80 | 0 | 0 | 320 | 370 | 198 | 8 | 138 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 18 | 72 | 184 | 8 | 20 | 1 | 30 | 30 | 5 | 0 | 110 | 120 | 40 | 5 | 0 | 165 | 0 | 0 | 10 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 72 | 0 | 70 | 0 | 0 | 322 | 0 | 0 | 0 | 3 | 139 | 54 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 15 | 17 |  | 720 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 165 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 150 | 0 | 0 | 3 |  | 5411 | 2289 | 7700 | 4095 | 720 | 1851 | 0 | 500 | 331 | 104 | 0 | 0 | 72 | 27 | 0 | 103.84
10:00 | 0 | 0 | 0 | 110 | 0 | 53 | 0 | 351 | 281 |  | 0 | 250 | 245 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 3 | 21 | 25 | 29 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 80 | 0 | 0 | 340 | 320 | 188 | 8 | 139 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 18 | 74 | 172 | 0 | 20 | 2 | 30 | 30 | 5 | 0 | 110 | 120 | 40 | 5 | 0 | 165 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 115 | 0 | 76 | 0 | 2 | 322 | 0 | 0 | 2 | 4 | 281 | 54 | 8 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 20 |  | 720 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 174 | 0 | 417 | 0 | 0 | 7 | 0 | 0 | 0 | 6 | 0 | 250 | 151 | 0 | 0 | 4 |  | 5663 | 2336 | 7999 | 4101 | 720 | 1922 | 0 | 744 | 332 | 70 | 0 | 0 | 74 | 36 | 0 | 103.83
11:00 | 0 | 0 | 0 | 110 | 0 | 53 | 0 | 355 | 282 |  | 0 | 250 | 250 | 0 | 0 | 20 | 250 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 21 | 25 | 23 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 3 | 80 | 0 | 0 | 365 | 345 | 198 | 8 | 138 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 18 | 78 | 168 | 0 | 20 | 2 | 30 | 30 | 8 | 0 | 110 | 120 | 40 | 20 | 0 | 179 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 115 | 0 | 40 | 0 | 20 | 322 | 0 | 0 | 43 | 4 | 304 | 54 | 89 | 0 | 17 | 10 | 320 | 0 | 0 | 20 | 0 | 0 | 17 | 31 |  | 720 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 172 | 0 | 406 | 0 | 0 | 35 | 0 | 0 | 0 | 7 | 0 | 250 | 151 | 0 | 0 | 5 |  | 5991 | 2321 | 8312 | 4135 | 720 | 1926 | 0 | 1004 | 330 | 70 | 0 | 0 | 78 | 49 | 0 | 103.83
12:00 | 0 | 0 | 0 | 110 | 0 | 87 | 0 | 356 | 282 |  | 0 | 250 | 260 | 0 | 0 | 43 | 300 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 21 | 25 | 23 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 7 | 100 | 0 | 0 | 335 | 310 | 182 | 8 | 138 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 18 | 84 | 156 | 0 | 20 | 2 | 30 | 30 | 44 | 0 | 130 | 117 | 61 | 81 | 0 | 205 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 117 | 0 | 40 | 0 | 20 | 322 | 0 | 0 | 51 | 4 | 303 | 54 | 108 | 0 | 17 | 10 | 320 | 0 | 53 | 88 | 0 | 0 | 17 | 32 |  | 719 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 196 | 0 | 390 | 0 | 0 | 35 | 0 | 0 | 0 | 7 | 0 | 250 | 220 | 0 | 0 | 5 |  | 6387 | 2370 | 8757 | 4144 | 719 | 2156 | 0 | 1150 | 331 | 70 | 0 | 0 | 84 | 103 | 0 | 103.83
13:00 | 0 | 0 | 0 | 110 | 0 | 95 | 0 | 353 | 252 |  | 0 | 250 | 255 | 0 | 0 | 43 | 300 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 23 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 9 | 100 | 0 | 0 | 335 | 310 | 182 | 8 | 140 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 18 | 80 | 153 | 0 | 20 | 2 | 30 | 30 | 50 | 0 | 163 | 119 | 62 | 83 | 0 | 193 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 4 | 0 | 0 | 89 | 0 | 115 | 0 | 76 | 0 | 20 | 322 | 0 | 0 | 66 | 4 | 303 | 54 | 108 | 0 | 17 | 10 | 320 | 0 | 49 | 134 | 0 | 0 | 17 | 29 |  | 719 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 170 | 0 | 341 | 27 | 0 | 35 | 0 | 0 | 0 | 7 | 0 | 250 | 220 | 0 | 0 | 5 |  | 6506 | 2304 | 8810 | 4064 | 719 | 2155 | 0 | 1295 | 331 | 70 | 0 | 0 | 80 | 96 | 0 | 103.82
14:00 | 0 | 0 | 0 | 110 | 0 | 94 | 0 | 353 | 242 |  | 0 | 250 | 250 | 0 | 0 | 42 | 250 | 0 | 0 | 0 | 64 | 0 | 3 | 0 | 0 | 0 | 54 | 17 | 17 | 21 | 25 | 24 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 8 | 100 | 0 | 0 | 350 | 320 | 185 | 8 | 138 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 19 | 82 | 146 | 0 | 20 | 2 | 30 | 30 | 50 | 0 | 130 | 118 | 40 | 82 | 0 | 179 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 117 | 15 | 40 | 0 | 26 | 322 | 0 | 0 | 89 | 3 | 306 | 54 | 108 | 0 | 17 | 10 | 320 | 0 | 39 | 162 | 0 | 0 | 17 | 24 |  | 719 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 163 | 0 | 347 | 33 | 0 | 35 | 0 | 0 | 0 | 7 | 0 | 250 | 221 | 0 | 0 | 4 |  | 6441 | 2291 | 8732 | 3992 | 719 | 2111 | 0 | 1331 | 333 | 70 | 0 | 0 | 82 | 94 | 0 | 103.82
15:00 | 0 | 0 | 0 | 110 | 0 | 85 | 0 | 350 | 235 |  | 0 | 250 | 260 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 64 | 0 | 24 | 0 | 0 | 0 | 54 | 17 | 55 | 21 | 25 | 26 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 3 | 80 | 0 | 0 | 355 | 315 | 192 | 8 | 136 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 19 | 96 | 147 | 0 | 20 | 1 | 30 | 30 | 50 | 0 | 163 | 0 | 61 | 82 | 0 | 192 | 18 | 0 | 10 | 295 | 24 | 5 | 0 | 15 | 0 | 0 | 80 | 0 | 125 | 11 | 40 | 0 | 48 | 322 | 0 | 0 | 98 | 2 | 305 | 54 | 108 | 0 | 17 | 10 | 320 | 0 | 27 | 162 | 0 | 0 | 17 | 16 |  | 717 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 163 | 0 | 335 | 35 | 0 | 35 | 0 | 0 | 0 | 5 | 0 | 250 | 220 | 0 | 0 | 2 |  | 6518 | 2191 | 8709 | 3891 | 717 | 2108 | 0 | 1430 | 333 | 70 | 0 | 0 | 96 | 64 | 0 | 103.82
16:00 | 0 | 0 | 0 | 110 | 0 | 94 | 0 | 350 | 242 |  | 0 | 250 | 265 | 0 | 0 | 42 | 335 | 0 | 0 | 0 | 64 | 0 | 25 | 0 | 0 | 0 | 54 | 17 | 55 | 21 | 25 | 26 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 2 | 80 | 0 | 0 | 340 | 295 | 180 | 8 | 136 | 26 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 16 | 19 | 90 | 147 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 163 | 0 | 40 | 82 | 0 | 179 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 15 | 0 | 0 | 80 | 0 | 126 | 5 | 60 | 0 | 50 | 322 | 0 | 0 | 105 | 0 | 231 | 54 | 108 | 0 | 34 | 40 | 320 | 0 | 12 | 162 | 0 | 0 | 17 | 7 |  | 717 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 130 | 0 | 306 | 35 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 260 | 220 | 0 | 0 | 1 |  | 6418 | 2154 | 8572 | 3786 | 717 | 2106 | 0 | 1434 | 341 | 70 | 0 | 0 | 90 | 28 | 0 | 103.81
17:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 355 | 251 |  | 0 | 250 | 255 | 0 | 0 | 43 | 280 | 0 | 0 | 0 | 64 | 16 | 24 | 0 | 0 | 0 | 54 | 17 | 55 | 21 | 25 | 26 | 33 | 25 | 2 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 8 | 2 | 26 | 21 | 6 | 80 | 0 | 0 | 310 | 270 | 180 | 8 | 138 | 29 | 10 | 0 | 10 | 0 | 0 | 2 | 22 | 8 | 16 | 19 | 98 | 149 | 0 | 20 | 0 | 30 | 30 | 14 | 0 | 130 | 25 | 40 | 20 | 0 | 179 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 24 | 0 | 0 | 80 | 0 | 126 | 0 | 86 | 17 | 61 | 322 | 0 | 5 | 105 | 0 | 301 | 54 | 108 | 17 | 43 | 40 | 320 | 7 | 1 | 162 | 6 | 0 | 17 | 1 |  | 717 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 130 | 0 | 291 | 35 | 0 | 35 | 0 | 60 | 0 | 1 | 50 | 330 | 152 | 0 | 0 | 0 |  | 6281 | 2256 | 8537 | 3718 | 717 | 1763 | 0 | 1741 | 411 | 70 | 0 | 16 | 98 | 3 | 0 | 103.81
18:00 | 0 | 0 | 0 | 110 | 0 | 94 | 0 | 352 | 269 |  | 0 | 250 | 250 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 84 | 16 | 25 | 0 | 0 | 0 | 54 | 17 | 55 | 21 | 25 | 18 | 33 | 25 | 8 | 0 | 0 | 70 | 120 | 0 | 7 | 0 | 0 | 0 | 0 |  | 22 | 0 | 68 | 30 | 11 | 47 | 21 | 10 | 80 | 0 | 0 | 370 | 340 | 180 | 8 | 136 | 26 | 10 | 0 | 32 | 0 | 0 | 8 | 22 | 11 | 16 | 22 | 120 | 146 | 0 | 20 | 0 | 30 | 30 | 47 | 0 | 163 | 110 | 63 | 79 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 5 | 0 | 130 | 0 | 0 | 132 | 0 | 128 | 0 | 90 | 54 | 102 | 322 | 8 | 17 | 105 | 0 | 301 | 54 | 107 | 32 | 105 | 100 | 303 | 72 | 0 | 162 | 21 | 0 | 17 | 0 |  | 716 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 8 | 26 | 19 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 20 | 0 | 130 | 0 | 360 | 92 | 0 | 95 | 0 | 106 | 0 | 0 | 100 | 370 | 220 | 0 | 14 | 0 |  | 7488 | 2761 | 10249 | 4017 | 716 | 2152 | 0 | 2565 | 450 | 70 | 0 | 159 | 120 | 0 | 0 | 103.81
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 0 | 96 | 0 | 395 | 262 |  | 0 | 250 | 255 | 0 | 0 | 48 | 335 | 0 | 0 | 0 | 64 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 25 | 8 | 0 | 33 | 70 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 30 | 0 | 25 | 21 | 10 | 80 | 0 | 0 | 340 | 340 | 171 | 8 | 138 | 29 | 10 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 22 | 116 | 147 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 130 | 132 | 40 | 80 | 0 | 218 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 175 | 0 | 0 | 170 | 0 | 117 | 0 | 90 | 85 | 100 | 322 | 8 | 17 | 68 | 0 | 305 | 54 | 68 | 34 | 70 | 80 | 320 | 70 | 0 | 162 | 52 | 0 | 17 | 0 |  | 716 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 21 | 0 | 130 | 0 | 363 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 113 | 430 | 221 | 0 | 0 | 0 |  | 7521 | 2753 | 10274 | 4057 | 716 | 2133 | 0 | 2572 | 509 | 103 | 0 | 68 | 116 | 0 | 0 | 103.8
19:30 | 0 | 0 | 0 | 110 | 0 | 98 | 0 | 398 | 257 |  | 0 | 250 | 250 | 0 | 0 | 49 | 335 | 0 | 0 | 0 | 64 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 25 | 8 | 0 | 33 | 70 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 30 | 0 | 25 | 21 | 8 | 80 | 0 | 0 | 275 | 270 | 218 | 8 | 138 | 29 | 10 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 22 | 118 | 149 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 130 | 132 | 40 | 83 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 120 | 0 | 0 | 170 | 0 | 110 | 0 | 90 | 85 | 100 | 322 | 8 | 17 | 68 | 0 | 304 | 54 | 68 | 32 | 70 | 80 | 320 | 53 | 0 | 162 | 34 | 0 | 17 | 0 |  | 716 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 21 | 0 | 130 | 0 | 364 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 440 | 222 | 0 | 0 | 0 |  | 7349 | 2724 | 10073 | 3974 | 716 | 2144 | 0 | 2430 | 520 | 103 | 0 | 68 | 118 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 110 | 0 | 100 | 0 | 397 | 256 |  | 0 | 250 | 245 | 0 | 0 | 47 | 335 | 0 | 0 | 0 | 64 | 0 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 25 | 8 | 0 | 33 | 70 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 10 | 0 | 25 | 21 | 14 | 80 | 0 | 0 | 275 | 270 | 220 | 8 | 137 | 29 | 10 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 22 | 116 | 151 | 0 | 20 | 0 | 30 | 30 | 47 | 0 | 130 | 128 | 40 | 83 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 120 | 0 | 0 | 170 | 0 | 112 | 0 | 90 | 85 | 100 | 322 | 0 | 17 | 68 | 0 | 305 | 54 | 68 | 3 | 70 | 80 | 320 | 53 | 0 | 162 | 34 | 0 | 17 | 0 |  | 717 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 20 | 0 | 130 | 0 | 363 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 440 | 221 | 0 | 0 | 0 |  | 7287 | 2709 | 9996 | 3971 | 717 | 2142 | 0 | 2356 | 523 | 103 | 0 | 68 | 116 | 0 | 0 | 103.8
21:00 | 0 | 0 | 0 | 110 | 0 | 104 | 0 | 396 | 258 |  | 0 | 250 | 255 | 0 | 0 | 48 | 335 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 25 | 21 | 26 | 80 | 0 | 0 | 275 | 270 | 221 | 8 | 136 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 112 | 152 | 0 | 20 | 0 | 30 | 30 | 47 | 0 | 130 | 134 | 40 | 83 | 0 | 218 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 60 | 0 | 0 | 130 | 0 | 114 | 0 | 90 | 85 | 100 | 322 | 0 | 0 | 68 | 0 | 305 | 54 | 68 | 0 | 70 | 80 | 320 | 53 | 0 | 162 | 34 | 0 | 17 | 0 |  | 717 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 21 | 0 | 130 | 0 | 364 | 105 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 440 | 223 | 0 | 0 | 0 |  | 7106 | 2677 | 9783 | 3991 | 717 | 2179 | 0 | 2090 | 523 | 103 | 0 | 68 | 112 | 0 | 0 | 103.8
22:00 | 0 | 0 | 0 | 110 | 0 | 104 | 0 | 355 | 253 |  | 0 | 250 | 250 | 0 | 0 | 50 | 335 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 25 | 20 | 33 | 80 | 0 | 0 | 270 | 265 | 180 | 8 | 137 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 108 | 155 | 0 | 20 | 0 | 30 | 30 | 47 | 0 | 130 | 127 | 40 | 84 | 0 | 218 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 40 | 0 | 0 | 100 | 0 | 94 | 0 | 60 | 34 | 50 | 322 | 0 | 0 | 68 | 0 | 304 | 54 | 68 | 0 | 46 | 50 | 320 | 48 | 0 | 162 | 0 | 0 | 17 | 0 |  | 717 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 21 | 0 | 130 | 0 | 362 | 53 | 0 | 70 | 0 | 35 | 0 | 0 | 35 | 440 | 218 | 0 | 0 | 0 |  | 6662 | 2545 | 9207 | 3897 | 717 | 2154 | 0 | 1637 | 523 | 103 | 0 | 68 | 108 | 0 | 0 | 103.79
23:00 | 0 | 0 | 0 | 110 | 0 | 104 | 0 | 363 | 241 |  | 0 | 250 | 250 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 10 | 20 | 35 | 80 | 0 | 0 | 320 | 300 | 180 | 8 | 135 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 102 | 152 | 0 | 20 | 0 | 30 | 30 | 44 | 0 | 130 | 128 | 63 | 84 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 87 | 0 | 60 | 0 | 10 | 321 | 0 | 0 | 68 | 0 | 304 | 54 | 68 | 0 | 8 | 50 | 320 | 35 | 0 | 162 | 0 | 0 | 17 | 0 |  | 716 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 21 | 0 | 130 | 0 | 360 | 17 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 410 | 215 | 0 | 0 | 0 |  | 6460 | 2384 | 8844 | 3989 | 716 | 2146 | 0 | 1244 | 493 | 103 | 0 | 51 | 102 | 0 | 0 | 103.79
24:00 | 0 | 0 | 0 | 110 | 0 | 104 | 0 | 397 | 256 |  | 0 | 250 | 260 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 33 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 35 | 80 | 0 | 0 | 360 | 340 | 200 | 8 | 137 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 22 | 100 | 153 | 0 | 20 | 0 | 30 | 30 | 47 | 0 | 130 | 132 | 63 | 84 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 64 | 0 | 10 | 0 | 0 | 322 | 0 | 0 | 17 | 0 | 304 | 54 | 17 | 0 | 0 | 0 | 320 | 0 | 0 | 54 | 0 | 0 | 17 | 0 |  | 717 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 130 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 222 | 0 | 0 | 0 |  | 6223 | 2162 | 8385 | 4021 | 717 | 2180 | 0 | 751 | 462 | 103 | 0 | 51 | 100 | 0 | 0 | 103.79
KWH | 0 | 0 | 0 | 2614500 | 0 | 1454227 | 0 | 8785920 | 6288000 |  | 0 | 6163250 | 5912756 | 0 | 0 | 875411 | 7295812 | 0 | 0 | 0 | 829008 | 25920 | 157229 | 0 | 0 | 0 | 1305360 | 324723 | 593015 | 305316 | 600000 | 631800 | 826400 | 628700 | 25459 | 0 | 426000 | 1696000 | 2900000 | 0 | 45320 | 0 | 0 | 0 | 0 |  | 78480 | 0 | 435412 | 69840 | 16320 | 340320 | 366384 | 455520 | 2283666 | 0 | 0 | 7660000 | 7172000 | 4535000 | 200727 | 3119540 | 627624 | 357120 | 0 | 946426 | 0 | 0 | 29803 | 398412 | 166680 | 414300 | 508910 | 2128320 | 4064640 | 67200 | 321372 | 12450 | 716000 | 706560 | 595800 | 0 | 3319527 | 2581000 | 1125984 | 1070400 | 0 | 4499470 | 240000 | 0 | 165780 | 7151000 | 337296 | 180000 | 0 | 664909 | 0 | 0 | 1886400 | 0 | 2075040 | 35235 | 1653120 | 387360 | 806251 | 7728000 | 25200 | 60000 | 1125745 | 28201 | 6039382 | 1300821 | 1341526 | 84360 | 662760 | 594240 | 7647600 | 374400 | 343990 | 1990080 | 176891 | 0 | 433440 | 194133 |  | 17371636 | 0 | 5556960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1363000 | 413700 | 0 | 0 | 0 | 0 | 0 | 0 | 38136 | 0 | 0 | 0 | 56640 | 15169 | 263760 | 0 | 148266 | 1947054 | 0 | 0 | 0 | 0 | 0 | 0 | 3620755 | 0 | 156006 | 0 | 3940809 | 0 | 8575236 | 821280 | 0 | 812736 | 6912 | 448310 | 0 | 36765 | 453600 | 8248500 | 4573450 | 0 | 16080 | 32460 |  | 147834493 | 58917220 | 206751713 | 96618676 | 17371636 | 48062685 | 0 | 29054971 | 10195554 | 2122000 | 0 | 514637 | 2128320 | 683234 | 0
Fuel Cost | 0 | 0 | 0 | 3843315 | 0 | 1919579.64 | 0 | 8873779.2 | 6476640 |  | 0 | 6717942.5 | 6563159.16 | 0 | 0 | 7405977.06 | 7587644.48 | 0 | 0 | 0 | 7560552.96 | 255052.8 | 1449651.38 | 0 | 0 | 0 | 9529128 | 2510108.79 | 5847127.9 | 228987 | 450000 | 0 | 0 | 0 | 246188.53 | 0 | 115020 | 457920 | 5249000 | 0 | 421022.8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4223496.4 | 666972 | 141984 | 2695334.4 | 461643.84 | 1352894.4 | 3379825.68 | 0 | 0 | 5668400 | 7172000 | 4172200 | 258937.83 | 3587471 | 709215.12 | 499968 | 0 | 1618388.46 | 0 | 0 | 284618.65 | 505983.24 | 125010 | 725025 | 381682.5 | 15962400 | 4308518.4 | 610176 | 408142.44 | 198453 | 1174240 | 1130496 | 1060524 | 0 | 3784260.78 | 2684240 | 2218188.48 | 2044464 | 0 | 7784083.1 | 525600 | 0 | 338191.2 | 7222510 | 252972 | 136800 | 0 | 5026712.04 | 0 | 0 | 9809280 | 0 | 20418393.6 | 411897.15 | 13472928 | 4202856 | 5684069.55 | 7187040 | 229824 | 567000 | 9805238.95 | 0 | 45657727.92 | 11330150.91 | 11792013.54 | 841912.8 | 5679853.2 | 3957638.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100060623.36 | 0 | 5834808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1540190 | 641235 | 0 | 0 | 0 | 0 | 0 | 0 | 337503.6 | 0 | 0 | 0 | 548841.6 | 147139.3 | 506419.2 | 0 | 112237.362 | 11740735.62 | 0 | 0 | 0 | 0 | 0 | 0 | 4779396.6 | 0 | 234009 | 0 | 4610746.53 | 0 | 8489483.64 | 8574163.2 | 0 | 7712864.64 | 65249.28 | 3478885.6 | 0 | 406253.25 | 3352104 | 36210915 | 0 | 0 | 0 | 0 |  | 330257643.18 | 199383803.782 | 529641446.962 | 97808880.972 | 100060623.36 | 49728606.81 | 0 | 211576549.7 | 47951650.62 | 572940 | 0 | 4963192.1 | 15962400 | 1016603.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 0 | 87 | 0 | 356 | 282 |  | 0 | 250 | 260 | 0 | 0 | 43 | 300 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 21 | 25 | 23 | 33 | 25 | 0 | 0 | 0 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 7 | 100 | 0 | 0 | 335 | 310 | 182 | 8 | 138 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 18 | 84 | 156 | 0 | 20 | 2 | 30 | 30 | 44 | 0 | 130 | 117 | 61 | 81 | 0 | 205 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 117 | 0 | 40 | 0 | 20 | 322 | 0 | 0 | 51 | 4 | 303 | 54 | 108 | 0 | 17 | 10 | 320 | 0 | 53 | 88 | 0 | 0 | 17 | 32 |  | 719 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 196 | 0 | 390 | 0 | 0 | 35 | 0 | 0 | 0 | 7 | 0 | 250 | 220 | 0 | 0 | 5 |  | 8757 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 96 | 0 | 395 | 262 | 0 | 0 | 250 | 255 | 0 | 0 | 48 | 335 | 0 | 0 | 0 | 64 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 25 | 8 | 0 | 33 | 70 | 120 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 68 | 30 | 0 | 25 | 21 | 10 | 80 | 0 | 0 | 340 | 340 | 171 | 8 | 138 | 29 | 10 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 25 | 22 | 116 | 147 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 130 | 132 | 40 | 80 | 0 | 218 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 175 | 0 | 0 | 170 | 0 | 117 | 0 | 90 | 85 | 100 | 322 | 8 | 17 | 68 | 0 | 305 | 54 | 68 | 34 | 70 | 80 | 320 | 70 | 0 | 162 | 52 | 0 | 17 | 0 |  | 716 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 21 | 0 | 130 | 0 | 363 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 113 | 430 | 221 | 0 | 0 | 0 |  | 10274 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 110 | 0 | 100 | 0 | 412 | 360 | 0 | 0 | 250 | 300 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 33 | 70 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 100 | 100 | 90 | 50 | 21 | 15 | 80 | 0 | 0 | 340 | 340 | 215 | 8 | 138 | 29 | 10 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 25 | 22 | 164 | 170 | 8 | 22 | 0 | 30 | 30 | 50 | 0 | 163 | 132 | 65 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 135 | 324 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 733 | 0 | 350 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 65 | 30 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 40 | 40 | 52 | 35 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 100 | 210 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 110 | 0 | 90 | 0 | 350 | 290 | 0 | 0 | 250 | 300 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 51 | 0 | 33 | 70 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 21 | 5 | 80 | 0 | 0 | 320 | 320 | 200 | 8 | 138 | 29 | 10 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 25 | 20 | 138 | 170 | 8 | 22 | 1.6 | 30 | 30 | 50 | 0 | 163 | 131 | 60 | 81 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 0 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 135 | 324 | 115 | 105 | 105 | 5 | 300 | 35 | 110 | 114 | 100 | 100 | 320 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 733 | 0 | 350 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 25 | 0 | 0 | 52 | 17 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 210 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 55 | 0 | 400 | 281 | 0 | 0 | 250 | 250 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 21 | 25 | 26 | 33 |  | 0 | 0 | 32 | 70 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 80 | 0 | 0 | 290 | 270 | 180 | 8 | 137 | 29 | 10 | 0 | 15 | 0 | 0 | 0 | 22 | 8 | 25 | 19 | 86 | 170 | 0 | 20 | 1 | 30 | 30 | 46 | 0 | 130 | 132 | 40 | 50 | 0 | 205 | 18 | 0 | 10 | 300 | 23 | 5 | 0 | 0 | 0 | 0 | 74 | 0 | 58 | 11 | 10 | 0 | 0 | 321 | 0 | 0 | 17 | 1 | 123 | 54 | 17 | 0 | 0 | 0 | 320 | 0 | 22 | 0 | 0 | 0 | 17 | 15 | 0 | 717 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 167 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 131 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 6986 | 5:00
| Highest Generation |  | 10274 | 19:00
| Day Peak Generation |  | 8757 | 12:00
| Evening Peak Generation |  | 10274 | 19:00
| HVDC Max Flow |  | 723 | 1:00
| HVDC EvPeak Flow |  | 716 | 19:00
| Load factor L.F |  | 83.85%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-11-03
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-11-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8757 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7085 | MW
Evening Peak Generation : |  | 10274 | MW Hour : | 19:00 | Available Max Generation : |  | 14571 | MW
E.P. Demand (at gen end) : |  | 10274 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 10274 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4071 | MW
Total Gen. (MKWH) : |  | 206.7517 | System Load Factor : | 83.85% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -334 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-11-03
Actual : | 103.76 | Ft.(MSL) , | Rule curve : | 108.8 | Ft.( MSL )
Gas Consumed : | Total = | 1091.12 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 147537487.782
: |  | Coal : | 47951650.62 | Oil : | 216539741.8 | Total : | 412028880.202
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3736.8743 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1269.2138 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1136.9008 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1027.189 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 928.3092 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 749.1088 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 420.834 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 192.9275 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 577.7405 |  |  | 0 | 0%
Total | 0 |  | 10039.0979 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan #02
7) Sirajganj-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar 230/132 kV T-03 transformer was under shut down from 11:40 to 16:19 for A/M.
b) B.Baria 132/33 kV T-1 transformer was under shut down from 08:43 to 12:04 for A/M.
c) Ashuganj-Cumilla(N) 230 kV Ckt-2 was under shut down from 09:25 to 00:28(3/11/21) for A/M.
d) Cumilla(S) 132/33 kV T-3 transformer was under shut down from 10:19 for D/W.
e) Dhamrai 132/33 kV T-1 transformer was under shut down from 08:18 to 14:10 for D/W.
f) Dhamrai 132/33 kV T-2 transformer was under shut down from 08:28 to 11:17 for D/W. |  |  |  |  | About 20 MW power interruption occurred under Dhamrai S/S
g) HVDC 10CF12 shunt reactor was under shut down from 09:18 to 16:03 for A/M. |  |  |  |  | area from 08:28 to 11:17.
h) Kamrangirchar 132/33 kV GT-2 transformer was under shut down from 08:30 to 16:50 for A/M.
i) Khulna(S) 230/132 kV T-01 transformer was under shut down from 08:07 to 16:31 for A/M.
j) Madaripur 132/33 kV T-2 transformer was under shut down from 08:06 to 16:49 for A/M.
k) Madunaghat-Sikalbaha 132 kV Ckt was under shut down from 08:45 to 15:17 for A/M.
l) Megnaghat-Shyampur 230 kV Ckt-1 was under shut down from 08:25 to 13:56 for A/M.
m) Mymensing-Bhaluka 132 kV Ckt-1 was under shut down from 09:44 to 17:37 for D/W.
n) Mymensing-Kishorganj 132 kV Ckt-1 was under shut down from 09:15 to 17:19 for A/M.
o) Netrokona 132/33 kV T-1 transformer was under shut down from 09:11 to 15:50 for A/M.
p) Panchaghar 132/33 kV T-3 transformer was under shut down from 08:08 to 17:02 for A/M.
q) Rajshahi 132/33 kV T-1 transformer was under shut down from 08:12 to 16:40 for A/M.
r) Satkhira 132/33 kV T-1 transformer was under shut down from 09:03 to 12:58 for A/M.
s) Sonargaon-IEL 132 kV Ckt-2 was under shut down from 08:35 to 15:45 for A/M.
t) Bheramara GK 132/33 kV T-2 transformer was under shut down from 08:11 to 15:27 for A/M.
u) Kodda 33 kV Bus section-2 was under shut down from 12:51 to 13:29 for C/M.
v) Shahjibazar-330 MW CCPP GT-2 tripped at 14:15 due to gas pressure low and was synchronized at 16:14.
w) Bhola-225 MW CCPP GT-2 was synchronized at 15:12 for testing & GT-1 was shut down at 15:50
due to gas shortage.
x) Sylhet-Fenchuganj 132 kV Ckt tripped at 05:06(3/11/21) showing dist.Z1,A-phase and was switched
on at 05:17(3/11/21).
y) Sirajganj #2 CCPP ST & GT were shut down at 23:50 & 23:55 respectively.
z) Barapukuria 230/132 kV T-01 transformer is under shut down since 07:56(3/11/21) for A/M.
aa) Panchaghar 132/33 kV T-3 transformer is under shut down since 08:00(3/11/21) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-11-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2614500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 1454227
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 395 | 8785920 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 262 | 6288000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6163250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 255 | 5912756 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 48 | 875411 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 25 | 157229 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 305316
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7295812
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 829008 | Low demand.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1305360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 25920 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 324723
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 593015
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1231800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 826400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 628700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 25459 | Low demand.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 175 | 664909 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 117 | 2075040 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 60000 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 374400 | Low demand.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1990080
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 194133
| Dhaka area Total |  |  |  | 5560 | 2683 | 51001368
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 45320 | Low demand.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 35235
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 340320 | Low demand.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 103 | 2122000 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 68 | 1125745 | Low demand.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 435412 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 69840 | Low demand.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1653120 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 366384 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 455520
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 16320 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28201
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 6039382
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1300821
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 68 | 1341526 | Low demand.
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 80 | 594240 | Low demand.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 52 | 176891 | Low demand.
| Chattogram area Total |  |  |  | 2382 | 1102 | 19046277
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2283666 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 171 | 4535000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 340 | 7660000 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 340 | 7172000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 627624 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 357120 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 946426
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 806251 | Low demand.
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3119540 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 85 | 387360 | Low demand.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 398412
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 166680
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2128320
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 414300 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 29803 | Low demand.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 508910 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 84360 | Low demand.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 662760 | Low demand.
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 433440 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1677 | 32922699
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 147 | 4064640 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 321372
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 67200
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12450
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 170 | 1886400 | Low demand.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 25200 | Low demand.
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 343990
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 78480
| Mymensingh Area Total |  |  |  | 622 | 369 | 6799732
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 706560 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3319527 | frequency control.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 132 | 2581000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 595800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 180000
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1125984 | frequency control.
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1070400
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 4499470
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 240000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 337296
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7151000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 322 | 7728000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 165780
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7647600 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1690 | 38064417
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 716 | 17371636
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 125 | 5556960 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 821280
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 6912 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 946 | 23756788
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 413700 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1363000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 21 | 156006 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 8248500 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 4573450
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 16080 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 760 | 14770736
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 123 | 3620755 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 3940809 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 363 | 8575236 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 15169 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 263760
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 148266
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 56640 | Low demand.
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 38136 | Reserve.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 70 | 812736 | Low demand.
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 453600
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32460
| Rajshahi Area Total |  |  |  | 2179 | 855 | 17957567
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1947054
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 448310
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36765
| Rangpur Area Total |  |  |  | 605 | 192 | 2432129
| Total |  |  |  | 20934 | 10274 | 206751713
| Eastern Grid Total |  |  |  | 13975 | 7521 | 147834493
| Western Grid Total |  |  |  | 6959 | 2753 | 58917220
| National Grid Total |  |  |  | 20934 | 10274 | 206751713
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-11-02
(a) ENTIRE EASTERN GRID : |  | 6989 | MW | (b) ENTIRE WESTERN GRID : |  | 2824 | MW
i) Dhaka area |  | 3794 | MW | i) Khulna area |  | 1111 | MW
ii) Chittagong area |  | 1245 | MW | ii) Rajshahi area |  | 899 | MW
iii) Comilla area |  | 839 | MW | iii) Barisal area |  | 251 | MW
iv) Mymensingh area |  | 727 | MW | iv) Rangpur area |  | 563 | MW
v) Sylhet area |  | 384 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9813 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 12:00 | Kishoreganj | 94 | 19:30 | Benapol | 36 | 18:00
Munsiganj | 70 | 19:30 | Netrokona | 80 | 18:00 | Jhenida(Old) | 85 | 18:00
Sonargaon | 66 | 1:00 | Jamalpur | 102 | 19:30 | Bottail | 94 | 18:00
Shyampur | 176 | 11:00 | Sherpur | 96 | 18:00 | G.K Project | 38 | 18:00
Bhulta | 171 | 18:30 | Srimongal | 40 | 18:00 | Faridpur | 102 | 18:00
Madanganj | 48 | 11:00 | Shahjibazar | 79 | 18:00 | Rajbari | 102 | 18:00
Shitalakhya | 104 | 18:00 | Fenchuganj | 33 | 17:00 | Madaripur | 42 | 18:00
Rahim steel | 17 | 11:00 | Kulawara | 34 | 19:00 | Sariatpur | 44 | 19:30
Matuail | 70 | 22:00 | Sylhet | 114 | 18:00 | Gopalganj | 67 | 19:30
Ghorasal | 75 | 8:00 | Chatak | 20 | 18:00 | Bagerhat | 76 | 18:00
Narsingdi | 133 | 19:30 | Sunamganj | 32 | 19:30 | Mongla | 28 | 12:00
Haripur (SBU) | 112 | 13:00 | Biani Bazar | 47 | 18:00 | Satkhira | 79 | 18:30
Sreenagar | 29 | 21:00 | Comilla (S) | 120 | 18:00 | Gallamari | 29 | 18:00
Ullon | 57 | 18:00 | Comilla(N) | 79 | 18:00 | Magura | 40 | 18:00
Hasnabad | 68 | 15:00 | Chandpur | 49 | 20:00 | Norail | 37 | 18:00
Magbazar | 80 | 13:00 | Feni | 93 | 18:00 | Chuadanga | 68 | 18:00
Maniknagar | 60 | 13:00 | Chowmuhani | 138 | 19:00 | Barisal(N) | 29 | 19:30
Bangabhaban | 9 | 10:00 | Ashuganj | 31 | 24:00 | Barisal (S) | 82 | 18:00
Motijheel | 24 | 11:00 | Daudkandi | 106 | 19:00 | Patuakhali | 77 | 20:00
Narinda | 60 | 13:00 | B.Baria | 113 | 18:30 | Bhandaria | 37 | 19:30
Kazla | 75 | 16:00 | Ramganj | 58 | 19:00 | Borguna | 12 | 18:00
Dhanmondi | 152 | 13:00 | Chaddagram | 31 | 18:00 | Borhan Uddin | 29 | 21:00
Lalbag | 72 | 13:00 | PHP | 10 | 19:00 | Ishurdi | 54 | 18:00
Madartek | 59 | 18:00 | Kochua | 44 | 20:00 | Ruppur Paromanobik | 3 | 20:00
Dhaka University | 29 | 13:00 | Madunaghat | 53 | 18:30 | Natore | 93 | 18:00
Aftabnagar | 12 | 11:00 | Hathazari | 83 | 18:00 | Bogra | 114 | 18:30
Fatullah | 55 | 12:00 | Khulshi | 186 | 12:00 | Noagaon | 80 | 19:00
Nawabganj | 34 | 20:00 | Halishahar | 85 | 17:00 | Rajshahi | 106 | 18:30
Keraniganj | 61 | 18:00 | Baraulia | 140 | 12:00 | Rajshahi New | 14 | 18:00
Banani | 28 | 13:00 | Sikalbaha | 41 | 18:00 | C.Nawabganj | 46 | 12:00
Mirpur | 106 | 18:00 | Dohazari | 86 | 18:00 | Amnura | 34 | 18:00
Kalyanpur | 84 | 18:00 | Cox'sbazar | 84 | 17:00 | Pabna | 77 | 18:00
Gulshan | 96 | 12:00 | Chandraghona | 22 | 18:00 | Shahjadpur | 68 | 19:00
Uttara | 68 | 18:30 | Kaptai | 4 | 18:00 | Serajganj | 74 | 18:30
Uttara New | 22 | 18:00 | A. Khaer Stl. | 13 | 4:00 | Niyamatpur | 47 | 18:00
Kamrangirchar | 89 | 18:00 | Bakulia | 104 | 18:00 | Joypurhat | 41 | 18:00
Savar | 164 | 15:00 | Julda | 25 | 15:00 | Sherpur(Bogura) | 48 | 18:00
Bhasantec | 91 | 13:00 | TK chemical | 25.5 | 18:00 | Mohastangor | 46 | 18:00
Agargaon | 79 | 13:00 | Modern Steel | 5 | 10:00 | Bhangura | 20 | 20:00
Satmosjid | 84 | 13:00 | Shahmirpur | 22.5 | 22:00 | Rangpur | 102 | 18:00
Tongi | 106 | 18:00 | Khagrachhari | 22 | 18:00 | Lalmonirhat | 44 | 18:00
Kabirpur | 215 | 15:00 | Matarbari | 28 | 17:00 | Saidpur | 80 | 18:30
Basundhara | 173 | 15:00 | Baroiar Hat | 36 | 18:00 | Purbasadipur | 80 | 18:00
Manikganj | 48 | 18:00 | Rangamati | 12 | 18:00 | Thakurgaon | 60 | 18:00
Joydevpur | 153 | 18:00 | Abul Khair 230 | 120 | 16:00 | Palashbari | 88 | 18:00
New Tongi | 77 | 18:00 | BSRM | 155 | 21:00 | Barapukuria | 40 | 18:30
Kodda | 218 | 18:30 | GPH Ispat | 90 | 1:00 | Panchagar | 27 | 7:00
Dhamrai | 80 | 18:00 | Agrabad | 60 | 18:00 | Joldhaka | 28 | 19:30
Rajendrapur | 92 | 18:30 | Goalpara | 22 | 13:00 | Kurigram | 47 | 18:00
Valuka | 98 | 15:00 | Central S/S | 78 | 18:30 | Mithapukur | 22 | 18:00
Tangail | 158 | 18:00 | Noapara | 42 | 18:30
Mymensing | 157 | 18:00 | Jessore | 81 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-11-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 22:00 | 403 | 11:00 | Kaliakoir | 399 | 0.20833 | 389 | 0.41667
| Bheramara | 404 | 19:00 | 400 | 18:00 | Bhulta | 394 | 0.75 | 381 | 0.41667
| Ashuganj(N) | 400 | 17:00 | 388 | 10:00 | Gopalganj | 407 | 0.625 | 395 | 0.77083
| Payra | 412 | 18:00 | 404 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 18:00 | 235 | 1:00 | Hathazari | 236 | 17:00 | 220 | 9:00
| Ishurdi | 239 | 5:00 | 229 | 18:30 | Megnaghat | 236 | 21:00 | 232 | 1:00
| Ashuganj | 245 | 12:00 | 238 | 9:00 | Fenchuganj | 246 | 18:00 | 242 | 1:00
| Serajganj | 235 | 3:00 | 231 | 11:00 | Siddhirganj | 235 | 18:00 | 228 | 11:00
| Baghabari | 236 | 6:00 | 230 | 18:00 | Maniknagar | 233 | 18:00 | 226 | 10:00
| Barapukuria | 236 | 17:00 | 232 | 7:00 | Agargaon | 231 | 3:00 | 221 | 10:00
| Bogra | 227 | 15:00 | 221 | 8:00 | Barisal | 245 | 17:00 | 239 | 20:00
| Rajshahi | 233 | 3:00 | 223 | 18:30 | Bhola 225 MW | 247 | 3:00 | 243 | 13:00
| Khulna South | 242 | 5:00 | 222 | 18:30 | AKSML | 237 | 17:00 | 217 | 4:00
| Rampura | 232 | 7:00 | 227 | 11:00 | BSRM | 237 | 18:00 | 218 | 4:00
| Haripur | 233 | 18:00 | 226 | 9:00 | Bibiyana | 246 | 18:00 | 240 | 10:00
| Hasnabad | 232 | 20:00 | 225 | 1:00 | Bhulta | 237 | 20:00 | 228 | 10:00
| Shyampur | 232 | 18:00 | 223 | 10:00 | Ashuganj (S) | 241 | 18:00 | 233 | 10:00
| Aminbazar | 232 | 1:00 | 225 | 2:00 | Kaliakoir | 231 | 18:00 | 223 | 10:00
| Tongi | 230 | 18:00 | 217 | 11:00 | GPH | 237 | 18:00 | 217 | 4:00
| Comilla (N) | 236 | 18:00 | 226 | 10:00 | Jhenaidah | 236 | 6:00 | 219 | 18:30
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 18:00 | 131 | 10:00 | Madanhat | 137 | 0.70833 | 130 | 0.041667
| Munsiganj | 138 | 18:00 | 132 | 10:00 | Hathazari | 139 | 0.75 | 129 | 0.375
| Sonargaon | 134 | 4:00 | 131 | 9:00 | Khulshi | 136 | 0.75 | 124 | 0.375
| Shyampur | 139 | 22:00 | 133 | 10:00 | Halishahar | 138 | 0.75 | 124 | 0.16667
| Bhulta | 131 | 2:00 | 127 | 10:00 | Baraulia | 137 | 0.70833 | 128 | 0.5
| Madanganj | 137 | 17:00 | 131 | 10:00 | Sikalbaha | 139 | 0.75 | 127 | 0.33333
| Shitalakhya | 137 | 18:00 | 132 | 9:00 | Dohazari | 133 | 0.75 | 125 | 0.20833
| Rahim steal | 136 | 18:00 | 132 | 9:00 | Cox'sbazar | 121 | 0.33333 | 108 | 0.625
| Matuail | 136 | 18:00 | 131 | 10:00 | Chandraghona | 137 | 0.75 | 130 | 0.20833
| Ghorasal | 141 | 22:00 | 137 | 9:00 | Kaptai | 135 | 0.70833 | 131 | 0.41667
| Narsinghdi | 136 | 18:00 | 133 | 1:00 | A. Khaer Stl. | 136 | 0.75 | 126 | 0.20833
| Haripur (SBU) | 136 | 9:00 | 132 | 13:00 | Bakulia | 137 | 0.75 | 126 | 0.375
| Sreenagar | 135 | 3:00 | 129 | 10:00 | Julda | 137 | 0.70833 | 127 | 0.083333
| Ullon | 136 | 5:00 | 131 | 10:00 | TK Chemical | 137 | 0.75 | 127 | 0.20833
| Hasnabad | 135 | 4:00 | 130 | 9:00 | Modern Steel | 135 | 0.8125 | 125 | 0.20833
| Magbazar | 135 | 1:00 | 131 | 10:00 | Shahmirpur | 137 | 0.75 | 125 | 0.375
| Maniknagar | 136 | 6:00 | 131 | 12:00 | Khagrachhari | 135 | 0.75 | 129 | 0.20833
| Bangabhaban | 136 | 6:00 | 131 | 12:00 | Matarbari | 132 | 0.79167 | 120 | 0.041667
| Motijheel | 136 | 6:00 | 131 | 12:00 | Baroiar Hat | 137 | 0.8125 | 130 | 0.041667
| Narinda | 136 | 6:00 | 131 | 12:00 | Rangamati | 137 | 18:00 | 129 | 9:00
| Kazla | 136 | 6:00 | 131 | 12:00 | Agrabad | 136 | 18:00 | 126 | 2:00
| Dhanmondi | 135 | 5:00 | 131 | 10:00 | Goalpara S/S | 139 | 3:00 | 130 | 0.77083
| Lalbag | 133 | 20:00 | 122 | 10:00 | Khulna Central S/S | 139 | 6:00 | 127 | 0.77083
| Madartek | 136 | 21:00 | 131 | 10:00 | Noapara | 139 | 4:00 | 130 | 0.5
| Dhaka University | 136 | 5:00 | 131 | 10:00 | Jessore | 139 | 4:00 | 130 | 0.79167
| Aftabnagar | 136 | 3:00 | 131 | 10:00 | Benapol | 139 | 0.16667 | 127 | 0.77083
| Fatullah | 139 | 20:00 | 133 | 10:00 | Jhenida(Old) | 142 | 5:00 | 131 | 0.77083
| Nawabganj | 136 | 17:00 | 130 | 10:00 | Bottail | 140 | 0.125 | 132 | 0.77083
| Keraniganj | 137 | 20:00 | 129 | 10:00 | G.K Project | 142 | 0.16667 | 138 | 0.5
| Banani | 136 | 6:00 | 131 | 10:00 | Faridpur | 142 | 0.25 | 135 | 0.75
| Mirpur | 133 | 19:30 | 123 | 9:00 | Rajbari | 141 | 0.125 | 134 | 0.77083
| Kalyanpur | 133 | 18:00 | 124 | 9:00 | Madaripur | 143 | 0.33333 | 139 | 0.83333
| Gulshan | 135 | 3:00 | 131 | 10:00 | Shariyatpur S/S | 143 | 4:00 | 139 | 0.58333
| Uttara | 136 | 20:00 | 128 | 1:00 | Gopalganj | 146 | 0.25 | 140 | 0.5
| Uttara New | 133 | 20:00 | 123 | 9:00 | Bagerhat | 139 | 6:00 | 125 | 0.77083
| Kamrangirchar | 136 | 18:00 | 130 | 9:00 | Mongla | 137 | 1:00 | 127 | 0.77083
| Savar | 135 | 19:30 | 122 | 9:00 | Satkhira | 138 | 6:00 | 124 | 18:30
| Bhasantec | 137 | 19:30 | 130 | 9:00 | Gallamari | 142 | 0.70833 | 131 | 12:00
| Agargaon | 138 | 19:30 | 131 | 9:00 | Magura | 142 | 1:00 | 132 | 0.75
| Satmosjid | 138 | 19:30 | 131 | 9:00 | Narail | 141 | 0.25 | 129 | 0.77083
| Tongi | 139 | 22:00 | 132 | 11:00 | Chuadanga | 139 | 6:00 | 128 | 0.77083
| Kabirpur | 138 | 22:00 | 133 | 15:00 | Barisal(N) | 143 | 3:00 | 137 | 0.83333
| Basundhara | 136 | 22:00 | 128 | 11:00 | Barisal (S) | 143 | 6:00 | 137 | 12:00
| Manikganj | 141 | 22:00 | 138 | 15:00 | Patuakhali(S) | 142 | 0.20833 | 135 | 0.54167
| Joydevpur | 139 | 0:00 | 133 | 11:00 | Bhandaria | 140 | 0.25 | 132 | 0.5
| New Tongi | 139 | 20:00 | 130 | 11:00 | Borguna | 141 | 0.70833 | 136 | 0.8125
| Kodda | 133 | 22:00 | 125 | 11:00 | Jhenaidah(New) | 141 | 4:00 | 130 | 18:30
| Dhamrai | 139 | 21:00 | 136 | 1:00 | Ishurdi | 140 | 5:00 | 134 | 18:30
| Rajendrapur | 133 | 20:00 | 124 | 11:00 | Ruppur Paromanobik | 141 | 6:00 | 134 | 20:00
| Valuka | 130 | 20:00 | 120 | 15:00 | Natore | 137 | 17:00 | 133 | 18:30
| Tangail | 136 | 1:00 | 131 | 11:00 | Bogra | 136 | 18:00 | 132 | 7:00
| Mymensing | 133 | 9:00 | 129 | 7:00 | Noagaon | 134 | 19:00 | 128 | 8:00
| Kishorganj | 134 | 3:00 | 132 | 11:00 | Rajshahi | 137 | 6:00 | 131 | 12:00
| Netrokona | 132 | 9:00 | 128 | 15:00 | Rajshahi New | 138 | 6:00 | 131 | 18:30
| Jamalpur | 140 | 20:00 | 121 | 2:00 | C.Nawabganj | 135 | 6:00 | 130 | 18:30
| Sherpur | 138 | 18:30 | 122 | 7:00 | Amnura | 136 | 3:00 | 129 | 18:30
| Srimongal | 140 | 4:00 | 136 | 10:00 | Pabna | 138 | 3:00 | 133 | 18:00
| Shahjibazar | 139 | 16:00 | 135 | 9:00 | Shahjadpur | 139 | 14:00 | 137 | 18:00
| Fenchuganj | 138 | 19:00 | 135 | 9:00 | Serajganj | 136 | 1:00 | 132 | 12:00
| Khulawara | 137 | 13:00 | 135 | 2:00 | Niyamatpur | 134 | 17:00 | 126 | 8:00
| Sylhet | 135 | 22:00 | 133 | 1:00 | Joypurhat | 136 | 17:00 | 123 | 9:00
| Chatak | 136 | 24:00 | 134 | 1:00 | Sherpur(Bogura) | 137 | 17:00 | 131 | 12:00
| Sunamganj | 134 | 12:00 | 132 | 1:00 | Mohastangor | 138 | 17:00 | 131 | 8:00
| Biani Bazar | 134 | 1:00 | 133 | 9:00 | Bangura | 139 | 3:00 | 135 | 12:00
| Comilla(s) | 130 | 23:00 | 124 | 18:00 | Rangpur | 134 | 17:00 | 126 | 8:00
| Comilla(n) | 142 | 18:00 | 135 | 9:00 | Lalmonirhat | 132 | 3:00 | 125 | 13:00
| Chandpur | 138 | 18:00 | 132 | 1:00 | Saidpur | 133 | 4:00 | 126 | 18:30
| Feni | 139 | 18:00 | 128 | 6:00 | Purbasadipur | 134 | 3:00 | 125 | 18:00
| Chowmuhani | 137 | 18:00 | 127 | 1:00 | Thakurgaon | 134 | 17:00 | 126 | 18:00
| Ashuganj | 140 | 18:00 | 139 | 9:00 | Palashbari | 134 | 4:00 | 129 | 7:00
| Daudkandi | 137 | 18:00 | 131 | 12:00 | Barapukuria | 136 | 20:00 | 132 | 7:00
| B.Baria | 137 | 18:00 | 134 | 10:00 | Panchagar | 138 | 0.70833 | 123 | 0.77083
| Ramganj | 138 | 18:00 | 128 | 2:00 | Joldhaka | 134 | 0.20833 | 125 | 0.77083
| Chaddagram | 139 | 18:00 | 131 | 6:00 | Kurigram | 133 | 0.16667 | 126 | 0.54167
| PHP | 138 | 20:00 | 126 | 5:00 | Mithapukur | 136 | 0.70833 | 130 | 0.625
| Kochua | 139 | 18:00 | 132 | 1:00

## L-Curve
Date | 2021-11-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 106 | 6223 | 2162 | 8385 |  |  |  | QF-LDC-11
0:30 | 220 | 5907.5 | 2332 | 8239.5 | Date: | 2021-11-02
1:00 | 334 | 5592 | 2502 | 8094
1:30 | 345 | 5416 | 2462.5 | 7878.5
2:00 | 356 | 5240 | 2423 | 7663
2:30 | 363 | 5189 | 2348 | 7537 | [5 empty] | Gen. at Eve. Peak | 10274 | 10274 MW (19:00 )
3:00 | 370 | 5138 | 2273 | 7411 | [6 empty] | 19:00
3:30 | 368 | 5047 | 2187.5 | 7234.5 | [5 empty] | Gen. at Day Peak | 8757 | 8757 MW (12:00 )
4:00 | 366 | 4956 | 2102 | 7058 | [6 empty] | 12:00
4:30 | 345 | 4931.5 | 2090.5 | 7022 | [5 empty] | Highest Generation | 10274
5:00 | 324 | 4907 | 2079 | 6986 | [6 empty] | 19:00
5:30 | 312 | 4956 | 2088 | 7044
6:00 | 300 | 5005 | 2097 | 7102
6:30 | 194 | 5056.5 | 2148.5 | 7205
7:00 | 88 | 5108 | 2200 | 7308
7:30 | 109 | 5198.5 | 2239 | 7437.5
8:00 | 130 | 5289 | 2278 | 7567
8:30 | 219 | 5350 | 2283.5 | 7633.5
9:00 | 308 | 5411 | 2289 | 7700
9:30 | 328 | 5537 | 2312.5 | 7849.5
10:00 | 348 | 5663 | 2336 | 7999
10:30 | 293 | 5827 | 2328.5 | 8155.5
11:00 | 238 | 5991 | 2321 | 8312
11:30 | 168 | 6189 | 2345.5 | 8534.5
12:00 | 98 | 6387 | 2370 | 8757
12:30 | 90 | 6446.5 | 2337 | 8783.5
13:00 | 82 | 6506 | 2304 | 8810
13:30 | 77 | 6473.5 | 2297.5 | 8771
14:00 | 72 | 6441 | 2291 | 8732
14:30 | 61 | 6479.5 | 2241 | 8720.5
15:00 | 50 | 6518 | 2191 | 8709
15:30 | 91 | 6468 | 2172.5 | 8640.5
16:00 | 132 | 6418 | 2154 | 8572
16:30 | 106 | 6349.5 | 2205 | 8554.5
17:00 | 80 | 6281 | 2256 | 8537
17:30 | 189 | 6884.5 | 2508.5 | 9393
18:00 | 298 | 7488 | 2761 | 10249
18:30 | 263 | 7504.5 | 2757 | 10261.5
19:00 | 228 | 7521 | 2753 | 10274
19:30 | 234 | 7349 | 2724 | 10073
20:00 | 240 | 7287 | 2709 | 9996 |  |  |  | Executive Engineer
20:30 | 195 | 7196.5 | 2693 | 9889.5 |  |  |  | Network Operation Division
21:00 | 150 | 7106 | 2677 | 9783
21:30 | 125 | 6884 | 2611 | 9495
22:00 | 100 | 6662 | 2545 | 9207 |  |  |  |  | Page 6 of 7
22:30 | 86 | 6561 | 2464.5 | 9025.5
23:00 | 72 | 6460 | 2384 | 8844
23:30 | 89 | 6341.5 | 2273 | 8614.5
24:00 | 106 | 6223 | 2162 | 8385
10274 MW (19:00 )
8757 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-11-02 |  | Energy |  | 206751713
[13 empty] | 2021-11-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4021 | 717 | 2180 | 0 | 751 | 462 | 103 | 0 | 51 | 100 | 0 | 0
0:30 | 4083.5 | 720 | 2056.5 | 0 | 731 | 421.5 | 103 | 0 | 34 | 90 | 0 | 0 | Date: | 2021-11-02
1:00 | 4146 | 723 | 1933 | 0 | 711 | 381 | 103 | 0 | 17 | 80 | 0 | 0
1:30 | 4101 | 723 | 1868 | 0 | 619 | 376 | 103 | 0 | 8.5 | 80 | 0 | 0 | [8 empty] | Total Energy | 206.7517 | Total Energy Gen 206.752 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 206.752 MKWHr
2:00 | 4056 | 723 | 1803 | 0 | 527 | 371 | 103 | 0 | 0 | 80 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4006.5 | 723 | 1732 | 0 | 526.5 | 366 | 103 | 0 | 0 | 80 | 0 | 0 | [8 empty] | Energy Requirement | 206.7517
3:00 | 3957 | 723 | 1661 | 0 | 526 | 361 | 103 | 0 | 0 | 80 | 0 | 0
3:30 | 3880 | 723 | 1657.5 | 0 | 446.5 | 346.5 | 103 | 0 | 0 | 78 | 0 | 0 | [6 empty] | Shortage
4:00 | 3803 | 723 | 1654 | 0 | 367 | 332 | 103 | 0 | 0 | 76 | 0 | 0
4:30 | 3785 | 723 | 1637.5 | 0 | 366.5 | 332 | 103 | 0 | 0 | 75 | 0 | 0
5:00 | 3767 | 723 | 1621 | 0 | 366 | 332 | 103 | 0 | 0 | 74 | 0 | 0
5:30 | 3761 | 722.5 | 1670 | 0 | 383 | 331.5 | 103 | 0 | 0 | 73 | 0 | 0
6:00 | 3755 | 722 | 1719 | 0 | 400 | 331 | 103 | 0 | 0 | 72 | 0 | 0
6:30 | 3814.5 | 722 | 1758 | 0 | 401 | 331 | 103.5 | 0 | 0 | 68 | 7 | 0 |  |  |  |  | Coal
7:00 | 3874 | 722 | 1797 | 0 | 402 | 331 | 104 | 0 | 0 | 64 | 14 | 0
7:30 | 3961 | 720.5 | 1812.5 | 0 | 428.5 | 330.5 | 104 | 0 | 0 | 68 | 12.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 4048 | 719 | 1828 | 0 | 455 | 330 | 104 | 0 | 0 | 72 | 11 | 0
8:30 | 4071.5 | 719.5 | 1839.5 | 0 | 477.5 | 330.5 | 104 | 0 | 0 | 72 | 19 | 0
9:00 | 4095 | 720 | 1851 | 0 | 500 | 331 | 104 | 0 | 0 | 72 | 27 | 0
9:30 | 4098 | 720 | 1886.5 | 0 | 622 | 331.5 | 87 | 0 | 0 | 73 | 31.5 | 0
10:00 | 4101 | 720 | 1922 | 0 | 744 | 332 | 70 | 0 | 0 | 74 | 36 | 0
10:30 | 4118 | 720 | 1924 | 0 | 874 | 331 | 70 | 0 | 0 | 76 | 42.5 | 0
11:00 | 4135 | 720 | 1926 | 0 | 1004 | 330 | 70 | 0 | 0 | 78 | 49 | 0
11:30 | 4139.5 | 719.5 | 2041 | 0 | 1077 | 330.5 | 70 | 0 | 0 | 81 | 76 | 0
12:00 | 4144 | 719 | 2156 | 0 | 1150 | 331 | 70 | 0 | 0 | 84 | 103 | 0
12:30 | 4104 | 719 | 2155.5 | 0 | 1222.5 | 331 | 70 | 0 | 0 | 82 | 99.5 | 0
13:00 | 4064 | 719 | 2155 | 0 | 1295 | 331 | 70 | 0 | 0 | 80 | 96 | 0
13:30 | 4064 | 719 | 2155 | 0 | 1295 | 331 | 70 | 0 | 0 | 80 | 96 | 0
14:00 | 4064 | 719 | 2155 | 0 | 1295 | 331 | 70 | 0 | 0 | 80 | 96 | 0
14:30 | 3977.5 | 718 | 2131.5 | 0 | 1362.5 | 332 | 70 | 0 | 0 | 88 | 80 | 0
15:00 | 3891 | 717 | 2108 | 0 | 1430 | 333 | 70 | 0 | 0 | 96 | 64 | 0
15:30 | 3838.5 | 717 | 2107 | 0 | 1432 | 337 | 70 | 0 | 0 | 93 | 46 | 0
16:00 | 3786 | 717 | 2106 | 0 | 1434 | 341 | 70 | 0 | 0 | 90 | 28 | 0
16:30 | 3752 | 717 | 1934.5 | 0 | 1587.5 | 376 | 70 | 0 | 8 | 94 | 15.5 | 0
17:00 | 3718 | 717 | 1763 | 0 | 1741 | 411 | 70 | 0 | 16 | 98 | 3 | 0
17:30 | 3867.5 | 716.5 | 1957.5 | 0 | 2153 | 430.5 | 70 | 0 | 87.5 | 109 | 1.5 | 0
18:00 | 4017 | 716 | 2152 | 0 | 2565 | 450 | 70 | 0 | 159 | 120 | 0 | 0
18:30 | 4037 | 716 | 2142.5 | 0 | 2568.5 | 479.5 | 86.5 | 0 | 113.5 | 118 | 0 | 0
19:00 | 4057 | 716 | 2133 | 0 | 2572 | 509 | 103 | 0 | 68 | 116 | 0 | 0
19:30 | 3974 | 716 | 2144 | 0 | 2430 | 520 | 103 | 0 | 68 | 118 | 0 | 0
20:00 | 3971 | 717 | 2142 | 0 | 2356 | 523 | 103 | 0 | 68 | 116 | 0 | 0
20:30 | 3981 | 717 | 2160.5 | 0 | 2223 | 523 | 103 | 0 | 68 | 114 | 0 | 0
21:00 | 3991 | 717 | 2179 | 0 | 2090 | 523 | 103 | 0 | 68 | 112 | 0 | 0
21:30 | 3944 | 717 | 2166.5 | 0 | 1863.5 | 523 | 103 | 0 | 68 | 110 | 0 | 0
22:00 | 3897 | 717 | 2154 | 0 | 1637 | 523 | 103 | 0 | 68 | 108 | 0 | 0
22:30 | 3943 | 716.5 | 2150 | 0 | 1440.5 | 508 | 103 | 0 | 59.5 | 105 | 0 | 0
23:00 | 3989 | 716 | 2146 | 0 | 1244 | 493 | 103 | 0 | 51 | 102 | 0 | 0
23:30 | 4005 | 716.5 | 2163 | 0 | 997.5 | 477.5 | 103 | 0 | 51 | 101 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 30.4° C
24:00 | 4021 | 717 | 2180 | 0 | 751 | 462 | 103 | 0 | 51 | 100 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 206.752 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 206.752 MKWHr
Note on W13: Author:

## Generation
g | 2021-11-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 33 | 33 | 33 | 33 | 33 | 33 | 34 | 34 | 34 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 426000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1696000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 7 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 45320
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | [6 empty] | 15 | 11 | 5 | 0 | [9 empty] | 35235
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 0 | [15 empty] | 68 |  | 68 | 68 | 68 | 68 | 68 | 51 | 51 | 435412
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 0 | [7 empty] | 2 | 43 | 51 | 66 | 89 | 98 | 105 | 105 | 105 |  | 68 | 68 | 68 | 68 | 68 | 68 | 17 | 1125745
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 300 | 300 | 250 | 335 | 335 | 280 | 335 |  | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 7295812
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 4 | 15 | 15 | 15 | 24 | 130 |  | 175 | 120 | 120 | 60 | 40 |  | 0 | 664909
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2614500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2283666
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 26 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 627624
33 | Ashuganj 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 198 | 188 | 198 | 182 | 182 | 185 | 192 | 180 | 180 | 180 |  | 171 | 218 | 220 | 221 | 180 | 180 | 200 | 4535000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 310 | 370 | 320 | 345 | 310 | 310 | 320 | 315 | 295 | 270 | 340 |  | 340 | 270 | 270 | 270 | 265 | 300 | 340 | 7172000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 270 | 270 | 275 | 270 | 290 | 320 | 340 | 365 | 335 | 335 | 350 | 355 | 340 | 310 | 370 |  | 340 | 275 | 275 | 275 | 270 | 320 | 360 | 7660000
35 | Ashuganj 55 MW PP (Precision) | 24 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 30 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 357120
36 | Chandpur 150 MW CCPP | 136 | 137 | 136 | 136 | 137 | 135 | 137 | 137 | 138 | 139 | 138 | 138 | 140 | 138 | 136 | 136 | 138 | 136 |  | 138 | 138 | 137 | 136 | 137 | 135 | 137 | 3119540
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 351 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 351 | 355 | 356 | 353 | 353 | 350 | 350 | 355 | 352 |  | 395 | 398 | 397 | 396 | 355 | 363 | 397 | 8785920
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6163250
41 | Haripur 360MW CCPP(HPL) | 303 | 302 | 252 | 231 | 231 | 252 | 283 | 282 | 281 | 281 | 282 | 282 | 252 | 242 | 235 | 242 | 251 | 269 |  | 262 | 257 | 256 | 258 | 253 | 241 | 256 | 6288000
42 | RPCL 210MW CCPP | 179 | 205 | 204 | 212 | 219 | 221 | 219 | 207 | 184 | 172 | 168 | 156 | 153 | 146 | 147 | 147 | 149 | 146 |  | 147 | 149 | 151 | 152 | 155 | 152 | 153 | 4064640
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 6 |  |  |  |  | 53 | 49 | 39 | 27 | 12 | 1 | [9 empty] | 343990
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 706560
46 | Shajibazar 330 MW CCPP | 135 | 136 | 134 | 126 | 138 | 119 | 136 | 123 | 120 | 120 | 120 | 117 | 119 | 118 | 0 | 0 | 25 | 110 |  | 132 | 132 | 128 | 134 | 127 | 128 | 132 | 2581000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 61 | 62 | 40 | 61 | 40 | 40 | 63 |  | 40 | 40 | 40 | 40 | 40 | 63 | 63 | 1125984
48 | Shahjibazar 86MW PP (Shahjibazar) | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 81 | 83 | 82 | 82 | 82 | 20 | 79 |  | 80 | 83 | 83 | 83 | 84 | 84 | 84 | 1070400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 179 | 179 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 179 | 205 | 193 | 179 | 192 | 179 | 179 | 218 |  | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 4499470
51 | Sylhet 20 MW GTPP | [9 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 240000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [8 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 165780
54 | Hobiganj 11MW PP Cofidence-E | 11 | 0 | [5 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 180000
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 8 | 44 | 50 | 50 | 50 | 50 | 14 | 47 |  | 50 | 50 | 47 | 47 | 47 | 44 | 47 | 595800
56 | Shahjahanulla 25 MW PP | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 337296
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 280 | 285 | 290 | 290 | 290 | 295 | 290 | 310 | 300 | 300 | 305 | 305 | 295 | 300 | 300 | 290 |  | 275 | 290 | 290 | 295 | 280 | 290 | 290 | 7151000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 303 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7647600
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 3 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 593015
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 3 | 22 |  | 24 | 24 | 24 |  |  |  | 0 | 78480
60 | Barabkunda 22 MW PP (Regent) | 21 | 0 |  |  |  | 0 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 366384
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 305316
62 | Tangail 22 MW PP (Doreen) | 20 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 321372
63 | Impoprt (Tripura) | 80 | 80 | 80 | 76 | 74 | 72 | 64 | 72 | 72 | 74 | 78 | 84 | 80 | 82 | 96 | 90 | 98 | 120 |  | 116 | 118 | 116 | 112 | 108 | 102 | 100 | 2128320
64 | Malancha, Ctg. EPZ (United) | 40 | 2 | 2 | 2 | 2 | 39 | 35 | 10 | 5 | 3 | 3 | 7 | 9 | 8 | 3 | 2 | 6 | 10 |  | 10 | 8 | 14 | 26 | 33 | 35 | 35 | 455520
65 | Feni 22MW PP (Doreen) | [5 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 398412
66 | Feni 11 MW PP (Doreen) |  |  |  |  | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 166680
67 | Jangalia 33MW PP (Summit) | 25 | 0 | [5 empty] | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 414300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 21 | 21 | 21 | 22 | 508910
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 28 | 25 | 25 | 25 | 25 | 29 | 23 | 23 | 23 | 24 | 26 | 26 | 26 | 18 |  | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 631800
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826400
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 628700
73 | Ghorashal 108MW PP (Regent) | 55 | 10 | 11 | 11 | 11 | 11 | 11 | 53 | 53 | 53 | 53 | 87 | 95 | 94 | 85 | 94 | 22 | 94 |  | 96 | 98 | 100 | 104 | 104 | 104 | 104 | 1454227
| Feni Lanka Power | [16 empty] | 17 | 32 |  | 34 | 32 | 3 |  |  |  | 0 | 84360
| Chowmuhani 113 MW | [9 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 34 | 43 | 105 |  | 70 | 70 | 70 | 70 | 46 | 8 | 0 | 662760
| Manikgonj 162MW PP(MPGL) | [10 empty] | 20 | 88 | 134 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 54 | 1990080
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [16 empty] | 2 | 8 |  | 8 | 8 | 8 |  |  |  | 0 | 25459
79 | Kodda 150MW PP | [16 empty] | 16 | 16 | [7 empty] | 0 | 25920
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [16 empty] | 0 | 67200
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 2 | 8 |  | 8 | 8 | 8 |  |  |  |  | 29803
| Gazipur 100 MW PP | [16 empty] | 5 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 60000
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 28201
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1300821
| Karnaphuli Power Ltd. | 17 | 0 | [7 empty] | 8 | 89 | 108 | 108 | 108 | 108 | 108 | 108 | 107 |  | 68 | 68 | 68 | 68 | 68 | 68 | 17 | 1341526
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [13 empty] | 3 | 24 | 25 | 24 | 25 |  | 25 | 25 | 24 |  |  |  | 0 | 157229
86 | Meghnaghat CCPP ( Summit) | 225 | 230 | 240 | 240 | 230 | 225 | 240 | 240 | 235 | 245 | 250 | 260 | 255 | 250 | 260 | 265 | 255 | 250 |  | 255 | 250 | 245 | 255 | 250 | 250 | 260 | 5912756
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [16 empty] | 7 | 72 |  | 70 | 53 | 53 | 53 | 48 | 35 | 0 | 374400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 8 | 30 |  | 30 | 30 | 10 |  |  |  | 0 | 69840
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 19 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 32 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 946426
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 3 | 40 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 84 |  | 64 | 64 | 64 | 40 | 40 |  | 0 | 829008
95 | Patenga 50MW PP (Baraka) | [10 empty] | 15 | 25 | 25 | 25 | 25 | 25 | 26 | 47 |  | 25 | 25 | 25 | 25 | 25 | 10 | 0 | 340320
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 2 | 11 | [7 empty] | 0 | 16320
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 42 | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 43 | 43 | 42 | 42 | 42 | 43 | 45 |  | 48 | 49 | 47 | 48 | 50 | 55 | 45 | 875411
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 17 |  | 0 | 324723
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 110 | 110 | 110 | 130 | 130 | 130 | 110 | 110 | 110 | 130 | 163 | 130 | 163 | 163 | 130 | 163 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3319527
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12450
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1305360
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 40 | 8 | 8 | 8 | 8 | 8 | 10 | 70 | 70 | 70 | 70 | 70 | 89 | 80 | 80 | 80 | 80 | 132 |  | 170 | 170 | 170 | 130 | 100 | 80 | 80 | 1886400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 45 | 72 | 115 | 115 | 117 | 115 | 117 | 125 | 126 | 126 | 128 |  | 117 | 110 | 112 | 114 | 94 | 87 | 64 | 2075040
115 | Juldah 100 MW PP Unit-3 (Acorn) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 76 | 40 | 40 | 76 | 40 | 40 | 60 | 86 | 90 |  | 90 | 90 | 90 | 90 | 60 | 60 | 10 | 1653120
116 | Chandpur 200MW (Desh energy) | [16 empty] | 17 | 54 |  | 85 | 85 | 85 | 85 | 34 |  | 0 | 387360
117 | Ashuganj 150MW PP (Midland) | [9 empty] | 2 | 20 | 20 | 20 | 26 | 48 | 50 | 61 | 102 |  | 100 | 100 | 100 | 100 | 50 | 10 | 0 | 806251
118 | Bibiyana-III 400 MW CCPP | 323 | 322 | 319 | 321 | 320 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 |  | 322 | 322 | 322 | 322 | 322 | 321 | 322 | 7728000
| Jamalpur 115 MW PP (United) | [17 empty] | 8 |  | 8 | 8 |  |  |  |  | 0 | 25200
| Anwara 300 MW PP (United) | 304 | 251 | 250 | 106 | 105 | 139 | 139 | 139 | 139 | 281 | 304 | 303 | 303 | 306 | 305 | 231 | 301 | 301 |  | 305 | 304 | 305 | 305 | 304 | 304 | 304 | 6039382
| Juldah unit-2 (Acorn) | [10 empty] | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 100 |  | 80 | 80 | 80 | 80 | 50 | 50 | 0 | 594240
| Anlima Energy Ltd. | [16 empty] | 6 | 21 |  | 52 | 34 | 34 | 34 |  |  | 0 | 176891
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433440
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 6 | 17 | 20 | 31 | 32 | 29 | 24 | 16 | 7 | 1 | [9 empty] | 194133
120 | Eastern Zone Total | 5592 | 5240 | 5138 | 4956 | 4907 | 5005 | 5108 | 5289 | 5411 | 5663 | 5991 | 6387 | 6506 | 6441 | 6518 | 6418 | 6281 | 7488 |  | 7521 | 7349 | 7287 | 7106 | 6662 | 6460 | 6223 | 147834493
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 0 | [10 empty] | 27 | 33 | 35 | 35 | 35 | 92 |  | 105 | 105 | 105 | 105 | 53 | 17 | 0 | 821280
130
131
132 | United Payra Power Ltd. | [17 empty] | 14 | [7 empty] | 0 | 16080
133 | Bhola Nutan Biddut BD LTD (GAS) | 190 | 180 | 155 | 150 | 150 | 149 | 150 | 151 | 150 | 151 | 151 | 220 | 220 | 221 | 220 | 220 | 152 | 220 |  | 221 | 222 | 221 | 223 | 218 | 215 | 222 | 4573450
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 18 | 0 | [15 empty] | 20 |  | 21 | 21 | 20 | 21 | 21 | 21 | 21 | 156006
| Bhola 225 MW CCPP | 65 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 65 | 65 | 30 | 60 | 65 | 65 |  | 67 | 69 | 67 | 69 | 69 | 64 | 68 | 1363000
140 | Bhola 33 MW PP (Venture) | 18 | 19 | 18 | 17 | 17 | 17 | 15 | 14 | 13 | 13 | 14 | 15 | 16 | 16 | 14 | 15 | 16 | 21 |  | 21 | 22 | 23 | 23 | 22 | 22 | 21 | 413700
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [25 empty] | 0 | 6912
146 | Bheramara HVDC | 723 | 723 | 723 | 723 | 723 | 722 | 722 | 719 | 720 | 720 | 720 | 719 | 719 | 719 | 717 | 717 | 717 | 716 |  | 716 | 716 | 717 | 717 | 717 | 716 | 717 | 17371636
147 | Bheramara 410 MW CCPP | 380 | 380 | 320 | 220 | 220 | 220 | 250 | 320 | 300 | 275 | 250 | 225 | 200 | 190 | 150 | 140 | 140 | 135 |  | 125 | 125 | 125 | 125 | 125 | 125 | 135 | 5556960
148 | Payra 1320 MW | 300 | 290 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 260 | 330 | 370 |  | 430 | 440 | 440 | 440 | 440 | 410 | 380 | 8248500
149
150 | Barapukuria TPP Unit-1 | 81 | 81 | 81 | 82 | 82 | 81 | 81 | 80 | 81 | 82 | 80 | 81 | 81 | 83 | 83 | 81 | 81 | 80 |  | 79 | 80 | 83 | 83 | 83 | 83 | 82 | 1947054
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 32460
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 162 | 164 | 165 | 140 | 140 | 140 | 154 | 162 | 169 | 174 | 168 | 153 | 143 | 133 | 127 | 125 | 125 | 124 |  | 123 | 121 | 122 | 135 | 136 | 122 | 0 | 3620755
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 164 | 166 | 140 | 140 | 140 | 158 | 163 | 165 | 174 | 172 | 196 | 170 | 163 | 163 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3940809
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 340 | 372 | 315 | 330 | 302 | 328 | 365 | 356 | 375 | 417 | 406 | 390 | 341 | 347 | 335 | 306 | 291 | 360 |  | 363 | 364 | 363 | 364 | 362 | 360 | 360 | 8575236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 5 | 0 |  |  |  |  | 0 | 5 | 5 | 5 | 5 | 16 | 17 | 17 | 17 | 18 | 18 | 19 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 263760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 0 | 0 | 0 | 5 | 0 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 148266
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 26 | [8 empty] | 15169
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 2 | 8 |  | 25 | 25 | 8 |  |  |  | 0 | 56640
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 49 | [8 empty] | 38136
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [9 empty] | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 95 |  | 70 | 70 | 70 | 70 | 70 | 70 | 0 | 812736
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 50 | 100 |  | 113 | 70 | 70 | 70 | 35 |  | 0 | 453600
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 60 | 106 |  | 113 | 113 | 113 | 70 | 35 |  | 0 | 448310
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 6 | 7 | 7 | 7 | 7 | 5 | 3 | 1 | [9 empty] | 36765
178
178