## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:September 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-09-01 |  | 2021-08-01 |  | 2020-09-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13509 | 2021-09-11 | 13271 | 2021-08-22 | 12892 | 05/09/20 | 13792 | 2021-04-27
|  |  | 20:00 |  | 21:00 |  | 19:30 |  | 20:00
2 | Minimum Generation (MW) | 8491 | 2021-09-17 | 8249 | 2021-08-01 | 7634 | 25/09/20 | - | -
|  |  | 1:00 |  | 22:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13509 | 2021-09-11 | 13271 | 2021-08-22 | 12892 | 05/09/20 | 13792 | 2021-04-27
|  |  | 20:00 |  | 21:00 |  | 19:30 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 11723 | 2021-09-05 | 11410 | 2021-08-31 | 10888 | 05/09/20 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13509 | 2021-09-11 | 13271 | 2021-08-22 | 12892 | 05/09/20 | 14097 | 2021-04-27
|  |  | 20:00 |  | 21:00 |  | 19:30 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 12742.1667 |  | 12483.5806 |  | 11890.0667 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 10804.6667 |  | 10126.9918 |  | 9851.3753 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 907 | 2021-07-01 | 907 | 2021-07-01 | 937 | 23/09/2020 | 956 | 27/3/2019
|  |  | 0:30 |  | 0:30 |  | 1:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 2021-07-10 | 172 | 2021-07-10 | 184 | 07/09/2020 | 194 | 12/06/19
|  |  | 23:00 |  | 23:00 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 0 |  | 0 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1586.2039 |  | 1762.3785 |  | 3387.808 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 134.2992 |  | 118.3845 |  | 137.7396
22 | Net Generation of BPDB (MKWH) | 1451.9047 |  | 1643.994 |  | 3250.0684
23 | Net Generation of IPP (MKWH) | 5324.0599 |  | 5157.2882 |  | 2551.8684
24 | Net Generation of REB (MKWH) | 141.3247 |  | 144.3267 |  | 139.565
24 | Net Generation of Rental Power Plant (MKWH) | 490.1064 |  | 511.1298 |  | 614.8876
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7407.3956 |  | 7456.7388 |  | 6556.3894 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 4494.9287 |  | 4736.6321 |  | 4127.7738 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 614.1861 |  | 442.1105 |  | 388.8315 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1887.4763 |  | 1803.3426 |  | 1679.4648 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 104.8774 |  | 86.881 |  | 42.0017 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 23.2163 |  | 30.5606 |  | 4.8414 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 417.01 |  | 475.5964 |  | 451.2158 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 600.369 |  | 593.113 |  | 764.6635 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 81.01 |  | 82.7278 |  | 80.3555 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:September 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13509 | 2021-09-11 | 20:00
Generation Period
| Dhaka | MW | 4637
| Chattogram | MW | 1273
| Cumilla | MW | 1280
| Mymensingh | MW | 967
| Sylhet | MW | 591
a) | Total supply in East zone | MW | 8748
| Khulna | MW | 1613
| Barisal | MW | 391
| Rajshahi | MW | 1359
| Rangpur | MW | 657
b) | Total supply in West zone | MW | 4020
c) | Total supply in both zone ( a+b) | MW | 12768
Ref: | 27.21.0000.603.16.087.20.447 | Date: 18/10/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 620 | 2021-09-06 | 22:00
| b) Ishurdi end | MW | 272 | 2021-09-14 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 650 | 2021-09-15 | 12:00
| b) Ishurdi end | MW | 240 | 2021-09-03 | 19:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 24.09
| b) Ishurdi end | MKWH | 34.64
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 33.61
| b) Ishurdi end | MKWH | 23.39
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 410 | 2021-09-03 | 21:00
| b)Serajganj end | MW | 250 | 2021-09-14 | 10:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 240 | 2021-09-14 | 10:00
| b)Sirajganj end | MW | 370 | 2021-09-03 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.002 | 2021-09-10
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 3.954 | 2021-09-10
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 60.18
| b)Sirajganj end | MKWH | 20.64
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 20.33
| b)Sirajganj end | MKWH | 60.82
30 | Transmission loss of EWI /NO-2 | % | 0.181
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Uttara | 132/33 kV Transformer T3 | 2021-09-02 09:40 | 2021-09-02 15:20 | 5:40 | E/O | Due to winding temperature high | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer GT2 | 2021-09-03 10:31 | 2021-09-03 11:07 | 0:36 | E/O | Due to high temperature. | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer GT3 | 2021-09-03 19:14 | 2021-09-03 19:24 | 0:10 | T | Tripped showing O/C relay | 120 | 20 | Power interruption
Mymensing | 132/33 kV Transformer T3 | 2021-09-04 11:15 | 2021-09-04 12:14 | 0:59 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-1 | 2021-09-10 19:42 | 2021-09-11 03:03 | 7:21 | T | Tripped due to Y-phase Bus PT got burst | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-2 | 2021-09-10 19:42 | 2021-09-11 01:32 | 5:50 | T | Tripped due to Y-phase Bus PT got burst | 90 | 525 | Power interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-09-10 22:40 | 2021-09-11 01:32 | 2:52 | T | Tripped due to burst of 33 kV LA of auxiliary transformer | 48 | 137.6 | Power interruption
Sherpur | 132/33 kV transformer T-1&T-2 | 2021-09-11 02:59 | 2021-09-11 04:30 | 1:31 | T | Tripped showing O/C relay | 122 | 185.0333 | Power interruption
Ullon | 132/33 kV transformer T-1, T-2 & T-3 | 2021-09-11 04:40 | 2021-09-11 05:30 | 0:50 | T | Tripped showing O/C relay | 53 | 44.1667 | Power interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-09-10 08:34 | 2021-09-10 09:28 | 0:54 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-2 | 2021-09-10 10:45 | 2021-09-10 16:10 | 5:25 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 | 2021-09-11 07:38 | 2021-09-11 07:38 | 0:00 | E/O | Due to CT oil leakage | 0 | 0 | No interruption
Kodda | 33 kV bus-2 | 2021-09-12 13:05 | 2021-09-12 13:55 | 0:50 | E/O | Due to red-hot maint | 60 | 50 | Power interruption
Sherpur | 132/33 kV transformer T-1&T-2 | 2021-09-13 00:07 | 2021-09-13 00:15 | 0:08 | T | Tripped showing O/C relay | 94 | 12.5333 | Power interruption
Kabirpur | 132 kV main bus | 2021-09-14 05:22 | 2021-09-14 07:38 | 2:16 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer T-2 | 2021-09-14 15:34 | 2021-09-14 17:52 | 2:18 | E/O | Due to operating PRD | 25 | 57.5 | Power interruption
Kishoreganj | 132/33 kV transformer T-1&T-2 | 2021-09-16 03:12 | 2021-09-16 03:48 | 0:36 | E/O | Due to fire originated from 33 kV Karimganj | 10 | 6 | Power interruption
Meghnaghat | Meghnaghat 230 kV bus-1 | 2021-09-21 12:55 | 2021-09-21 14:02 | 1:07 | T | Tripped showing TCS & lockout relay | 0 | 0 | No interruption
Mogbazar | 132/33 kV transformer T-2 | 2021-09-25 05:10 | 2021-09-25 05:10 | 0:00 | T | Tripped showing Diff relay | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-1&T-2 | 2021-09-27 12:40 | 2021-09-27 13:40 | 1:00 | T | Tripped showing O/C, E/F relays | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2021-09-28 05:38 | 2021-09-28 05:38 | 0:00 | T | Due to 132 kV mechanical protection. | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-2 | 2021-09-28 20:20 | 2021-09-28 22:53 | 2:33 | E/O | Due to red-hot maint | 25 | 63.75 | Power interruption
Mymensingh | 132/33 kV transformer T-1&T-2 | 2021-09-29 10:30 | 2021-09-29 10:36 | 0:06 | T | Due to Akua feeder fault | 126 | 12.6 | Power interruption
Kodda | 132/33 kV transformer T-2 & T-4 | 2021-09-29 12:01 | 2021-09-29 12:14 | 0:13 | T | Due to feeder fault | 100 | 21.6667 | Power interruption
Sreenagar | 132/33 kV transformer T-1 | 2021-09-30 07:25 | 2021-09-30 09:11 | 1:46 | E/O | Due to red-hot maint | 15 | 26.5 | Power interruption
Manikganj | 132/33 kV transformer T-3 | 2021-09-30 09:25 | 2021-09-30 11:28 | 2:03 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 47:04 |  | Unserved Energy: |  | 1162.35
Dhaka (South) Grid Circle :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baraulia | 132/33 kV transformer T-1 | 2021-09-05 20:37 | 2021-09-05 21:16 | 0:39 | T | Tripped showing no relay | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer T1 | 2021-09-02 07:13 | 2021-09-02 07:13 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T-1&T-2 | 2021-09-07 18:10 | 2021-09-07 18:18 | 0:08 | T | Tripped showing Dir. E/F at 33 kV feeder fault | 96 | 12.8 | Power interruption
Chowmuhoni | 132/33 kV transformer T-1 | 2021-09-12 13:14 | 2021-09-12 15:28 | 2:14 | T | Tripped showing PRD relay | 85 | 189.8333 | Power interruption
Chowmuhoni | 132/33 kV transformer T-3 | 2021-09-19 03:52 | 2021-09-19 04:27 | 0:35 | T | Tripped due to 33 kV Kabirhat feeder flashing | 46 | 26.8333 | Power interruption
Chowmuhoni | 132/33 kV transformer T-3 | 2021-09-22 06:29 | 2021-09-22 06:58 | 0:29 | T | Tripped showing O/C relay | 40 | 19.3333 | Power interruption
Kulshi | 132/33 kV transformer T-1 | 2021-09-22 07:03 | 2021-09-22 07:27 | 0:24 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 4:29 |  | Unserved Energy: |  | 248.8
Cumilla Grid Circle :
Shahjibazar | 132/33 kV transformer T-2 | 2021-09-02 07:36 | 2021-09-02 08:08 | 0:32 | E/O | Due to red-hot maint | 20 | 10.6667 | Power interruption
Ramganj | 132/33 kV transformer T-1&T-2 | 2021-09-03 14:20 | 2021-09-03 14:37 | 0:17 | T | Tripped showing O/C relay | 55 | 15.5833 | Power interruption
Comilla(N) | 230/132 kV transformer T-2 | 2021-09-06 20:25 | 2021-09-06 20:25 | 0:00 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Sylhet | 230/132 kV transformer T-3 | 2021-09-08 16:20 | 2021-09-08 17:33 | 1:13 | T | Tripped showing PRD relay | 50 | 60.8333 | Power interruption
Cumilla(N) | 132/33 kV transformer T-3 | 2021-09-11 07:30 | 2021-09-11 08:15 | 0:45 | E/O | Due to red-hot maint | 50 | 37.5 | Power interruption
Chattak | 132/33 kV transformer T-2 | 2021-09-11 11:35 | 2021-09-12 00:37 | 13:02 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Fenchuganj P/S | 132 kV Bus | 2021-09-14 01:15 | 2021-09-14 02:02 | 0:47 | E/O | Due to P/S problem | 0 | 0 | No interruption
Ashuganj | 132/33 kV transformer T-4 | 2021-09-14 03:21 | 2021-09-14 04:20 | 0:59 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Kochua | 132/33 kV transformer T-1 | 2021-09-21 11:40 | 2021-09-21 12:10 | 0:30 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Comilla(N) | 132/33 kV transformer T-2 | 2021-09-26 09:19 | 2021-09-26 09:19 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T-1&T-2 | 2021-09-28 05:18 | 2021-09-28 05:36 | 0:18 | T | Tripped showing O/C, E/F relays | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-1A & T-1B | 2021-09-29 20:50 | 2021-09-29 21:48 | 0:58 | E/O | Due to red-hot maint | 30 | 29 | Power interruption
|  |  | Total : | 19:21 |  |  |  | 153.5833
Khulna Grid Circle :
Faridpur | 132/33 kV transformer T-1&T-2 | 2021-09-03 22:27 | 2021-09-03 22:35 | 0:08 | T | Tripped showing E/F relay | 140 | 18.6667 | Power interruption
Mongla | 132/33 kV transformer T-2 | 2021-09-04 09:29 | 2021-09-04 12:55 | 3:26 | E/O | Due to red-hot maint | 15 | 51.5 | Power interruption
Noapara | 132/33 kV transformer T-1&T-2 | 2021-09-04 12:16 | 2021-09-04 13:20 | 1:04 | E/O | Due to red-hot maint | 9 | 9.6 | Power interruption
Barisal(N) | 230/132 kV transformer T-2 | 2021-09-04 17:22 | 2021-09-04 18:00 | 0:38 | E/O | Due to oil leakage | 10 | 6.3333 | Power interruption
Satkhira | 132/33 kV transformers T-1 & T2 with 33 kV | 2021-09-06 13:40 | 2021-09-06 13:55 | 0:15 | T | Tripped showing 33 kV feeder CT blast | 50 | 12.5 | Power interruption
Bottail | 132/33 kV transformer T-2 and 33 kV | 2021-09-06 20:10 | 2021-09-06 20:16 | 0:06 | T | Due to 33 kV feeder fault | 56 | 5.6 | Power interruption
Magura | 132/33 kV transformer T-2 | 2021-09-09 03:44 | 2021-09-09 07:32 | 3:48 | T | Tripped showing differential relay | 5 | 19 | Power interruption
Benapole | 132/33 kV transformer T-1&T-2 | 2021-09-10 17:02 | 2021-09-10 17:40 | 0:38 | T | Tripped showing O/C relays | 10 | 6.3333 | Power interruption
Jhenaidah | 132/33 kV transformer T-1&T-2 | 2021-09-10 18:16 | 2021-09-10 18:27 | 0:11 | T | Tripped showing E/F, O/C relays | 75 | 13.75 | Power interruption
Shariatpur | 132/33 kV transformer T-2 | 2021-09-18 12:10 | 2021-09-18 14:05 | 1:55 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Jhenaidah(N) | 230/132 kV transformer T-1 | 2021-09-18 16:05 | 2021-09-18 21:04 | 4:59 | T | Due to operating PRD | 50 | 249.1667 | Power interruption
Jhenaidah | 230/132 kV transformer T-2 | 2021-09-22 13:27 | 2021-09-22 19:33 | 6:06 | T | Tripped showing O/L relay | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-1 | 2021-09-25 06:58 | 2021-09-25 07:07 | 0:09 | T | Tripped showing O/L relay | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-2 | 2021-09-25 06:58 | 2021-09-25 07:10 | 0:12 | T | Tripped showing O/C relay | 10 | 2 | Power interruption
Barishal | 132/33 kV transformer T-4 | 2021-09-25 06:44 | 2021-09-25 06:44 | 0:00 | T | Tripped showing U/F relay | 0 | 0 | No interruption
Barishal | 132/33 kV transformer T-2 | 2021-09-25 11:50 | 2021-09-25 13:20 | 1:30 | E/O | Due to red-hot maint | 20 | 30 | Power interruption
Barishal | 132/33 kV transformer T-1 | 2021-09-25 13:16 | 2021-09-25 13:19 | 0:03 | T | Tripped showing O/C relay | 80 | 4 | Power interruption
Goalpara | 132/33 kV transformer T-5 and T6 | 2021-09-26 10:02 | 2021-09-26 10:15 | 0:13 | T | Tripped showing O/C relay | 20 | 4.3333 | Power interruption
Satkhira | 132/33 kV transformer T-1 and T2 | 2021-09-27 19:25 | 2021-09-27 19:25 | 0:00 | T | Tripped showing O/C, E/F relays | 0 | 0 | No interruption
Norail | 132/33 kV transformer T-2 | 2021-09-28 06:45 | 2021-09-28 08:05 | 1:20 | E/O | Due to red-hot maint | 14 | 18.6667 | Power interruption
Gollamari | 132/33 kV transformer T-1 and T2 | 2021-09-30 12:56 | 2021-09-30 13:22 | 0:26 | T | Tripped showing O/C relays | 48 | 20.8 | Power interruption
|  |  | Total : | 27:07 |  | Unserved Energy: |  | 472.25
HVDC Grid Circle :
HVDC | HVDC Pole-1 | 2021-09-26 05:53 | 2021-09-26 10:57 | 5:04 | T | Tripped showing external protection | 0 | 0 | No interruption
HVDC | HVDC block-1 | 2021-09-09 11:19 | 2021-09-09 14:12 | 2:53 | T | Tripped showing external trip | 0 | 0 | No interruption
|  |  | Total : | 5:04 |  |  |  | 0
Bogura Grid Circle:
Pabna | 132/33 kv transformers T-1 | 2021-09-04 12:51 | 2021-09-04 14:01 | 1:10 | E/O | Due to red-hot maint | 20 | 23.3333 | Power interruption
Naogaon | 132/33 kv transformers T-2 and 33 kV bus-2 | 2021-09-04 14:36 | 2021-09-04 15:31 | 0:55 | E/O | Due to red-hot maint | 21 | 19.25 | Power interruption
Ishwardi | 132/33 kv transformers T-2 | 2021-09-07 10:46 | 2021-09-07 14:02 | 3:16 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Natore | 132/33 kv transformers T-4 | 2021-09-08 11:12 | 2021-09-08 16:51 | 5:39 | E/O | Due to 33 kV DS breaking. | 0 | 0 | No interruption
Polashbari | 132 kV main bus | 2021-09-12 06:55 | 2021-09-12 08:30 | 1:35 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Joypurhat | 132/33 kv transformers T-4 | 2021-09-19 13:12 | 2021-09-19 16:09 | 2:57 | T | Tripped showing OLTC,Bucchlz relay | 0 | 0 | No interruption
Barapukuria | 132/33 kv transformers T-4 | 2021-09-19 15:16 | 2021-09-19 21:42 | 6:26 | T | Due to 33 kV Parbotipur isolator flashing | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 | 2021-09-22 19:40 | 2021-09-22 20:55 | 1:15 | E/O | Due to red-hot maint | 30 | 37.5 | Power interruption
Joypurhat | 132/33 kv transformers T-4 | 2021-09-22 15:55 | 2021-09-24 15:55 | 48:00 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Naogaon | 132/33 kv transformers T-3 | 2021-09-25 23:25 | 2021-09-26 00:25 | 1:00 | E/O | Due to red-hot maint | 40 | 40 | Power interruption
Barapukuria | 132/33 kv transformers T-4 | 2021-09-27 16:36 | 2021-09-27 17:55 | 1:19 | E/O | Due to red-hot maint | 25 | 32.9167 | Power interruption
Naogaon | 132/33 kv transformers T-5 | 2021-09-28 18:55 | 2021-09-28 20:10 | 1:15 | E/O | Due to red-hot maint | 15 | 18.75 | Power interruption
|  |  | Total : | 74:47 |  |  |  | 171.75
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 177:52 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1&2 | 2021-09-01 06:32 | 2021-09-01 06:41 | 0:09 | T | Tripped showing SPS | 0 | 0 | No interruption
Madanganj | Madanganj-Haripur 132 kV Ckt | 2021-09-02 07:56 | 2021-09-02 07:56 | 0:00 | E/O | Due to red hot maint | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2021-09-02 12:26 | 2021-09-02 12:50 | 0:24 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-2 | 2021-09-02 12:30 | 2021-09-02 12:51 | 0:21 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Rampura | Rampura-Aftabnagar-Madartek 132 kV Ckt | 2021-09-04 17:11 | 2021-09-04 17:11 | 0:00 | T | Tripped showing differential O/C,E/F relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2021-09-05 12:34 | 2021-09-05 12:48 | 0:14 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2021-09-05 12:36 | 2021-09-05 12:43 | 0:07 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV Ckt-1 | 2021-09-07 10:14 | 2021-09-07 10:25 | 0:11 | T | Tripped showing Dist. Z1 relay. | 180 | 33 | Power interruption
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV Ckt-2 | 2021-09-07 10:14 | 2021-09-07 10:27 | 0:13 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
ARP P/P | ARP P/P-Shyampur(O) 132 kV Ckt-2 | 2021-09-07 10:14 | 2021-09-07 10:27 | 0:13 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV both Ckts | 2021-09-09 10:15 | 2021-09-09 10:52 | 0:37 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj(S) 230 kV Ckt-1 | 2021-09-09 10:15 | 2021-09-09 10:56 | 0:41 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj(S) 230 kV Ckt-1 | 2021-09-09 11:30 | 2021-09-09 17:05 | 5:35 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Shyampur(old) | Shyampur(old)-Shyampur(new) 132 kV Ckt-1 | 2021-09-09 10:24 | 2021-09-09 11:03 | 0:39 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Shyampur(old) | Shyampur(old)-Shyampur(new) 132 kV Ckt-2 | 2021-09-09 10:24 | 2021-09-09 10:55 | 0:31 | T | Tripped showing Dist. Z1 relay. | 200 | 103.3333 | Power interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-09-11 18:05 | 2021-09-11 18:11 | 0:06 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ashuganj 132 kV Ckt-1 | 2021-09-16 03:21 | 2021-09-16 04:18 | 0:57 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Rampura | Rampura-Aftabnagar-Mothertek 132 kV Ckt-1 | 2021-09-16 14:25 | 2021-09-16 14:51 | 0:26 | T | Tripped showing Dist. Z1 relay. | 15 | 6.5 | Power interruption
Tongi | Tongi-Ghorashal 230 kV Ckt-2 | 2021-09-17 11:40 | 2021-09-17 11:40 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Lalbag | Lalbag-Kalyanpur 132 kV Ckt-2 | 2021-09-19 08:24 | 2021-09-19 15:41 | 7:17 | T | Tripped showing O/C, auto reclose | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-2 | 2021-09-19 16:16 | 2021-09-19 16:48 | 0:32 | T | Tripped showing Dist. Z1,E/F relay | 0 | 0 | No interruption
Tongi | Tongi-Tongi-3(Millgate) 132 kV Ckt | 2021-09-20 00:42 | 2021-09-20 00:42 | 0:00 | T | D/C supply problem at Tongi end. | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-09-22 07:00 | 2021-09-22 07:50 | 0:50 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Shyampur | Shyampur-Fatullah 132 kV Ckt | 2021-09-23 06:27 | 2021-09-23 06:45 | 0:18 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Lalbag | Lalbag-Keraniganj GIS 132 kV Ckt | 2021-09-24 11:50 | 2021-09-25 | 12:10 | T | Tripped showing Dist. Z1 relay | 65 | 790.8333 | Power interruption
Ghorashal | Ghorashal-Ashuganj 132 kV Ckt-2 | 2021-09-25 10:01 | 2021-09-25 10:21 | 0:20 | T | Tripped showing Dist. Z1 relay | 66 | 22 | Power interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2021-09-25 14:17 | 2021-09-25 15:06 | 0:49 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2021-09-25 14:17 | 2021-09-25 15:24 | 1:07 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV Ckt-2 | 2021-09-27 06:55 | 2021-09-27 08:19 | 1:24 | E/O | Due to red hot maint | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-1 | 2021-09-27 16:58 | 2021-09-27 17:56 | 0:58 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2021-09-28 06:09 | 2021-09-28 06:24 | 0:15 | T | Tripped showing Dist. Z1 relay | 82 | 20.5 | Power interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-2 | 2021-09-28 06:09 | 2021-09-28 06:31 | 0:22 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2021-09-28 13:47 | 2021-09-28 14:35 | 0:48 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-1 | 2021-09-30 09:25 | 2021-09-30 11:28 | 2:03 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-09-30 13:55 | 2021-09-30 14:03 | 0:08 | T | Tripped showing Dist. B phase relay | 0 | 0 | No interruption
|  |  | Total : | 39:06 |  | Unserved Energy: |  | 976.1667 |  | 23428:00
Dhaka (South) Grid Circle : | [9 empty] | 0:00
Haripur | Haripur-Fatulla 132 kV Ckt | 2021-09-02 12:15 | 2021-09-02 12:15 | 0:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2021-09-03 09:47 | 2021-09-03 10:12 | 0:25 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2021-09-05 04:48 | 2021-09-05 07:29 | 2:41 | T | Due to high temperature | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-2 | 2021-09-11 01:11 | 2021-09-11 01:22 | 0:11 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2021-09-11 10:49 | 2021-09-11 11:07 | 0:18 | T | Tripped showing Directional E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV Ckt-1 | 2021-09-11 10:49 | 2021-09-12 03:04 | 16:15 | T | Tripped showing Directional E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV Ckt-2 | 2021-09-11 10:49 | 2021-09-12 03:05 | 16:16 | T | Tripped showing Differential E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2021-09-11 12:35 | 2021-09-12 12:50 | 24:15 | T | Tripped showing Differential E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV Ckt | 2021-09-26 09:20 | 2021-09-26 09:30 | 0:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 60:31 |  | Unserved Energy: |  | 0
Chattogram Grid Circle : | [9 empty] | 0:00
AKMS | AKMS-Hathazari 230 kV Ckt | 2021-09-02 13:31 | 2021-09-02 13:47 | 0:16 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Kulshi | Kulshi-Bakulia 132 kV Ckt-1 | 2021-09-04 10:27 | 2021-09-05 16:45 | 30:18 | T | Tripped showing Dist.Z1 relay | 210 | 6363 | Power interruption
Kulshi | Kulshi- Modren Ckt | 2021-09-04 10:27 | 2021-09-04 10:27 | 0:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Kulshi | Kulshi-Hathazari Ckt | 2021-09-04 10:27 | 2021-09-04 10:27 | 0:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Kulshi | Kulshi-Modunaghat Ckt | 2021-09-04 10:27 | 2021-09-04 10:27 | 0:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Hatahazari | Hatahazari-Juldah Ckt | 2021-09-04 10:27 | 2021-09-04 10:27 | 0:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Baroulia | Kulshi-Baroulia Ckt | 2021-09-04 10:27 | 2021-09-04 10:27 | 0:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Hathazari | Hathazari-Sikalbaha 230 kV Ckt-2 | 2021-09-05 12:14 | 2021-09-05 15:35 | 3:21 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
BSRM | BSRM-Cumilla(N) 132 kV Ckt-2 | 2021-09-08 11:06 | 2021-09-08 11:31 | 0:25 | T | Tripped showing Dist.Z2 relay | 0 | 0 | No interruption
BSRM | BSRM-Mirsharai 230 kV Ckt-2 | 2021-09-08 10:50 | 2021-09-08 10:50 | 0:00 | T | Tripped showing Dist.Z2 relay | 0 | 0 | No interruption
BSRM | BSRM-GPH 230 kV Ckt | 2021-09-12 19:39 | 2021-09-12 20:34 | 0:55 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Kaptai | Kaptai-Chuadanga 132 kV Ckt-1 | 2021-09-17 15:01 | 2021-09-17 15:10 | 0:09 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2021-09-19 03:52 | 2021-09-19 04:39 | 0:47 | T | Tripped showing no signal | 0 | 0 | No interruption
Hathazari | Hathazari-GPH 230 kV Ckt | 2021-09-23 11:34 | 2021-09-23 11:42 | 0:08 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
BSRM | BSRM-GPH 230 kV Ckt | 2021-09-22 08:52 | 2021-09-22 09:07 | 0:15 | T | Tripped showing dist Z1,R-phase relay | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2021-09-25 12:17 | 2021-09-25 13:46 | 1:29 | T | Tripped showing dist Z1 relay | 0 | 0 | No interruption
BSRM | BSRM-GPS 230 kV Ckt | 2021-09-26 13:38 | 2021-09-26 13:38 | 0:00 | T | Tripped showing pole discrepancy | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 & 2 | 2021-09-26 16:25 | 2021-09-26 17:16 | 0:51 | T | Tripped showing Dist. Z1 Y-phase relays | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-2 | 2021-09-26 17:45 | 2021-09-26 17:53 | 0:08 | T | Tripped showing Dist. Z1 Y-phase relays | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-1 | 2021-09-28 12:09 | 2021-09-28 12:26 | 0:17 | T | Tripped showing dist.Z1,C-phase relays | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2021-09-29 14:02 | 2021-09-29 14:44 | 0:42 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2021-09-29 14:02 | 2021-09-29 14:46 | 0:44 | T | Tripped showing Dist.Z1, E/F relays | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt | 2021-09-30 09:07 | 2021-09-30 09:32 | 0:25 | T | Tripped showing Dist.Z1, E/F relays | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-2 | 2021-09-30 13:16 | 2021-09-30 14:05 | 0:49 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 41:59 |  | Unserved Energy: |  | 6363 |  | 6363
Cumilla Grid Circle : | [9 empty] | 0:00
Fenchuganj | Fenchuganj-Srimongal 132 kV Ckt-2 | 2021-09-02 10:11 | 2021-09-02 16:27 | 6:16 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-09-02 10:57 | 2021-09-02 11:39 | 0:42 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Cumilla | Cumilla-Surjomoni 132 kV Ckt-2 | 2021-09-03 06:19 | 2021-09-03 07:13 | 0:54 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kochua 132 kV Ckt -2 | 2021-09-05 02:20 | 2021-09-05 06:35 | 4:15 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chaddogram 132 kV Ckt -2 | 2021-09-05 03:35 | 2021-09-05 05:35 | 2:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV Ckt -2 | 2021-09-05 03:31 | 2021-09-05 07:31 | 4:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2021-09-05 12:30 | 2021-09-05 12:45 | 0:15 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV Ckt-2 | 2021-09-05 23:18 | 2021-09-05 23:35 | 0:17 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Tripura 132 kV Ckt-1 | 2021-09-05 23:02 | 2021-09-05 23:38 | 0:36 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-1 | 2021-09-05 22:48 | 2021-09-05 23:29 | 0:41 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV Ckt | 2021-09-10 06:11 | 2021-09-10 08:24 | 2:13 | E/O | Due to red hot maint | 30 | 66.5 | Power interruption
Chatak | Chatak-Sylhet 132 kV Ckt | 2021-09-10 06:11 | 2021-09-10 08:04 | 1:53 | E/O | Due to red hot maint | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-2 | 2021-09-10 12:31 | 2021-09-10 17:18 | 4:47 | E/O | Due to red hot maint | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Megnaghat 230 Ckt-2 | 2021-09-13 12:55 | 2021-09-13 17:20 | 4:25 | E/O | Due to red hot maint | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt | 2021-09-14 15:22 | 2021-09-14 18:05 | 2:43 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-09-16 03:22 | 2021-09-16 04:16 | 0:54 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV Ckt-1 | 2021-09-05 12:30 | 2021-09-05 15:15 | 2:45 | T | Tripped showing no relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-09-05 12:30 | 2021-09-05 12:53 | 0:23 | T | Tripped showing no relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-09-04 14:26 | 2021-09-04 14:37 | 0:11 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Chattak | Chattak-Sunamganj 132 kV Ckt | 2021-09-15 10:54 | 2021-09-15 14:00 | 3:06 | T | Tripped showing Dist. relay | 30 | 93 | Power interruption
B.Baria | B.Baria-Norsingdi 132 kV Ckt-1 | 2021-09-16 00:53 | 2021-09-16 01:47 | 0:54 | T | Tripped showing Dist. relay | 55 | 49.5 | Power interruption
B.Baria | B.Baria-Norsingdi 132 kV Ckt-2 | 2021-09-16 00:53 | 2021-09-16 01:20 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Cumilla (N) | Cumilla (N)-Meghnaghat 230 kV Ckt-2 | 2021-09-12 20:15 | 2021-09-13 00:39 | 4:24 | E/O | Due to red hot maint | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt-3 | 2021-09-16 03:21 | 2021-09-16 04:17 | 0:56 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 Ckt-2 | 2021-09-25 20:48 | 2021-09-25 23:00 | 2:12 | T | Tripped showing Diff. R-phase | 80 | 176 | Power interruption
Comilla(N) | Comilla(N)-Daudkandi 132 kV Ckt-1 | 2021-09-26 18:45 | 2021-09-26 20:03 | 1:18 | T | Tripped showing O/C, Auxiliary transformer fault | 0 | 0 | No interruption
Comilla(N) | Cumilla(N)-Choddagram 132 kV Ckt-1 | 2021-09-28 03:20 | 2021-09-28 03:33 | 0:13 | T | Tripped showing Dist. A-phase relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-09-28 07:01 | 2021-09-28 07:34 | 0:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-09-28 15:00 | 2021-09-28 15:00 | 0:00 | T | Tripped showing no relay | 0 | 0 | No interruption
|  |  | Total : | 54:13 |  | Unserved Energy: |  | 385 |  | 9240:00
Khulna Grid Circle : | [9 empty] | 0:00
Bagerhat | Bagerhat-Mongla 132 kV Ckt-2 | 2021-09-03 13:06 | 2021-09-03 13:52 | 0:46 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Barisal(N) 132 kV Ckt-2 | 2021-09-04 11:09 | 2021-09-04 12:41 | 1:32 | E/O | Due to red hot maint | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 & 2 | 2021-09-08 20:46 | 2021-09-08 21:12 | 0:26 | T | Tripped showing Dist. Z1 relay | 760 | 329.3333 | Power interruption
Madaripur | Madaripur-Gopalganj 132 kV Ckt-1 | 2021-09-10 10:54 | 2021-09-10 15:38 | 4:44 | E/O | Due to red hot maint | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV Ckt | 2021-09-13 10:59 | 2021-09-13 11:21 | 0:22 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV Ckt-1,2 | 2021-09-18 01:28 | 2021-09-18 01:37 | 0:09 | T | Tripped showing Dist. Z2 relay | 125 | 18.75 | Power interruption
Jhenaidah(N) | Jhenaidah(N)-Jashore 132/33 kV Ckt-1 | 2021-09-17 23:01 | 2021-09-18 01:28 | 2:27 | T | Tripped showing Dist. Z2 relay | 0 | 0 | No interruption
Jessore | Jessore-Jhenaidah(N) 132 kV Ckt-1 | 2021-09-22 11:53 | 2021-09-22 12:25 | 0:32 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola P/P 230 kV Ckt-2 | 2021-09-27 12:24 | 2021-09-27 12:54 | 0:30 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 11:28 |  | Unserved Energy: |  | 348.0833 |  | 8354:00
HVDC Grid Circle : | [9 empty] | 0:00
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0 |  | 0:00
Bogura Grid Circle: | [9 empty] | 0:00
Rangpur | Rangpur-Saidpur 132 kV Ckt-2 | 2021-09-02 07:35 | 2021-09-02 08:45 | 1:10 | T | Due to bad weather | 0 | 0 | No interruption
Ishwardi | Ishwardi-Ghorasal 230 kV Ckt-1 | 2021-09-02 10:15 | 2021-09-02 10:44 | 0:29 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Ishwardi | Ishwardi-Ghorasal 230 kV Ckt-1 | 2021-09-02 17:15 | 2021-09-02 17:21 | 0:06 | T | Tripped showing Dist. Z2 relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV Ckt-2 | 2021-09-03 12:53 | 2021-09-03 13:02 | 0:09 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Noagaon | Noagaon-Niamotpur 132 kV Ckt | 2021-09-17 00:05 | 2021-09-17 00:20 | 0:15 | T | Tripped showing Dist. Z1 relay | 67 | 16.75 | Power interruption
Ishurdi | Ishurdi-Ruppur 132 kV Ckt-1 | 2021-09-19 10:25 | 2021-09-19 11:31 | 1:06 | E/O | Due to red hot maint | 0 | 0 | No interruption
Polashbari | Polashbari-Mohasthangarh 132 kV Ckt-1 | 2021-09-24 14:01 | 2021-09-24 14:30 | 0:29 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Polashbari | Polashbari-Mohasthangarh 132 kV Ckt-2 | 2021-09-24 14:06 | 2021-09-24 14:30 | 0:24 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Polashbari | Polashbari-Mohasthangarh 132 kV Ckt-1 | 2021-09-24 18:35 | 2021-09-24 19:03 | 0:28 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Polashbari | Polashbari-Mohasthangarh 132 kV Ckt-2 | 2021-09-24 18:36 | 2021-09-24 18:54 | 0:18 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV Ckt-1 | 2021-09-24 14:07 | 2021-09-24 14:18 | 0:11 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Polashbari | Polashbari-Mithapukur 132 kV Ckt-1 & 2 | 2021-09-24 18:36 | 2021-09-24 18:57 | 0:21 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV Ckt-1 | 2021-09-25 10:11 | 2021-09-25 12:21 | 2:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 7:36 |  | Unserved Energy: |  | 16.75 |  | 402:00
Others :Nil | [9 empty] | 0:00
Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 214:53 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | 132 kV Bus-1 | 2021-09-01 11:25 | 2021-09-01 11:25 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 33 kV extension Bus | 2021-09-02 07:42 | 2021-09-02 08:15 | 0:33 | S/O | Due to C/M work | 40 | 22 | Power interruption
Bhulta | 132/33 kV transformer GT-1 | 2021-09-03 11:20 | 2021-09-03 19:40 | 8:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 33 kV Bus of 132/33 kV T-1 transformer | 2021-09-04 05:50 | 2021-09-04 22:51 | 17:01 | S/O | Due to D/W work | 55 | 935.9167 | Power interruption
Mirpur | 132/33 kV transformer T-1 | 2021-09-04 09:58 | 2021-09-04 15:30 | 5:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2021-09-05 07:16 | 2021-09-05 07:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-01 | 2021-09-05 15:09 | 2021-09-05 16:14 | 1:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer T2 | 2021-09-07 10:38 | 2021-09-07 13:22 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2021-09-07 09:50 | 2021-09-07 18:20 | 8:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T-1 | 2021-09-07 14:16 | 2021-09-07 17:51 | 3:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T2 | 2021-09-08 08:25 | 2021-09-08 17:39 | 9:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2021-09-10 07:04 | 2021-09-10 12:54 | 5:50 | S/O | Due to C/M work | 25 | 145.8333 | Power interruption
Dhamrai | 132/33 kV transformer T-2 | 2021-09-10 07:05 | 2021-09-10 07:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | 132 kV main bus | 2021-09-12 10:43 | 2021-09-12 13:45 | 3:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | 132 kV reserve bus | 2021-09-12 14:18 | 2021-09-12 16:30 | 2:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-1 | 2021-09-13 09:26 | 2021-09-13 11:50 | 2:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-2 | 2021-09-13 11:53 | 2021-09-13 12:30 | 0:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-3 | 2021-09-13 12:28 | 2021-09-13 12:58 | 0:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-3 | 2021-09-14 08:39 | 2021-09-14 21:28 | 12:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer T-2 | 2021-09-16 11:22 | 2021-09-16 12:29 | 1:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T02 |  | 2021-09-16 12:48 |  | S/O | After maintenance | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T02 | 2021-09-17 06:40 | 2021-09-17 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-2 | 2021-09-17 07:16 | 2021-09-17 07:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-3 |  | 2021-09-17 09:12 |  | S/O | After maintenance | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformers T-02 | 2021-09-15 11:42 | 2021-09-15 11:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2021-09-18 09:53 | 2021-09-18 09:53 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132 kV main bus | 2021-09-18 10:50 | 2021-09-18 17:59 | 7:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishorganj | 132/33 kV transformer T-1 | 2021-09-19 08:50 | 2021-09-19 14:34 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132/33 kV transformer T-1 | 2021-09-20 15:49 | 2021-09-20 16:39 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-3 | 2021-09-20 15:49 | 2021-09-20 16:39 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV bus-A | 2021-09-21 08:31 | 2021-09-21 15:31 | 7:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrokona | 132/33 kV transformer T-1 | 2021-09-21 10:50 | 2021-09-21 13:07 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-2 | 2021-09-21 09:30 | 2021-09-21 10:15 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-3 | 2021-09-21 07:47 | 2021-09-21 08:30 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV bus-A | 2021-09-22 07:56 | 2021-09-22 07:56 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-1 | 2021-09-22 09:17 | 2021-09-22 09:45 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-2 | 2021-09-22 08:42 | 2021-09-22 09:12 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur(mymen) | 132/33 kV transformer T-1 | 2021-09-22 11:25 | 2021-09-22 11:51 | 0:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur(mymen) | 132/33 kV transformer T-2 | 2021-09-22 12:14 | 2021-09-22 12:53 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-2 | 2021-09-22 15:32 | 2021-09-22 16:22 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishorganj | 132 kV Bus-A | 2021-09-22 08:28 | 2021-09-22 15:25 | 6:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishorganj | 133 kV Bus-A | 2021-09-23 15:45 | 2021-09-23 16:55 | 1:10 | S/O | Due to replacing Y-phase clamp of T-3. | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-2 | 2021-09-27 11:17 | 2021-09-27 11:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 132/33 kV transformer T-2 | 2021-09-27 11:22 | 2021-09-27 15:30 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2021-09-27 08:20 | 2021-09-27 17:28 | 9:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 | 2021-09-28 07:22 | 2021-09-28 10:20 | 2:58 | S/O | Due to 33 kV Bus maintenance | 80 | 237.3333 | No interruption
Kabirpur | 132/33 kV transformer T-3 | 2021-09-28 07:22 | 2021-09-28 10:46 | 3:24 | S/O | Due to 33 kV Bus maintenance | 0 | 0 | No interruption
Aminbazar | 132/33 kV transformer T-3 | 2021-09-28 08:58 | 2021-09-28 13:59 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2021-09-28 08:48 | 2021-09-28 08:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformers T-02 | 2021-09-29 09:42 | 2021-09-29 12:06 | 2:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 | 2021-09-29 08:39 | 2021-09-29 15:18 | 6:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbachal | 132 kV Bus-1 & 2 |  | 2021-09-29 12:15 |  | S/O | Energized at 1st time | 0 | 0 | No interruption
Purbachal | 132/33 kV transformer T-1 |  | 2021-09-29 13:07 |  | S/O | Energized at 1st time | 0 | 0 | No interruption
Purbachal | 132/33 kV transformer T-2 |  | 2021-09-29 12:28 |  | S/O | Energized at 1st time | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus |  | 2021-09-29 21:11 |  | S/O | After maintenance | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2021-09-30 09:26 | 2021-09-30 14:43 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirsharai EPZ | 230 Bus-2 | 2021-09-30 12:50 | 2021-09-30 12:50 | 0:00 | S/O | Due to SAS work | 0 | 0 | No interruption
|  |  | Total : | 160:22 |  | Unserved Energy: |  | 1341.0833
Dhaka (South) Grid Circle :
Haripur | 230 kV Bus-1 | 2021-09-07 08:33 | 2021-09-07 13:07 | 4:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV transformers T-02 | 2021-09-15 14:28 | 2021-09-15 17:34 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 | 2021-09-20 09:24 | 2021-09-20 13:34 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-2 | 2021-09-20 13:55 | 2021-09-20 16:48 | 2:53 | S/O | Due to Protection Test | 0 | 0 | No interruption
|  |  | Total : | 14:43 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Bhaluka | 132/33 kv transformers T-2 | 2021-09-05 14:39 | 2021-09-05 15:39 | 1:00 | S/O | Due to C/M work | 20 | 20 | Power interruption
Khulshi | 132/33 kV transformer T1 | 2021-09-10 06:07 | 2021-09-10 07:31 | 1:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T1 | 2021-09-12 10:48 | 2021-09-12 11:52 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T2 | 2021-09-12 09:14 | 2021-09-12 10:38 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T2 | 2021-09-12 12:24 | 2021-09-12 13:49 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T1 and T2 | 2021-09-12 17:05 | 2021-09-12 18:55 | 1:50 | S/O | Due to 33 kV PBS work | 90 | 165 | Power interruption
Hathazari | 132/33 kV transformer T1 | 2021-09-13 06:30 | 2021-09-13 08:49 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Khagrachori | 132/33 kV transformer T2 | 2021-09-14 08:04 | 2021-09-14 08:44 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV transformer T4 | 2021-09-21 08:50 | 2021-09-21 12:13 | 3:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T1 | 2021-09-27 09:06 | 2021-09-27 11:36 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T2 | 2021-09-27 12:55 | 2021-09-27 14:56 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T3 | 2021-09-28 09:50 | 2021-09-28 12:28 | 2:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhoni | 132/33 kV transformer T3 | 2021-09-29 11:30 | 2021-09-29 16:37 | 5:07 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 26:45 |  | Unserved Energy : |  | 185
Cumilla Grid Circle :
Shahjibazar | 132/33 kV transformer T-2 | 2021-09-05 15:15 | 2021-09-05 15:47 | 0:32 | S/O | Due to C/M work | 20 | 10.6667 | Power interruption
Daudkandi | 132/33 kV transformer T-2 | 2021-09-10 06:41 | 2021-09-10 10:18 | 3:37 | S/O | Due to D/W work | 75 | 271.25 | Power interruption
Daudkandi | 132/33 kV transformer T-3 | 2021-09-10 06:41 | 2021-09-10 10:17 | 3:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-2 | 2021-09-11 09:06 | 2021-09-11 10:01 | 0:55 | S/O | Due to C/M work | 70 | 64.1667 | Power interruption
Sylhet | 132/33 kV transformer T-3 | 2021-09-11 14:20 | 2021-09-11 15:18 | 0:58 | S/O | Due to C/M work | 70 | 67.6667 | Power interruption
Ramganj | 132/33 kV transformer T-2 | 2021-09-12 18:09 | 2021-09-12 18:20 | 0:11 | S/O | Due to removing bird nest | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer T-4 | 2021-09-13 07:44 | 2021-09-13 10:23 | 2:39 | S/O | Due to bus maintenance | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T1 | 2021-09-18 07:16 | 2021-09-18 09:52 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T-02 | 2021-09-20 09:37 | 2021-09-20 09:37 | 0:00 | S/O | Due to inspection & checking. | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T1 & T2 and 33 kV Bus | 2021-09-26 08:19 | 2021-09-26 14:14 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2021-09-29 09:37 | 2021-09-29 10:42 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T2 | 2021-09-29 10:44 | 2021-09-29 12:02 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-4 |  | 2021-09-30 21:38 |  | S/O | After maintenance | 0 | 0 | No interruption
|  |  | Total : | 23:22 |  | Unserved Energy : |  | 413.75
Khulna Grid Circle :
Barisal(N) | 132/33 kv transformers T-5 |  | 2021-09-04 18:11 |  | S/O | After maintenance | 0 | 0 | No interruption
Barishal | 132/33 kv transformers T-6 | 2021-09-05 10:08 | 2021-09-05 12:15 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kv transformers T-4 |  | 2021-09-10 04:18 |  | S/O | After maintenance | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1and 33 KV Bus section-1 | 2021-09-10 07:15 | 2021-09-10 09:55 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 | 2021-09-10 08:17 | 2021-09-10 11:35 | 3:18 | S/O | Due to CT replacement. | 20 | 66 | Power interruption
Chuadanga | 132 kV main Bus | 2021-09-11 07:05 | 2021-09-11 11:38 | 4:33 | S/O | Due to D/W work | 50 | 227.5 | Power interruption
Faridpur | 132/33 kV transformer T2 | 2021-09-10 10:16 | 2021-09-10 10:57 | 0:41 | S/O | Due to C/M work | 51 | 34.85 | Power interruption
Jhenaidah | 132/33 kV transformer T1 | 2021-09-11 07:17 | 2021-09-11 07:17 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | 132/33 kv transformers T-4 | 2021-09-12 10:12 | 2021-09-12 13:41 | 3:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kv transformers T-3 | 2021-09-13 09:40 | 2021-09-13 13:19 | 3:39 | S/O | Due to oil leakage. | 0 | 0 | No interruption
Barishal | 132/33 kv transformers T-5 | 2021-09-14 08:18 | 2021-09-14 17:24 | 9:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal | 132/33 kv transformers T-4 | 2021-09-15 09:14 | 2021-09-15 18:51 | 9:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kv transformers T-5 | 2021-09-16 07:43 | 2021-09-16 12:05 | 4:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T-5 & T-6 | 2021-09-17 16:03 | 2021-09-17 16:59 | 0:56 | S/O | Due to C/M work | 7 | 6.5333 | Power interruption
Gallamari | 132 kV bay E01 & E02 | 2021-09-21 13:13 | 2021-09-21 13:13 | 0:00 | S/O | Due to project work. | 0 | 0 | No interruption
Gallamari | 132 kV Bus-1 | 2021-09-28 11:52 | 2021-09-28 16:07 | 4:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | 133 kV Bus-2 | 2021-09-28 16:26 | 2021-09-28 19:09 | 2:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 | 2021-09-29 08:10 | 2021-09-29 09:26 | 1:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | 230/132 kV transformer T-02 |  | 2021-09-30 19:46 |  | S/O | After maintenance | 0 | 0 | No interruption
Jhenaidah | 230/132 kV transformer T-03 | 2021-09-30 20:22 | 2021-09-30 20:22 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 52:42 |  | Unserved Energy : |  | 334.8833
HVDC Grid Circle :Nil
HVDC Bheramara | HVDC Bheramara 20DF 22 filter | 2021-08-16 15:34 | 2021-08-16 20:24 | 4:50 | S/O | Due to maintenance work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara Filter 20DF13 at 400 kV | 2021-08-18 11:54 | 2021-08-18 13:11 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC 230 kV 20DF24 shunt reactor | 2021-08-23 09:40 | 2021-08-23 11:01 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 7:28 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Bogura Old | 132/33 kV transformer T1 | 2021-09-01 07:22 | 2021-09-01 08:52 | 1:30 | S/O | Due to C/M work | 50 | 75 | Power interruption
Ishwardi | 132/33 kV transformer T1 | 2021-09-01 09:48 | 2021-09-01 10:48 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 | 2021-09-02 12:10 | 2021-09-02 15:56 | 3:46 | S/O | Due to relay checking. | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T4 | 2021-09-04 16:22 | 2021-09-04 16:52 | 0:30 | S/O | Due to CB maint | 20 | 10 | Power interruption
Rangpur | 132/33 kV transformer T2 | 2021-09-06 09:20 | 2021-09-06 14:50 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV transformer T1 | 2021-09-06 10:38 | 2021-09-06 13:40 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV transformer T2 | 2021-09-07 08:19 | 2021-09-07 09:46 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T2 | 2021-09-07 09:22 | 2021-09-07 16:20 | 6:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T3 | 2021-09-09 08:50 | 2021-09-09 14:18 | 5:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T3 | 2021-09-10 06:02 | 2021-09-10 09:58 | 3:56 | S/O | Due to PBS work | 15 | 59 | Power interruption
Natore | 132 kV main Bus | 2021-09-11 07:18 | 2021-09-11 08:44 | 1:26 | S/O | Due to C/M work | 80 | 114.6667 | Power interruption
Pabna | 132/33 kV transformer T3 | 2021-09-11 10:09 | 2021-09-11 12:32 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV transformer T3 | 2021-09-12 10:52 | 2021-09-12 14:51 | 3:59 | S/O | Due to oil leakage maintenance | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T2 | 2021-09-13 08:30 | 2021-09-13 16:34 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T2 | 2021-09-14 08:27 | 2021-09-14 13:30 | 5:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T3 | 2021-09-16 08:35 | 2021-09-16 16:03 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T4 | 2021-09-16 08:25 | 2021-09-16 11:35 | 3:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T4 | 2021-09-19 07:15 | 2021-09-19 07:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T1 | 2021-09-19 08:30 | 2021-09-19 16:25 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T5 | 2021-09-20 08:27 | 2021-09-20 16:30 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T6 | 2021-09-21 08:26 | 2021-09-21 15:50 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T4 | 2021-09-22 08:55 | 2021-09-22 13:45 | 4:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV transformer T4 | 2021-09-23 09:30 | 2021-09-23 09:30 | 0:00 | S/O | Due to PT replacement work. | 0 | 0 | No interruption
Sirajganj | 33 kV Bus-1 | 2021-09-24 11:24 | 2021-09-24 12:04 | 0:40 | S/O | Due to C/M work | 20 | 13.3333 | Power interruption
Naogaon | 132/33 kV transformer T1 | 2021-09-24 08:46 | 2021-09-24 08:46 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV transformer T1 | 2021-09-28 08:30 | 2021-09-28 15:51 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T4 | 2021-09-28 11:10 | 2021-09-28 11:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 100:53 |  | Unserved Energy : |  | 272
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 386:15 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Tongi New 132 kV Ckt-1 | 2021-09-01 12:14 | 2021-09-01 17:48 | 5:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV Ckt | 2021-09-02 12:14 | 2021-09-02 17:48 | 5:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV Ckt-2 | 2021-09-03 09:59 | 2021-09-03 11:54 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV Ckt | 2021-09-04 08:56 | 2021-09-04 19:50 | 10:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 132 kV Ckt-1 | 2021-09-05 10:08 | 2021-09-05 12:18 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 132 kV Ckt-2 | 2021-09-05 12:21 | 2021-09-05 15:04 | 2:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(Old) | Tongi(Old)-New Tongi 132 kV Ckt-1 | 2021-09-05 11:21 | 2021-09-05 17:24 | 6:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Madartek 132 kV Ckt-1 | 2021-09-05 15:12 | 2021-09-05 21:15 | 6:03 | S/O | Due to C/M work | 40 | 20 | Power interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2021-09-06 10:28 | 2021-09-06 12:12 | 1:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2021-09-06 12:15 | 2021-09-06 13:19 | 1:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 132 kV Ckt-2 |  | 2021-09-06 14:45 |  | S/O | After maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2021-09-07 10:55 | 2021-09-07 12:36 | 1:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2021-09-07 12:39 | 2021-09-07 14:37 | 1:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2021-09-07 09:11 | 2021-09-07 18:25 | 9:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2021-09-07 08:19 | 2021-09-07 13:12 | 4:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Sitalakhya 132 kV Ckt | 2021-09-07 10:53 | 2021-09-07 19:24 | 8:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV Ckt-1 | 2021-09-07 16:16 | 2021-09-07 17:01 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV Ckt-2 | 2021-09-08 06:08 | 2021-09-08 08:01 | 1:53 | S/O | Due to C/M work | 46 | 86.6333 | Power interruption
Aminbazar | Aminbazar-Manikganj P/S132 kV Ckt-2 | 2021-09-08 10:31 | 2021-09-08 15:55 | 5:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-2 | 2021-09-08 10:02 | 2021-09-08 11:44 | 1:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ashuganj 132 kV Ckt-1 | 2021-09-08 11:31 | 2021-09-08 13:09 | 1:38 | S/O | Due to protection test. | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-2 | 2021-09-08 11:50 | 2021-09-08 12:46 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ashuganj 132 kV Ckt-2 | 2021-09-08 13:40 | 2021-09-08 15:22 | 1:42 | S/O | Due to protection test. | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV Ckt | 2021-09-09 08:48 | 2021-09-09 09:39 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2021-09-09 09:47 | 2021-09-09 17:50 | 8:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Aurahati | Aurahati-Hasnabad 132 kV Ckt | 2021-09-09 07:22 | 2021-09-09 09:19 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Aurahati | Aurahati-Keraniganj 132 kV Ckt | 2021-09-09 07:23 | 2021-09-09 09:17 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV Ckt-2 | 2021-09-11 10:14 | 2021-09-11 16:13 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-1 | 2021-09-12 10:25 | 2021-09-12 15:15 | 4:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal- Ashuganj 132 kV Ckt-1 | 2021-09-12 14:18 | 2021-09-12 17:30 | 3:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-2 | 2021-09-12 15:22 | 2021-09-12 17:39 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV Ckt-1 | 2021-09-13 09:59 | 2021-09-13 13:39 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensingh-Jamalpur 132 kV Ckt-2 | 2021-09-14 13:30 | 2021-09-14 15:36 | 2:06 | S/O | Due to relay test | 0 | 0 | No interruption
Jamalpur S/S | Jamalpur S/S-Jamalpur United 132 kV Ckt-2 | 2021-09-14 09:52 | 2021-09-14 10:39 | 0:47 | S/O | Due to relay test | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-09-14 10:43 | 2021-09-14 13:26 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur S/S | Jamalpur S/S-Jamalpur United 132 kV Ckt-1 | 2021-09-14 08:25 | 2021-09-14 09:52 | 1:27 | S/O | Due to relay test | 0 | 0 | No interruption
Ghorasal | Ghorasal-Joydebpur 132 kV Ckt-1 | 2021-09-15 11:50 | 2021-09-15 13:47 | 1:57 | S/O | Due to relay test | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2021-09-15 12:31 | 2021-09-15 13:05 | 0:34 | S/O | Due to tree trimming. | 0 | 0 | No interruption
Ghorasal | Ghorasal-Joydebpur 132 kV Ckt-2 | 2021-09-15 14:28 | 2021-09-15 15:40 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-1 | 2021-09-16 12:03 | 2021-09-16 13:02 | 0:59 | S/O | Due to tree trimming. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kv Ckt-2 |  | 2021-09-17 13:24 |  | S/O | After maintenance | 0 | 0 | No interruption
Shyampur | Shyampur-Hasnabad 230 kV Ckt-1 | 2021-09-17 12:26 | 2021-09-17 12:58 | 0:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-1 | 2021-09-17 08:19 | 2021-09-17 12:28 | 4:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2021-09-19 10:42 | 2021-09-19 15:34 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Metro Rail 132 kV Bay | 2021-09-19 09:58 | 2021-09-19 11:21 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd 132 kV Ckt | 2021-09-19 08:30 | 2021-09-19 09:42 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2021-09-19 10:34 | 2021-09-19 15:11 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-09-20 10:02 | 2021-09-20 11:05 | 1:03 | S/O | Due to Protection Test. | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-2 | 2021-09-20 11:07 | 2021-09-20 12:05 | 0:58 | S/O | Due to Protection Test. | 0 | 0 | No interruption
Tongi | Tongi-Uttara(Old) 132 kV Ckt | 2021-09-20 12:15 | 2021-09-20 12:44 | 0:29 | S/O | Due to Protection Test. | 0 | 0 | No interruption
Tongi | Tongi-Mill Gate 132 kV Ckt-1 |  | 2021-09-20 16:26 |  | S/O | After maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-09-21 07:44 | 2021-09-21 07:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-09-21 07:44 | 2021-09-21 17:56 | 10:12 | S/O | Due to CT replacement | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-09-22 07:00 | 2021-09-22 07:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensing-RPCL 132 kV Ckt-1 | 2021-09-22 07:32 | 2021-09-23 08:12 | 24:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | Mymensing-RPCL 132 kV Ckt-1 | 2021-09-23 07:32 | 2021-09-23 08:12 | 0:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV Ckt-1 | 2021-09-25 09:34 | 2021-09-25 15:46 | 6:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2021-09-27 07:42 | 2021-09-27 07:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV Ckt-1 | 2021-09-28 07:12 | 2021-09-28 07:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | Uttara-Mirpur 132 kV Ckt | 2021-09-29 07:45 | 2021-09-29 07:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-09-30 07:36 | 2021-09-30 07:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-1 | 2021-09-29 12:14 | 2021-09-29 16:16 | 4:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2021-09-30 10:24 | 2021-09-30 13:01 | 2:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV Ckt-2 |  | 2021-09-29 10:07 |  | S/O | After maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-09-30 07:36 | 2021-09-30 07:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-2 | 2021-09-30 13:04 | 2021-09-30 15:30 | 2:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara(3rd phase) 132 kV Ckt | 2021-09-30 08:49 | 2021-09-30 21:03 | 12:14 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 210:47 |  | Unserved Energy: |  | 106.6333
Dhaka (South) Grid Circle :
Haripur | Bhulta-Haripur 132 kV Ckt | 2021-09-03 06:30 | 2021-09-03 06:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Bhulta-Haripur 230 kV CKt-2 and Busbar-1 | 2021-09-09 08:26 | 2021-09-09 17:17 | 8:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-2 | 2021-09-11 15:35 | 2021-09-11 16:02 | 0:27 | S/O | Due to replacement of spring | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur-360 MW P/S 230 kV Ckt-1 | 2021-09-13 08:11 | 2021-09-13 12:15 | 4:04 | S/O | Due to maintenance charge motor. | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2021-09-13 09:15 | 2021-09-13 18:00 | 8:45 | S/O | Due to maintenance work. | 0 | 0 | No interruption
Haripur | Haripur-Siddirganj 230 kV Ckt-1 | 2021-09-13 12:30 | 2021-09-13 19:10 | 6:40 | S/O | Due to maintenance work. | 0 | 0 | No interruption
Haripur | Haripur-Siddirganj 230 kV Ckt-1 |  | 2021-09-14 14:01 |  | S/O | After maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kv Ckt | 2021-09-15 08:38 | 2021-09-15 08:38 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kv Ckt-2 | 2021-09-15 12:25 | 2021-09-15 12:25 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj Peaking 132 kV Ckt | 2021-09-21 10:36 | 2021-09-21 10:36 | 0:00 | S/O | Due to Energy meter work | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV Ckt |  | 2021-09-27 11:07 |  | S/O | After maintenance | 0 | 0 | No interruption
Haripur | Haripur 230 kV S/S-Haripur(HPL) 360 MW P.P. 230 kV Ckt-1 | 2021-09-30 12:03 | 2021-09-30 16:07 | 4:04 | S/O | Due to HT cable maintenance at HPL | 0 | 0 | No interruption
|  |  | Total : | 32:51 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Sikalbaha 230 kV Ckt-1 |  | 2021-09-02 12:25 |  | S/O | After maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV Ckt | 2021-09-04 07:32 | 2021-09-04 07:32 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-2 | 2021-09-05 07:40 | 2021-09-05 07:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 |  | 2021-09-05 16:44 |  | S/O | After maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-2 |  | 2021-09-07 18:09 |  | S/O | After maintenance | 0 | 0 | No interruption
Mirshorai | Mirshorai-Powergen 230 kV Ckt-2 | 2021-09-08 12:50 | 2021-09-08 12:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 | 2021-09-09 06:12 | 2021-09-09 06:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Khulshi 132 kV Ckt | 2021-09-09 07:07 | 2021-09-09 07:07 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-1 | 2021-09-11 06:39 | 2021-09-11 17:21 | 10:42 | S/O | Due to D/W work | 33 | 353.1 | Power interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-09-14 08:20 | 2021-09-14 18:06 | 9:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-3 | 2021-09-15 06:41 | 2021-09-15 06:41 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Anowara 230 kV Ckt-2 | 2021-09-17 07:13 | 2021-09-17 07:13 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-1 | 2021-09-17 06:00 | 2021-09-17 06:00 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-1 | 2021-09-21 08:53 | 2021-09-21 13:46 | 4:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Modunaghat | Modunaghat-Chandrogona 132 kV Ckt-1 & 2 | 2021-09-21 11:40 | 2021-09-21 13:28 | 1:48 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-1 | 2021-09-22 15:58 | 2021-09-22 19:50 | 3:52 | S/O | Due to Matarbari loop connection. | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV Ckt | 2021-09-23 15:57 | 2021-09-23 18:03 | 2:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-09-24 05:58 | 2021-09-24 05:58 | 0:00 | S/O | Due to high temperature maint | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV both Ckts | 2021-09-25 10:56 | 2021-09-25 12:03 | 1:07 | S/O | Due to main power strengthening project | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-1 | 2021-09-26 14:38 | 2021-09-26 15:46 | 1:08 | S/O | Due to meter change | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-2 | 2021-09-26 16:01 | 2021-09-26 16:40 | 0:39 | S/O | Due to meter change | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kulshi 132 kv Ckt-1 | 2021-09-28 10:15 | 2021-09-28 12:00 | 1:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kv Ckt-1 | 2021-09-30 05:43 | 2021-09-30 10:36 | 4:53 | S/O | Due to D/W work | 100 | 488.3333 | Power interruption
Dohazari | Dohazari-Cox'sbazar 132 kv Ckt-2 | 2021-09-30 05:43 | 2021-09-30 11:48 | 6:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kv Ckt-2 | 2021-09-30 10:06 | 2021-09-30 16:01 | 5:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 & Ckt-2 | 2021-09-30 09:43 | 2021-09-30 10:55 | 1:12 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 55:51 |  | Unserved Energy: |  | 841.4333
Cumilla Grid Circle :
Sreemangal | Sreemangal-Fenchuganj 132 kV Ckt-1 | 2021-09-02 06:35 | 2021-09-02 06:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/P 132 kV Ckt-1 | 2021-09-02 15:07 | 2021-09-02 16:43 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/P 132 kV Ckt-2 | 2021-09-02 16:55 | 2021-09-02 17:25 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2021-09-03 10:29 | 2021-09-04 17:52 | 31:23 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2021-09-05 07:41 | 2021-09-05 07:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2021-09-05 16:51 | 2021-09-05 16:51 | 0:00 | S/O | After maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Tripura 132 kV Ckt-1 | 2021-09-08 12:40 | 2021-09-08 19:58 | 7:18 | S/O | Due to maint. work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Barakatullah 132 kV Ckt | 2021-09-14 12:57 | 2021-09-14 12:57 | 0:00 | S/O | Due to CB maintenance | 0 | 0 | No interruption
Sylhet S/S | Sylhet S/S-Fenchuganj P/S 132 kV Ckt | 2021-09-16 08:28 | 2021-09-16 12:08 | 3:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV Ckt | 2021-09-20 06:28 | 2021-09-20 08:59 | 2:31 | S/O | Due to C/M work | 30 | 75.5 | Power interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2021-09-21 06:48 | 2021-09-21 06:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-09-22 11:13 | 2021-09-22 11:33 | 0:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-09-22 11:33 | 2021-09-22 11:56 | 0:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV Ckt-2 | 2021-09-23 11:46 | 2021-09-23 21:30 | 9:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kv Ckt-2 | 2021-09-28 12:42 | 2021-09-28 13:39 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-09-29 09:24 | 2021-09-29 22:20 | 12:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Chauddagram 132 kv Ckt-2 | 2021-09-29 12:25 | 2021-09-29 13:25 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kv Ckt-2 | 2021-09-29 14:57 | 2021-09-29 15:44 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 73:05 |  | Unserved Energy: |  | 75.5
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Mongla 230 kV Ckt-1 | 2021-09-02 11:30 | 2021-09-02 12:27 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV Ckt-2 | 2021-09-04 08:10 | 2021-09-04 10:04 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Mongla 230 kV Ckt-1 & 2 | 2021-09-06 09:54 | 2021-09-06 13:19 | 3:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Mongla(Rampal) 230 kV Both Ckts |  | 2021-09-09 13:02 |  | S/O | After project work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Chuadanga 132 kV Ckt | 2021-09-11 07:05 | 2021-09-11 07:05 | 0:00 | S/O | Due to maint. work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj P/S 132 kV Ckt | 2021-09-13 07:46 | 2021-09-13 07:46 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-Faridpur P/S 132 kV Ckt | 2021-09-15 11:26 | 2021-09-15 13:47 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(old) | Gopalganj(old)- Gallamari 132 kv Ckt-1,2 | 2021-09-15 09:53 | 2021-09-15 17:25 | 7:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Orion Rupsha 132 kV Ckt | 2021-09-17 05:15 | 2021-09-17 05:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj(old) | Gopalganj(old)- Gallamari 132 kv Ckt-1,2 | 2021-09-16 08:04 | 2021-09-16 17:50 | 9:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt 1,2 | 2021-09-17 13:32 | 2021-09-17 14:01 | 0:29 | S/O | Due to D/W work | 490 | 236.8333 | Power interruption
Ishurdi | Ishurdi-Natore 132 kV Ckt-2 | 2021-09-17 08:49 | 2021-09-17 10:41 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-HVDC Bheramara 230 kV Ckt 1 | 2021-09-17 08:40 | 2021-09-17 14:58 | 6:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-HVDC Bheramara 230 kV Ckt 2 | 2021-09-17 08:40 | 2021-09-17 15:30 | 6:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-HVDC Khulna(S) 230 kV Ckt 1 | 2021-09-17 08:27 | 2021-09-17 14:55 | 6:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-HVDC Khulna(S) 230 kV Ckt 2 | 2021-09-17 08:27 | 2021-09-17 15:29 | 7:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt 1 | 2021-09-17 16:17 | 2021-09-17 23:01 | 6:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt 2 | 2021-09-18 16:18 | 2021-09-18 16:18 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV express Ckt | 2021-09-18 08:01 | 2021-09-18 08:01 | 0:00 | S/O | Due to project work. | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalganj 132 kV Ckt-1 and 2 | 2021-09-18 07:33 | 2021-09-18 07:33 | 0:00 | S/O | Due to project work. | 0 | 0 | No interruption
Jhenaidah(old) | Jhenaidah(old)-Jhenaidah(new) 132 kV Ckt-1 |  | 2021-09-18 22:55 |  | S/O | After project work | 0 | 0 | No interruption
Jhenaidah(old) | Jhenaidah(old)-Jhenaidah(new) 132 kV Ckt-2 |  | 2021-09-18 22:58 |  | S/O | After project work | 0 | 0 | No interruption
Gallamari | Gallamari-Gopalganj 132 kV Ckt-1 & 2 | 2021-09-20 08:05 | 2021-09-20 17:15 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | Gallamari-Gopalganj 132 kV Ckt-1 & 2 | 2021-09-21 08:11 | 2021-09-21 17:30 | 9:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV Ckt-1 | 2021-09-25 15:31 | 2021-09-25 16:28 | 0:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV Ckt-2 | 2021-09-25 16:38 | 2021-09-25 17:00 | 0:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Rajbari 132 kV Ckt-1 & 2 | 2021-09-24 06:56 | 2021-09-24 07:15 | 0:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 & 2 | 2021-09-24 06:38 | 2021-09-24 07:12 | 0:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | Gallamari-Gopalganj 132 kV Ckt-1 | 2021-09-28 08:53 | 2021-09-28 08:53 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 81:22 |  | Unserved Energy: |  | 236.8333
HVDC Grid Circle :
Bheramara | Bheramara-Bahrampur 400 kV Ckt-3 | 2021-09-05 11:17 | 2021-09-05 17:03 | 5:46 | S/O | Due to Bay maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV Ckt-4 |  | 2021-09-19 16:04 |  | S/O | After maintenance | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 473.6667
Bogura Grid Circle :
Rangpur Confi. | Rangpur Confi. P.P.-Mithapukur 132 kV Ckt-2 | 2021-09-04 07:02 | 2021-09-04 07:38 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-1 | 2021-09-07 10:25 | 2021-09-07 11:33 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Natore 132 kV Ckt-2 | 2021-09-08 11:35 | 2021-09-08 12:52 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-NPSL 132 kV Ckt | 2021-09-08 09:28 | 2021-09-08 11:27 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur confi. | Rangpur confi.-mithapukur 132 kV Ckt-2 | 2021-09-09 07:28 | 2021-09-09 07:28 | 0:00 | S/O | Due to SF6 gas filling. | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV Ckt-1 | 2021-09-11 10:11 | 2021-09-11 18:11 | 8:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur Confidence | Rangpur Confidence-Mithapukur 132 kV Ckt-2 | 2021-09-14 07:58 | 2021-09-14 08:29 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Polashbari | Polashbari-Mohastangor 132 kV Ckt-1 | 2021-09-17 07:43 | 2021-09-17 07:43 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Polashbari | Polashbari-Mohasthangarh 132 kV Ckt-2 | 2021-09-18 08:02 | 2021-09-18 08:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohasthangarh | Mohasthangarh-Palashbari 132 kV Ckt-2 | 2021-09-18 08:02 | 2021-09-18 15:16 | 7:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura Conf. | Bogura Confidence-Mithapukur 132 kV Ckt-2 | 2021-09-19 06:52 | 2021-09-19 06:52 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rangpur Confi.-Mithapukur 132 kV Ckt-2 | Rangpur Confi.-Mithapukur 132 kV Ckt-2 |  | 2021-09-20 14:08 |  | S/O | After maintenance | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2021-09-21 07:18 | 2021-09-21 09:15 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Polashbari | Polashbari-Mahasthangar 132 kV Ckt-1 | 2021-09-25 08:26 | 2021-09-25 13:00 | 4:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Polashbari | Polashbari-Mahasthangar 132 kV Ckt-2 | 2021-09-25 13:20 | 2021-09-25 14:54 | 1:34 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 28:50 |  | Unserved Energy: |  | 0
Others :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 482:46 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September 2021
| Area | Previous Month (August' 2021) |  |  |  | Current Month (September '2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 34 | 25 | 95 | 154 | 30 | 15 | 124 | 169
2 | Dhaka (South) Grid Circle. | 2 | 2 | 3 | 7 | 9 | 0 | 16 | 25
3 | Chattogram Grid Circle. | 15 | 7 | 24 | 46 | 29 | 2 | 39 | 70
4 | Cumilla Grid Circle. | 16 | 4 | 19 | 39 | 30 | 11 | 31 | 72
5 | Khulna Grid Circle. | 15 | 10 | 36 | 61 | 22 | 8 | 49 | 79
6 | HVDC Grid Circle | 0 | 0 | 1 | 1 | 2 | 0 | 5 | 7
7 | Bogura Grid Circle. | 16 | 6 | 22 | 44 | 16 | 9 | 42 | 67
8 | Others |  |  |  | 0 | 0 | 0 | 0 | 0
9 | Total | 98 | 54 | 200 | 352 | 138 | 45 | 306 | 489
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September 2021
| Area | Previous Month (August' 2021) |  |  |  | Current Month (September '2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 785.56 | 468.2 | 289.17 | 1542.93 | 1934.77 | 203.75 | 1230.39 | 3368.91
2 | Dhaka (South) Grid Circle. | 360.1 | 0 | 58 | 418.1 | 0 | 0 | 0 | 0
3 | Chattogram Grid Circle. | 96.97 | 139.43 | 2387.45 | 2623.85 | 6611.8 | 0 | 1006.43 | 7618.23
4 | Cumilla Grid Circle. | 127.18 | 79 | 350.8 | 556.98 | 218.92 | 143.67 | 489.25 | 851.84
5 | Khulna Grid Circle. | 416.94 | 122.67 | 107.98 | 647.59 | 880.23 | 116.1 | 571.71 | 1568.04
6 | HVDC Grid Circle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Bogura Grid Circle. | 84.67 | 733.97 | 1042.58 | 1861.22 | 16.75 | 171.75 | 272 | 460.5
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 1871.42 | 1543.27 | 4235.98 | 7650.67 | 9662.47 | 635.27 | 3569.78 | 13867.52
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September 2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 13 | 4 | 17 | 4 | 5 | 8 | 2286.1
2 | Dhaka (South) | 5031.6 | - | - | - | - | - | - | 0
3 | Chattogram | 2042 | 4 | 1 | 5 | 2 | 1 | 2 | 413.8
4 | Khulna | 2434 | 16 | 4 | 20 | 8 | 4 | 8 | 807.13
5 | HVDC | 5954.3 | - | - | - | - | - | - | 0
6 | Bogura | 3145.6 | 6 | 5 | 11 | 1 | 3 | 7 | 443.75
7 | Cumilla | 2981 | 5 | 4 | 9 | 1 | 6 | 2 | 567.33
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 4518.11
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.93%
2 | Dhaka (South) | 100%
3 | Chattogram | 99.97%
4 | Khulna | 99.86%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.87% | [6 empty] | Information Management Division
7 | Cumilla | 99.97% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 6 | 2 | 8 | 4 | 1 | 3 | 1082.8
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | 1 | 2 | 3 | - | - | 3 | 7204.43
4 | Khulna | 1238.4 | - | 2 | 1 | 3 | 3 | - | - | 584.91 | -
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 | - | - | 1 | - | - | 16.75
7 | Cumilla | 1648.16 | - | 4 | 1 | 5 | - | 1 | 4 | 460.5
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 9349.39
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.94%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.88%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.99% | [7 empty] | Information Management Division
7 | Cumilla | 99.92% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-09-18 | 8 | - | 19 | 25hr 10 min | 1 | 2hr13 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:September 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishoreganj | 3 | 5:50 | 90 | 525 | Due to Tripping of 132/33 kV transformer T-2
|  | 2:52 | 48 | 137.6 | Due to Tripping of 132/33 kV transformer T-3
|  | 0:36 | 10 | 6 | Due to fire originated from 33 kV Karimganj
Sherpur | 2 | 1:31 | 122 | 185.0333 | Due to Tripping of 132/33 kV transformer T-1&T-2
|  | 0:08 | 94 | 12.5333 | Due to Tripping of 132/33 kV transformer T-1&T-2
Ullon | 1 | 0:50 | 53 | 44.1667 | Due to Tripping of 132/33 kV transformer T-1, T-2 & T-3
Madanganj | 1 | 2:18 | 25 | 57.5 | Due to operating PRD
Bhulta | 3 | 0:10 | 120 | 20 | Due to Tripping of 132/33 kV Transformer GT3
|  | 2:33 | 25 | 63.75 | Due to red-hot maint
|  | 17:01 | 55 | 935.9167 | 33 kV Bus of 132/33 kV T-1 transformer
Mymensingh | 1 | 0:06 | 126 | 12.6 | Due to Akua feeder fault
Kodda | 3 | 0:13 | 100 | 21.6667 | Due to feeder fault
|  | 0:15 | 82 | 20.5 | Due to Tripping of Kodda-Rajendrapur 132 kV Ckt-1
|  | 0:50 | 60 | 50 | Due to red-hot maint
Sreenagar | 1 | 1:46 | 15 | 26.5 | Due to red-hot maint
Shyampur(N) | 2 | 0:11 | 180 | 33 | Due to Tripping of Shyampur(N)-Shyampur(O) 132 kV Ckt-1
|  | 1:53 | 46 | 86.6333 | Due to S/D of Shyampur(N)-Shyampur(O) 132 kV Ckt-2
Shyampur(old) | 1 | 0:31 | 200 | 103.3333 | Due to Tripping of Shyampur(old)-Shyampur(new) 132 kV Ckt-2
Rampura | 2 | 0:26 | 15 | 6.5 | Due to Tripping of Rampura-Aftabnagar-Mothertek 132 kV Ckt-1
|  | 6:03 | 40 | 20 | Due to S/D of Rampura-Madartek 132 kV Ckt-1
Lalbag | 1 | 12:10 | 65 | 790.8333 | Due to Tripping of Lalbag-Keraniganj GIS 132 kV Ckt
Ghorashal | 1 | 0:20 | 66 | 22 | Due to Tripping of Ghorashal-Ashuganj 132 kV Ckt-2
Jamalpur | 1 | 0:33 | 40 | 22 | 33 kV extension Bus
Dhamrai | 1 | 0:00 | 25 | 145.8333 | 132/33 kV transformer T-1
Bhaluka | 1 | 1:00 | 20 | 20 | 132/33 kv transformers T-2
Kulshi | 1 | 30:18 | 210 | 6363 | Due to Tripping of Kulshi-Bakulia 132 kV Ckt-1
Dohazari | 2 | 10:42 | 33 | 353.1 | Due to S/D of Dohazari-Cox's Bazar 132 kV Ckt-1
Dohazari |  | 4:53 | 100 | 488.3333 | Due to S/D of Dohazari-Cox'sbazar 132 kv Ckt-1
Chowmuhoni | 5 | 1:50 | 90 | 165 | Due to S/D of 132/33 kV transformer T1 and T2
|  | 0:08 | 96 | 12.8 | Due to Tripping of 132/33 kV transformer T-1&T-2
|  | 2:14 | 85 | 189.8333 | Due to Tripping of 132/33 kV transformer T-1
|  | 0:35 | 46 | 26.8333 | Due to Tripping of 132/33 kV transformer T-3
|  | 0:29 | 40 | 19.3333 | Due to Tripping of 132/33 kV transformer T-3
Shahjibazar | 4 | 0:32 | 20 | 10.6667 | Due to red-hot maint
|  | 0:32 | 20 | 10.6667 | Due to S/D of 132/33 kV transformer T-2
Ramganj | 1 | 0:17 | 55 | 15.5833 | Due to Tripping of 132/33 kV transformer T-1&T-2
Cumilla(N) | 1 | 0:45 | 50 | 37.5 | Due to red-hot maint
Sylhet | 4 | 1:13 | 50 | 60.8333 | Due to Tripping of 230/132 kV transformer T-3
|  | 0:58 | 30 | 29 | Due to red-hot maint
|  | 0:55 | 70 | 64.1667 | Due to S/D of 132/33 kV transformer T-2
|  | 0:58 | 70 | 67.6667 | Due to S/D of 132/33 kV transformer T-3
Chatak | 3 | 2:13 | 30 | 66.5 | Due to red hot maint
|  | 3:06 | 30 | 93 | Due to Tripping of Chattak-Sunamganj 132 kV Ckt
|  | 2:31 | 30 | 75.5 | Due to S/D of Chatak-Sunamganj 132 kV Ckt
B.Baria | 1 | 0:54 | 55 | 49.5 | Due to Tripping of B.Baria-Norsingdi 132 kV Ckt-1
Rampur | 1 | 2:12 | 80 | 176 | Due to Tripping of Rampur-Agrabad 132 Ckt-2
Daudkandi | 1 | 3:37 | 75 | 271.25 | Due to S/D of 132/33 kV transformer T-2
Faridpur | 3 | 0:41 | 51 | 34.85 | Due to S/D of 132/33 kV transformer T2
|  | 0:08 | 140 | 18.6667 | Due to Tripping of 132/33 kV transformer T-1&T-2
|  | 0:26 | 760 | 329.3333 | Due to Tripping of Faridpur-Rajbari 132 kV Ckt-1 & 2
Noapara | 2 | 0:09 | 125 | 18.75 | Due to Tripping of Noapara-Jashore 132 kV Ckt-1,2
|  | 1:04 | 9 | 9.6 | Due to red-hot maint
Mongla | 1 | 3:26 | 15 | 51.5 | Due to red-hot maint
Jhenaidah | 1 | 0:11 | 75 | 13.75 | Due to Tripping of 132/33 kV transformer T-1&T-2
Jhenaidah(N) | 1 | 4:59 | 50 | 249.1667 | Due to Tripping of 230/132 kV transformer T-1
Barisal(N) | 1 | 0:38 | 10 | 6.3333 | Due to oil leakage
Satkhira | 2 | 0:15 | 50 | 12.5 | Due to Tripping of 132/33 kV transformers T-1 & T2 with 33 kV
|  | 3:18 | 20 | 66 | Due to CT replacement.
Bottail | 1 | 0:06 | 56 | 5.6 | Due to Tripping of 132/33 kV transformer T-2 and 33 kV
Magura | 1 | 3:48 | 5 | 19 | Due to Tripping of 132/33 kV transformer T-2
Benapole | 1 | 0:38 | 10 | 6.3333 | Due to Tripping of 132/33 kV transformer T-1&T-2
Bagerhat | 1 | 0:12 | 10 | 2 | Due to Tripping of 132/33 kV transformer T-2
Barishal | 2 | 1:30 | 20 | 30 | Due to red-hot maint
|  | 0:03 | 80 | 4 | Due to Tripping of 132/33 kV transformer T-1
Goalpara | 2 | 0:13 | 20 | 4.3333 | Due to Tripping of 132/33 kV transformer T-5 and T6
|  | 0:56 | 7 | 6.5333 | Due to S/D of 132/33 kV transformer T-5 & T-6
Norail | 1 | 1:20 | 14 | 18.6667 | Due to red-hot maint
Gollamari | 1 | 0:26 | 48 | 20.8 | Due to Tripping of 132/33 kV transformer T-1 and T2
Chuadanga | 1 | 4:33 | 50 | 227.5 | Due to S/D of 132 kV main Bus
Jashore | 1 | 0:29 | 490 | 236.8333 | Due to S/D of Jashore-Jhenaidah 132 kV Ckt 1,2
Pabna | 1 | 1:10 | 20 | 23.3333 | Due to red-hot maint
|  | 0:55 | 21 | 19.25 | Due to red-hot maint
|  | 1:15 | 30 | 37.5 | Due to red-hot maint
Naogaon | 5 | 1:00 | 40 | 40 | Due to red-hot maint
|  | 1:15 | 15 | 18.75 | Due to red-hot maint
|  | 0:15 | 67 | 16.75 | Due to Tripping of Noagaon-Niamotpur 132 kV Ckt
| 2 | 1:19 | 25 | 32.9167 | Due to red-hot maint
Barapukuria |  | 0:30 | 20 | 10 | Due to S/D of 132/33 kV transformer T4
Bogura Old | 1 | 1:30 | 50 | 75 | Due to S/D of 132/33 kV transformer T1
Rajshahi | 1 | 3:56 | 15 | 59 | Due to S/D of 132/33 kV transformer T3
Natore | 1 | 1:26 | 80 | 114.6667 | Due to S/D of 132 kV main Bus
Sirajganj | 1 | 0:40 | 20 | 13.3333 | Due to S/D of 33 kV Bus-1
| Total Unserved energy : |  |  | 13867.5167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: September '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 134 | 25 | 2021-09-01 | 12:00
2 | Munsiganj | 110 | 10 | 2021-09-01 | 22:00
3 | Sonargaon | 90 | 16 | 2021-09-01 | 12:00
4 | Shyampur | 208 | 1 | 2021-09-01 | 12:00
5 | Bhulta | 237 | 5 | 2021-09-01 | 17:00
6 | Madanganj | 59 | 27 | 2021-09-01 | 18:00
7 | Shitalakhya | 126 | 9 | 2021-09-01 | 12:00
8 | Rahim steel | 31 | 5 | 2021-09-01 | 14:00
9 | Matuail | 69 | 6 | 2021-09-01 | 10:00
10 | Ghorasal | 86 | 15 | 2021-09-01 | 21:00
11 | Narsingdi | 192 | 5 | 2021-09-01 | 22:00
12 | Haripur (SBU) | 135 | 5 | 2021-09-01 | 10:00
13 | Sreenagar | 46 | 11 | 2021-09-01 | 21:00
14 | Ullon | 77 | 25 | 2021-09-01 | 12:00
15 | Hasnabad | 96 | 13 | 2021-09-01 | 18:00
16 | Magbazar | 130 | 12 | 2021-09-01 | 13:00
17 | Maniknagar | 82 | 5 | 2021-09-01 | 13:00
18 | Bangabhaban | 14 | 12 | 2021-09-01 | 11:00
19 | Motijheel | 33 | 12 | 2021-09-01 | 11:00
20 | Narinda | 76 | 8 | 2021-09-01 | 13:00
21 | Kazla | 88 | 5 | 2021-09-01 | 19:00
22 | Dhanmondi | 224 | 27 | 2021-09-01 | 13:00
23 | Lalbag | 98 | 2 | 2021-09-01 | 13:00
24 | Madartek | 81 | 24 | 2021-09-01 | 23:00
25 | Dhaka University | 43 | 12 | 2021-09-01 | 12:00
26 | Aftabnagar | 27 | 2 | 2021-09-01 | 12:00
27 | Fatullah | 68 | 21 | 2021-09-01 | 11:00
28 | Nawabganj | 55 | 5 | 2021-09-01 | 21:00
29 | Keraniganj | 80 | 16 | 2021-09-01 | 19:30
30 | Mirpur | 139 | 26 | 2021-09-01 | 18:00
31 | Kalyanpur | 120 | 3 | 2021-09-01 | 19:00
32 | Gulshan | 140 | 5 | 2021-09-01 | 15:00
33 | Uttara | 93 | 5 | 2021-09-01 | 18:30
34 | Uttara(new) | 38 | 4 | 2021-09-01 | 15:00
35 | Kamrangirchar | 103 | 5 | 2021-09-01 | 13:00
36 | Savar | 178 | 16 | 2021-09-01 | 18:30
37 | Bhasantec | 144 | 2 | 2021-09-01 | 13:00
38 | Agargaon | 96 | 26 | 2021-09-01 | 13:00
39 | Satmosjid | 114 | 26 | 2021-09-01 | 18:30
40 | Tongi | 141 | 18 | 2021-09-01 | 18:00
41 | Kabirpur | 275 | 13 | 2021-09-01 | 12:00
42 | Basundhara | 246 | 6 | 2021-09-01 | 14:00
43 | Manikganj | 82 | 3 | 2021-09-01 | 22:00
44 | Joydevpur | 194 | 8 | 2021-09-01 | 19:00
45 | New Tongi | 110 | 20 | 2021-09-01 | 12:00
46 | Kodda | 310 | 26 | 2021-09-01 | 18:30
47 | Dhamrai | 134 | 21 | 2021-09-01 | 14:00
48 | Rajendrapur | 116 | 26 | 2021-09-01 | 18:30
49 | Valuka | 156 | 18 | 2021-09-01 | 16:00
50 | Tangail | 221 | 24 | 2021-09-01 | 20:00
51 | Mymensing | 236 | 13 | 2021-09-01 | 19:30
52 | Kishorganj | 156 | 15 | 2021-09-01 | 19:30
53 | Netrokona | 127 | 8 | 2021-09-01 | 21:00
54 | Jamalpur | 153 | 18 | 2021-09-01 | 23:00
55 | Sherpur | 146 | 10 | 2021-09-01 | 19:00
56 | Srimongal | 69 | 15 | 2021-09-01 | 18:30
57 | Shahjibazar | 129 | 1 | 2021-09-01 | 1:00
58 | Fenchuganj | 55 | 26 | 2021-09-01 | 18:00
59 | Kulawara | 54 | 4 | 2021-09-01 | 20:00
60 | Sylhet | 164 | 26 | 2021-09-01 | 18:00
61 | Chatak | 52 | 19 | 2021-09-01 | 22:00
62 | Sunamganj | 59 | 12 | 2021-09-01 | 21:00
63 | Bianibazar | 80 | 12 | 2021-09-01 | 20:00
64 | Cumilla (S) | 180 | 5 | 2021-09-01 | 18:30
65 | Cumilla(N) | 155 | 29 | 2021-09-01 | 13:00
66 | Chandpur | 84 | 24 | 2021-09-01 | 23:00
67 | Feni | 135 | 11 | 2021-09-01 | 19:00
68 | Chowmuhani | 226 | 4 | 2021-09-01 | 0:00
69 | Ashuganj | 52 | 4 | 2021-09-01 | 23:00
70 | Daudkandi | 160 | 9 | 2021-09-01 | 21:00
71 | B.Baria | 179 | 11 | 2021-09-01 | 20:00
72 | Ramganj | 98 | 6 | 2021-09-01 | 22:00
73 | Chaddagram | 54 | 11 | 2021-09-01 | 3:00
74 | PHP | 12 | 17 | 2021-09-01 | 19:00
75 | Kochua | 78 | 4 | 2021-09-01 | 20:00
76 | Madanhat | 73 | 5 | 2021-09-01 | 18:30
77 | Hathazari | 105 | 15 | 2021-09-01 | 18:30
78 | Khulshi | 232 | 30 | 2021-09-01 | 15:00
79 | Halishahar | 145 | 27 | 2021-09-01 | 18:30
80 | Baraulia | 167 | 23 | 2021-09-01 | 16:00
81 | Sikalbaha | 48 | 23 | 2021-09-01 | 11:00
82 | Dohazari | 112 | 7 | 2021-09-01 | 18:30
83 | Cox'sbazar | 111 | 9 | 2021-09-01 | 18:30
84 | Chandraghona | 30 | 2 | 2021-09-01 | 20:00
85 | Kaptai | 5.5 | 14 | 2021-09-01 | 20:00
86 | A. Khaer Stl. | 7 | 1 | 2021-09-01 | 5:00
87 | Bakulia | 126 | 4 | 2021-09-01 | 12:00
88 | Julda | 26 | 2 | 2021-09-01 | 1:00
89 | TK chemical | 33 | 5 | 2021-09-01 | 16:00
90 | Modern Steel | 5 | 29 | 2021-09-01 | 16:00
91 | Shahmirpur | 33 | 5 | 2021-09-01 | 18:30
92 | Khagrachhari | 32 | 10 | 2021-09-01 | 21:00
93 | Matarbari | 43 | 24 | 2021-09-01 | 20:00
94 | Baroiar Hat | 64 | 25 | 2021-09-01 | 18:00
95 | Rangamati | 14.5 | 5 | 2021-09-01 | 18:30
96 | Abul Khair 230 | 179 | 29 | 2021-09-01 | 16:00
97 | BSRM | 160 | 8 | 2021-09-01 | 12:00
98 | GPH Ispat | 99 | 4 | 2021-09-01 | 3:00
99 | Agrabad | 90 | 5 | 2021-09-01 | 16:00
100 | Goalpara | 30 | 3 | 2021-09-01 | 5:00
101 | Central s/s | 114 | 1 | 2021-09-01 | 20:00
102 | Noapara | 56 | 18 | 2021-09-01 | 20:00
103 | Jashore | 125 | 5 | 2021-09-01 | 19:30
104 | Benapol | 68 | 24 | 2021-09-01 | 22:00
105 | Jhenidah | 122 | 4 | 2021-09-01 | 21:00
106 | Bottail | 144 | 4 | 2021-09-01 | 19:30
107 | G.K Project | 62 | 4 | 2021-09-01 | 21:00
108 | Faridpur | 159 | 4 | 2021-09-01 | 22:00
109 | Rajbari | 66 | 4 | 2021-09-01 | 19:00
110 | Madaripur | 113 | 4 | 2021-09-01 | 22:00
111 | Sariatpur | 76 | 5 | 2021-09-01 | 21:00
112 | Gopalganj | 102 | 5 | 2021-09-01 | 21:00
113 | Bagerhat | 109 | 9 | 2021-09-01 | 20:00
114 | Mongla | 52 | 8 | 2021-09-01 | 10:00
115 | Satkhira | 120 | 2 | 2021-09-01 | 21:00
116 | Gallamari | 50 | 18 | 2021-09-01 | 13:00
117 | Magura | 60 | 3 | 2021-09-01 | 21:00
118 | Norail | 55 | 26 | 2021-09-01 | 19:30
119 | Chuadanga | 106 | 4 | 2021-09-01 | 21:00
120 | Borguna | 20 | 5 | 2021-09-01 | 22:00
121 | Barsal(N) | 50 | 4 | 2021-09-01 | 21:00
122 | Barsal(S) | 118 | 9 | 2021-09-01 | 23:00
123 | Patuakhali | 131 | 9 | 2021-09-01 | 23:00
124 | Bhandaria | 58 | 5 | 2021-09-01 | 21:00
125 | Borhan Uddin | 48 | 15 | 2021-09-01 | 21:00
126 | Ishurdi | 73 | 4 | 2021-09-01 | 19:00
127 | Ruppur Paromanobik | 4 | 1 | 2021-09-01 | 9:00
128 | Natore | 141 | 5 | 2021-09-01 | 21:00
129 | Bogura | 171 | 15 | 2021-09-01 | 20:00
130 | Naogaon | 119 | 5 | 2021-09-01 | 20:00
131 | Rajshahi | 166 | 5 | 2021-09-01 | 21:00
132 | Rajshahi New | 26 | 4 | 2021-09-01 | 15:00
133 | C.Nawabganj | 65 | 25 | 2021-09-01 | 19:30
134 | Amnura | 55 | 12 | 2021-09-01 | 21:00
135 | Pabna | 121 | 25 | 2021-09-01 | 19:30
136 | Shahjadpur | 107 | 26 | 2021-09-01 | 19:30
137 | Serajganj | 118 | 26 | 2021-09-01 | 19:30
138 | Niyamatpur | 83 | 26 | 2021-09-01 | 22:00
139 | Joypurhat | 69 | 27 | 2021-09-01 | 20:00
140 | Sherpur(Bogura) | 62 | 12 | 2021-09-01 | 20:00
141 | Mohastangar | 74 | 24 | 2021-09-01 | 20:00
142 | Bangura | 35 | 4 | 2021-09-01 | 21:00
143 | Rangpur | 212 | 12 | 2021-09-01 | 8:00
144 | Lalmonirhat | 48 | 5 | 2021-09-01 | 19:30
145 | Saidpur | 104 | 1 | 2021-09-01 | 21:00
146 | Purbasadipur | 112 | 10 | 2021-09-01 | 22:00
147 | Thakurgaon | 93 | 27 | 2021-09-01 | 20:00
148 | Palshbari | 126 | 27 | 2021-09-01 | 21:00
149 | Barapukuria | 60 | 27 | 2021-09-01 | 21:00
150 | Panchugar | 59 | 5 | 2021-09-01 | 20:00
151 | Joldhaka | 63 | 6 | 2021-09-01 | 21:00
152 | Kurigram | 63 | 7 | 2021-09-01 | 19:30
153 | Mitha Pukur | 44 | 5 | 2021-09-01 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:September 2021
Area | MW | Date | Hour | Remarks
Dhaka | 5405 | 16.09.21 | 14:00
Chattogram | 1579 | 30.09.21 | 18:00
Khulna | 1673 | 04.09.21 | 21:00
Rajshahi | 1398 | 26.09.21 | 19:30
Cumilla | 1297 | 04.09.21 | 21:00
Mymensingh | 1058 | 24.09.21 | 20:00
Sylhet | 611 | 12.09.21 | 20:00
Barisal | 416 | 09.09.21 | 23:00
Rangpur | 843 | 10.09.21 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 410 | 27 | 2021-09-01 | 6:00 | 399 | 1 | 2021-09-01 | 8:00
2 | Bheramara | 400 | 412 | 26 | 2021-09-01 | 6:00 | 392 | 30 | 2021-09-01 | 15:00
3 | Ashuganj(N) | 400 | 398 | 5 | 2021-09-01 | 2:00 | 381 | 5 | 2021-09-01 | 12:00
4 | Payra | 400 | 414 | 8 | 2021-09-01 | 24:00 | 0 | 8 | 2021-09-01 | 1:00
5 | Kaliakoir | 400 | 399 | 11 | 2021-09-01 | 5:00 | 338 | 22 | 2021-09-01 | 1:00
6 | Bhulta | 400 | 394 | 5 | 2021-09-01 | 6:00 | 373 | 13 | 2021-09-01 | 16:00
7 | Gopalganj | 400 | 412 | 8 | 2021-09-01 | 15:00 | 0 | 8 | 2021-09-01 | 21:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2021-09-01 | 20:00 | 227 | 2 | 2021-09-01 | 10:00
2 | Ishurdi | 230 | 236 | 4 | 2021-09-01 | 7:00 | 223 | 6 | 2021-09-01 | 19:30
3 | Ashuganj | 230 | 245 | 11 | 2021-09-01 | 5:00 | 235 | 5 | 2021-09-01 | 13:00
4 | Serajganj | 230 | 232 | 2 | 2021-09-01 | 11:00 | 223 | 12 | 2021-09-01 | 23:00
5 | Baghabari | 230 | 237 | 11 | 2021-09-01 | 7:00 | 203 | 25 | 2021-09-01 | 11:00
6 | Barapukuria | 230 | 240 | 2 | 2021-09-01 | 9:00 | 217 | 11 | 2021-09-01 | 23:00
7 | Bogura | 230 | 230 | 2 | 2021-09-01 | 9:00 | 207 | 11 | 2021-09-01 | 23:00
8 | Rajshahi | 230 | 234 | 28 | 2021-09-01 | 18:00 | 216 | 19 | 2021-09-01 | 23:00
9 | Khulna South | 230 | 242 | 10 | 2021-09-01 | 17:00 | 210 | 7 | 2021-09-01 | 2:00
10 | Rampura | 230 | 232 | 11 | 2021-09-01 | 4:00 | 221 | 2 | 2021-09-01 | 12:00
11 | Haripur | 230 | 233 | 6 | 2021-09-01 | 3:00 | 221 | 2 | 2021-09-01 | 10:00
12 | Hasnabad | 230 | 232 | 7 | 2021-09-01 | 1:00 | 218 | 16 | 2021-09-01 | 12:00
13 | Shyampur | 230 | 229 | 4 | 2021-09-01 | 21:00 | 216 | 30 | 2021-09-01 | 7:00
14 | Aminbazar | 230 | 234 | 5 | 2021-09-01 | 1:00 | 220 | 15 | 2021-09-01 | 2:00
15 | Tongi | 230 | 237 | 11 | 2021-09-01 | 13:00 | 215 | 15 | 2021-09-01 | 10:00
16 | Comilla (N) | 230 | 238 | 30 | 2021-09-01 | 15:00 | 226 | 5 | 2021-09-01 | 13:00
17 | Hathazari | 230 | 239 | 10 | 2021-09-01 | 18:30 | 207 | 5 | 2021-09-01 | 13:00
18 | Megnaghat | 230 | 242 | 27 | 2021-09-01 | 7:00 | 226 | 1 | 2021-09-01 | 14:00
19 | Fenchuganj | 230 | 244 | 4 | 2021-09-01 | 6:00 | 236 | 15 | 2021-09-01 | 18:00
20 | Siddhirganj | 230 | 235 | 6 | 2021-09-01 | 6:00 | 223 | 2 | 2021-09-01 | 11:00
21 | Maniknagar | 230 | 233 | 5 | 2021-09-01 | 3:00 | 221 | 2 | 2021-09-01 | 11:00
22 | Old Airport | 230 | 233 | 5 | 2021-09-01 | 7:00 | 218 | 15 | 2021-09-01 | 12:00
23 | Barisal | 230 | 251 | 23 | 2021-09-01 | 2:00 | 0 | 8 | 2021-09-01 | 21:00
24 | Bhola 225 MW | 230 | 251 | 23 | 2021-09-01 | 3:00 | 0 | 8 | 2021-09-01 | 21:00
25 | AKSML | 230 | 238 | 7 | 2021-09-01 | 21:00 | 210 | 5 | 2021-09-01 | 13:00
26 | BSRM | 230 | 237 | 9 | 2021-09-01 | 3:00 | 211 | 5 | 2021-09-01 | 13:00
27 | Bibiyana | 230 | 245 | 27 | 2021-09-01 | 6:00 | 234 | 1 | 2021-09-01 | 16:00
28 | Bhulta | 230 | 237 | 24 | 2021-09-01 | 6:00 | 223 | 2 | 2021-09-01 | 11:00
29 | Ashuganj (S) | 230 | 232 | 0 | 2021-09-01 | 15:00 | 232 | 2 | 2021-09-01 | 15:00
30 | Kaliakoir | 230 | 233 | 6 | 2021-09-01 | 5:00 | 216 | 15 | 2021-09-01 | 12:00
31 | GPH | 230 | 238 | 24 | 2021-09-01 | 18:30 | 206 | 5 | 2021-09-01 | 13:00
32 | Jhenaidah | 230 | 0 | 0 | 2021-09-01 | 0:00 | 0 | 0 | 2021-09-01 | 0:00
132 kV Substation
1 | Siddhirganj | 132 | 139 | 12 | 2021-09-01 | 0.77083 | 127 | 2 | 2021-09-01 | 0.45833
2 | Munsiganj | 132 | 139 | 3 | 2021-09-01 | 0.79167 | 128 | 14 | 2021-09-01 | 0.41667
3 | Sonargaon | 132 | 136 | 5 | 2021-09-01 | 0 | 126 | 16 | 2021-09-01 | 0.5
4 | Shyampur | 132 | 140 | 3 | 2021-09-01 | 0.79167 | 129 | 15 | 2021-09-01 | 0.5
5 | Bhulta | 132 | 136 | 12 | 2021-09-01 | 0.8125 | 117 | 3 | 2021-09-01 | 0.29167
6 | Madanganj | 132 | 139 | 6 | 2021-09-01 | 0.041667 | 127 | 14 | 2021-09-01 | 0.375
7 | Shitalakhya | 132 | 139 | 1 | 2021-09-01 | 0.083333 | 127 | 12 | 2021-09-01 | 0.625
8 | Rahim Steal | 132 | 136 | 4 | 2021-09-01 | 0.20833 | 116 | 12 | 2021-09-01 | 0.625
9 | Matuail | 132 | 137 | 12 | 2021-09-01 | 0.83333 | 127 | 2 | 2021-09-01 | 0.45833
10 | Ghorasal | 132 | 142 | 17 | 2021-09-01 | 0.75 | 135 | 3 | 2021-09-01 | 0.29167
11 | Narsinghdi | 132 | 136 | 24 | 2021-09-01 | 0.29167 | 122 | 8 | 2021-09-01 | 0.91667
12 | Haripur (SBU) | 132 | 137 | 6 | 2021-09-01 | 0.041667 | 128 | 2 | 2021-09-01 | 0.54167
13 | Sreenagar | 132 | 137 | 12 | 2021-09-01 | 0.041667 | 120 | 16 | 2021-09-01 | 0.45833
14 | Ullon | 132 | 137 | 12 | 2021-09-01 | 0.83333 | 125 | 2 | 2021-09-01 | 0.45833
15 | Hasnabad | 132 | 139 | 1 | 2021-09-01 | 0.54167 | 128 | 14 | 2021-09-01 | 0.45833
16 | Magbazar | 132 | 138 | 12 | 2021-09-01 | 0.79167 | 124 | 2 | 2021-09-01 | 0.45833
17 | Maniknagar | 132 | 137 | 6 | 2021-09-01 | 0.125 | 127 | 15 | 2021-09-01 | 0.54167
18 | Bangabhaban | 132 | 137 | 6 | 2021-09-01 | 0.125 | 119 | 12 | 2021-09-01 | 0.77083
19 | Motijheel | 132 | 138 | 12 | 2021-09-01 | 0.70833 | 127 | 15 | 2021-09-01 | 0.54167
20 | Narinda | 132 | 137 | 6 | 2021-09-01 | 0.125 | 125 | 12 | 2021-09-01 | 0.083333
21 | Kazla | 132 | 137 | 6 | 2021-09-01 | 0.125 | 127 | 15 | 2021-09-01 | 0.54167
22 | Dhanmondi | 132 | 139 | 12 | 2021-09-01 | 0.29167 | 126 | 2 | 2021-09-01 | 0.5
23 | Lalbag | 132 | 138 | 12 | 2021-09-01 | 0.20833 | 120 | 15 | 2021-09-01 | 0.5
24 | Madartek | 132 | 137 | 11 | 2021-09-01 | 0.20833 | 124 | 5 | 2021-09-01 | 0.625
25 | Dhaka University | 132 | 137 | 11 | 2021-09-01 | 0.25 | 124 | 4 | 2021-09-01 | 0.25
26 | Aftabnagar | 132 | 136 | 11 | 2021-09-01 | 0.083333 | 124 | 12 | 2021-09-01 | 0.95833
27 | Fatullah | 132 | 140 | 3 | 2021-09-01 | 0.79167 | 119 | 12 | 2021-09-01 | 0.95833
28 | Nawabganj | 132 | 136 | 17 | 2021-09-01 | 0.77083 | 121 | 15 | 2021-09-01 | 0.5
29 | Keraniganj | 132 | 138 | 12 | 2021-09-01 | 0.375 | 121 | 15 | 2021-09-01 | 0.5
30 | Mirpur | 132 | 135 | 7 | 2021-09-01 | 0 | 124 | 15 | 2021-09-01 | 0.5
31 | Kalyanpur | 132 | 136 | 5 | 2021-09-01 | 0.125 | 125 | 15 | 2021-09-01 | 0.54167
32 | Gulshan | 132 | 141 | 12 | 2021-09-01 | 0.29167 | 124 | 2 | 2021-09-01 | 0.5
33 | Uttara | 132 | 140 | 12 | 2021-09-01 | 0.41667 | 123 | 15 | 2021-09-01 | 0.66667
34 | Uttara(New) | 132 | 146 | 12 | 2021-09-01 | 0.25 | 123 | 3 | 2021-09-01 | 0.8125
35 | Kamrangirchar | 132 | 138 | 1 | 2021-09-01 | 0.125 | 120 | 16 | 2021-09-01 | 0.45833
36 | Savar | 132 | 137 | 6 | 2021-09-01 | 0.25 | 124 | 17 | 2021-09-01 | 0.45833
37 | Bhasantec | 132 | 139 | 5 | 2021-09-01 | 0.125 | 127 | 15 | 2021-09-01 | 0.5
38 | Agargaon | 132 | 139 | 5 | 2021-09-01 | 0.16667 | 128 | 15 | 2021-09-01 | 0.5
39 | Satmosjid | 132 | 139 | 5 | 2021-09-01 | 0.16667 | 117 | 12 | 2021-09-01 | 0.91667
40 | Tongi | 132 | 141 | 3 | 2021-09-01 | 18:30 | 117 | 12 | 2021-09-01 | 0.91667
41 | Kabirpur | 132 | 139 | 3 | 2021-09-01 | 18:00 | 122 | 12 | 2021-09-01 | 0.91667
42 | Basundhara | 132 | 140 | 5 | 2021-09-01 | 0.25 | 125 | 15 | 2021-09-01 | 0.625
43 | Manikganj | 132 | 143 | 24 | 2021-09-01 | 0.54167 | 130 | 12 | 2021-09-01 | 0.91667
44 | Joydevpur | 132 | 141 | 7 | 2021-09-01 | 16:00 | 128 | 12 | 2021-09-01 | 0.95833
45 | New Tongi | 132 | 140 | 3 | 2021-09-01 | 17:00 | 125 | 12 | 2021-09-01 | 0.95833
46 | Kodda | 132 | 139 | 25 | 2021-09-01 | 0.54167 | 120 | 6 | 2021-09-01 | 15:00
47 | Dhamrai | 132 | 138 | 24 | 2021-09-01 | 6.00 | 124 | 15 | 2021-09-01 | 0.41667
48 | Rajendrapur | 132 | 137 | 5 | 2021-09-01 | 0.16667 | 117 | 6 | 2021-09-01 | 15:00
49 | Valuka | 132 | 135 | 12 | 2021-09-01 | 0.41667 | 105 | 23 | 2021-09-01 | 0.77083
50 | Tangail | 132 | 138 | 16 | 2021-09-01 | 0.25 | 121 | 20 | 2021-09-01 | 0.8125
51 | Mymensing | 132 | 134 | 16 | 2021-09-01 | 0.16667 | 111 | 15 | 2021-09-01 | 0.5
52 | Kishorganj | 132 | 134 | 12 | 2021-09-01 | 0.79167 | 117 | 3 | 2021-09-01 | 0.91667
53 | Netrokona | 132 | 136 | 12 | 2021-09-01 | 0.8125 | 107 | 13 | 2021-09-01 | 0.54167
54 | Jamalpur | 132 | 139 | 28 | 2021-09-01 | 0.70833 | 110 | 10 | 2021-09-01 | 0.33333
55 | Sherpur | 132 | 137 | 11 | 2021-09-01 | 0.20833 | 107 | 13 | 2021-09-01 | 0.29167
56 | Srimongal | 132 | 140 | 27 | 2021-09-01 | 0.33333 | 128 | 14 | 2021-09-01 | 0.875
57 | Shahjibazar | 132 | 139 | 25 | 2021-09-01 | 0.625 | 126 | 5 | 2021-09-01 | 0.54167
58 | Fenchuganj | 132 | 138 | 18 | 2021-09-01 | 0.33333 | 127 | 12 | 2021-09-01 | 0.041667
59 | Khulawara | 132 | 136 | 8 | 2021-09-01 | 0.29167 | 115 | 12 | 2021-09-01 | 0.041667
60 | Sylhet | 132 | 134 | 18 | 2021-09-01 | 0.33333 | 118 | 12 | 2021-09-01 | 0.041667
61 | Chattak | 132 | 135 | 12 | 2021-09-01 | 0.70833 | 124 | 13 | 2021-09-01 | 0.875
62 | Sunamganj | 132 | 133 | 21 | 2021-09-01 | 0.29167 | 0 | 20 | 2021-09-01 | 0.29167
63 | Biani Bazar | 132 | 136 | 12 | 2021-09-01 | 0.70833 | 120 | 4 | 2021-09-01 | 0.25
64 | Comilla(South) | 132 | 134 | 5 | 2021-09-01 | 0.95833 | 115 | 12 | 2021-09-01 | 0.875
65 | Comilla (North) | 132 | 142 | 5 | 2021-09-01 | 1899-12-31 | 115 | 12 | 2021-09-01 | 0.041667
66 | Chandpur | 132 | 142 | 3 | 2021-09-01 | 0.70833 | 116 | 12 | 2021-09-01 | 0.041667
67 | Feni | 132 | 140 | 26 | 2021-09-01 | 0.79167 | 110 | 12 | 2021-09-01 | 0.125
68 | Chowmuhani | 132 | 137 | 5 | 2021-09-01 | 0.33333 | 113 | 12 | 2021-09-01 | 0.041667
69 | Ashuganj | 132 | 141 | 25 | 2021-09-01 | 0.58333 | 120 | 12 | 2021-09-01 | 0.041667
70 | Daudkandi | 132 | 141 | 5 | 2021-09-01 | 1899-12-31 | 122 | 12 | 2021-09-01 | 0.041667
71 | Brahminbaria | 132 | 140 | 30 | 2021-09-01 | 0.29167 | 110 | 12 | 2021-09-01 | 0.125
72 | Ramganj | 132 | 139 | 21 | 2021-09-01 | 0.54167 | 108 | 12 | 2021-09-01 | 0.125
73 | Chaddagram | 132 | 141 | 5 | 2021-09-01 | 0.91667 | 114 | 12 | 2021-09-01 | 0.041667
74 | PHP | 132 | 139 | 26 | 2021-09-01 | 0.77083 | 118 | 12 | 2021-09-01 | 0.041667
75 | Kochua | 132 | 140 | 5 | 2021-09-01 | 1899-12-31 | 132 | 23 | 2021-09-01 | 0.33333
76 | Madanhat | 132 | 140 | 2 | 2021-09-01 | 0.20833 | 125 | 5 | 2021-09-01 | 0.5
77 | Hathazari | 132 | 140 | 18 | 2021-09-01 | 0.79167 | 125 | 5 | 2021-09-01 | 0.54167
78 | Khulshi | 132 | 137 | 18 | 2021-09-01 | 0.79167 | 118 | 5 | 2021-09-01 | 0.54167
79 | Halishahar | 132 | 138 | 6 | 2021-09-01 | 0.83333 | 118.1 | 5 | 2021-09-01 | 0.54167
80 | Baraulia | 132 | 138 | 3 | 2021-09-01 | 0.79167 | 120 | 5 | 2021-09-01 | 0.54167
81 | Sikalbaha | 132 | 140 | 5 | 2021-09-01 | 0.77083 | 119 | 5 | 2021-09-01 | 0.54167
82 | Dohazari | 132 | 136 | 5 | 2021-09-01 | 0.79167 | 114 | 5 | 2021-09-01 | 0.54167
83 | Cox'sbazar | 132 | 132 | 30 | 2021-09-01 | 0.45833 | 96 | 5 | 2021-09-01 | 0.54167
84 | Chandraghona | 132 | 139 | 18 | 2021-09-01 | 0.77083 | 123 | 5 | 2021-09-01 | 0.54167
85 | Kaptai | 132 | 137 | 6 | 2021-09-01 | 0.75 | 130 | 5 | 2021-09-01 | 0.41667
86 | A. Khaer Stl. | 132 | 138 | 18 | 2021-09-01 | 0.79167 | 120 | 5 | 2021-09-01 | 0.54167
87 | Bakulia | 132 | 138 | 2 | 2021-09-01 | 0.29167 | 118 | 5 | 2021-09-01 | 0.54167
88 | Julda | 132 | 140 | 19 | 2021-09-01 | 0.75 | 120 | 5 | 2021-09-01 | 0.54167
89 | TK Chemical | 132 | 139 | 6 | 2021-09-01 | 0.83333 | 119 | 5 | 2021-09-01 | 0.54167
90 | Modern Steel | 132 | 138 | 18 | 2021-09-01 | 0.79167 | 118 | 5 | 2021-09-01 | 0.54167
91 | Shahmirpur | 132 | 139 | 6 | 2021-09-01 | 0.875 | 122 | 5 | 2021-09-01 | 0.54167
92 | Khagrachhari | 132 | 138 | 6 | 2021-09-01 | 0.75 | 122 | 5 | 2021-09-01 | 0.58333
93 | Matarbari | 132 | 135 | 2 | 2021-09-01 | 0.16667 | 100 | 5 | 2021-09-01 | 0.54167
94 | Baroiar Hat | 132 | 138 | 1 | 2021-09-01 | 0.75 | 127 | 5 | 2021-09-01 | 0.54167
95 | Rangamati | 132 | 138 | 6 | 2021-09-01 | 0.75 | 122 | 5 | 2021-09-01 | 0.54167
96 | Agrabad | 132 | 138 | 6 | 2021-09-01 | 0.83333 | 0 | 26 | 2021-09-01 | 1900-05-09
97 | Goalpara | 132 | 141 | 4 | 2021-09-01 | 0.041667 | 124 | 10 | 2021-09-01 | 0.91667
98 | Khulna Central | 132 | 140 | 10 | 2021-09-01 | 0.70833 | 123 | 10 | 2021-09-01 | 0.91667
99 | Noapara | 132 | 138 | 2 | 2021-09-01 | 0.70833 | 122 | 10 | 2021-09-01 | 0.91667
100 | Jessore | 132 | 137 | 10 | 2021-09-01 | 0.70833 | 117 | 10 | 2021-09-01 | 0.91667
101 | Benapol | 132 | 137 | 18 | 2021-09-01 | 0.91667 | 116 | 30 | 2021-09-01 | 0.83333
102 | Jhenida | 132 | 134 | 10 | 2021-09-01 | 0.70833 | 102 | 18 | 2021-09-01 | 0.79167
103 | Bottail | 132 | 136 | 10 | 2021-09-01 | 0.75 | 119 | 18 | 2021-09-01 | 0.79167
104 | G.K Project | 132 | 140 | 21 | 2021-09-01 | 0.375 | 130 | 23 | 2021-09-01 | 0.79167
105 | Faridpur | 132 | 139 | 24 | 2021-09-01 | 0.25 | 126 | 11 | 2021-09-01 | 0.875
106 | Rajbari | 132 | 137 | 8 | 2021-09-01 | 0.75 | 125 | 6 | 2021-09-01 | 0.875
107 | Madaripur | 132 | 142 | 10 | 2021-09-01 | 0.70833 | 130 | 8 | 2021-09-01 | 0.83333
108 | Sariatpur | 132 | 141 | 6 | 2021-09-01 | 0.75 | 128 | 24 | 2021-09-01 | 0.91667
109 | Gopalganj | 132 | 146 | 12 | 2021-09-01 | 0.25 | 129 | 16 | 2021-09-01 | 0.95833
110 | Bagerhat | 132 | 138 | 10 | 2021-09-01 | 0.625 | 119 | 10 | 2021-09-01 | 0.91667
111 | Mongla | 132 | 137 | 10 | 2021-09-01 | 0.625 | 121 | 10 | 2021-09-01 | 0.91667
112 | Satkhira | 132 | 139 | 2 | 2021-09-01 | 0.70833 | 119 | 10 | 2021-09-01 | 0.91667
113 | Gallamari | 132 | 141 | 2 | 2021-09-01 | 0.70833 | 124 | 10 | 2021-09-01 | 0.91667
114 | Magura | 132 | 135 | 8 | 2021-09-01 | 0.66667 | 100 | 18 | 2021-09-01 | 0.79167
115 | Norail | 132 | 133 | 14 | 2021-09-01 | 0.375 | 99 | 18 | 2021-09-01 | 0.83333
116 | Chuadanga | 132 | 138 | 14 | 2021-09-01 | 0.375 | 91 | 18 | 2021-09-01 | 0.79167
117 | Borguna | 132 | 141 | 7 | 2021-09-01 | 0.33333 | 122 | 8 | 2021-09-01 | 0.91667
118 | Barisal(N) | 132 | 143 | 25 | 2021-09-01 | 0.29167 | 124 | 8 | 2021-09-01 | 0.91667
119 | Barisal(S) | 132 | 141 | 25 | 2021-09-01 | 0.29167 | 121 | 8 | 2021-09-01 | 0.91667
120 | Patuakhali | 132 | 141 | 25 | 2021-09-01 | 0.33333 | 113 | 8 | 2021-09-01 | 0.91667
121 | Bhandaria | 132 | 145 | 25 | 2021-09-01 | 0.33333 | 120 | 1 | 2021-09-01 | 0.91667
122 | Jhenaidah(New) 132kV Bus | 132 | 140 | 29 | 2021-09-01 | 0.75 | 130 | 0 | 2021-09-01 | 0.41667
123 | Ishurdi | 132 | 137 | 3 | 2021-09-01 | 0.70833 | 130 | 1 | 2021-09-01 | 0.83333
124 | Ruppur paromanobik | 132 | 137 | 9 | 2021-09-01 | 0.75 | 129 | 23 | 2021-09-01 | 0.79167
125 | Natore | 132 | 138 | 22 | 2021-09-01 | 0.75 | 126 | 11 | 2021-09-01 | 0.95833
126 | Bogra | 132 | 139 | 2 | 2021-09-01 | 0.70833 | 122 | 11 | 2021-09-01 | 0.91667
127 | Noagaon | 132 | 133 | 1 | 2021-09-01 | 0.75 | 115 | 10 | 2021-09-01 | 0.91667
128 | Rajshahi | 132 | 136 | 5 | 2021-09-01 | 0.25 | 126 | 20 | 2021-09-01 | 0.875
129 | Rajshahi New | 132 | 138 | 28 | 2021-09-01 | 0.75 | 118 | 9 | 2021-09-01 | 0.875
130 | C.Nawabganj | 132 | 139 | 29 | 2021-09-01 | 0.75 | 124 | 20 | 2021-09-01 | 0.041667
131 | Amnura | 132 | 138 | 6 | 2021-09-01 | 0.75 | 121 | 27 | 2021-09-01 | 0.083333
132 | Pabna | 132 | 137 | 10 | 2021-09-01 | 0.75 | 127 | 6 | 2021-09-01 | 0.8125
133 | Shahjadpur | 132 | 140 | 3 | 2021-09-01 | 0.54167 | 130 | 19 | 2021-09-01 | 0.875
134 | Serajganj | 132 | 135 | 2 | 2021-09-01 | 0.70833 | 123 | 21 | 2021-09-01 | 0.16667
135 | Niyamatpur | 132 | 133 | 2 | 2021-09-01 | 0.70833 | 110 | 10 | 2021-09-01 | 0.875
136 | Joypurhat | 132 | 134 | 2 | 2021-09-01 | 0.41667 | 113 | 10 | 2021-09-01 | 0.875
137 | Sherpur(Bogura) | 132 | 137 | 2 | 2021-09-01 | 0.375 | 122 | 11 | 2021-09-01 | 0.91667
138 | Mohastangor | 132 | 137 | 2 | 2021-09-01 | 0.375 | 120 | 10 | 2021-09-01 | 0.875
139 | Bangura | 132 | 138 | 22 | 2021-09-01 | 0.75 | 128 | 19 | 2021-09-01 | 0.875
140 | Rangpur | 132 | 137 | 2 | 2021-09-01 | 0.375 | 111 | 11 | 2021-09-01 | 0.95833
141 | Lalmonirhat | 132 | 136 | 2 | 2021-09-01 | 0.29167 | 110 | 24 | 2021-09-01 | 0.79167
142 | Saidpur | 132 | 136 | 2 | 2021-09-01 | 0.25 | 110 | 10 | 2021-09-01 | 0.875
143 | Purbasadipur | 132 | 136 | 2 | 2021-09-01 | 0.33333 | 106 | 11 | 2021-09-01 | 0.95833
144 | Thakurgaon | 132 | 135 | 2 | 2021-09-01 | 0.25 | 103 | 24 | 2021-09-01 | 0.79167
145 | Palashbari | 132 | 136 | 2 | 2021-09-01 | 0.41667 | 115 | 10 | 2021-09-01 | 0.875
146 | Barapukuria | 132 | 140 | 2 | 2021-09-01 | 0.375 | 117 | 11 | 2021-09-01 | 0.95833
147 | Panchagar | 132 | 138 | 2 | 2021-09-01 | 0.25 | 100 | 24 | 2021-09-01 | 0.79167
148 | Joldhaka | 132 | 135 | 2 | 2021-09-01 | 0.33333 | 105 | 11 | 2021-09-01 | 0.95833
149 | Kurigram | 132 | 136 | 2 | 2021-09-01 | 0.41667 | 112 | 11 | 2021-09-01 | 0.95833
150 | Mithapukur | 132 | 138 | 2 | 2021-09-01 | 0.375 | 116 | 11 | 2021-09-01 | 0.95833
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:September 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 90 | 225 | 2021-07-08 | 9:00
Hasnabad | TR2 | 225 | 90 | 225
| TR3 | 225 | 90 | 225
| TR1 | 225 | 180 | 520
Tongi | TR2 | 225 | 180 | 520 | 16/08/21 | 8:00
| TR3 | 225 | 180 | 520
Haripur | TR1 | 225 | 122 | 365
| TR2 | 225 | 122 | 365 | 29/08/21 | 17:00
| TR3 | 225 | 122 | 365
| TR1 | 225 | 188 | 515
Rampura | TR2 | 225 | 188 | 515 | 29.08.2022 | 13:00
| TR3 | 225 | 188 | 515
Keraniganj | ATR1 | 300 | 98 | 280
| ATR2 | 300 | 98 | 280 | 30/08/21 | 17:00
| ATR3 | 300 | 98 | 280
| TR1 | 225 | 121 | 327
Aminbazar | TR2 | 225 | 121 | 327 | 20/08/21 | 11:00
| TR3 | 225 | 125 | 337
Agargaon | TR1 | 300 | 162 | 444
| TR2 | 300 | 162 | 444 | 2021-05-23 | 14:00
Maniknagar | TR1 | 300 | 139 | 400 | 31/08/21 | 13:00
| TR2 | 300 | 139 | 400
Cumilla (N) | TR1 | 225 | 185 | 512 | 2021-12-08 | 6:00
| TR2 | 225 | 182 | 501
Fenchuganj | AT2 | 300 | 284 | 750 | 25.08.2021 | 18:30
| MT1 | 150 | 90 | 260 | 2021-12-08
Hathazari | MT2 | 150 | 90 | 260 |  | 18:00
| MT3 | 150 | 90 | 260
| MT4 | 150 | 90 | 260
| TR1 | 225 | 110 | 284 | 06.08.21 | 05.00 AM
Ishurdi | TR2 | 225 | 110 | 284
| TR3 | 225 | 110 | 284
Khulna(S) | TR1 | 225 | 123 | 343 |  | 7:00
| TR2 | 225 | 123 | 343 | 2021-08-21 | 7:00
| TR3 | 300 | 158 | 445 |  | 7:00
Bogura | TR1 | 225 | 123 | 353
| TR2 | 225 | 123 | 353 | 2021-02-08 | 7:00
| TR3 | 225 | 167 | 462
Baghabari | TR1 | 300 | 166 | 450 | 2021-07-08 | 20:00
| TR2 | 225 | 123 | 335
Rajshahi | ATR-01 | 300 | 119 | 328 | 06.08.2021 | 6:00
| ATR-02 | 300 | 119 | 328 | 06.08.2021 | 6:00
Barapukuria | TR1 | 225 | 214 | 637 | 2021-07-08 | 12:00 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 176 | 561 | 2021-07-08 | 12:00 | 132 kV current is being provided
| TR6 | 300 | 233 | 709 | 2021-07-08 | 12:00
Bheramara | Transformer-1 | 225 | 100 | 266 | 18/08/21 | 7:00
| Transformer-2 | 225 | 100 | 266
Shyampur | ATR-01 | 300 | 128 | 409 | 31-08-2021 | 10:00
| ATR-02 | 300 | 128 | 409 | 31-08-2021 | 10:00
Kaliakoir | TR1 | 300 | 125.8 | 360 | 25.08.21 | 14:30
Sikalbaha | ATR-1 | 300 | 274 | 722 | 31/08/21 | 22:00
Jhenaidah | Tr-1 | 300 | 110 | 297 | 2021-08-11 | 21:00
| Tr-2 | 300 | 110 | 297 | 2021-08-11 | 21:00
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:September 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 311.2 | 468.9 | 16/08/21 | 9:30
| TR2(400/230 kV) | 520 | 314.5 | 472
| TR1(400/132 kV) | 325 | 291.1 | 483 | 31/08/21 | 20:30
| TR2(400/132 kV) | 325 | 291.9 | 485
Bibiyana | ICT1(400/230 kV) | 520 | 159 | 232A | 25.08.21 | 23..00
| ICT2(400/230kV) | 520 | 155 | 226A | 25.08.21 | 23..00
Bhulta | ATR1(400/230 kV) | 520 | 187 | 355 | 17/08/21 | 9:00
| ATR2(400/230kV) | 520 | 187 | 355
Ashuganj(N) | GSUT1 | 567 | 371 | 601.5 | 20/08/21 | 22:03
Gopalganj | ATR1(400/138 kV) | 325 | 311 | 453 | 31/08/21 | 23:00
| ATR2(400/138kV) | 325 | 311 | 453
Payra | GSUT1 | 270 | 208 | 938 | 28/08/21 | 21:00
| GSUT2 | 270 | 209 | 921
| GSUT3 | 270 | 208 | 929
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:September 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:September 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-09-01 | 13075 | 13075 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-01 | 11135 | 11135 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-02 | 12964 | 12964 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-02 | 11166 | 11166 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-03 | 12602 | 12602 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-03 | 9805 | 9805 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-04 | 13343 | 13343 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-04 | 10530 | 10530 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-05 | 13148 | 13148 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-05 | 11723 | 11723 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-06 | 13082 | 13082 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-06 | 11421 | 11421 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-07 | 13060 | 13060 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-07 | 11003 | 11003 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-08 | 13130 | 13130 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-08 | 11201 | 11201 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-09 | 13314 | 13314 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-09 | 11320 | 11320 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-10 | 12581 | 12581 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-10 | 10074 | 10074 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-11 | 13509 | 13509 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-11 | 10978 | 10978 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-12 | 13025 | 13025 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-12 | 11415 | 11415 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-13 | 12951 | 12951 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-13 | 11105 | 11105 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-14 | 12442 | 12442 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-14 | 10553 | 10553 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-15 | 13085 | 13085 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-15 | 11168 | 11168 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-16 | 13020 | 13020 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-16 | 11051 | 11051 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-17 | 8941 | 8941 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-17 | 8941 | 8941 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-18 | 12647 | 12647 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-18 | 10002 | 10002 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-19 | 12370 | 12370 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-19 | 10431 | 10431 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-20 | 12571 | 12571 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-20 | 10671 | 10671 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-21 | 12523 | 12523 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-21 | 10511 | 10511 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-22 | 12491 | 12491 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-22 | 10870 | 10870 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-23 | 13052 | 13052 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-23 | 11229 | 11229 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-24 | 12696 | 12696 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-24 | 9875 | 9875 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-25 | 13052 | 13052 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-25 | 10961 | 10961 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-26 | 12936 | 12936 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-26 | 11506 | 11506 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-27 | 12716 | 12716 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-27 | 11458 | 11458 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-28 | 12371 | 12371 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-28 | 10875 | 10875 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-29 | 12503 | 12503 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-29 | 10236 | 10236 | - | - | - | - | - | - | - | - | - | - | - | -
2021-09-30 | 13065 | 13065 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-09-30 | 10926 | 10926 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:September 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13509 | 2021-09-11 | 20:00
2 | Maximum Day Peak Genaration | MW | 11723 | 2021-09-05 | 12:00
3 | Maximum Evening Peak Demand | MW | 13509 | 2021-09-11 | 20:00
4 | Minimum Generation | MW | 8491 | 2021-09-17 | 1:00
5 | Average of the daily evening peak Genaration | MW | 12742.1667
6 | Average of the daily day peak Genaration | MW | 10804.6667
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 8142.0638
12 | Total Generation by BPDB | MkWh | 1586.2039 | % of total Gen. | 19.48%
13 | Total Generation by IPP | MkWh | 3209.7608 | '' | 39.42%
14 | A) Total Generation by Generation Companies | MkWh | 2114.2991 | '' | 25.97%
| B) Total Generation by REB | MkWh | 141.3247 | " | 1.736%
| C) Total Generation by RENTAL | MkWh | 490.1064 | " | 6.019%
| D) Total Imported from India (BIPTC) | MkWh | 515.096 | " | 6.326%
| E) Total Imported from Tripura, India (A.C) | MkWh | 85.273 | " | 1.047%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4494.9287 | % of total Gen. | 55.21%
| B) Oil | MkWh | 2501.6624 | '' | 30.73%
| C) Hydro | MkWh | 104.8774 | '' | 1.288%
| D) Solar | MkWh | 23.2163 | '' | 0.2851%
| E) Coal | MkWh | 417.01 | '' | 5.122%
| F) BIPTC (Import from India) | MkWh | 515.096 | '' | 6.326%
| G) A.C (Import from Tripura, India) | MkWh | 85.273 | '' | 1.047%
16 | Maximun of the daily total Generation . | MkWh | 286.13 | 2021-09-05
17 | Monthly Load factor | % | 81.01
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 30296.8035
| A) Gas | M.Taka | 4408.7273
| B) Liquid fuel | M.Taka | 20693.938
| C) Coal | M.Taka | 1927.6014
| D) BIPTC (Import from India) | M.Taka | 2626.9895
| E) Tripura(Import from India) | M.Taka | 639.5472
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1166.0717 | 2021-09-06
| A) Gas | M.Taka | 166.0243 | 2021-09-22
| B) Liquid fuel | M.Taka | 948.0157 | 2021-09-06
| C) Coal | M.Taka | 79.9451 | 2021-09-02
| D) BIPTC (Import from India) | M.Taka | 88.4655 | 2021-09-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.9999
| B) Excluding Hydro & Solar | Taka/kWhR | 4.0634
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.34 | 31/8/2021 | 06:00
b) | Actual | FT (MSL) | 97.78 | 31/8/2021 | 06:00
22 | Peak Genaration of September 2020 | MW | 12892 | 05/09/20 | 19:30
23 | Peak Demand of September 2020 | MW | 12892 | 05/09/20 | 19:30
24 | Maximum peak Generation recorded upto 30/09/2021 | MW | 13792 | 2021-04-27 | 20:00
25 | Maximum peak Demand recorded upto 30/09/2021 | MW | 14097 | 2021-04-27 | 19:00
26 | Maximum load shed recorded upto 30/09/2021 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.