## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-11-29 | Monday
|  |  | Date (day): | 2021-11-29 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11867.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13301 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-11-28 | 2021-11-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 389 | 360 | 360 | 52 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 200 | 160 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | FGMO & GT-2 S/D due to gas shortage.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 25 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 18 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 118 | ST Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 53 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 25 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 195 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 52 | 147 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 52 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 1588 | 2150 | 2659 | 3179 | 757 | 1263
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 14 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 72 | 108 | 110 | 110 |  | 120 | Low Water Level & Unit 2 & 4,5 U/M.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 34 | 17 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 80 |  | 22 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 60 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 7 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 23 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 267 | 291 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 10 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 107 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 824 | 920 | 1341 | 1375 | 180 | 813
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 120 | 120 | 120 | 120 | 14 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 183 | 220 | 220 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 265 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 54 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 68 | 68 | 68 | 68 | 127 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 108 | 140 | 140 |  | 10 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | ST Under maint.
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 17 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 0 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 105 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 30 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 6 | 9 | 9 | 9
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 66 | 118 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 18 | 0 | 0 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1257 | 1324 | 1892 | 2118 | 405 | 496
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 145 | 200 | 200 |  |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 24 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 65 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 299 | 330 | 610.6 | 559 | 0 | 8
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 42 | 42 |  | 28 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 140 | 140 | 144 | 144 |  | 186 | GT-1 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 32 | 33 | 33 |  | 33 | GT-8 S/D for gas shortage.
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 77 | 80 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 100 | 100
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 199 | 218 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 387 | 401 | 400 | 400 |  |  | FGMO
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1445 | 1481 | 1666 | 1670 | 0 | 690
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 727 | 727 | 746 | 746
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 780 | 832 | 901 | 1341 | 0 | 503
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 21 | 25 | 25 |  | 8 | Engine problem
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 67 | 68 | 68 |  | 126 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 410 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 150 | 219 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 539 | 728 | 1054 | 1204 | 84 | 134
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 18 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 16 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 177 | 174 | 200 | 220
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 188 | 200 | 200
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 407 | 414 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 20 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 42 | 95 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 109 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 930 | 1224 | 1539 | 1658 | 310 | 89
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 79 | 84 | 84
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 29 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 105 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 149 | 184 | 205 | 197 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 7811 | 9173 | 11867.6 | 13301 | 1736 | 4395
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7545.3255 | 8861 | 11463.9489 | 12848.5949
| A. |  | 2021-11-28 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 9173 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5959 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9173 | MW
| 3 | Day peak Generation : |  |  | 7811 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8861 | MW
| 4 | Evening peak Generation : |  |  | 9173 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 182.409 | MKWHr | By Solar | 0.72084 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 116.7247 | MKWHr |  | By Oil: | 35.0602 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 10.8079 | MKWHr |  | By Hydro: | 1.933 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1736 | MW | Dhaka | 3376 | 3376 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 4395 | MW | Chittagong | 1082 | 1082 |  | 0 |  | 18:00 |  | 110
|  |  |  | Total = |  |  | 6131 | MW | Khulna | 1029 | 1029 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 892.17 | MMCFD |  |  | Rajshahi | 839 | 839 |  | 0 |  | 19:00 |  | 105
| 8 | Fuel Cost : | i) Gas : | Taka | 129221096.508 | ii) Oil : | Taka | 231606194.6 | Comilla | 760 | 760 |  | 0 |  | 19:30 |  | 106
|  |  | iii) Coal : |  | 50557428.16 | Total | Taka | 411384719.268 | Mymensingh | 653 | 653 |  | 0 |  | 20:00 |  | 103
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.2615 | MKWHr. | Sylhet | 322 | 322 |  | 0 |  | 21:00 |  | 101
|  | ii) During Peak Demand : |  |  | 154 | MW (E to W) at | 19:00 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 97
|  | iii) Maximum : |  |  | -175 | MW at | 8:00 | hrs | Rangpur | 563 | 563 |  | 0 |  | 23:00 |  | 92
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.9° C |  |  | Total | 8861 | 8861 |  | 0
| B. |  | 2021-11-29 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 27.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13301 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
| 4 | Reserve(Generation end) |  |  |  | 4001 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 185.0259 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5965 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.9985 | MKWHr. | ii) HVDC Flow at Peak Time |  | 727 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1638 | MKWHr. | iii) Maximum HVDC Flow : |  | 727 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.19 |  | (b) Today: | 101.02 |  | (c) Rule Curve: |  | 106.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-11-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 343 | 144 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 25 | 16 | 24 | 0 | 0 | 120 | 0 | 305 | 184 | 68 | 88 | 28 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 9 | 80 | 152 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 130 | 98 | 33 | 80 | 0 | 217 | 0 | 0 | 10 | 285 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 400 | 35 | 0 | 0 | 0 | 285 | 54 | 17 | 0 | 115 | 0 | 0 | 50 | 0 | 162 | 70 | 0 | 17 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 23 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 185 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 |  | 4924 | 1934 | 6858 | 2950 | 444 | 1972 | 0 | 946 | 381 | 73 | 0 | 12 | 80 | 0 | 0 | 101.2
2:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 338 | 173 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 24 | 16 | 26 | 0 | 0 | 120 | 0 | 300 | 184 | 68 | 90 | 28 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 25 | 9 | 78 | 166 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 130 | 95 | 33 | 80 | 0 | 218 | 0 | 0 | 10 | 280 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 35 | 0 | 0 | 0 | 210 | 54 | 17 | 0 | 26 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 22 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 185 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 |  | 4486 | 1955 | 6441 | 2952 | 444 | 2019 | 0 | 483 | 380 | 73 | 0 | 12 | 78 | 0 | 0 | 101.2
3:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 339 | 192 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 24 | 16 | 33 | 0 | 0 | 120 | 0 | 305 | 184 | 68 | 91 | 28 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 28 | 9 | 76 | 166 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 130 | 95 | 33 | 40 | 0 | 217 | 0 | 0 | 10 | 290 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 16 | 0 | 0 | 0 | 65 | 54 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 21 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 0 | 184 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 220 | 0 | 0 | 0 |  | 4253 | 1941 | 6194 | 2961 | 444 | 2028 | 0 | 248 | 352 | 72 | 0 | 13 | 76 | 0 | 0 | 101.2
4:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 338 | 213 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 24 | 16 | 34 | 0 | 0 | 120 | 0 | 305 | 185 | 68 | 90 | 28 | 54 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 74 | 166 | 0 | 22 | 0 | 41 | 30 | 8 | 0 | 163 | 95 | 33 | 10 | 0 | 217 | 0 | 0 | 10 | 300 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 16 | 0 | 0 | 0 | 65 | 54 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 19 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 11 | 0 | 182 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 200 | 0 | 0 | 0 |  | 4242 | 1898 | 6140 | 2965 | 444 | 1974 | 0 | 248 | 352 | 72 | 0 | 11 | 74 | 0 | 0 | 101.19
5:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 349 | 232 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 34 | 0 | 0 | 120 | 0 | 305 | 193 | 68 | 90 | 28 | 51 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 8 | 9 | 72 | 166 | 0 | 22 | 0 | 41 | 30 | 8 | 0 | 110 | 96 | 20 | 10 | 0 | 217 | 0 | 0 | 10 | 300 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 8 | 0 | 0 | 0 | 45 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 19 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 0 | 174 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 170 | 0 | 0 | 0 |  | 4102 | 1857 | 5959 | 2931 | 444 | 1913 | 0 | 165 | 351 | 72 | 0 | 11 | 72 | 0 | 0 | 101.19
6:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 356 | 231 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 25 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 34 | 0 | 0 | 120 | 0 | 285 | 183 | 68 | 90 | 28 | 51 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 69 | 168 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 7 | 34 | 75 | 0 | 190 | 0 | 0 | 10 | 305 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 340 | 8 | 0 | 0 | 0 | 100 | 54 | 4 | 0 | 13 | 0 | 0 | 6 | 0 | 10 | 14 | 0 | 17 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 19 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 11 | 0 | 170 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 170 | 0 | 0 | 0 |  | 4209 | 1791 | 6000 | 2756 | 444 | 2009 | 0 | 270 | 370 | 72 | 0 | 10 | 69 | 0 | 0 | 101.19
7:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 349 | 212 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 21 | 25 | 25 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 20 | 0 | 0 | 120 | 0 | 285 | 190 | 68 | 90 | 28 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 6 | 67 | 168 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 0 | 33 | 75 | 0 | 191 | 0 | 0 | 10 | 310 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 395 | 16 | 0 | 0 | 0 | 210 | 54 | 18 | 0 | 65 | 0 | 0 | 18 | 3 | 71 | 57 | 0 | 17 | 3 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 11 | 0 | 170 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 150 | 0 | 0 | 0 |  | 4594 | 1847 | 6441 | 2804 | 444 | 2027 | 0 | 632 | 381 | 72 | 0 | 8 | 67 | 6 | 0 | 101.18
8:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 361 | 140 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 25 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 10 | 0 | 0 | 120 | 0 | 315 | 190 | 68 | 90 | 28 | 53 | 0 | 43 | 0 | 0 | 7 | 22 | 11 | 33 | 6 | 76 | 166 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 8 | 33 | 75 | 0 | 191 | 0 | 0 | 10 | 300 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 97 | 399 | 52 | 0 | 0 | 0 | 275 | 54 | 34 | 0 | 65 | 0 | 0 | 34 | 17 | 144 | 108 | 0 | 17 | 11 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 165 | 0 | 370 | 5 | 0 | 37 | 0 | 70 | 0 | 1 | 50 | 330 | 150 | 0 | 0 | 1 |  | 4967 | 2003 | 6970 | 2849 | 444 | 1902 | 0 | 1183 | 409 | 72 | 0 | 5 | 76 | 30 | 0 | 101.18
9:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 365 | 126 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 18 | 25 | 28 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 16 | 2 | 0 | 0 | 120 | 0 | 305 | 183 | 68 | 88 | 26 | 53 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 6 | 85 | 166 | 0 | 22 | 1 | 41 | 30 | 53 | 0 | 130 | 8 | 20 | 75 | 0 | 218 | 0 | 0 | 10 | 285 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 30 | 0 | 110 | 399 | 65 | 0 | 0 | 1 | 287 | 54 | 53 | 0 | 65 | 0 | 0 | 43 | 33 | 152 | 108 | 0 | 17 | 20 | 0 |  | 543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 13 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 187 | 0 | 366 | 30 | 0 | 70 | 0 | 70 | 0 | 3 | 50 | 320 | 150 | 0 | 0 | 3 |  | 5038 | 2164 | 7202 | 2858 | 543 | 1827 | 0 | 1337 | 400 | 72 | 0 | 5 | 85 | 75 | 0 | 101.18
10:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 366 | 99 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 18 | 25 | 25 | 28 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 16 | 2 | 0 | 0 | 120 | 0 | 305 | 222 | 68 | 88 | 29 | 55 | 0 | 43 | 0 | 0 | 8 | 22 | 9 | 33 | 6 | 89 | 161 | 0 | 22 | 2 | 40 | 30 | 53 | 0 | 163 | 8 | 32 | 75 | 0 | 218 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 10 | 0 | 50 | 376 | 45 | 0 | 0 | 4 | 286 | 54 | 51 | 0 | 45 | 0 | 0 | 53 | 43 | 162 | 108 | 0 | 17 | 26 | 24 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 195 | 0 | 330 | 0 | 0 | 35 | 0 | 34 | 0 | 5 | 0 | 310 | 152 | 0 | 0 | 4 |  | 5012 | 2189 | 7201 | 2905 | 727 | 1806 | 0 | 1080 | 395 | 72 | 0 | 2 | 89 | 101 | 0 | 101.17
11:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 318 | 74 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 35 | 18 | 25 | 25 | 33 | 33 | 2 | 0 | 32 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 40 | 18 | 2 | 0 | 0 | 120 | 0 | 305 | 223 | 68 | 88 | 26 | 56 | 0 | 43 | 0 | 0 | 13 | 22 | 9 | 33 | 6 | 94 | 158 | 0 | 22 | 2 | 40 | 30 | 53 | 0 | 163 | 50 | 32 | 75 | 0 | 218 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 88 | 0 | 50 | 400 | 50 | 0 | 0 | 4 | 230 | 54 | 69 | 0 | 57 | 0 | 0 | 59 | 48 | 138 | 108 | 0 | 17 | 30 | 34 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 84 | 0 | 33 | 0 | 0 | 0 | 0 | 193 | 0 | 11 | 0 | 192 | 0 | 340 | 10 | 0 | 48 | 0 | 20 | 0 | 5 | 20 | 320 | 151 | 0 | 0 | 5 |  | 5112 | 2265 | 7377 | 2921 | 727 | 1797 | 0 | 1182 | 437 | 72 | 0 | 0 | 94 | 113 | 0 | 101.17
12:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 365 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 18 | 25 | 25 | 33 | 33 | 25 | 0 | 32 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 39 | 18 | 2 | 0 | 0 | 120 | 0 | 340 | 204 | 68 | 90 | 29 | 52 | 0 | 43 | 0 | 0 | 25 | 22 | 9 | 30 | 6 | 98 | 151 | 0 | 22 | 2 | 42 | 30 | 53 | 0 | 163 | 140 | 20 | 77 | 0 | 199 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 18 | 90 | 0 | 20 | 387 | 65 | 0 | 34 | 4 | 267 | 54 | 110 | 0 | 66 | 0 | 0 | 104 | 49 | 162 | 108 | 0 | 17 | 30 | 18 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 29 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 165 | 0 | 407 | 53 | 0 | 109 | 0 | 34 | 0 | 5 | 35 | 300 | 150 | 0 | 0 | 4 |  | 5413 | 2398 | 7811 | 2989 | 727 | 1792 | 0 | 1593 | 410 | 72 | 0 | 0 | 98 | 112 | 0 | 101.17
13:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 367 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 53 | 18 | 25 | 22 | 33 | 33 | 33 | 0 | 32 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 41 | 18 | 8 | 0 | 0 | 120 | 0 | 305 | 182 | 68 | 88 | 29 | 51 | 0 | 43 | 0 | 0 | 38 | 22 | 9 | 28 | 6 | 102 | 147 | 0 | 20 | 2 | 42 | 30 | 53 | 0 | 163 | 142 | 31 | 77 | 0 | 219 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 17 | 90 | 8 | 20 | 402 | 65 | 0 | 55 | 4 | 270 | 54 | 110 | 0 | 68 | 0 | 0 | 104 | 47 | 162 | 108 | 0 | 0 | 30 | 11 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 0 | 195 | 0 | 412 | 53 | 0 | 113 | 0 | 70 | 0 | 5 | 60 | 360 | 151 | 0 | 0 | 4 |  | 5474 | 2541 | 8015 | 3009 | 727 | 1814 | 0 | 1730 | 441 | 72 | 0 | 0 | 102 | 109 | 0 | 101.16
14:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 374 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 53 | 18 | 25 | 21 | 33 | 25 | 42 | 0 | 32 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 18 | 6 | 0 | 0 | 120 | 0 | 300 | 182 | 68 | 90 | 27 | 54 | 0 | 43 | 0 | 0 | 52 | 22 | 9 | 28 | 6 | 103 | 142 | 0 | 20 | 2 | 42 | 30 | 53 | 0 | 130 | 145 | 20 | 77 | 0 | 219 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 14 | 90 | 17 | 20 | 352 | 45 | 0 | 34 | 3 | 286 | 54 | 110 | 0 | 68 | 0 | 0 | 104 | 37 | 162 | 108 | 0 | 0 | 25 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 195 | 0 | 328 | 53 | 0 | 113 | 0 | 70 | 0 | 4 | 70 | 320 | 151 | 0 | 0 | 4 |  | 5316 | 2399 | 7715 | 2909 | 727 | 1658 | 0 | 1756 | 401 | 72 | 0 | 0 | 103 | 89 | 0 | 101.08
15:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 368 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 18 | 25 | 21 | 33 | 25 | 42 | 0 | 33 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 18 | 2 | 0 | 0 | 120 | 0 | 300 | 183 | 68 | 90 | 27 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 9 | 33 | 6 | 98 | 142 | 0 | 22 | 1 | 42 | 30 | 53 | 0 | 130 | 142 | 20 | 77 | 0 | 219 | 0 | 0 | 10 | 295 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 10 | 90 | 17 | 20 | 352 | 45 | 0 | 34 | 2 | 286 | 54 | 110 | 0 | 67 | 0 | 0 | 104 | 26 | 162 | 108 | 0 | 0 | 17 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 173 | 0 | 372 | 17 | 0 | 50 | 0 | 49 | 0 | 2 | 50 | 300 | 151 | 0 | 0 | 2 |  | 5289 | 2262 | 7551 | 2890 | 727 | 1722 | 0 | 1600 | 381 | 73 | 0 | 0 | 98 | 60 | 0 | 101.08
16:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 353 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 18 | 25 | 21 | 33 | 25 | 42 | 0 | 33 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 50 | 18 | 2 | 0 | 0 | 120 | 0 | 325 | 205 | 68 | 90 | 29 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 9 | 33 | 6 | 98 | 142 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 130 | 141 | 20 | 77 | 0 | 219 | 0 | 0 | 10 | 300 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 5 | 90 | 17 | 10 | 352 | 45 | 0 | 34 | 1 | 286 | 54 | 110 | 0 | 67 | 0 | 0 | 104 | 11 | 162 | 108 | 0 | 0 | 8 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 175 | 0 | 373 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 300 | 151 | 0 | 0 | 0 |  | 5279 | 2207 | 7486 | 2933 | 727 | 1725 | 0 | 1524 | 380 | 73 | 0 | 0 | 98 | 26 | 0 | 101.07
17:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 315 | 0 |  | 0 | 270 | 150 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 2 | 16 | 10 | 0 | 0 | 0 | 54 | 23 | 53 | 18 | 25 | 21 | 33 | 25 | 42 | 0 | 68 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 5 | 43 | 18 | 3 | 0 | 0 | 120 | 0 | 265 | 181 | 68 | 87 | 29 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 9 | 33 | 6 | 99 | 148 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 110 | 141 | 32 | 78 | 0 | 218 | 0 | 0 | 10 | 285 | 24 | 2 | 0 | 8 | 0 | 0 | 5 | 0 | 54 | 0 | 100 | 19 | 15 | 388 | 63 | 5 | 34 | 0 | 283 | 54 | 110 | 17 | 87 | 10 | 0 | 104 | 0 | 162 | 106 | 0 | 0 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 0 | 0 | 5 | 14 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 170 | 0 | 340 | 18 | 0 | 40 | 0 | 70 | 0 | 0 | 60 | 300 | 151 | 0 | 0 | 0 |  | 5355 | 2283 | 7638 | 2852 | 727 | 1662 | 0 | 1763 | 379 | 108 | 0 | 48 | 99 | 0 | 0 | 101.07
18:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 350 | 0 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 48 | 24 | 0 | 0 | 0 | 54 | 55 | 53 | 18 | 25 | 29 | 33 | 25 | 52 | 0 | 68 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 16 | 45 | 18 | 4 | 0 | 0 | 120 | 0 | 270 | 186 | 68 | 90 | 29 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 9 | 33 | 9 | 110 | 149 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 143 | 32 | 78 | 0 | 218 | 0 | 0 | 10 | 290 | 24 | 2 | 0 | 175 | 0 | 0 | 24 | 0 | 122 | 0 | 100 | 51 | 55 | 401 | 115 | 52 | 34 | 0 | 286 | 54 | 110 | 34 | 115 | 40 | 0 | 104 | 0 | 162 | 107 | 0 | 0 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 18 | 16 | 0 | 25 | 36 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 11 | 0 | 166 | 0 | 418 | 70 | 0 | 93 | 0 | 105 | 0 | 0 | 113 | 350 | 219 | 0 | 0 | 0 |  | 6294 | 2794 | 9088 | 2927 | 727 | 1883 | 0 | 2705 | 428 | 108 | 0 | 200 | 110 | 0 | 0 | 101.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 389 | 0 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 16 | 25 | 0 | 0 | 0 | 54 | 55 | 53 | 18 | 25 | 30 | 33 | 25 | 25 | 0 | 68 | 40 | 0 | 0 | 14 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 23 | 50 | 18 | 7 | 0 | 0 | 120 | 0 | 265 | 183 | 68 | 90 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 22 | 0 | 33 | 9 | 105 | 145 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 140 | 32 | 77 | 0 | 218 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 195 | 0 | 0 | 24 | 0 | 147 | 0 | 60 | 17 | 108 | 401 | 115 | 52 | 17 | 0 | 291 | 54 | 110 | 0 | 118 | 10 | 0 | 104 | 0 | 162 | 107 | 0 | 0 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 25 | 0 | 42 | 18 | 16 | 0 | 52 | 36 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 188 | 0 | 414 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 410 | 219 | 0 | 0 | 0 |  | 6205 | 2968 | 9173 | 2984 | 727 | 1870 | 0 | 2720 | 489 | 108 | 0 | 170 | 105 | 0 | 0 | 101.06
19:30 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 395 | 0 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 16 | 25 | 0 | 0 | 0 | 54 | 55 | 53 | 18 | 25 | 30 | 33 | 33 | 25 | 0 | 67 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 10 | 50 | 18 | 2 | 0 | 0 | 120 | 0 | 265 | 183 | 68 | 90 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 9 | 106 | 145 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 142 | 32 | 77 | 0 | 218 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 195 | 0 | 0 | 24 | 0 | 113 | 0 | 60 | 0 | 133 | 400 | 115 | 52 | 0 | 0 | 291 | 54 | 110 | 0 | 118 | 0 | 0 | 104 | 0 | 162 | 107 | 0 | 0 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 18 | 16 | 0 | 52 | 36 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 0 | 186 | 0 | 401 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 420 | 220 | 0 | 0 | 0 |  | 6171 | 2943 | 9114 | 3006 | 727 | 1868 | 0 | 2656 | 499 | 107 | 0 | 145 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 395 | 0 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 0 | 24 | 0 | 0 | 0 | 54 | 55 | 54 | 18 | 25 | 30 | 33 | 33 | 25 | 0 | 66 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 0 | 50 | 18 | 4 | 0 | 0 | 120 | 0 | 265 | 183 | 68 | 89 | 29 | 55 | 0 | 51 | 0 | 0 | 25 | 22 | 11 | 33 | 9 | 103 | 145 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 140 | 33 | 77 | 0 | 218 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 24 | 0 | 117 | 0 | 60 | 0 | 130 | 400 | 115 | 52 | 0 | 0 | 286 | 54 | 110 | 0 | 116 | 0 | 0 | 104 | 0 | 162 | 107 | 0 | 0 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 185 | 0 | 412 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 420 | 220 | 0 | 0 | 0 |  | 6093 | 2883 | 8976 | 3010 | 727 | 1877 | 0 | 2579 | 498 | 106 | 0 | 76 | 103 | 0 | 0 | 101.06
21:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 393 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 54 | 20 | 25 | 30 | 33 | 33 | 0 | 0 | 68 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 50 | 18 | 5 | 0 | 0 | 120 | 0 | 350 | 183 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 101 | 147 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 142 | 33 | 78 | 0 | 218 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 8 | 0 | 104 | 0 | 60 | 0 | 137 | 400 | 85 | 0 | 0 | 0 | 286 | 54 | 110 | 0 | 115 | 0 | 0 | 104 | 0 | 162 | 105 | 0 | 0 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 188 | 0 | 394 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 420 | 221 | 0 | 0 | 0 |  | 5932 | 2787 | 8719 | 3107 | 727 | 1863 | 0 | 2299 | 497 | 108 | 0 | 17 | 101 | 0 | 0 | 101.06
22:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 393 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 23 | 0 | 0 | 0 | 54 | 0 | 54 | 20 | 25 | 30 | 33 | 33 | 0 | 0 | 63 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 18 | 22 | 0 | 0 | 120 | 0 | 295 | 183 | 68 | 90 | 29 | 54 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 97 | 149 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 140 | 33 | 78 | 0 | 217 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 71 | 0 | 30 | 0 | 140 | 400 | 85 | 0 | 0 | 0 | 286 | 54 | 110 | 0 | 117 | 0 | 0 | 104 | 0 | 162 | 108 | 0 | 10 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 190 | 0 | 323 | 53 | 0 | 113 | 0 | 68 | 0 | 0 | 35 | 400 | 221 | 0 | 0 | 0 |  | 5624 | 2513 | 8137 | 3045 | 727 | 1786 | 0 | 1902 | 477 | 103 | 0 | 0 | 97 | 0 | 0 | 101.05
23:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 393 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 54 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 64 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 26 | 0 | 0 | 120 | 0 | 295 | 183 | 68 | 90 | 29 | 54 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 92 | 148 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 130 | 143 | 33 | 78 | 0 | 217 | 0 | 0 | 10 | 280 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 138 | 400 | 65 | 0 | 0 | 0 | 300 | 54 | 68 | 0 | 117 | 0 | 0 | 104 | 0 | 162 | 108 | 40 | 17 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 179 | 0 | 379 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 390 | 190 | 0 | 0 | 0 |  | 5288 | 2363 | 7651 | 3071 | 727 | 1792 | 0 | 1397 | 468 | 104 | 0 | 0 | 92 | 0 | 0 | 101.05
24:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 343 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 65 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 31 | 0 | 0 | 120 | 0 | 295 | 182 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 85 | 148 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 143 | 33 | 78 | 0 | 217 | 0 | 0 | 10 | 290 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 399 | 55 | 0 | 0 | 0 | 265 | 54 | 0 | 0 | 75 | 0 | 0 | 25 | 0 | 162 | 34 | 80 | 17 | 0 | 0 |  | 649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 11 | 0 | 204 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 190 | 0 | 0 | 0 |  | 4840 | 2186 | 7026 | 3105 | 649 | 1848 | 0 | 805 | 429 | 105 | 0 | 0 | 85 | 0 | 0 | 101.05
KWH | 0 | 0 | 0 | 4536000 | 0 | 0 | 0 | 8740860 | 1922000 |  | 0 | 6583250 | 3601716 | 0 | 0 | 139481 | 0 | 0 | 0 | 0 | 473328 | 82560 | 136074 | 0 | 0 | 0 | 1115640 | 319662 | 770026 | 462312 | 600000 | 612180 | 804500 | 795800 | 363360 | 0 | 968962 | 964000 | 0 | 0 | 151005 | 0 | 0 | 0 | 0 |  | 276480 | 0 | 183016 | 23880 | 98880 | 922560 | 395136 | 350880 | 0 | 0 | 2885184 | 0 | 7420000 | 4621000 | 1656000 | 2131130 | 650736 | 1295520 | 0 | 1170218 | 0 | 0 | 478598 | 517932 | 224820 | 753000 | 228210 | 2163840 | 3621120 | 0 | 505440 | 12950 | 980000 | 702000 | 1165800 | 0 | 3741054 | 2204000 | 706272 | 1674240 | 0 | 5192660 | 0 | 0 | 251460 | 7238560 | 490704 | 176448 | 0 | 958472 | 0 | 0 | 120000 | 0 | 947520 | 105165 | 1023360 | 183840 | 1572363 | 9344000 | 1381200 | 0 | 344581 | 23521 | 5999236 | 1288132 | 1669381 | 47880 | 1808520 | 59520 | 0 | 1681920 | 314160 | 3090240 | 2083800 | 94782 | 283320 | 200530 | 90240 |  | 14998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1577000 | 424200 | 0 | 0 | 0 | 0 | 44496 | 96266 | 126072 | 53800 | 47963 | 0 | 197760 | 96082 | 492000 | 0 | 233604 | 1896872 | 0 | 0 | 0 | 0 | 0 | 0 | 4515555 | 0 | 266549 | 0 | 4634664 | 0 | 9186618 | 814080 | 0 | 1488672 | 0 | 996412 | 0 | 32409 | 1020768 | 8911000 | 4347627 | 0 | 0 | 32100 |  | 125968127 | 56531114 | 182499241 | 71357049 | 14998545 | 45367692 | 0 | 34431714 | 10807872 | 1932962 | 0 | 628492 | 2163840 | 720835 | 0
Fuel Cost | 0 | 0 | 0 | 6667920 | 0 | 0 | 0 | 8828268.6 | 1979660 |  | 0 | 7175742.5 | 3997904.76 | 0 | 0 | 1180009.26 | 0 | 0 | 0 | 0 | 4316751.36 | 812390.4 | 1254602.28 | 0 | 0 | 0 | 8144172 | 2470987.26 | 7592456.36 | 346734 | 450000 | 0 | 0 | 0 | 3513691.2 | 0 | 261619.74 | 260280 | 0 | 0 | 1402836.45 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1775255.2 | 228054 | 860256 | 7306675.2 | 497871.36 | 1042113.6 | 0 | 0 | 4241220.48 | 0 | 7420000 | 4251320 | 2136240 | 2450799.5 | 735331.68 | 1813728 | 0 | 2001072.78 | 0 | 0 | 4570610.9 | 657773.64 | 168615 | 1317750 | 171157.5 | 16228800 | 3838387.2 | 0 | 641908.8 | 206423 | 1607200 | 1123200 | 2075124 | 0 | 4264801.56 | 2292160 | 1391355.84 | 3197798.4 | 0 | 8983301.8 | 0 | 0 | 512978.4 | 7310945.6 | 368028 | 134100.48 | 0 | 7246048.32 | 0 | 0 | 624000 | 0 | 9323596.8 | 1229378.85 | 8340384 | 1994664 | 11085159.15 | 8689920 | 12596544 | 0 | 3001300.51 | 0 | 45354224.16 | 11219629.72 | 14673858.99 | 477842.4 | 15499016.4 | 396403.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 86391619.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1782010 | 657510 | 0 | 0 | 0 | 0 | 437840.64 | 978062.56 | 1115737.2 | 414260 | 648459.76 | 0 | 1916294.4 | 931995.4 | 944640 | 0 | 176838.228 | 11438138.16 | 0 | 0 | 0 | 0 | 0 | 0 | 5960532.6 | 0 | 399823.5 | 0 | 5422556.88 | 0 | 9094751.82 | 8498995.2 | 0 | 14127497.28 | 0 | 7732157.12 | 0 | 358119.45 | 7543475.52 | 39119290 | 0 | 0 | 0 | 0 |  | 310230354.59 | 206090604.918 | 516320959.508 | 80616261.588 | 86391619.2 | 48604834.92 | 0 | 225554913.2 | 50557428.16 | 521899.74 | 0 | 6051281.4 | 16228800 | 1793921.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 365 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 18 | 25 | 25 | 33 | 33 | 25 | 0 | 32 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 39 | 18 | 2 | 0 | 0 | 120 | 0 | 340 | 204 | 68 | 90 | 29 | 52 | 0 | 43 | 0 | 0 | 25 | 22 | 9 | 30 | 6 | 98 | 151 | 0 | 22 | 2 | 42 | 30 | 53 | 0 | 163 | 140 | 20 | 77 | 0 | 199 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 18 | 90 | 0 | 20 | 387 | 65 | 0 | 34 | 4 | 267 | 54 | 110 | 0 | 66 | 0 | 0 | 104 | 49 | 162 | 108 | 0 | 17 | 30 | 18 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 81 | 0 | 29 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 165 | 0 | 407 | 53 | 0 | 109 | 0 | 34 | 0 | 5 | 35 | 300 | 150 | 0 | 0 | 4 |  | 7811 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 16 | 25 | 0 | 0 | 0 | 54 | 55 | 53 | 18 | 25 | 30 | 33 | 25 | 25 | 0 | 68 | 40 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 0 | 23 | 50 | 18 | 7 | 0 | 0 | 120 | 0 | 265 | 183 | 68 | 90 | 29 | 54 | 0 | 51 | 0 | 0 | 52 | 22 | 0 | 33 | 9 | 105 | 145 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 140 | 32 | 77 | 0 | 218 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 195 | 0 | 0 | 24 | 0 | 147 | 0 | 60 | 17 | 108 | 401 | 115 | 52 | 17 | 0 | 291 | 54 | 110 | 0 | 118 | 10 | 0 | 104 | 0 | 162 | 107 | 0 | 0 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 25 | 0 | 42 | 18 | 16 | 0 | 52 | 36 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 188 | 0 | 414 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 410 | 219 | 0 | 0 | 0 |  | 9173 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 360 | 200 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 80 | 100 | 90 | 50 | 20 | 15 | 0 | 0 | 120 | 0 | 360 | 220 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 200 | 0 | 22 | 0 | 42 | 30 | 50 | 0 | 163 | 144 | 33 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 140 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 0 | 162 | 116 | 100 | 17 |  |  |  | 746 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 68 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 50 | 40 | 52 | 35 | 22 | 0 | 11 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 20 | 5 | 0 | 0 | 120 | 0 | 360 | 220 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 200 | 0 | 22 | 1.6 | 42 | 30 | 50 | 0 | 163 | 144 | 33 | 80 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 300 | 0 | 100 | 200 | 50 | 149 | 20 | 100 | 200 | 140 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 50 | 162 | 116 | 100 | 17 | 30 |  |  | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 0 | 25 | 25 | 33 |  | 0 | 0 | 68 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 5 | 18 | 9 | 0 | 0 | 120 | 0 | 300 | 161 | 68 | 90 | 26 | 30 | 0 | 43 | 0 | 0 | 4 | 22 | 5 | 33 | 8 | 74 | 166 | 0 | 22 | 1 | 41 | 30 | 47 | 0 | 110 | 144 | 20 | 75 | 0 | 217 | 0 | 0 | 10 | 280 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 90 | 0 | 35 | 400 | 48 | 0 | 0 | 1 | 300 | 54 | 62 | 0 | 9 | 0 | 0 | 87 | 16 | 154 | 107 | 70 | 17 | 12 | 0 | 0 | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 193 | 0 | 301 | 28 | 0 | 85 | 0 | 34 | 0 | 2 | 80 | 330 | 162 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 5959 | 5:00
| Highest Generation |  | 9173 | 19:00
| Day Peak Generation |  | 7811 | 12:00
| Evening Peak Generation |  | 9173 | 19:00
| HVDC Max Flow |  | 727 | 10:00
| HVDC EvPeak Flow |  | 727 | 19:00
| Load factor L.F |  | 82.9%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-11-29
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-11-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7811 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5965 | MW
Evening Peak Generation : |  | 9173 | MW Hour : | 19:00 | Available Max Generation : |  | 13301 | MW
E.P. Demand (at gen end) : |  | 9173 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 9173 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4001 | MW
Total Gen. (MKWH) : |  | 182.409 | System Load Factor : | 82.9% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -175 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-11-29
Actual : | 101.02 | Ft.(MSL) , | Rule curve : | 106.2 | Ft.( MSL )
Gas Consumed : | Total = | 892.17 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129221096.508
: |  | Coal : | 50557428.16 | Oil : | 231606194.6 | Total : | 411384719.268
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3351.8782 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1135.5026 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1016.6027 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 918.3129 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 830.0168 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 669.7833 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 380.0709 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 172.5984 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 516.5435 |  |  | 0 | 0%
Total | 0 |  | 8991.3094 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,7
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-1
6) Raozan #02
7) Sirajganj-1,3
8) Ashuganj(N)-360 MW.
9) Shahjibazar GT-8.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Cumilla(N)-Meghnaghat 230 kV Ckt-2 was under shut down from 08:36 to 11:55 for C/M.
b) Fenchuganj-Bibiyana 230 kV Ckt-1 was under shut down from 09:06 to 16:50 for A/M.
c) Feni-Chauddagram 132 kV Ckt-1 was under shut down from 09:06 to 10:48 for C/M.
d) Kabirpur-Manikganj 132 kV Ckt-2 was under shut down from 08:25 to 18:19 for A/M.
e) Kaliakoir-Tangail 132 kV Ckt-1 was under shut down from 09:03 to 10:55 for protection test.
f) Uttara-Mirpur 132 kV Ckt was under shut down from 08:35 to 17:11 for A/M.
g) Bheramara HVDC-Jhenaidah 230 kV Ckt-1 was under shut down from 08:05 to 17:11 for D/W.
h) Amnura 132/33 kV T-1 transformer was under shut down from 08:15 to 13:24 for A/M.
i) Barishal(N) 230/132 kV TR-2 transformer was under shut down from 09:21 to 16:44 for A/M.
j) Khulna(S) 230/132 kV TR-3 transformer was under shut down from 08:30 to 15:49 for A/M.
k) Haripur 360 MW was force shut down at 11:44 due to gas shortage.
l) Barapukuria unit-3 was synchronized at 10:00 and was shut down at 12:58.
m) Kamrangirchar-Keraniganj(N) 132 kV Ckt was under shut down from 09:08 to 17:06 for A/M.
n) Keraniganj-Lalbag 132 kV Ckt-3 was under shut down from 14:54 to 15:46 for D/W.
o) Kabirpur-Manikganj 132 kV Ckt-2 was shut down at 07:25(29-11-2021) for A/M.
p) APR-Shympur 230 kV Ckt tripped at 06:40(29-11-2021) and was switched on at 06:56(29-11-2021).
q) Meghnaghat 450 MW GT-2 tripped at 06:41(29-11-2021) due to grid voltage fluctuation.
r) Shahzibazar 100 MW was synchronized at 22:49.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-11-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4536000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 389 | 8740860 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 1922000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6583250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3601716 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 139481 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 25 | 136074 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 462312 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 473328
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1115640
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 82560 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 319662
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 53 | 770026
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1212180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 804500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 795800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 363360 | Low demand.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 958472 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 147 | 947520
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 0 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1681920
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3090240
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 200530
| Dhaka area Total |  |  |  | 5560 | 2150 | 38937431
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 14 | 151005 | Low demand.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 105165
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 922560
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 108 | 1932962 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 344581 | Low demand.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 183016 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 23880 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 60 | 1023360 | Low demand.
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 395136 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 7 | 350880
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 23 | 98880 | Low demand.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23521
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 291 | 5999236
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1288132
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1669381
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 59520 | Low demand.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2083800
| Chattogram area Total |  |  |  | 2382 | 920 | 16655015
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 120 | 2885184 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4621000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Ashuganj 400 kV Bus S/D
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 7420000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 650736 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1295520
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1656000 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1170218
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 108 | 1572363 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2131130 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 183840 | Low demand.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 517932
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 224820 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 105 | 2163840
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 753000
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 478598
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 228210 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 47880 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 118 | 1808520
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 283320 | 33 kV feeder fault.
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 90240 | On test
| Cumilla Area Total |  |  |  | 3034 | 1324 | 30182351
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3621120 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 505440
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12950
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 24 | 120000 | Low demand.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1381200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 314160
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 276480
| Mymensingh Area Total |  |  |  | 622 | 330 | 6231350
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 980000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 702000 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3741054
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 2204000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1165800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 176448
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 706272 | GT-8 under maint
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1674240
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 94782 | Gas shortage
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 5192660
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 490704
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7238560 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9344000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251460
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2377 | 1481 | 33961980
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 727 | 14998545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 814080
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 832 | 15812625
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 424200 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1577000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 266549 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 410 | 8911000 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 219 | 4347627
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 728 | 15526376
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 44496 | Low demand.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 96266 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 18 | 53800 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 16 | 47963 | Low demand.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4515555 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4634664 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9186618 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 96082 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 492000
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 233604
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 197760
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 126072 | Low demand.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1488672
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1020768
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32100
| Rajshahi Area Total |  |  |  | 2179 | 1224 | 22266420
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1896872
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 996412
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32409
| Rangpur Area Total |  |  |  | 605 | 184 | 2925693
| Total |  |  |  | 20934 | 9173 | 182499241
| Eastern Grid Total |  |  |  | 13975 | 6205 | 125968127
| Western Grid Total |  |  |  | 6959 | 2968 | 56531114
| National Grid Total |  |  |  | 20934 | 9173 | 182499241
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-11-28
(a) ENTIRE EASTERN GRID : |  | 6193 | MW | (b) ENTIRE WESTERN GRID : |  | 2668 | MW
i) Dhaka area |  | 3376 | MW | i) Khulna area |  | 1029 | MW
ii) Chittagong area |  | 1082 | MW | ii) Rajshahi area |  | 839 | MW
iii) Comilla area |  | 760 | MW | iii) Barisal area |  | 237 | MW
iv) Mymensingh area |  | 653 | MW | iv) Rangpur area |  | 563 | MW
v) Sylhet area |  | 322 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8861 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 18:30 | Mymensing | 148 | 18:00 | Jessore | 74 | 18:00
Munsiganj | 62 | 21:00 | Kishoreganj | 88 | 19:00 | Benapol | 36 | 18:00
Sonargaon | 55 | 21:00 | Netrokona | 72 | 18:30 | Jhenida(Old) | 80 | 18:00
Shyampur | 164 | 8:00 | Jamalpur | 94 | 18:00 | Bottail | 90 | 18:00
Bhulta | 159 | 21:00 | Sherpur | 86 | 18:00 | G.K Project | 33 | 18:00
Madanganj | 34 | 10:00 | Srimongal | 35 | 18:00 | Faridpur | 100 | 19:30
Shitalakhya | 104 | 11:00 | Shahjibazar | 76 | 18:00 | Rajbari | 32 | 18:00
Rahim steel | 22 | 9:00 | Fenchuganj | 30 | 17:00 | Madaripur | 61 | 19:00
Matuail | 45 | 18:30 | Kulawara | 24 | 18:00 | Sariatpur | 40 | 20:00
Ghorasal | 55 | 18:00 | Sylhet | 83 | 18:00 | Gopalganj | 62 | 18:00
Narsingdi | 116 | 20:00 | Chatak | 16 | 18:00 | Bagerhat | 64 | 18:30
Haripur (SBU) | 111 | 11:00 | Sunamganj | 28 | 18:00 | Mongla | 52 | 19:30
Sreenagar | 26 | 20:00 | Biani Bazar | 37 | 19:00 | Satkhira | 64 | 18:00
Ullon | 46 | 18:00 | Comilla (S) | 110 | 18:00 | Gallamari | 20 | 10:00
Hasnabad | 58 | 18:30 | Comilla(N) | 75 | 19:00 | Magura | 36 | 18:00
Magbazar | 73 | 15:00 | Chandpur | 44 | 18:00 | Norail | 33 | 18:30
Maniknagar | 52 | 13:00 | Feni | 86 | 19:00 | Chuadanga | 61 | 18:00
Bangabhaban | 8 | 10:00 | Chowmuhani | 126 | 20:00 | Barisal(N) | 27 | 19:30
Motijheel | 20 | 13:00 | Ashuganj | 41 | 14:00 | Barisal (S) | 74 | 18:00
Narinda | 46 | 13:00 | Daudkandi | 86 | 20:00 | Patuakhali | 72 | 21:00
Kazla | 68 | 19:00 | B.Baria | 98 | 20:00 | Bhandaria | 36 | 19:00
Dhanmondi | 130 | 13:00 | Ramganj | 50 | 19:30 | Borguna | 12 | 19:30
Lalbag | 84 | 13:00 | Chaddagram | 23 | 18:00 | Borhan Uddin | 27 | 21:00
Madartek | 46 | 18:00 | PHP | 3 | 13:00 | Ishurdi | 41 | 20:00
Dhaka University | 24 | 12:00 | Kochua | 36 | 18:00 | Ruppur Paromanobik | 3 | 20:00
Aftabnagar | 12 | 13:00 | Madunaghat | 39 | 18:00 | Natore | 91 | 18:00
Fatullah | 50 | 10:00 | Hathazari | 66 | 18:00 | Bogra | 102 | 18:00
Nawabganj | 31 | 20:00 | Khulshi | 152 | 14:00 | Noagaon | 80 | 18:00
Keraniganj | 46 | 13:00 | Halishahar | 82 | 18:00 | Rajshahi | 93 | 19:00
Banani | 39 | 12:00 | Baraulia | 137 | 13:00 | Rajshahi New | 13 | 20:00
Mirpur | 92 | 18:00 | Sikalbaha | 33 | 18:30 | C.Nawabganj | 39 | 20:00
Kalyanpur | 66 | 18:00 | Dohazari | 72 | 19:00 | Amnura | 31 | 18:00
Gulshan | 74 | 13:00 | Cox'sbazar | 66 | 19:30 | Pabna | 68 | 18:00
Uttara | 62 | 13:00 | Chandraghona | 18 | 18:00 | Shahjadpur | 64 | 19:30
Uttara New | 7 | 18:00 | Kaptai | 3.5 | 18:00 | Serajganj | 60 | 18:00
Kamrangirchar | 80 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 37 | 18:00
Savar | 126 | 18:00 | Bakulia | 90 | 18:00 | Joypurhat | 45 | 18:00
Bhasantec | 76 | 18:00 | Julda | 20 | 9:00 | Sherpur(Bogura) | 42 | 18:00
Agargaon | 48 | 13:00 | TK chemical | 14.5 | 17:00 | Mohastangor | 42 | 18:00
Satmosjid | 76 | 13:00 | Modern Steel | 0 | 1:00 | Bhangura | 18 | 18:00
Tongi | 100 | 20:00 | Shahmirpur | 23.5 | 18:30 | Rangpur | 93 | 18:00
Kabirpur | 177 | 12:00 | Khagrachhari | 20 | 17:00 | Lalmonirhat | 43 | 18:00
Basundhara | 162 | 13:00 | Matarbari | 22 | 17:00 | Saidpur | 80 | 18:00
Purbachal | 12 | 18:00 | Baroiar Hat | 30 | 18:00 | Purbasadipur | 87 | 18:30
Manikganj | 54 | 20:00 | Rangamati | 10 | 18:00 | Thakurgaon | 66 | 18:00
Joydevpur | 146 | 18:00 | Abul Khair 230 | 110 | 23:00 | Palashbari | 82 | 18:00
New Tongi | 66 | 12:00 | BSRM | 154 | 18:00 | Barapukuria | 37 | 20:00
Kodda | 206 | 18:30 | GPH Ispat | 95 | 16:00 | Panchagar | 41 | 18:00
Dhamrai | 64 | 18:30 | Agrabad | 64 | 18:00 | Joldhaka | 26 | 18:00
Rajendrapur | 80 | 18:00 | Goalpara | 24 | 13:00 | Kurigram | 43 | 18:00
Valuka | 72 | 18:00 | Central S/S | 75 | 18:00 | Mithapukur | 22 | 18:00
Tangail | 126 | 21:00 | Noapara | 38 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-11-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 415 | 20:00 | 404 | 12:00 | Kaliakoir | 405 | 0.70833 | 390 | 0.5
| Bheramara | 406 | 1:00 | 394 | 10:00 | Bhulta | 378 | 0.041667 | 356 | 0.66667
| Ashuganj(N) | 0 | 12:00 | 0 | 1:00 | Gopalganj | 414 | 0.625 | 404 | 0.875
| Payra | 416 | 22:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 15:00 | 238 | 1:00 | Hathazari | 241 | 20:00 | 228 | 9:00
| Ishurdi | 239 | 3:00 | 228 | 16:00 | Megnaghat | 235 | 6:00 | 229 | 11:00
| Ashuganj | 247 | 22:00 | 236 | 12:00 | Fenchuganj | 246 | 19:00 | 240 | 12:00
| Serajganj | 238 | 20:00 | 233 | 16:00 | Siddhirganj | 235 | 22:00 | 223 | 12:00
| Baghabari | 238 | 21:00 | 230 | 12:00 | Maniknagar | 234 | 22:00 | 222 | 12:00
| Barapukuria | 236 | 14:00 | 228 | 7:00 | Agargaon | 235 | 9:00 | 223 | 12:00
| Bogra | 235 | 22:00 | 226 | 8:00 | Barisal | 246 | 11:00 | 239 | 19:30
| Rajshahi | 236 | 3:00 | 224 | 12:00 | Bhola 225 MW | 247 | 9:00 | 243 | 11:00
| Khulna South | 244 | 18:30 | 228 | 7:00 | AKSML | 241 | 11:00 | 219 | 5:00
| Rampura | 232 | 5:00 | 221 | 16:00 | BSRM | 237 | 17:00 | 222 | 5:00
| Haripur | 234 | 18:30 | 222 | 12:00 | Bibiyana | 246 | 18:30 | 239 | 4:00
| Hasnabad | 233 | 21:00 | 222 | 13:00 | Bhulta | 235 | 1:00 | 222 | 12:00
| Shyampur | 233 | 22:00 | 222 | 6:00 | Ashuganj (S) | 242 | 18:30 | 232 | 12:00
| Aminbazar | 236 | 1:00 | 223 | 2:00 | Kaliakoir | 236 | 20:00 | 222 | 12:00
| Tongi | 232 | 18:00 | 215 | 16:00 | GPH | 239 | 11:00 | 218 | 5:00
| Comilla (N) | 238 | 18:30 | 228 | 12:00 | Jhenaidah | 236 | 2:00 | 224 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 20:00 | 131 | 11:00 | Kachua | 141 | 0.70833 | 137 | 0.5
| Munsiganj | 140 | 19:30 | 131 | 12:00 | Madanhat | 142 | 0.79167 | 137 | 0.33333
| Sonargaon | 136 | 21:00 | 131 | 10:00 | Hathazari | 140 | 0.125 | 135 | 0.375
| Shyampur | 140 | 6:00 | 133 | 12:00 | Khulshi | 138 | 0.91667 | 132 | 0.41667
| Bhulta | 133 | 3:00 | 127 | 12:00 | Halishahar | 138 | 0.70833 | 128 | 0.20833
| Madanganj | 139 | 20:00 | 130 | 16:00 | Baraulia | 141 | 0.95833 | 136 | 0.41667
| Shitalakhya | 140 | 18:30 | 131 | 12:00 | Sikalbaha | 141 | 0.70833 | 129 | 0.16667
| Rahim steal | 137 | 1:00 | 132 | 13:00 | Dohazari | 137 | 0.70833 | 129 | 0.41667
| Matuail | 138 | 20:00 | 131 | 11:00 | Cox'sbazar | 123 | 0.25 | 115 | 0.5
| Ghorasal | 140 | 1:00 | 135 | 15:00 | Chandraghona | 141 | 0.75 | 131 | 0.16667
| Narsinghdi | 136 | 5:00 | 132 | 12:00 | Kaptai | 140 | 0.79167 | 135 | 0.45833
| Haripur (SBU) | 138 | 20:00 | 131 | 12:00 | A. Khaer Stl. | 137 | 0.041667 | 135 | 0.29167
| Sreenagar | 138 | 6:00 | 129 | 11:00 | Bakulia | 139 | 0.70833 | 128 | 0.20833
| Ullon | 135 | 1:00 | 127 | 12:00 | Julda | 140 | 0.70833 | 134 | 0.5
| Hasnabad | 140 | 18:00 | 131 | 11:00 | TK Chemical | 139 | 0.70833 | 131 | 0.16667
| Magbazar | 135 | 2:00 | 126 | 12:00 | Modern Steel | 139 | 0.75 | 134 | 0.5
| Maniknagar | 137 | 1:00 | 130 | 12:00 | Shahmirpur | 139 | 0.70833 | 134 | 0.041667
| Bangabhaban | 137 | 1:00 | 130 | 12:00 | Khagrachhari | 139 | 0.70833 | 130 | 0.16667
| Motijheel | 137 | 1:00 | 130 | 12:00 | Matarbari | 123 | 0.25 | 112 | 0.75
| Narinda | 137 | 1:00 | 130 | 12:00 | Baroiar Hat | 140 | 7:00 | 134 | 18:30
| Kazla | 137 | 1:00 | 130 | 12:00 | Rangamati | 140 | 18:00 | 133 | 4:00
| Dhanmondi | 138 | 19:30 | 131 | 12:00 | Agrabad | 137 | 7:00 | 128 | 0.125
| Lalbag | 134 | 1:00 | 125 | 16:00 | Goalpara S/S | 138 | 3:00 | 129 | 0.66667
| Madartek | 135 | 1:00 | 126 | 12:00 | Khulna Central S/S | 137 | 17:00 | 126 | 0.29167
| Dhaka University | 136 | 6:00 | 127 | 12:00 | Noapara | 139 | 17:00 | 129 | 0.66667
| Aftabnagar | 135 | 1:00 | 127 | 12:00 | Jessore | 138 | 0.70833 | 129 | 0.66667
| Fatullah | 140 | 18:30 | 132 | 16:00 | Benapol | 138 | 1:00 | 129 | 0.66667
| Nawabganj | 138 | 22:00 | 130 | 12:00 | Jhenida(Old) | 140 | 0.91667 | 131 | 0.66667
| Keraniganj | 138 | 22:00 | 130 | 12:00 | Bottail | 137 | 0.70833 | 130 | 0.66667
| Banani | 136 | 22:00 | 127 | 12:00 | G.K Project | 139 | 0.20833 | 133 | 0.66667
| Mirpur | 134 | 7:00 | 127 | 11:00 | Faridpur | 139 | 0.70833 | 132 | 0.41667
| Kalyanpur | 134 | 1:00 | 126 | 15:00 | Rajbari | 137 | 0.125 | 132 | 0.41667
| Gulshan | 134 | 1:00 | 126 | 12:00 | Madaripur | 142 | 8:00 | 139 | 0.041667
| Uttara | 135 | 22:00 | 126 | 11:00 | Shariyatpur S/S | 143 | 0.29167 | 138 | 0.8125
| Uttara New | 134 | 7:00 | 126 | 15:00 | Gopalganj | 143 | 4:00 | 137 | 0.5
| Kamrangirchar | 138 | 5:00 | 124 | 15:00 | Bagerhat | 135 | 3:00 | 124 | 0.29167
| Savar | 134 | 2:00 | 127 | 11:00 | Mongla | 136 | 18:00 | 123 | 7:00
| Bhasantec | 138 | 6:00 | 129 | 15:00 | Satkhira | 136 | 0.70833 | 125 | 7:00
| Agargaon | 138 | 6:00 | 130 | 12:00 | Gallamari | 142 | 4:00 | 132 | 0.5
| Satmosjid | 137 | 1:00 | 129 | 15:00 | Magura | 141 | 0.125 | 131 | 0.66667
| Tongi | 140 | 18:00 | 129 | 12:00 | Narail | 138 | 21:00 | 131 | 0.45833
| Kabirpur | 137 | 17:00 | 133 | 14:00 | Chuadanga | 137 | 3:00 | 128 | 0.29167
| Basundhara | 139 | 20:00 | 126 | 16:00 | Barisal(N) | 143 | 9:00 | 138 | 18:00
| Purbachal | 140 | 22:00 | 131 | 12:00 | Barisal (S) | 141 | 0.083333 | 137 | 0.5
| Manikganj | 140 | 18:00 | 130 | 12:00 | Patuakhali(S) | 140 | 0.20833 | 134 | 0.79167
| Joydevpur | 140 | 20:00 | 127 | 16:00 | Bhandaria | 142 | 0.25 | 135 | 0.875
| New Tongi | 140 | 20:00 | 124 | 12:00 | Borguna | 142 | 4:00 | 136 | 18:30
| Kodda | 139 | 22:00 | 129 | 12:00 | Jhenaidah(New) | 138 | 2:00 | 132 | 7:00
| Dhamrai | 137 | 18:00 | 121 | 11:00 | Ishurdi | 138 | 17:00 | 132 | 12:00
| Rajendrapur | 136 | 22:00 | 126 | 16:00 | Ruppur Paromanobik | 137 | 6:00 | 132 | 12:00
| Valuka | 132 | 18:30 | 127 | 14:00 | Natore | 139 | 19:00 | 132 | 10:00
| Tangail | 138 | 6:00 | 130 | 12:00 | Bogra | 139 | 20:00 | 132 | 8:00
| Mymensing | 133 | 18:30 | 129 | 16:00 | Noagaon | 136 | 20:00 | 128 | 7:00
| Kishorganj | 135 | 6:00 | 131 | 18:00 | Rajshahi | 139 | 18:30 | 130 | 10:00
| Netrokona | 132 | 6:00 | 128 | 13:00 | Rajshahi New | 141 | 17:00 | 132 | 12:00
| Jamalpur | 140 | 18:00 | 127 | 3:00 | C.Nawabganj | 139 | 18:30 | 131 | 10:00
| Sherpur | 138 | 18:30 | 126 | 4:00 | Amnura | 139 | 18:00 | 131 | 12:00
| Srimongal | 140 | 9:00 | 137 | 12:00 | Pabna | 138 | 6:00 | 132 | 12:00
| Shahjibazar | 138 | 17:00 | 136 | 10:00 | Shahjadpur | 142 | 17:00 | 136 | 10:00
| Fenchuganj | 139 | 6:00 | 136 | 3:00 | Serajganj | 138 | 20:00 | 132 | 10:00
| Khulawara | 138 | 1:00 | 136 | 13:00 | Niyamatpur | 135 | 20:00 | 129 | 8:00
| Sylhet | 135 | 1:00 | 134 | 5:00 | Joypurhat | 137 | 20:00 | 130 | 7:00
| Chatak | 137 | 1:00 | 135 | 12:00 | Sherpur(Bogura) | 138 | 20:00 | 132 | 7:00
| Sunamganj | 135 | 6:00 | 133 | 11:00 | Mohastangor | 139 | 20:00 | 132 | 7:00
| Biani Bazar | 136 | 01:00 | 134 | 12:00 | Bangura | 140 | 20:00 | 134 | 16:00
| Comilla(s) | 129 | 24:00 | 123 | 18:00 | Rangpur | 134 | 17:00 | 126 | 7:00
| Comilla(n) | 144 | 18:30 | 139 | 12:00 | Lalmonirhat | 132 | 17:00 | 123 | 7:00
| Chandpur | 142 | 1:00 | 138 | 11:00 | Saidpur | 132 | 6:00 | 125 | 7:00
| Feni | 141 | 18:30 | 133 | 5:00 | Purbasadipur | 132 | 17:00 | 124 | 18:00
| Chowmuhani | 141 | 17:00 | 132 | 4:00 | Thakurgaon | 130 | 6:00 | 122 | 18:00
| Ashuganj | 140 | 18:00 | 138 | 13:00 | Palashbari | 135 | 17:00 | 127 | 10:00
| Daudkandi | 139 | 17:00 | 136 | 10:00 | Barapukuria | 136 | 0.66667 | 128 | 0.29167
| B.Baria | 137 | 6:00 | 133 | 12:00 | Panchagar | 133 | 0.70833 | 124 | 0.75
| Ramganj | 140 | 22:00 | 137 | 14:00 | Joldhaka | 132 | 0.70833 | 124 | 0.75
| Chaddagram | 142 | 18:00 | 135 | 5:00 | Kurigram | 133 | 0.70833 | 124 | 0.29167
| PHP | 141 | 18:00 | 132 | 5:00 | Mithapukur | 137 | 0.83333 | 130 | 0.29167

## L-Curve
Date | 2021-11-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 170 | 4840 | 2186 | 7026 |  |  |  | QF-LDC-11
0:30 | 96 | 4882 | 2060 | 6942 | Date: | 2021-11-28
1:00 | 22 | 4924 | 1934 | 6858
1:30 | 56 | 4705 | 1944.5 | 6649.5
2:00 | 90 | 4486 | 1955 | 6441
2:30 | 123 | 4369.5 | 1948 | 6317.5 | [5 empty] | Gen. at Eve. Peak | 9173 | 9173 MW (19:00 )
3:00 | 156 | 4253 | 1941 | 6194 | [6 empty] | 19:00
3:30 | 186 | 4247.5 | 1919.5 | 6167 | [5 empty] | Gen. at Day Peak | 7811 | 7811 MW (12:00 )
4:00 | 216 | 4242 | 1898 | 6140 | [6 empty] | 12:00
4:30 | 173 | 4172 | 1877.5 | 6049.5 | [5 empty] | Highest Generation | 9173
5:00 | 130 | 4102 | 1857 | 5959 | [6 empty] | 19:00
5:30 | 67 | 4155.5 | 1824 | 5979.5
6:00 | 4 | 4209 | 1791 | 6000
6:30 | 78 | 4401.5 | 1819 | 6220.5
7:00 | 152 | 4594 | 1847 | 6441
7:30 | 163.5 | 4780.5 | 1925 | 6705.5
8:00 | 175 | 4967 | 2003 | 6970
8:30 | 195.5 | 5002.5 | 2083.5 | 7086
9:00 | 216 | 5038 | 2164 | 7202
9:30 | 267 | 5025 | 2176.5 | 7201.5
10:00 | 318 | 5012 | 2189 | 7201
10:30 | 347.5 | 5062 | 2227 | 7289
11:00 | 377 | 5112 | 2265 | 7377
11:30 | 371.5 | 5262.5 | 2331.5 | 7594
12:00 | 366 | 5413 | 2398 | 7811
12:30 | 370 | 5443.5 | 2469.5 | 7913
13:00 | 374 | 5474 | 2541 | 8015
13:30 | 363.5 | 5395 | 2470 | 7865
14:00 | 353 | 5316 | 2399 | 7715
14:30 | 391 | 5302.5 | 2330.5 | 7633
15:00 | 429 | 5289 | 2262 | 7551
15:30 | 408 | 5284 | 2234.5 | 7518.5
16:00 | 387 | 5279 | 2207 | 7486
16:30 | 325 | 5317 | 2245 | 7562
17:00 | 263 | 5355 | 2283 | 7638
17:30 | 146.5 | 5824.5 | 2538.5 | 8363
18:00 | 30 | 6294 | 2794 | 9088
18:30 | 92 | 6249.5 | 2881 | 9130.5
19:00 | 154 | 6205 | 2968 | 9173
19:30 | 146 | 6171 | 2943 | 9114
20:00 | 108 | 6093 | 2883 | 8976 |  |  |  | Executive Engineer
20:30 | 120 | 6012.5 | 2835 | 8847.5 |  |  |  | Network Operation Division
21:00 | 132 | 5932 | 2787 | 8719
21:30 | 96 | 5778 | 2650 | 8428
22:00 | 60 | 5624 | 2513 | 8137 |  |  |  |  | Page 6 of 7
22:30 | 128 | 5456 | 2438 | 7894
23:00 | 196 | 5288 | 2363 | 7651
23:30 | 183 | 5064 | 2274.5 | 7338.5
24:00 | 170 | 4840 | 2186 | 7026
9173 MW (19:00 )
7811 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-11-28 |  | Energy |  | 182499241
[13 empty] | 2021-11-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3105 | 649 | 1848 | 0 | 805 | 429 | 105 | 0 | 0 | 85 | 0 | 0
0:30 | 3027.5 | 546.5 | 1910 | 0 | 875.5 | 405 | 89 | 0 | 6 | 82.5 | 0 | 0 | Date: | 2021-11-28
1:00 | 2950 | 444 | 1972 | 0 | 946 | 381 | 73 | 0 | 12 | 80 | 0 | 0
1:30 | 2951 | 444 | 1995.5 | 0 | 714.5 | 380.5 | 73 | 0 | 12 | 79 | 0 | 0 | [8 empty] | Total Energy | 182.4992 | Total Energy Gen 182.499 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.499 MKWHr
2:00 | 2952 | 444 | 2019 | 0 | 483 | 380 | 73 | 0 | 12 | 78 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2956.5 | 444 | 2023.5 | 0 | 365.5 | 366 | 72.5 | 0 | 12.5 | 77 | 0 | 0 | [8 empty] | Energy Requirement | 182.4992
3:00 | 2961 | 444 | 2028 | 0 | 248 | 352 | 72 | 0 | 13 | 76 | 0 | 0
3:30 | 2963 | 444 | 2001 | 0 | 248 | 352 | 72 | 0 | 12 | 75 | 0 | 0 | [6 empty] | Shortage
4:00 | 2965 | 444 | 1974 | 0 | 248 | 352 | 72 | 0 | 11 | 74 | 0 | 0
4:30 | 2948 | 444 | 1943.5 | 0 | 206.5 | 351.5 | 72 | 0 | 11 | 73 | 0 | 0
5:00 | 2931 | 444 | 1913 | 0 | 165 | 351 | 72 | 0 | 11 | 72 | 0 | 0
5:30 | 2843.5 | 444 | 1961 | 0 | 217.5 | 360.5 | 72 | 0 | 10.5 | 70.5 | 0 | 0
6:00 | 2756 | 444 | 2009 | 0 | 270 | 370 | 72 | 0 | 10 | 69 | 0 | 0
6:30 | 2780 | 444 | 2018 | 0 | 451 | 375.5 | 72 | 0 | 9 | 68 | 3 | 0 |  |  |  |  | Coal
7:00 | 2804 | 444 | 2027 | 0 | 632 | 381 | 72 | 0 | 8 | 67 | 6 | 0
7:30 | 2826.5 | 444 | 1964.5 | 0 | 907.5 | 395 | 72 | 0 | 6.5 | 71.5 | 18 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2849 | 444 | 1902 | 0 | 1183 | 409 | 72 | 0 | 5 | 76 | 30 | 0
8:30 | 2853.5 | 493.5 | 1864.5 | 0 | 1260 | 404.5 | 72 | 0 | 5 | 80.5 | 52.5 | 0
9:00 | 2858 | 543 | 1827 | 0 | 1337 | 400 | 72 | 0 | 5 | 85 | 75 | 0
9:30 | 2881.5 | 635 | 1816.5 | 0 | 1208.5 | 397.5 | 72 | 0 | 3.5 | 87 | 88 | 0
10:00 | 2905 | 727 | 1806 | 0 | 1080 | 395 | 72 | 0 | 2 | 89 | 101 | 0
10:30 | 2913 | 727 | 1801.5 | 0 | 1131 | 416 | 72 | 0 | 1 | 91.5 | 107 | 0
11:00 | 2921 | 727 | 1797 | 0 | 1182 | 437 | 72 | 0 | 0 | 94 | 113 | 0
11:30 | 2955 | 727 | 1794.5 | 0 | 1387.5 | 423.5 | 72 | 0 | 0 | 96 | 112.5 | 0
12:00 | 2989 | 727 | 1792 | 0 | 1593 | 410 | 72 | 0 | 0 | 98 | 112 | 0
12:30 | 2999 | 727 | 1803 | 0 | 1661.5 | 425.5 | 72 | 0 | 0 | 100 | 110.5 | 0
13:00 | 3009 | 727 | 1814 | 0 | 1730 | 441 | 72 | 0 | 0 | 102 | 109 | 0
13:30 | 3009 | 727 | 1814 | 0 | 1730 | 441 | 72 | 0 | 0 | 102 | 109 | 0
14:00 | 3009 | 727 | 1814 | 0 | 1730 | 441 | 72 | 0 | 0 | 102 | 109 | 0
14:30 | 2949.5 | 727 | 1768 | 0 | 1665 | 411 | 72.5 | 0 | 0 | 100 | 84.5 | 0
15:00 | 2890 | 727 | 1722 | 0 | 1600 | 381 | 73 | 0 | 0 | 98 | 60 | 0
15:30 | 2911.5 | 727 | 1723.5 | 0 | 1562 | 380.5 | 73 | 0 | 0 | 98 | 43 | 0
16:00 | 2933 | 727 | 1725 | 0 | 1524 | 380 | 73 | 0 | 0 | 98 | 26 | 0
16:30 | 2892.5 | 727 | 1693.5 | 0 | 1643.5 | 379.5 | 90.5 | 0 | 24 | 98.5 | 13 | 0
17:00 | 2852 | 727 | 1662 | 0 | 1763 | 379 | 108 | 0 | 48 | 99 | 0 | 0
17:30 | 2889.5 | 727 | 1772.5 | 0 | 2234 | 403.5 | 108 | 0 | 124 | 104.5 | 0 | 0
18:00 | 2927 | 727 | 1883 | 0 | 2705 | 428 | 108 | 0 | 200 | 110 | 0 | 0
18:30 | 2955.5 | 727 | 1876.5 | 0 | 2712.5 | 458.5 | 108 | 0 | 185 | 107.5 | 0 | 0
19:00 | 2984 | 727 | 1870 | 0 | 2720 | 489 | 108 | 0 | 170 | 105 | 0 | 0
19:30 | 3006 | 727 | 1868 | 0 | 2656 | 499 | 107 | 0 | 145 | 106 | 0 | 0
20:00 | 3010 | 727 | 1877 | 0 | 2579 | 498 | 106 | 0 | 76 | 103 | 0 | 0
20:30 | 3058.5 | 727 | 1870 | 0 | 2439 | 497.5 | 107 | 0 | 46.5 | 102 | 0 | 0
21:00 | 3107 | 727 | 1863 | 0 | 2299 | 497 | 108 | 0 | 17 | 101 | 0 | 0
21:30 | 3076 | 727 | 1824.5 | 0 | 2100.5 | 487 | 105.5 | 0 | 8.5 | 99 | 0 | 0
22:00 | 3045 | 727 | 1786 | 0 | 1902 | 477 | 103 | 0 | 0 | 97 | 0 | 0
22:30 | 3058 | 727 | 1789 | 0 | 1649.5 | 472.5 | 103.5 | 0 | 0 | 94.5 | 0 | 0
23:00 | 3071 | 727 | 1792 | 0 | 1397 | 468 | 104 | 0 | 0 | 92 | 0 | 0
23:30 | 3088 | 688 | 1820 | 0 | 1101 | 448.5 | 104.5 | 0 | 0 | 88.5 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 29.9° C
24:00 | 3105 | 649 | 1848 | 0 | 805 | 429 | 105 | 0 | 0 | 85 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 182.499 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.499 MKWHr
Note on W13: Author:

## Generation
g | 2021-11-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 68 | 68 |  | 68 | 67 | 66 | 68 | 63 | 64 | 65 | 968962
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 14 | 16 | 16 | 16 | 8 | 8 | 8 | 151005
| Teknaf 20MW PP (Solartech) | [8 empty] | 14 | 17 | 19 | 18 | 17 | 14 | 10 | 5 | [10 empty] | 105165
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 34 | 17 |  |  |  | 183016
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 34 | 55 | 34 | 34 | 34 | 34 | 34 |  | 17 | [6 empty] | 344581
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 8 | 175 |  | 195 | 195 | 195 | 145 | 95 |  |  | 958472
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1656000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4536000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2885184
32 | Ashuganj 50 MW PP | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 29 | 26 | 29 | 29 | 27 | 27 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 650736
33 | Ashuganj 225 MW CCPP | 184 | 184 | 184 | 185 | 193 | 183 | 190 | 190 | 183 | 222 | 223 | 204 | 182 | 182 | 183 | 205 | 181 | 186 |  | 183 | 183 | 183 | 183 | 183 | 183 | 182 | 4621000
34 | Ashuganj 450 MW CCPP(South) | 305 | 300 | 305 | 305 | 305 | 285 | 285 | 315 | 305 | 305 | 305 | 340 | 305 | 300 | 300 | 325 | 265 | 270 |  | 265 | 265 | 265 | 350 | 295 | 295 | 295 | 7420000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 54 | 51 | 51 | 53 | 53 | 53 | 55 | 56 | 52 | 51 | 54 | 55 | 52 | 52 | 56 |  | 54 | 54 | 55 | 55 | 54 | 54 | 55 | 1295520
36 | Chandpur 150 MW CCPP | 88 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 88 | 88 | 88 | 90 | 88 | 90 | 90 | 90 | 87 | 90 |  | 90 | 90 | 89 | 90 | 90 | 90 | 90 | 2131130
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 343 | 338 | 339 | 338 | 349 | 356 | 349 | 361 | 365 | 366 | 318 | 365 | 367 | 374 | 368 | 353 | 315 | 350 |  | 389 | 395 | 395 | 393 | 393 | 393 | 343 | 8740860
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6583250
41 | Haripur 360MW CCPP(HPL) | 144 | 173 | 192 | 213 | 232 | 231 | 212 | 140 | 126 | 99 | 74 | [15 empty] | 1922000
42 | RPCL 210MW CCPP | 152 | 166 | 166 | 166 | 166 | 168 | 168 | 166 | 166 | 161 | 158 | 151 | 147 | 142 | 142 | 142 | 148 | 149 |  | 145 | 145 | 145 | 147 | 149 | 148 | 148 | 3621120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 17 | 33 | 43 | 48 | 49 | 47 | 37 | 26 | 11 | 0 | [9 empty] | 314160
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 980000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 702000
46 | Shajibazar 330 MW CCPP | 98 | 95 | 95 | 95 | 96 | 7 | 0 | 8 | 8 | 8 | 50 | 140 | 142 | 145 | 142 | 141 | 141 | 143 |  | 140 | 142 | 140 | 142 | 140 | 143 | 143 | 2204000
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 33 | 33 | 20 | 34 | 33 | 33 | 20 | 32 | 32 | 20 | 31 | 20 | 20 | 20 | 32 | 32 |  | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 706272
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 40 | 10 | 10 | 75 | 75 | 75 | 75 | 75 | 75 | 77 | 77 | 77 | 77 | 77 | 78 | 78 |  | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 1674240
| Shahjibazar 100 MW GTPP | [24 empty] | 40 | 80 | 94782
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 218 | 217 | 217 | 217 | 190 | 191 | 191 | 218 | 218 | 218 | 199 | 219 | 219 | 219 | 219 | 218 | 218 |  | 218 | 218 | 218 | 218 | 217 | 217 | 217 | 5192660
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251460
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 2 | 2 | 2 | 2 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 176448
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 8 | 8 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1165800
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 490704
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 290 | 300 | 300 | 305 | 310 | 300 | 285 | 290 | 295 | 300 | 310 | 270 | 295 | 300 | 285 | 290 |  | 280 | 295 | 290 | 290 | 270 | 280 | 290 | 7238560
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 10 | 35 | 35 | 35 | 35 | 35 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 54 | 54 | 54 | 54 |  | 770026
59 | Tangail Palli Power Gen 22 MW | [11 empty] | 10 | 24 | 24 | 24 | 22 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 |  |  | 276480
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 395136
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 462312
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 505440
63 | Impoprt (Tripura) | 80 | 78 | 76 | 74 | 72 | 69 | 67 | 76 | 85 | 89 | 94 | 98 | 102 | 103 | 98 | 98 | 99 | 110 |  | 105 | 106 | 103 | 101 | 97 | 92 | 85 | 2163840
64 | Malancha, Ctg. EPZ (United) | 24 | 26 | 33 | 34 | 34 | 34 | 20 | 10 | 2 | 2 | 2 | 2 | 8 | 6 | 2 | 2 | 3 | 4 |  | 7 | 2 | 4 | 5 | 22 | 26 | 31 | 350880
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 517932
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  | 5 | 11 | 11 | 11 | 11 | 11 | 224820
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 28 | 33 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 28 | 28 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 753000
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 228210
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 28 | 25 | 25 | 25 | 22 | 21 | 21 | 21 | 21 | 29 |  | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 612180
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 795800
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [16 empty] | 17 | 34 | [8 empty] | 47880
| Chowmuhani 113 MW | 115 | 26 | 8 | 8 |  | 13 | 65 | 65 | 65 | 45 | 57 | 66 | 68 | 68 | 67 | 67 | 87 | 115 |  | 118 | 118 | 116 | 115 | 117 | 117 | 75 | 1808520
| Manikgonj 162MW PP(MPGL) | 162 | 17 |  |  |  | 10 | 71 | 144 | 152 | 162 | 138 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3090240
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [10 empty] | 2 | 25 | 33 | 42 | 42 | 42 | 42 | 52 |  | 25 | 25 | 25 |  |  |  |  | 363360
79 | Kodda 150MW PP | [16 empty] | 16 | 48 |  | 16 | 16 | [5 empty] | 82560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 7 | 8 | 8 | 13 | 25 | 38 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 25 |  |  |  |  | 478598
| Gazipur 100 MW PP | [16 empty] | 5 | 52 |  | 52 | 52 | 52
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 23521
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1288132
| Karnaphuli Power Ltd. | 17 | 17 |  |  |  | 4 | 18 | 34 | 53 | 51 | 69 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 68 |  | 1669381
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 10 | 24 |  | 25 | 25 | 24 | 25 | 23 |  |  | 136074
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3601716
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 50 |  |  |  |  | 6 | 18 | 34 | 43 | 53 | 59 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 25 | 1681920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 10 | 10 | [8 empty] | 23880
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1170218
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 2 | 102 |  | 102 | 102 | 102 | 102 | 48 |  |  | 473328
95 | Patenga 50MW PP (Baraka) | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 36 | 39 | 40 | 39 | 41 | 50 | 50 | 50 | 43 | 45 |  | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 922560
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | [12 empty] | 5 | 16 |  | 23 | 10 | [5 empty] | 98880
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 4 | 30 |  | 30 | 30 | 30 |  |  |  |  | 139481
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 17 | 17 |  |  | 23 | 55 |  | 55 | 55 | 55 | 55 |  |  |  | 319662
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 163 | 110 | 163 | 163 | 163 | 130 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 110 | 163 |  | 163 | 163 | 163 | 163 | 163 | 130 | 163 | 3741054
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12950
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 35 | 35 | 17 | 17 | 17 | 54 | 54 | 35 | 49 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 1115640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 5 | 24 |  | 24 | 24 | 24 | 8 |  |  |  | 120000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 8 | 17 | 52 | 52 | 52 | 54 | 52 | 54 | 122 |  | 147 | 113 | 117 | 104 | 71 |  |  | 947520
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 10 | 30 | 10 | 88 | 90 | 90 | 90 | 90 | 90 | 100 | 100 |  | 60 | 60 | 60 | 60 | 30 | 10 | 0 | 1023360
116 | Chandpur 200MW (Desh energy) | [12 empty] | 8 | 17 | 17 | 17 | 19 | 51 |  | 17 | [6 empty] | 183840
117 | Ashuganj 150MW PP (Midland) | 50 |  |  |  |  | 3 | 55 | 97 | 110 | 50 | 50 | 20 | 20 | 20 | 20 | 10 | 15 | 55 |  | 108 | 133 | 130 | 137 | 140 | 138 | 50 | 1572363
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 400 | 399 | 399 | 340 | 395 | 399 | 399 | 376 | 400 | 387 | 402 | 352 | 352 | 352 | 388 | 401 |  | 401 | 400 | 400 | 400 | 400 | 400 | 399 | 9344000
| Jamalpur 115 MW PP (United) | 35 | 35 | 16 | 16 | 8 | 8 | 16 | 52 | 65 | 45 | 50 | 65 | 65 | 45 | 45 | 45 | 63 | 115 |  | 115 | 115 | 115 | 85 | 85 | 65 | 55 | 1381200
| Anwara 300 MW PP (United) | 285 | 210 | 65 | 65 | 45 | 100 | 210 | 275 | 287 | 286 | 230 | 267 | 270 | 286 | 286 | 286 | 283 | 286 |  | 291 | 291 | 286 | 286 | 286 | 300 | 265 | 5999236
| Juldah unit-2 (Acorn) | [16 empty] | 10 | 40 |  | 10 | [6 empty] | 59520
| Anlima Energy Ltd. | 70 | 17 | 17 | 17 |  | 14 | 57 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 106 | 107 |  | 107 | 107 | 107 | 105 | 108 | 108 | 34 | 2083800
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 10 | 17 | 17 | 283320
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 11 | 20 | 26 | 30 | 30 | 30 | 25 | 17 | 8 | 0 | [9 empty] | 200530
| Chandpur 115(Doreen) | [9 empty] | 24 | 34 | 18 | 11 | [13 empty] | 90240
120 | Eastern Zone Total | 4924 | 4486 | 4253 | 4242 | 4102 | 4209 | 4594 | 4967 | 5038 | 5012 | 5112 | 5413 | 5474 | 5316 | 5289 | 5279 | 5355 | 6294 |  | 6205 | 6171 | 6093 | 5932 | 5624 | 5288 | 4840 | 125968127
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 5 | 30 |  | 10 | 53 | 53 | 53 | 17 |  | 18 | 70 |  | 105 | 105 | 105 | 105 | 53 |  |  | 814080
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 200 | 170 | 170 | 150 | 150 | 150 | 152 | 151 | 150 | 151 | 151 | 151 | 151 | 151 | 219 |  | 219 | 220 | 220 | 221 | 221 | 190 | 190 | 4347627
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 266549
| Bhola 225 MW CCPP | 68 | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 61 | 65 | 59 | 64 | 64 | 58 | 65 | 65 | 50 | 66 |  | 67 | 66 | 66 | 68 | 60 | 68 | 68 | 1577000
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 19 | 19 | 19 | 17 | 14 | 13 | 13 | 14 | 14 | 15 | 15 | 13 | 13 | 16 | 20 |  | 21 | 21 | 21 | 22 | 20 | 20 | 19 | 424200
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 543 | 727 | 727 | 727 | 727 | 727 | 727 | 727 | 727 | 727 |  | 727 | 727 | 727 | 727 | 727 | 727 | 649 | 14998545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 300 | 300 | 270 | 270 | 270 | 290 | 300 | 330 | 320 | 310 | 320 | 300 | 360 | 320 | 300 | 300 | 300 | 350 |  | 410 | 420 | 420 | 420 | 400 | 390 | 350 | 8911000
149
150 | Barapukuria TPP Unit-1 | 81 | 80 | 82 | 82 | 81 | 80 | 81 | 79 | 80 | 85 | 84 | 81 | 81 | 81 | 81 | 80 | 79 | 78 |  | 79 | 79 | 78 | 77 | 77 | 78 | 79 | 1896872
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | [10 empty] | 33 | 29
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 25 |  | 25 | [6 empty] | 44496
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 4 | 4 | 4 | 2 | 0 | 0 | [9 empty] | 32100
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 185 | 185 | 186 | 189 | 181 | 172 | 176 | 173 | 169 | 188 | 193 | 177 | 187 | 166 | 166 | 174 | 177 | 165 |  | 174 | 179 | 180 | 182 | 182 | 175 | 199 | 4515555
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 185 | 184 | 182 | 174 | 170 | 170 | 165 | 187 | 195 | 192 | 165 | 195 | 195 | 173 | 175 | 170 | 166 |  | 188 | 186 | 185 | 188 | 190 | 179 | 204 | 4634664
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 375 | 397 | 411 | 391 | 416 | 326 | 392 | 370 | 366 | 330 | 340 | 407 | 412 | 328 | 372 | 373 | 340 | 418 |  | 414 | 401 | 412 | 394 | 323 | 379 | 387 | 9186618
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 12 | 12 | 13 | 11 | 11 | 10 | 8 | 5 | 5 | 2 | [16 empty] | 96266
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 492000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 233604
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 4 | 18 |  | 18 | 18 | [5 empty] | 53800
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 16 |  | 16 | 16 | [5 empty] | 47963
167 | Katakhali 50 MW Peaking PP | [17 empty] | 0
168 | Santahar 50 MW Peaking PP | [16 empty] | 14 | 36 |  | 36 | 36 | [5 empty] | 96082
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 5 | 25 |  | 52 | 52 | 52 | 8 |  |  |  | 197760
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 18 | 40 |  | 42 | 42 | 42 |  |  |  |  | 126072
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 37 | 70 | 35 | 48 | 109 | 113 | 113 | 50 | 35 | 40 | 93 |  | 113 | 113 | 113 | 113 | 113 | 113 |  | 1488672
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 50 | 50 |  | 20 | 35 | 60 | 70 | 50 | 35 | 60 | 113 |  | 113 | 113 | 113 | 113 | 35 |  |  | 1020768
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 70 | 70 | 34 | 20 | 34 | 70 | 70 | 49 | 34 | 70 | 105 |  | 105 | 105 | 105 | 105 | 68 |  |  | 996412
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 32409
178
178