## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-11-30 | Tuesday
|  |  | Date (day): | 2021-11-30 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12508.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13923 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-11-29 | 2021-11-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 369 | 336 | 360 | 360 | 52 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 240 | 240 | 240 | 120 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | FGMO & GT-2 S/D due to gas shortage.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 25 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 40 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 53 | 53 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 43 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 52 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 38 | 185 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 27 | 96 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 50 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 1678 | 2340 | 2899 | 3219 | 1052 | 1145
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 15 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 30 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 104 | 106 | 106 | 106 |  | 124 | Low Water Level & Unit 2 & 4,5 U/M.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 75 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 80 |  | 22 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 5 | 5 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 45 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 300 | 300 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 103 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 80 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 90 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 850 | 1112 | 1357 | 1366 | 0 | 997
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 120 | 120 | 120 | 120 | 14 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 218 | 220 | 220 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 265 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 50 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 68 | 68 | 68 | 127 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 100 | 118 | 140 | 140 |  | 10 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 86 | 90 | 90 |  | 73 | ST Under maint.
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 2 | 58 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 95 | 107 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 43 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 8 | 9 | 9 | 9
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 45 | 65 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 5 | 4 | 0 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1193 | 1423 | 1892 | 2118 | 405 | 496
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 120 | 131 | 200 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 39 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 55 | 88 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 270 | 302 | 610.6 | 559 | 0 | 8
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 41 | 42 | 42 |  | 28 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 142 | 142 | 144 | 144 |  | 186 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 33 | 33 | 33 |  | 33 | GT-8 S/D for gas shortage.
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 77 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 80 | 80 | 100 | 100
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 178 | 191 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 400 | 400 | 400 |  |  | FGMO
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 190 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1521 | 1486 | 1856 | 1986 | 63 | 307
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 723 | 723 | 737 | 737
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 758 | 828 | 892 | 1332 | 0 | 503
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 20 | 25 | 25 |  | 8 | Engine problem
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 66 | 68 | 68 |  | 126 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 310 | 330 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 168 | 219 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 568 | 646 | 1054 | 1204 | 84 | 134
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 16 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 24 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 70 | 150 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 166 | 163 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 209 | 169 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 370 | 367 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 20 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 5 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 41 | 95 | 95 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1010 | 1134 | 1609 | 1808 | 310 | 89
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 84 | 84
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 134 | 134
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 105 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 187 | 185 | 339 | 331 | 0 | 125
|  | Total |  |  |  |  | 22031 | 20934 | 8035 | 9456 | 12508.6 | 13923 | 1914 | 3804
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7850.6097 | 9239 | 12221.5477 | 13603.4895
| A. |  | 2021-11-29 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 9456 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
| 2 | Minimum Generation : |  |  | 5965 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9456 | MW
| 3 | Day peak Generation : |  |  | 8035 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9239 | MW
| 4 | Evening peak Generation : |  |  | 9456 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 185.4256 | MKWHr | By Solar | 0.74115 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 117.7876 | MKWHr |  | By Oil: | 37.0673 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 10.4834 | MKWHr |  | By Hydro: | 2.343 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1914 | MW | Dhaka | 3554 | 3554 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3804 | MW | Chittagong | 1097 | 1097 |  | 0 |  | 18:00 |  | 107
|  |  |  | Total = |  |  | 5718 | MW | Khulna | 1076 | 1076 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 926.45 | MMCFD |  |  | Rajshahi | 878 | 878 |  | 0 |  | 19:00 |  | 100
| 8 | Fuel Cost : | i) Gas : | Taka | 127341085.662 | ii) Oil : | Taka | 245645132.09 | Comilla | 745 | 745 |  | 0 |  | 19:30 |  | 99
|  |  | iii) Coal : |  | 49149496.27 | Total | Taka | 422135714.022 | Mymensingh | 708 | 708 |  | 0 |  | 20:00 |  | 100
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.212 | MKWHr. | Sylhet | 336 | 336 |  | 0 |  | 21:00 |  | 96
|  | ii) During Peak Demand : |  |  | -86 | MW (E to W) at | 18:00 | hrs | Barisal | 229 | 229 |  | 0 |  | 22:00 |  | 91
|  | iii) Maximum : |  |  | -160 | MW at | 8:00 | hrs | Rangpur | 616 | 616 |  | 0 |  | 23:00 |  | 85
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.5° C |  |  | Total | 9239 | 9239 |  | 0
| B. |  | 2021-11-30 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 27.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13923 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
| 4 | Reserve(Generation end) |  |  |  | 4623 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 182.4524 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6111 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.8844 | MKWHr. | ii) HVDC Flow at Peak Time |  | 723 | MW at | 18:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1187 | MKWHr. | iii) Maximum HVDC Flow : |  | 724 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.02 |  | (b) Today: | 100.9 |  | (c) Rule Curve: |  | 106.1
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-11-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 325 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 66 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 34 | 0 | 0 | 120 | 0 | 320 | 190 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 80 | 151 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 142 | 33 | 78 | 0 | 217 | 0 | 0 | 10 | 305 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 399 | 55 | 0 | 0 | 0 | 260 | 54 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 162 | 34 | 80 | 17 | 0 | 0 |  | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 11 | 0 | 205 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 192 | 0 | 0 | 0 |  | 4753 | 1967 | 6720 | 3124 | 446 | 1897 | 0 | 688 | 379 | 106 | 0 | 0 | 80 | 0 | 0 | 101.05
2:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 327 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 66 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 34 | 0 | 0 | 120 | 0 | 325 | 200 | 68 | 91 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 77 | 158 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 143 | 33 | 78 | 0 | 217 | 0 | 0 | 10 | 300 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 16 | 0 | 0 | 0 | 165 | 54 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 17 | 17 | 100 | 17 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 11 | 0 | 198 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 193 | 0 | 0 | 0 |  | 4444 | 1923 | 6367 | 3159 | 443 | 1892 | 0 | 341 | 349 | 106 | 0 | 0 | 77 | 0 | 0 | 101.04
3:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 329 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 28 | 33 | 33 | 0 | 0 | 66 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 34 | 0 | 0 | 120 | 0 | 310 | 187 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 30 | 8 | 75 | 166 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 138 | 33 | 10 | 0 | 217 | 0 | 0 | 10 | 305 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 16 | 0 | 0 | 0 | 115 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 11 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 11 | 0 | 194 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 193 | 0 | 0 | 0 |  | 4252 | 1893 | 6145 | 3127 | 443 | 1824 | 0 | 242 | 328 | 106 | 0 | 0 | 75 | 0 | 0 | 101.04
4:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 331 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 66 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 34 | 0 | 0 | 120 | 0 | 345 | 190 | 68 | 91 | 29 | 55 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 8 | 8 | 75 | 166 | 0 | 22 | 0 | 41 | 30 | 14 | 0 | 163 | 140 | 20 | 10 | 0 | 217 | 0 | 0 | 10 | 305 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 16 | 0 | 0 | 0 | 80 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 17 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 11 | 0 | 196 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 192 | 0 | 0 | 0 |  | 4130 | 1875 | 6005 | 3117 | 444 | 1727 | 0 | 213 | 323 | 106 | 0 | 0 | 75 | 0 | 0 | 101.03
5:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 335 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 67 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 34 | 0 | 0 | 120 | 0 | 340 | 184 | 68 | 89 | 29 | 55 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 8 | 8 | 73 | 166 | 0 | 22 | 0 | 41 | 30 | 14 | 0 | 130 | 143 | 20 | 10 | 0 | 217 | 0 | 0 | 10 | 310 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 16 | 0 | 0 | 0 | 80 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 17 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 11 | 0 | 200 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 192 | 0 | 0 | 0 |  | 4086 | 1879 | 5965 | 3107 | 443 | 1697 | 0 | 213 | 325 | 107 | 0 | 0 | 73 | 0 | 0 | 101.02
6:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 312 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 67 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13 | 18 | 34 | 0 | 0 | 120 | 0 | 325 | 200 | 68 | 90 | 26 | 55 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 8 | 8 | 71 | 168 | 0 | 22 | 0 | 41 | 30 | 14 | 0 | 130 | 140 | 33 | 50 | 0 | 217 | 0 | 0 | 10 | 330 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 16 | 0 | 0 | 0 | 100 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 31 | 100 | 17 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 11 | 0 | 209 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 192 | 0 | 0 | 0 |  | 4166 | 1919 | 6085 | 3107 | 443 | 1755 | 0 | 250 | 352 | 107 | 0 | 0 | 71 | 0 | 0 | 101.02
7:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 335 | 0 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 68 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 18 | 34 | 0 | 0 | 120 | 0 | 360 | 220 | 68 | 90 | 26 | 55 | 0 | 15 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 70 | 166 | 0 | 22 | 0 | 41 | 30 | 47 | 0 | 130 | 143 | 33 | 70 | 0 | 217 | 0 | 0 | 10 | 330 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 12 | 0 | 10 | 399 | 16 | 0 | 0 | 0 | 215 | 54 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 37 | 88 | 100 | 17 | 3 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 11 | 0 | 208 | 0 | 414 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 280 | 162 | 0 | 0 | 0 |  | 4565 | 1927 | 6492 | 3214 | 444 | 1739 | 0 | 549 | 359 | 108 | 0 | 0 | 70 | 9 | 0 | 101.01
8:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 363 | 0 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 68 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 5 | 18 | 9 | 0 | 0 | 120 | 0 | 300 | 161 | 68 | 90 | 26 | 30 | 0 | 43 | 0 | 0 | 4 | 22 | 5 | 33 | 8 | 74 | 166 | 0 | 22 | 1 | 41 | 30 | 47 | 0 | 110 | 144 | 20 | 75 | 0 | 217 | 0 | 0 | 10 | 280 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 90 | 0 | 35 | 400 | 48 | 0 | 0 | 1 | 300 | 54 | 62 | 0 | 9 | 0 | 0 | 87 | 16 | 154 | 107 | 70 | 17 | 12 | 0 |  | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 193 | 0 | 301 | 28 | 0 | 85 | 0 | 34 | 0 | 2 | 80 | 330 | 162 | 0 | 0 | 2 |  | 4935 | 2056 | 6991 | 3036 | 449 | 1557 | 0 | 1310 | 414 | 108 | 0 | 0 | 74 | 43 | 0 | 0
9:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 373 | 0 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 19 | 25 | 28 | 0 | 33 | 0 | 0 | 68 | 40 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 22 | 18 | 3 | 0 | 0 | 120 | 0 | 300 | 162 | 68 | 90 | 29 | 30 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 8 | 82 | 150 | 0 | 22 | 1 | 41 | 30 | 47 | 0 | 110 | 144 | 20 | 75 | 0 | 217 | 0 | 0 | 10 | 285 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 90 | 0 | 100 | 400 | 55 | 0 | 16 | 2 | 300 | 54 | 108 | 0 | 45 | 0 | 0 | 104 | 30 | 162 | 107 | 70 | 17 | 22 | 0 |  | 522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 169 | 0 | 319 | 35 | 0 | 113 | 0 | 34 | 0 | 3 | 108 | 330 | 162 | 0 | 0 | 3 |  | 5210 | 2171 | 7381 | 2991 | 522 | 1573 | 0 | 1618 | 412 | 108 | 0 | 0 | 82 | 75 | 0 | 0
10:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 373 | 0 |  | 0 | 250 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 64 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 3 | 0 | 0 | 120 | 0 | 270 | 162 | 78 | 90 | 29 | 30 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 8 | 90 | 139 | 0 | 22 | 2 | 41 | 30 | 47 | 0 | 110 | 142 | 20 | 78 | 0 | 192 | 0 | 0 | 10 | 270 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 90 | 0 | 100 | 374 | 55 | 0 | 17 | 4 | 300 | 54 | 110 | 0 | 45 | 0 | 0 | 104 | 41 | 162 | 108 | 70 | 17 | 28 | 0 |  | 644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 165 | 0 | 329 | 35 | 0 | 113 | 0 | 34 | 0 | 4 | 113 | 310 | 167 | 0 | 0 | 4 |  | 5214 | 2281 | 7495 | 2923 | 644 | 1606 | 0 | 1637 | 390 | 104 | 0 | 0 | 90 | 101 | 0 | 0
11:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 341 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 65 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 26 | 18 | 2 | 0 | 0 | 120 | 0 | 280 | 160 | 78 | 90 | 29 | 30 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 8 | 95 | 129 | 0 | 22 | 2 | 42 | 30 | 53 | 0 | 110 | 145 | 20 | 77 | 0 | 178 | 0 | 0 | 10 | 285 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 76 | 0 | 100 | 364 | 55 | 0 | 17 | 4 | 300 | 54 | 110 | 0 | 45 | 0 | 0 | 104 | 47 | 162 | 108 | 80 | 17 | 32 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 175 | 0 | 338 | 35 | 0 | 113 | 0 | 34 | 0 | 5 | 113 | 310 | 167 | 0 | 0 | 5 |  | 5229 | 2385 | 7614 | 2890 | 723 | 1656 | 0 | 1640 | 391 | 105 | 0 | 0 | 95 | 114 | 0 | 0
12:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 369 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 40 | 53 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 64 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 26 | 18 | 5 | 0 | 0 | 120 | 0 | 270 | 182 | 78 | 90 | 29 | 30 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 8 | 95 | 120 | 0 | 22 | 2 | 42 | 30 | 53 | 0 | 163 | 142 | 31 | 77 | 0 | 178 | 0 | 0 | 10 | 290 | 23 | 2 | 0 | 38 | 0 | 0 | 0 | 0 | 27 | 20 | 76 | 2 | 100 | 400 | 55 | 0 | 17 | 4 | 300 | 54 | 110 | 0 | 45 | 0 | 0 | 104 | 49 | 162 | 108 | 80 | 17 | 33 | 5 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 18 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 209 | 0 | 370 | 35 | 0 | 113 | 0 | 100 | 0 | 7 | 113 | 310 | 168 | 0 | 0 | 5 |  | 5512 | 2523 | 8035 | 2998 | 723 | 1750 | 0 | 1850 | 390 | 104 | 0 | 0 | 95 | 120 | 0 | 0
13:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 392 | 0 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 64 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 8 | 0 | 0 | 120 | 0 | 270 | 184 | 68 | 88 | 29 | 30 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 9 | 95 | 117 | 0 | 22 | 2 | 42 | 30 | 50 | 0 | 163 | 143 | 31 | 77 | 0 | 178 | 0 | 0 | 10 | 300 | 23 | 2 | 0 | 80 | 0 | 0 | 0 | 0 | 52 | 19 | 76 | 17 | 100 | 402 | 55 | 0 | 17 | 4 | 300 | 54 | 110 | 0 | 45 | 0 | 0 | 104 | 45 | 162 | 108 | 80 | 17 | 29 | 18 |  | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 11 | 0 | 203 | 0 | 405 | 35 | 0 | 113 | 0 | 105 | 0 | 7 | 113 | 310 | 162 | 0 | 0 | 5 |  | 5653 | 2588 | 8241 | 3049 | 722 | 1780 | 0 | 1971 | 391 | 104 | 0 | 0 | 95 | 111 | 0 | 0
14:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 376 | 0 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 65 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 5 | 0 | 0 | 120 | 0 | 270 | 151 | 78 | 91 | 29 | 30 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 9 | 102 | 115 | 0 | 22 | 2 | 41 | 30 | 53 | 0 | 110 | 143 | 20 | 40 | 0 | 178 | 0 | 0 | 10 | 270 | 23 | 2 | 0 | 80 | 0 | 0 | 0 | 0 | 53 | 7 | 100 | 17 | 100 | 350 | 55 | 0 | 17 | 3 | 300 | 54 | 110 | 0 | 45 | 0 | 0 | 104 | 38 | 162 | 108 | 80 | 17 | 25 | 18 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 10 | 0 | 191 | 0 | 343 | 35 | 0 | 113 | 0 | 105 | 0 | 5 | 113 | 300 | 142 | 0 | 0 | 4 |  | 5435 | 2453 | 7888 | 2896 | 723 | 1594 | 0 | 1996 | 380 | 95 | 0 | 0 | 102 | 84 | 0 | 100.98
15:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 348 | 0 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 53 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 66 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 3 | 0 | 0 | 120 | 0 | 265 | 151 | 68 | 90 | 29 | 30 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 9 | 98 | 121 | 0 | 22 | 1 | 41 | 30 | 50 | 0 | 110 | 143 | 20 | 40 | 0 | 179 | 0 | 0 | 10 | 290 | 13 | 2 | 0 | 80 | 0 | 0 | 0 | 0 | 43 | 6 | 70 | 17 | 40 | 352 | 35 | 0 | 17 | 2 | 300 | 54 | 110 | 0 | 45 | 0 | 0 | 104 | 26 | 162 | 108 | 80 | 17 | 18 | 15 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 170 | 0 | 344 | 35 | 0 | 113 | 0 | 70 | 0 | 4 | 95 | 300 | 142 | 0 | 0 | 2 |  | 5230 | 2370 | 7600 | 2834 | 723 | 1600 | 0 | 1785 | 380 | 106 | 0 | 0 | 98 | 59 | 0 | 100.97
16:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 348 | 57 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 0 | 6 | 0 | 0 | 0 | 35 | 17 | 53 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 3 | 0 | 0 | 120 | 0 | 305 | 203 | 68 | 91 | 29 | 30 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 9 | 96 | 138 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 140 | 143 | 32 | 40 | 0 | 179 | 0 | 0 | 10 | 290 | 23 | 2 | 0 | 80 | 0 | 0 | 0 | 0 | 32 | 4 | 40 | 17 | 40 | 377 | 35 | 0 | 17 | 1 | 288 | 54 | 51 | 0 | 45 | 0 | 0 | 86 | 10 | 162 | 70 | 80 | 17 | 8 | 13 |  | 724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 167 | 0 | 356 | 35 | 0 | 113 | 0 | 70 | 0 | 3 | 113 | 300 | 142 | 0 | 0 | 0 |  | 5207 | 2403 | 7610 | 2995 | 724 | 1699 | 0 | 1604 | 381 | 72 | 0 | 0 | 96 | 26 | 0 | 100.97
17:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 343 | 120 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 70 | 40 | 23 | 0 | 0 | 0 | 35 | 17 | 53 | 19 | 25 | 26 | 33 | 33 | 25 | 0 | 33 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 30 | 24 | 25 | 18 | 3 | 0 | 0 | 120 | 0 | 265 | 185 | 68 | 88 | 29 | 30 | 0 | 51 | 0 | 0 | 16 | 22 | 8 | 33 | 9 | 101 | 136 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 163 | 142 | 20 | 76 | 0 | 178 | 0 | 0 | 10 | 280 | 23 | 2 | 0 | 80 | 0 | 0 | 16 | 0 | 52 | 0 | 48 | 25 | 56 | 376 | 45 | 17 | 52 | 0 | 300 | 54 | 55 | 17 | 51 | 35 | 0 | 62 | 0 | 162 | 70 | 80 | 17 | 0 | 9 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 5 | 25 | 0 | 21 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 177 | 0 | 298 | 50 | 0 | 113 | 0 | 100 | 0 | 0 | 113 | 320 | 142 | 0 | 0 | 0 |  | 5568 | 2473 | 8041 | 2927 | 723 | 1759 | 0 | 1999 | 400 | 73 | 0 | 50 | 101 | 0 | 0 | 100.96
18:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 336 | 240 |  | 0 | 270 | 150 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 48 | 25 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 18 | 33 | 33 | 52 | 0 | 66 | 40 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 40 | 45 | 30 | 18 | 5 | 0 | 0 | 120 | 0 | 265 | 218 | 68 | 86 | 29 | 50 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 9 | 107 | 131 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 120 | 142 | 33 | 77 | 0 | 191 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 185 | 0 | 0 | 39 | 0 | 96 | 0 | 100 | 58 | 118 | 400 | 88 | 50 | 75 | 0 | 300 | 54 | 103 | 52 | 65 | 80 | 0 | 104 | 0 | 162 | 90 | 80 | 17 | 0 | 4 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 20 | 0 | 0 | 0 | 0 | 16 | 0 | 41 | 27 | 24 | 16 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 169 | 0 | 367 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 330 | 219 | 0 | 0 | 0 |  | 6663 | 2793 | 9456 | 2973 | 723 | 2010 | 0 | 2951 | 410 | 106 | 0 | 172 | 107 | 0 | 0 | 100.96
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 381 | 240 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 16 | 24 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 67 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 17 | 50 | 18 | 6 | 0 | 0 | 120 | 0 | 275 | 218 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 28 | 9 | 100 | 132 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 120 | 143 | 33 | 77 | 0 | 218 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 8 | 0 | 83 | 0 | 90 | 17 | 132 | 400 | 115 | 17 | 51 | 0 | 300 | 54 | 110 | 17 | 65 | 20 | 0 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20 | 0 | 0 | 0 | 0 | 16 | 0 | 41 | 27 | 24 | 16 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 188 | 0 | 418 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 400 | 219 | 0 | 0 | 0 |  | 6343 | 2956 | 9299 | 3113 | 723 | 2080 | 0 | 2556 | 480 | 107 | 0 | 140 | 100 | 0 | 0 | 100.94
19:30 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 379 | 243 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 16 | 24 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 30 | 33 | 33 | 34 | 0 | 60 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 12 | 50 | 18 | 6 | 0 | 0 | 120 | 0 | 275 | 217 | 68 | 89 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 24 | 9 | 99 | 132 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 143 | 32 | 77 | 0 | 218 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 8 | 0 | 70 | 0 | 90 | 17 | 133 | 400 | 115 | 17 | 51 | 0 | 300 | 54 | 110 | 17 | 65 | 20 | 0 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 27 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 11 | 0 | 189 | 0 | 414 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 400 | 219 | 0 | 0 | 0 |  | 6357 | 2876 | 9233 | 3109 | 723 | 2142 | 0 | 2497 | 480 | 100 | 0 | 83 | 99 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 379 | 243 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 16 | 25 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 30 | 33 | 33 | 34 | 0 | 60 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 8 | 10 | 12 | 50 | 18 | 8 | 0 | 0 | 120 | 0 | 265 | 217 | 68 | 90 | 29 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 25 | 9 | 100 | 135 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 143 | 33 | 77 | 0 | 218 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 30 | 0 | 0 | 8 | 0 | 69 | 0 | 90 | 17 | 133 | 400 | 115 | 17 | 51 | 0 | 300 | 54 | 110 | 17 | 65 | 20 | 0 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 196 | 0 | 416 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 400 | 219 | 0 | 0 | 0 |  | 6205 | 2870 | 9075 | 3112 | 723 | 2129 | 0 | 2407 | 480 | 100 | 0 | 24 | 100 | 0 | 0 | 100.95
21:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 371 | 243 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 54 | 35 | 53 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 60 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 18 | 20 | 0 | 0 | 120 | 0 | 285 | 218 | 68 | 90 | 29 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 25 | 9 | 96 | 141 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 142 | 32 | 78 | 0 | 218 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 90 | 17 | 133 | 400 | 85 | 17 | 51 | 0 | 300 | 54 | 110 | 0 | 65 | 10 | 57 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 11 | 0 | 200 | 0 | 416 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 400 | 220 | 0 | 0 | 0 |  | 5991 | 2810 | 8801 | 3183 | 723 | 2133 | 0 | 2089 | 477 | 100 | 0 | 0 | 96 | 0 | 0 | 100.94
22:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 357 | 242 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 53 | 19 | 25 | 30 | 8 | 33 | 0 | 0 | 59 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 49 | 18 | 28 | 0 | 0 | 120 | 0 | 265 | 217 | 68 | 88 | 29 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 25 | 9 | 91 | 138 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 168 | 33 | 78 | 0 | 217 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 133 | 328 | 85 | 0 | 0 | 0 | 300 | 54 | 110 | 0 | 65 | 0 | 180 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 0 | 196 | 0 | 361 | 53 | 0 | 113 | 0 | 49 | 0 | 0 | 50 | 400 | 220 | 0 | 0 | 0 |  | 5820 | 2565 | 8385 | 3197 | 723 | 2089 | 0 | 1707 | 479 | 99 | 0 | 0 | 91 | 0 | 0 | 100.94
23:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 356 | 242 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 18 | 30 | 0 | 0 | 120 | 0 | 270 | 179 | 68 | 91 | 29 | 55 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 25 | 9 | 85 | 138 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 42 | 33 | 78 | 0 | 218 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 328 | 50 | 0 | 0 | 0 | 303 | 54 | 68 | 0 | 65 | 0 | 190 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 186 | 0 | 332 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 222 | 0 | 0 | 0 |  | 5439 | 2263 | 7702 | 3054 | 723 | 2054 | 0 | 1228 | 448 | 110 | 0 | 0 | 85 | 0 | 0 | 100.93
24:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 360 | 242 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 65 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 18 | 18 | 0 | 0 | 120 | 0 | 265 | 180 | 68 | 91 | 29 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 6 | 80 | 140 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 21 | 33 | 78 | 0 | 218 | 0 | 0 | 10 | 285 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 328 | 50 | 0 | 0 | 0 | 230 | 54 | 17 | 0 | 65 | 0 | 190 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 |  | 578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 173 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 180 | 0 | 0 | 0 |  | 5235 | 1938 | 7173 | 2999 | 578 | 1967 | 0 | 1037 | 407 | 105 | 0 | 0 | 80 | 0 | 0 | 100.93
KWH | 0 | 0 | 0 | 4504500 | 0 | 0 | 0 | 8601600 | 1794000 |  | 0 | 6419250 | 3619113 | 0 | 0 | 171386 | 0 | 0 | 0 | 0 | 437184 | 93600 | 125079 | 0 | 0 | 0 | 1048680 | 440232 | 850261 | 338508 | 600000 | 639540 | 722000 | 817300 | 145920 | 0 | 1378991 | 964000 | 0 | 0 | 157172 | 0 | 0 | 0 | 0 |  | 350880 | 0 | 110407 | 78240 | 107520 | 677280 | 432144 | 422880 | 0 | 0 | 2875166 | 0 | 7140000 | 4602000 | 1722909 | 2129450 | 664200 | 1091040 | 0 | 1043808 | 0 | 0 | 441605 | 513036 | 233460 | 700700 | 208960 | 2118720 | 3361920 | 0 | 509472 | 13700 | 980000 | 708240 | 1106400 | 0 | 3569809 | 3022000 | 673344 | 1541760 | 0 | 4839580 | 0 | 0 | 252900 | 7274000 | 532656 | 134100 | 0 | 923345 | 0 | 0 | 98400 | 0 | 568800 | 121500 | 1213440 | 267840 | 1834981 | 9196000 | 1320000 | 1164000 | 465854 | 25318 | 6297818 | 1301405 | 1684430 | 95760 | 1047480 | 145920 | 526000 | 1813440 | 303480 | 3097440 | 1992218 | 1993873 | 438120 | 209888 | 87360 |  | 14884363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2432 | 0 | 1576000 | 399000 | 0 | 0 | 0 | 0 | 38720 | 0 | 74280 | 84200 | 65144 | 23516 | 264000 | 0 | 420240 | 0 | 237096 | 1906909 | 0 | 0 | 0 | 0 | 0 | 0 | 4622318 | 0 | 265779 | 0 | 4809736 | 0 | 9005127 | 863040 | 0 | 1787328 | 0 | 1177872 | 0 | 32763 | 1680672 | 8576500 | 4394673 | 0 | 0 | 34500 |  | 128286712 | 57226208 | 185512920 | 73444899 | 14884363 | 44342688 | 0 | 36724386 | 10483409 | 2342991 | 0 | 342955 | 2118720 | 741149 | 0
Fuel Cost | 0 | 0 | 0 | 6621615 | 0 | 0 | 0 | 8687616 | 1847820 |  | 0 | 6996982.5 | 4017215.43 | 0 | 0 | 1449925.56 | 0 | 0 | 0 | 0 | 3987118.08 | 921024 | 1153228.38 | 0 | 0 | 0 | 7655364 | 3402993.36 | 8383573.46 | 253881 | 450000 | 0 | 0 | 0 | 1411046.4 | 0 | 372327.57 | 260280 | 0 | 0 | 1460127.88 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1070947.9 | 747192 | 935424 | 5364057.6 | 544501.44 | 1255953.6 | 0 | 0 | 4226494.02 | 0 | 7140000 | 4233840 | 2222552.61 | 2448867.5 | 750546 | 1527456 | 0 | 1784911.68 | 0 | 0 | 4217327.75 | 651555.72 | 175095 | 1226225 | 156720 | 15890400 | 3563635.2 | 0 | 647029.44 | 218378 | 1607200 | 1133184 | 1969392 | 0 | 4069582.26 | 3142880 | 1326487.68 | 2944761.6 | 0 | 8372473.4 | 0 | 0 | 515916 | 7346740 | 399492 | 101916 | 0 | 6980488.2 | 0 | 0 | 511680 | 0 | 5596992 | 1420335 | 9889536 | 2906064 | 12936616.05 | 8552280 | 12038400 | 10999800 | 4057588.34 | 0 | 47611504.08 | 11335237.55 | 14806139.7 | 955684.8 | 8976903.6 | 971827.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85733930.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25487.36 | 0 | 1780880 | 618450 | 0 | 0 | 0 | 0 | 381004.8 | 0 | 657378 | 648340 | 880746.88 | 227870.04 | 2558160 | 0 | 806860.8 | 0 | 179481.672 | 11498661.27 | 0 | 0 | 0 | 0 | 0 | 0 | 6101459.76 | 0 | 398668.5 | 0 | 5627391.12 | 0 | 8915075.73 | 9010137.6 | 0 | 16961742.72 | 0 | 9140286.72 | 0 | 362031.15 | 12420166.08 | 37650835 | 0 | 0 | 0 | 0 |  | 313808350.54 | 212585046.082 | 526393396.622 | 80102746.952 | 85733930.88 | 47238338.71 | 0 | 242361419.99 | 49149496.27 | 632607.57 | 0 | 3283712.1 | 15890400 | 2000744.15 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 369 | 0 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 40 | 53 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 64 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 26 | 18 | 5 | 0 | 0 | 120 | 0 | 270 | 182 | 78 | 90 | 29 | 30 | 0 | 43 | 0 | 0 | 16 | 22 | 8 | 33 | 8 | 95 | 120 | 0 | 22 | 2 | 42 | 30 | 53 | 0 | 163 | 142 | 31 | 77 | 0 | 178 | 0 | 0 | 10 | 290 | 23 | 2 | 0 | 38 | 0 | 0 | 0 | 0 | 27 | 20 | 76 | 2 | 100 | 400 | 55 | 0 | 17 | 4 | 300 | 54 | 110 | 0 | 45 | 0 | 0 | 104 | 49 | 162 | 108 | 80 | 17 | 33 | 5 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 18 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 209 | 0 | 370 | 35 | 0 | 113 | 0 | 100 | 0 | 7 | 113 | 310 | 168 | 0 | 0 | 5 |  | 8035 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 336 | 240 | 0 | 0 | 270 | 150 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 48 | 25 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 18 | 33 | 33 | 52 | 0 | 66 | 40 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 40 | 45 | 30 | 18 | 5 | 0 | 0 | 120 | 0 | 265 | 218 | 68 | 86 | 29 | 50 | 0 | 51 | 0 | 0 | 43 | 22 | 8 | 33 | 9 | 107 | 131 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 120 | 142 | 33 | 77 | 0 | 191 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 185 | 0 | 0 | 39 | 0 | 96 | 0 | 100 | 58 | 118 | 400 | 88 | 50 | 75 | 0 | 300 | 54 | 103 | 52 | 65 | 80 | 0 | 104 | 0 | 162 | 90 | 80 | 17 | 0 | 4 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 20 | 0 | 0 | 0 | 0 | 16 | 0 | 41 | 27 | 24 | 16 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 169 | 0 | 367 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 330 | 219 | 0 | 0 | 0 |  | 9456 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 360 | 240 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 66 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 80 | 100 | 90 | 50 | 20 | 10 | 0 | 0 | 120 | 0 | 360 | 220 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 200 | 0 | 22 | 0 | 42 | 30 | 50 | 0 | 163 | 144 | 33 | 80 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 140 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 320 | 104 | 0 | 162 | 116 | 100 | 17 |  |  |  | 737 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 68 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 50 | 40 | 52 | 35 | 22 | 0 | 11 | 84 | 0 | 134 | 0 | 0 | 150 | 0 | 220 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 360 | 240 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 66 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 20 | 5 | 0 | 0 | 120 | 0 | 360 | 220 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 200 | 0 | 22 | 1.6 | 42 | 30 | 50 | 0 | 163 | 144 | 33 | 80 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 300 | 0 | 100 | 200 | 50 | 149 | 20 | 100 | 200 | 140 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 190 | 104 | 50 | 162 | 116 | 100 | 17 | 30 |  |  | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 84 | 0 | 134 | 0 | 0 | 70 | 0 | 200 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 381 | 240 | 0 | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 19 | 25 | 27 | 25 |  | 0 | 0 | 66 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 18 | 9 | 0 | 0 | 120 | 0 | 300 | 182 | 68 | 91 | 29 | 56 | 0 | 43 | 0 | 0 | 1 | 22 | 11 | 25 | 6 | 73 | 147 | 0 | 22 | 1 | 41 | 30 | 50 | 0 | 163 | 125 | 33 | 78 | 0 | 218 | 0 | 0 | 10 | 300 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 0 | 20 | 330 | 75 | 0 | 0 | 1 | 250 | 54 | 4 | 0 | 23 | 0 | 190 | 34 | 16 | 72 | 7 | 70 | 13 | 13 | 0 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 134 | 0 | 0 | 0 | 0 | 211 | 0 | 11 | 0 | 192 | 0 | 405 | 50 | 0 | 35 | 0 | 34 | 0 | 2 | 0 | 290 | 180 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 5965 | 5:00
| Highest Generation |  | 9456 | 18:00
| Day Peak Generation |  | 8035 | 12:00
| Evening Peak Generation |  | 9456 | 18:00
| HVDC Max Flow |  | 724 | 16:00
| HVDC EvPeak Flow |  | 723 | 18:00
| Load factor L.F |  | 81.74%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-11-30
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-11-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8035 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 6111 | MW
Evening Peak Generation : |  | 9456 | MW Hour : | 18:00 | Available Max Generation : |  | 13923 | MW
E.P. Demand (at gen end) : |  | 9456 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 9456 | MW Hour : | 18:00 | Reserve(Generation end) |  | 4623 | MW
Total Gen. (MKWH) : |  | 185.4256 | System Load Factor : | 81.74% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -160 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-11-30
Actual : | 100.9 | Ft.(MSL) , | Rule curve : | 106.1 | Ft.( MSL )
Gas Consumed : | Total = | 926.45 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 127341085.662
: |  | Coal : | 49149496.27 | Oil : | 245645132.09 | Total : | 422135714.022
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3388.6673 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1148.2797 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1028.098 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 928.7167 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 839.4093 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 677.3634 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 383.9661 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.541 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 522.3913 |  |  | 0 | 0%
Total | 0 |  | 9091.4328 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan unit-1&2
7) Ashuganj(N)-360 MW.
8) Shahjibazar GT-8.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Baghabari-Sirajganj 230 kV Ckt-1 was under shut down from 08:53 to 15:52 for A/M.
b) Barishal 230 KV Bus-1 was under shut down from 08:54 to 15:32 for A/M.
c) Chandpur 132 KV Bus-2 was under shut down from 08:28 to 19:35 for A/M.
d) Cumilla(N)-Kachua 132 KV Ckt-1 was under shut down from 11:31 to 12:21 for C/M.
e) Fenchuganj 230 KV Bus-2 was under shut down from 09:28 to 16:44 for A/M.
f) Fenchuganj-Bibiyana 230 kV Ckt-1 was under shut down from 09:10 to 16:43 for A/M.
g) Hathazari-Kaptai 132 KV Ckt-1 was under shut down from 09:08 to 17:52 for A/M.
h) HVDC Bheramara-Bahrampur 400 KV Ckt-1 was under shut down from 09:24 to 15:19 for A/M.
i) Jhenaidah 230/132 kV TR-01 transformer was under shut down from 08:29 to 12:06 for D/W.
j) Joydebpur 132/33 kV T-4 transformer was under shut down from 09:34 to 16:26 for A/M.
k) Jhenaidah-Magura 132 KV Ckt-2 was under shut down from 09:08 to 15:51 for A/M.
l) Kabirpur-Manikganj 132 KV Ckt-2 was under shut down from 07:25 to 16:33 for A/M.
m) Keraniganj-Nawabganj 132 KV Ckt-1 was under shut down from 12:18 to 12:42 for A/M.
n) Mirpur-Uttara(Old) 132 KV Ckt-1 was under shut down from 08:10 to 16:25 for A/M.
o) Mirsharai 230/132 kV TR-01 & TR-02 transformer is under shut down since 10:12 for SAS work.
p) Mymensingh-Bhaluka 132 KV Ckt-1 was under shut down from 09:24 to 15:32 for A/M.
q) Rampura-Mogbazar 132 KV Ckt-2 tripped at 08:19 from Rampura end showing Dist. Z1, Master trip and was
switched on at 09:12.
r) Saidpur-Barapukuria 132 KV Ckt-1 was under shut down from 08:26 to 16:21 for A/M.
s) Ullon-Haripur 132 KV Ckt-2 was under shut down from 10:41 to 17:34 for A/M.
t) Uttara 132/33 kV GT-1 transformer was under shut down from 08:58 to 14:50 for A/M.
u) Jhenaidah-Khulna(S) 230 KV Ckt-1 was under shut down from 12:33 to 16:55 for D/W.
v) Meghnaghat 450 MW CCPP GT-2 was synchronized at 09:46.
w) Haripur 360 MW CCPP GT was synchronized at 14:22 & ST at 16:45.
x) Bakulia 132/33 KV T-1 & T-2 transformers tripped at 15:15 showing O/C & E/F due to 33/0.4 KV Auxiliary | [5 empty] | About 50 MW power interruption occurred under Bakulia
transformer fault and was switched on at 15:35. | [5 empty] | S/S area from 15:15 to 15:35.
y) Siddhirganj 132/33 KV T-1 & T-2 transformers tripped at 14:28 due to 33 KV R,Y-phase L/A of T-1 got burst | [5 empty] | About 90 MW power interruption occurred under
and was switched on at 15:19(T-2). | [5 empty] | Siddhirganj S/S area from 14:28 to 15:19.
z) Jamalpur 132/33 kV T-4 transformer was under shut down from 14:24 to 16:57 for breaker replacing of 33 KV | [5 empty] | About 8 MW power interruption occurred under
Shekhervita-1 feeder(PDB). | [5 empty] | Jamalpur S/S area from 14:24 to 16:57.
aa) Keraniganj-Nawabganj 132 KV Ckt-2 was under shut down from 15:08 to 16:03 for D/W.
ab) Gopalganj(New)-Madaripur 132 KV Ckt-4 was under shut down from 17:43 to 20:02 for C/M.
ac) Mymensingh-Bhaluka 132 KV Ckt-2 was under shut down from 15:33 to 16:49 for D/W.
ad) Bibiyana South 400 MW CCPP GT was synchronized at 20:43.
ae) Shahjibazar 330 MW CCPP GT-1 was synchronized at 21:45 & ST at 23:07.
af) Shahjibazar 330 MW CCPP GT-2 was shutdown at 23:40.
ag) Barapukuria Unit-3 was synchronized at 03:38(30/11/2021).
ah) Gopalganj-Madaripur 132 KV Ckt-1&2 were shut down at 07:28(30/11/2021) & 07:34(30/11/2021) respectively for
A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-11-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4504500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 336 | 8601600 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 240 | 1794000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6419250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3619113 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 171386 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 25 | 125079 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 338508
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 437184
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1048680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 93600 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 440232
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 53 | 850261
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 1239540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 722000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 52 | 145920
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 185 | 923345 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 96 | 568800 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 50 | 1164000 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1813440
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3097440
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 209888
| Dhaka area Total |  |  |  | 5560 | 2340 | 39145066
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 15 | 157172 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 121500
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 677280
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 106 | 2342991 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 75 | 465854 | High Voltage.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 110407 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 78240 | High Voltage.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1213440
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 432144 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 422880
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 107520 | High Voltage.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25318
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 6297818
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1301405
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 103 | 1684430
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 80 | 145920 | High Voltage.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 1992218 | High Voltage.
| Chattogram area Total |  |  |  | 2382 | 1112 | 17576537
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 120 | 2875166 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 4602000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Ashuganj 400 kV Bus S/D
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 7140000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 664200 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1091040
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1722909 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1043808
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 118 | 1834981 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2129450 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 58 | 267840 | Low demand.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 513036
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 233460 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 107 | 2118720
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 700700
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 441605
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 208960 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 95760 | High Voltage.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 65 | 1047480 | High Voltage.
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 438120 | 33 kV feeder fault.
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 4 | 87360 | On test
| Cumilla Area Total |  |  |  | 3034 | 1423 | 29256595
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 131 | 3361920 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 509472
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13700
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 39 | 98400 | High Voltage.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 88 | 1320000 | High Voltage.
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 303480
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 350880
| Mymensingh Area Total |  |  |  | 622 | 302 | 5957852
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 980000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 708240 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3569809 | frequency control.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3022000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1106400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 134100
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 673344 | GT-8 under maint
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1541760
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 80 | 1993873 | Gas shortage
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 191 | 4839580
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 532656
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7274000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9196000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252900
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 526000 | Under maint.
| Sylhet Area Total |  |  |  | 2377 | 1486 | 36350662
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 723 | 14884363
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 2432 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 863040
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 828 | 15749835
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 399000 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 66 | 1576000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 265779 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 330 | 8576500 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 219 | 4394673
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 646 | 15211952
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 16 | 38720 | Low demand.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 84200 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 24 | 65144 | Low demand.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 23516 | Low demand.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 163 | 4622318 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 169 | 4809736 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 367 | 9005127 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 420240
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237096
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 264000
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 41 | 74280 | Low demand.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1787328
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1680672
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34500
| Rajshahi Area Total |  |  |  | 2179 | 1134 | 23146877
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1906909
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 1177872
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32763
| Rangpur Area Total |  |  |  | 605 | 185 | 3117544
| Total |  |  |  | 20934 | 9456 | 185512920
| Eastern Grid Total |  |  |  | 13975 | 6663 | 128286712
| Western Grid Total |  |  |  | 6959 | 2793 | 57226208
| National Grid Total |  |  |  | 20934 | 9456 | 185512920
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-11-29
(a) ENTIRE EASTERN GRID : |  | 6440 | MW | (b) ENTIRE WESTERN GRID : |  | 2799 | MW
i) Dhaka area |  | 3554 | MW | i) Khulna area |  | 1076 | MW
ii) Chittagong area |  | 1097 | MW | ii) Rajshahi area |  | 878 | MW
iii) Comilla area |  | 745 | MW | iii) Barisal area |  | 229 | MW
iv) Mymensingh area |  | 708 | MW | iv) Rangpur area |  | 616 | MW
v) Sylhet area |  | 336 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9239 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 9:00 | Mymensing | 153 | 18:00 | Jessore | 71 | 19:30
Munsiganj | 66 | 23:00 | Kishoreganj | 90 | 20:00 | Benapol | 38 | 18:30
Sonargaon | 50 | 22:00 | Netrokona | 76 | 18:00 | Jhenida(Old) | 79 | 18:00
Shyampur | 156 | 10:00 | Jamalpur | 105 | 18:00 | Bottail | 92 | 18:00
Bhulta | 159 | 18:30 | Sherpur | 84 | 18:00 | G.K Project | 34 | 18:30
Madanganj | 34 | 19:00 | Srimongal | 30 | 18:00 | Faridpur | 102 | 21:00
Shitalakhya | 100 | 15:00 | Shahjibazar | 81 | 18:00 | Rajbari | 32 | 18:00
Rahim steel | 18 | 1:00 | Fenchuganj | 29 | 17:00 | Madaripur | 65 | 19:30
Matuail | 50 | 9:00 | Kulawara | 30 | 18:00 | Sariatpur | 40 | 19:30
Ghorasal | 60 | 18:00 | Sylhet | 85 | 18:00 | Gopalganj | 64 | 18:00
Narsingdi | 122 | 19:30 | Chatak | 16 | 18:30 | Bagerhat | 67 | 18:00
Haripur (SBU) | 111 | 17:00 | Sunamganj | 29 | 18:30 | Mongla | 52 | 18:00
Sreenagar | 26 | 18:00 | Biani Bazar | 40 | 18:00 | Satkhira | 65 | 18:00
Ullon | 45 | 14:00 | Comilla (S) | 107 | 18:00 | Gallamari | 22 | 13:00
Hasnabad | 61 | 18:30 | Comilla(N) | 82 | 19:30 | Magura | 40 | 18:00
Magbazar | 70 | 12:00 | Chandpur | 45 | 20:00 | Norail | 35 | 18:00
Maniknagar | 52 | 18:00 | Feni | 82 | 17:00 | Chuadanga | 62 | 18:00
Bangabhaban | 8 | 10:00 | Chowmuhani | 128 | 18:30 | Barisal(N) | 27 | 19:30
Motijheel | 20 | 11:00 | Ashuganj | 25 | 21:00 | Barisal (S) | 74 | 19:30
Narinda | 44 | 13:00 | Daudkandi | 92 | 19:00 | Patuakhali | 74 | 22:00
Kazla | 69 | 18:30 | B.Baria | 99 | 19:30 | Bhandaria | 38 | 19:30
Dhanmondi | 130 | 13:00 | Ramganj | 52 | 20:00 | Borguna | 12 | 20:00
Lalbag | 82 | 17:00 | Chaddagram | 23 | 18:30 | Borhan Uddin | 28 | 20:00
Madartek | 51 | 18:30 | PHP | 2 | 3:00 | Ishurdi | 47 | 18:00
Dhaka University | 24 | 11:00 | Kochua | 38 | 18:30 | Ruppur Paromanobik | 3 | 20:00
Aftabnagar | 12 | 18:00 | Madunaghat | 40 | 18:00 | Natore | 86 | 18:00
Fatullah | 52 | 11:00 | Hathazari | 66 | 18:00 | Bogra | 110 | 18:00
Nawabganj | 31 | 20:00 | Khulshi | 152 | 18:30 | Noagaon | 82 | 18:30
Keraniganj | 52 | 18:00 | Halishahar | 76 | 16:00 | Rajshahi | 94 | 20:00
Banani | 41 | 14:00 | Baraulia | 122 | 12:00 | Rajshahi New | 13 | 20:00
Mirpur | 87 | 18:00 | Sikalbaha | 27 | 17:00 | C.Nawabganj | 40 | 20:00
Kalyanpur | 66 | 18:00 | Dohazari | 68 | 18:00 | Amnura | 30 | 19:30
Gulshan | 78 | 13:00 | Cox'sbazar | 88 | 17:00 | Pabna | 68 | 18:00
Uttara | 62 | 13:00 | Chandraghona | 20 | 18:00 | Shahjadpur | 67 | 18:00
Uttara New | 8 | 13:00 | Kaptai | 3.5 | 18:00 | Serajganj | 62 | 18:30
Kamrangirchar | 77 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 38 | 18:00
Savar | 109 | 19:00 | Bakulia | 87 | 17:00 | Joypurhat | 44 | 18:00
Bhasantec | 87 | 12:00 | Julda | 21 | 12:00 | Sherpur(Bogura) | 44 | 18:00
Agargaon | 54 | 18:00 | TK chemical | 21.8 | 18:00 | Mohastangor | 44 | 18:00
Satmosjid | 75 | 18:00 | Modern Steel | 0.2 | 9:00 | Bhangura | 19 | 18:30
Tongi | 92 | 15:00 | Shahmirpur | 25.3 | 18:00 | Rangpur | 97 | 18:00
Kabirpur | 194 | 15:00 | Khagrachhari | 22 | 18:00 | Lalmonirhat | 43 | 19:00
Basundhara | 159 | 14:00 | Matarbari | 24 | 18:30 | Saidpur | 82 | 18:00
Purbachal | 53 | 18:00 | Baroiar Hat | 32 | 18:30 | Purbasadipur | 82 | 19:00
Manikganj | 151 | 18:00 | Rangamati | 10 | 18:00 | Thakurgaon | 65 | 18:00
Joydevpur | 66 | 18:00 | Abul Khair 230 | 136 | 10:00 | Palashbari | 74 | 20:00
New Tongi | 216 | 18:00 | BSRM | 159 | 13:00 | Barapukuria | 39 | 20:00
Kodda | 72 | 18:00 | GPH Ispat | 96 | 6:00 | Panchagar | 43 | 18:30
Dhamrai | 82 | 18:30 | Agrabad | 63 | 18:00 | Joldhaka | 28 | 18:00
Rajendrapur | 13 | 12:00 | Goalpara | 24 | 13:00 | Kurigram | 44 | 18:00
Valuka | 74 | 18:30 | Central S/S | 75 | 18:00 | Mithapukur | 22 | 18:00
Tangail | 134 | 18:00 | Noapara | 41 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-11-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 6:00 | 405 | 11:00 | Kaliakoir | 402 | 0.125 | 390 | 0.45833
| Bheramara | 407 | 3:00 | 392 | 11:00 | Bhulta | 374 | 0.041667 | 360 | 0.41667
| Ashuganj(N) | 0 | 1:00 | 0 | 1:00 | Gopalganj | 414 | 0.625 | 403 | 0.77083
| Payra | 416 | 8:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 240 | 14:00 | 231 | 12:00
| Ishurdi | 240 | 17:00 | 229 | 9:00 | Megnaghat | 236 | 17:00 | 230 | 9:00
| Ashuganj | 245 | 24:00 | 237 | 11:00 | Fenchuganj | 246 | 6:00 | 242 | 11:00
| Serajganj | 240 | 17:00 | 234 | 7:00 | Siddhirganj | 234 | 6:00 | 225 | 12:00
| Baghabari | 237 | 3:00 | 230 | 12:00 | Maniknagar | 232 | 6:00 | 223 | 11:00
| Barapukuria | 237 | 15:00 | 230 | 18:00 | Agargaon | 232 | 2:00 | 224 | 11:00
| Bogra | 235 | 17:00 | 227 | 7:00 | Barisal | 245 | 1:00 | 238 | 19:30
| Rajshahi | 239 | 17:00 | 223 | 11:00 | Bhola 225 MW | 247 | 3:00 | 240 | 19:00
| Khulna South | 246 | 17:00 | 228 | 13:00 | AKSML | 237 | 1:00 | 223 | 4:00
| Rampura | 231 | 1:00 | 222 | 11:00 | BSRM | 238 | 18:00 | 223 | 4:00
| Haripur | 232 | 7:00 | 223 | 11:00 | Bibiyana | 245 | 22:00 | 239 | 20:00
| Hasnabad | 235 | 24:00 | 224 | 12:00 | Bhulta | 234 | 24:00 | 224 | 10:00
| Shyampur | 232 | 8:00 | 224 | 11:00 | Ashuganj (S) | 241 | 18:00 | 235 | 11:00
| Aminbazar | 233 | 1:00 | 225 | 2:00 | Kaliakoir | 233 | 17:00 | 223 | 11:00
| Tongi | 228 | 4:00 | 217 | 11:00 | GPH | 239 | 17:00 | 220 | 5:00
| Comilla (N) | 236 | 18:00 | 229 | 16:00 | Jhenaidah | 240 | 17:00 | 225 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 8:00 | 131 | 11:00 | Kachua | 141 | 0.75 | 137 | 0.20833
| Munsiganj | 138 | 17:00 | 132 | 11:00 | Madanhat | 142 | 0.25 | 134 | 0.625
| Sonargaon | 138 | 0:00 | 132 | 7:00 | Hathazari | 141 | 0.79167 | 136 | 0.041667
| Shyampur | 139 | 8:00 | 134 | 11:00 | Khulshi | 139 | 0.75 | 127 | 0.20833
| Bhulta | 133 | 3:00 | 127 | 11:00 | Halishahar | 139 | 0.75 | 129 | 0.20833
| Madanganj | 138 | 18:00 | 131 | 11:00 | Baraulia | 142 | 0.375 | 135 | 0.66667
| Shitalakhya | 138 | 8:00 | 132 | 11:00 | Sikalbaha | 141 | 0.75 | 132 | 0.20833
| Rahim steal | 137 | 7:00 | 132 | 15:00 | Dohazari | 137 | 0.75 | 126 | 0.16667
| Matuail | 136 | 8:00 | 131 | 11:00 | Cox'sbazar | 123 | 0.375 | 116 | 0.083333
| Ghorasal | 140 | 1:00 | 138 | 23:00 | Chandraghona | 140 | 0.33333 | 133 | 0.16667
| Narsinghdi | 136 | 4:00 | 132 | 15:00 | Kaptai | 139 | 0.041667 | 136 | 0.54167
| Haripur (SBU) | 137 | 4:00 | 132 | 11:00 | A. Khaer Stl. | 138 | 0.33333 | 132 | 0.625
| Sreenagar | 137 | 0:00 | 131 | 11:00 | Bakulia | 139 | 0.33333 | 132 | 0.083333
| Ullon | 134 | 1:00 | 128 | 10:00 | Julda | 140 | 0.75 | 133 | 0.29167
| Hasnabad | 140 | 17:00 | 135 | 11:00 | TK Chemical | 140 | 0.8125 | 133 | 0.66667
| Magbazar | 135 | 1:00 | 128 | 11:00 | Modern Steel | 140 | 0.75 | 132 | 0.66667
| Maniknagar | 137 | 7:00 | 130 | 11:00 | Shahmirpur | 140 | 0.75 | 132 | 0.083333
| Bangabhaban | 137 | 7:00 | 130 | 11:00 | Khagrachhari | 140 | 0.75 | 132 | 0.16667
| Motijheel | 137 | 7:00 | 130 | 11:00 | Matarbari | 123 | 0.625 | 115 | 0.16667
| Narinda | 137 | 7:00 | 130 | 11:00 | Baroiar Hat | 141 | 20:00 | 135 | 1:00
| Kazla | 137 | 7:00 | 130 | 11:00 | Rangamati | 140 | 18:00 | 131 | 5:00
| Dhanmondi | 137 | 1:00 | 131 | 12:00 | Agrabad | 139 | 18:00 | 129 | 0.083333
| Lalbag | 133 | 1:00 | 128 | 11:00 | Goalpara S/S | 139 | 3:00 | 128 | 0.29167
| Madartek | 134 | 1:00 | 127 | 11:00 | Khulna Central S/S | 135 | 4:00 | 126 | 0.41667
| Dhaka University | 134 | 1:00 | 128 | 11:00 | Noapara | 137 | 3:00 | 127 | 0.375
| Aftabnagar | 134 | 1:00 | 128 | 12:00 | Jessore | 136 | 0.041667 | 127 | 0.29167
| Fatullah | 140 | 7:00 | 133 | 11:00 | Benapol | 140 | 17:00 | 127 | 0.375
| Nawabganj | 137 | 6:00 | 134 | 14:00 | Jhenida(Old) | 139 | 0.70833 | 130 | 0.41667
| Keraniganj | 136 | 1:00 | 131 | 11:00 | Bottail | 139 | 0.70833 | 130 | 0.41667
| Banani | 135 | 7:00 | 127 | 11:00 | G.K Project | 141 | 0.70833 | 132 | 0.41667
| Mirpur | 134 | 3:00 | 128 | 10:00 | Faridpur | 139 | 0.083333 | 130 | 0.58333
| Kalyanpur | 134 | 1:00 | 129 | 10:00 | Rajbari | 138 | 0.125 | 132 | 0.77083
| Gulshan | 134 | 1:00 | 128 | 11:00 | Madaripur | 143 | 17:00 | 138 | 0.75
| Uttara | 133 | 1:00 | 127 | 10:00 | Shariyatpur S/S | 142 | 0.125 | 137 | 0.75
| Uttara New | 134 | 7:00 | 129 | 9:00 | Gopalganj | 143 | 17:00 | 137 | 0.54167
| Kamrangirchar | 137 | 3:00 | 131 | 10:00 | Bagerhat | 135 | 17:00 | 122 | 0.29167
| Savar | 134 | 18:00 | 129 | 10:00 | Mongla | 131 | 1:00 | 124 | 8:00
| Bhasantec | 136 | 1:00 | 130 | 10:00 | Satkhira | 138 | 0.70833 | 124 | 7:00
| Agargaon | 137 | 1:00 | 131 | 11:00 | Gallamari | 142 | 17:00 | 135 | 0.45833
| Satmosjid | 136 | 1:00 | 131 | 10:00 | Magura | 141 | 0.041667 | 130 | 0.375
| Tongi | 138 | 3:00 | 131 | 15:00 | Narail | 139 | 1:00 | 129 | 0.375
| Kabirpur | 137 | 1:00 | 131 | 18:29 | Chuadanga | 138 | 17:00 | 128 | 0.375
| Basundhara | 135 | 20:00 | 126 | 11:00 | Barisal(N) | 144 | 3:00 | 138 | 19:00
| Purbachal | 140 | 7.00 | 132 | 16:00 | Barisal (S) | 142 | 0.125 | 137 | 0.77083
| Manikganj | 139 | 17:00 | 130 | 13:00 | Patuakhali(S) | 140 | 0.25 | 134 | 0.8125
| Joydevpur | 138 | 18:00 | 127 | 11:00 | Bhandaria | 142 | 0.20833 | 135 | 0.75
| New Tongi | 138 | 18:00 | 123 | 11:00 | Borguna | 142 | 4:00 | 135 | 19:00
| Kodda | 135 | 18:00 | 129 | 12:00 | Jhenaidah(New) | 138 | 1:00 | 130 | 11:00
| Dhamrai | 136 | 19:00 | 122 | 11:00 | Ishurdi | 139 | 17:00 | 131 | 12:00
| Rajendrapur | 134 | 1:00 | 127 | 11:00 | Ruppur Paromanobik | 138 | 3:00 | 132 | 12:00
| Valuka | 131 | 1:00 | 122 | 16:00 | Natore | 139 | 17:00 | 132 | 11:00
| Tangail | 135 | 1:00 | 131 | 13:00 | Bogra | 140 | 17:00 | 134 | 6:00
| Mymensing | 133 | 4:00 | 127 | 16:00 | Noagaon | 136 | 17:00 | 129 | 7:00
| Kishorganj | 134 | 1:00 | 130 | 16:00 | Rajshahi | 139 | 17:00 | 132 | 9:00
| Netrokona | 132 | 1:00 | 126 | 16:00 | Rajshahi New | 141 | 17:00 | 133 | 9:00
| Jamalpur | 137 | 18:00 | 125 | 15:00 | C.Nawabganj | 139 | 17:00 | 131 | 13:00
| Sherpur | 133 | 17:00 | 124 | 13:00 | Amnura | 141 | 17:00 | 131 | 8:00
| Srimongal | 140 | 10:00 | 136 | 16:00 | Pabna | 138 | 17:00 | 132 | 9:00
| Shahjibazar | 137 | 1:00 | 134 | 11:00 | Shahjadpur | 144 | 2:00 | 138 | 18:30
| Fenchuganj | 138 | 1:00 | 136 | 12:00 | Serajganj | 139 | 17:00 | 133 | 7:00
| Khulawara | 137 | 1:00 | 136 | 5:00 | Niyamatpur | 135 | 14:00 | 128 | 7:00
| Sylhet | 135 | 1:00 | 134 | 9:00 | Joypurhat | 137 | 14:00 | 130 | 7:00
| Chatak | 137 | 2:00 | 135 | 9:00 | Sherpur(Bogura) | 140 | 17:00 | 132 | 7:00
| Sunamganj | 134 | 1:00 | 133 | 10:00 | Mohastangor | 140 | 17:00 | 133 | 18:00
| Biani Bazar | 136 | 1:00 | 134 | 11:00 | Bangura | 141 | 17:00 | 135 | 12:00
| Comilla(s) | 129 | 4:00 | 124 | 14:00 | Rangpur | 134 | 17:00 | 126 | 18:00
| Comilla(n) | 143 | 8:00 | 139 | 12:00 | Lalmonirhat | 133 | 17:00 | 125 | 9:00
| Chandpur | 141 | 13:00 | 137 | 2:00 | Saidpur | 133 | 6:00 | 124 | 9:00
| Feni | 142 | 18:00 | 133 | 4:00 | Purbasadipur | 132 | 5:00 | 120 | 18:00
| Chowmuhani | 139 | 8:00 | 135 | 4:00 | Thakurgaon | 130 | 6:00 | 118 | 18:00
| Ashuganj | 140 | 1:00 | 137 | 16:00 | Palashbari | 135 | 14:00 | 130 | 11:00
| Daudkandi | 139 | 7:00 | 134 | 11:00 | Barapukuria | 137 | 0.70833 | 130 | 0.75
| B.Baria | 137 | 6:00 | 132 | 16:00 | Panchagar | 132 | 0.70833 | 121 | 0.75
| Ramganj | 139 | 20:00 | 135 | 5:00 | Joldhaka | 134 | 0.20833 | 121 | 0.75
| Chaddagram | 140 | 6:00 | 136 | 3:00 | Kurigram | 135 | 0.70833 | 124 | 0.75
| PHP | 140 | 18:00 | 134 | 4:00 | Mithapukur | 138 | 0.70833 | 129 | 0.41667

## L-Curve
Date | 2021-11-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 134 | 5235 | 1938 | 7173 |  |  |  | QF-LDC-11
0:30 | 103 | 4994 | 1952.5 | 6946.5 | Date: | 2021-11-29
1:00 | 72 | 4753 | 1967 | 6720
1:30 | 115 | 4598.5 | 1945 | 6543.5
2:00 | 158 | 4444 | 1923 | 6367
2:30 | 169 | 4348 | 1908 | 6256 | [5 empty] | Gen. at Eve. Peak | 9456 | 9456 MW (18:00 )
3:00 | 180 | 4252 | 1893 | 6145 | [6 empty] | 18:00
3:30 | 197 | 4191 | 1884 | 6075 | [5 empty] | Gen. at Day Peak | 8035 | 8035 MW (12:00 )
4:00 | 214 | 4130 | 1875 | 6005 | [6 empty] | 12:00
4:30 | 240 | 4108 | 1877 | 5985 | [5 empty] | Highest Generation | 9456
5:00 | 266 | 4086 | 1879 | 5965 | [6 empty] | 18:00
5:30 | 217 | 4126 | 1899 | 6025
6:00 | 168 | 4166 | 1919 | 6085
6:30 | 87 | 4365.5 | 1923 | 6288.5
7:00 | 6 | 4565 | 1927 | 6492
7:30 | 83 | 4750 | 1991.5 | 6741.5
8:00 | 160 | 4935 | 2056 | 6991
8:30 | 140 | 5072.5 | 2113.5 | 7186
9:00 | 120 | 5210 | 2171 | 7381
9:30 | 219 | 5212 | 2226 | 7438
10:00 | 318 | 5214 | 2281 | 7495
10:30 | 342 | 5221.5 | 2333 | 7554.5
11:00 | 366 | 5229 | 2385 | 7614
11:30 | 352 | 5370.5 | 2454 | 7824.5
12:00 | 338 | 5512 | 2523 | 8035
12:30 | 302 | 5582.5 | 2555.5 | 8138
13:00 | 266 | 5653 | 2588 | 8241
13:30 | 313 | 5544 | 2520.5 | 8064.5
14:00 | 360 | 5435 | 2453 | 7888
14:30 | 375 | 5332.5 | 2411.5 | 7744
15:00 | 390 | 5230 | 2370 | 7600
15:30 | 442 | 5218.5 | 2386.5 | 7605
16:00 | 494 | 5207 | 2403 | 7610
16:30 | 372 | 5387.5 | 2438 | 7825.5
17:00 | 250 | 5568 | 2473 | 8041
17:30 | 168 | 6115.5 | 2633 | 8748.5
18:00 | 86 | 6663 | 2793 | 9456
18:30 | 77 | 6503 | 2874.5 | 9377.5
19:00 | 68 | 6343 | 2956 | 9299
19:30 | 18 | 6357 | 2876 | 9233
20:00 | 24 | 6205 | 2870 | 9075 |  |  |  | Executive Engineer
20:30 | 62 | 6098 | 2840 | 8938 |  |  |  | Network Operation Division
21:00 | 100 | 5991 | 2810 | 8801
21:30 | 77 | 5905.5 | 2687.5 | 8593
22:00 | 54 | 5820 | 2565 | 8385 |  |  |  |  | Page 6 of 7
22:30 | 29 | 5629.5 | 2414 | 8043.5
23:00 | 4 | 5439 | 2263 | 7702
23:30 | 69 | 5337 | 2100.5 | 7437.5
24:00 | 134 | 5235 | 1938 | 7173
9456 MW (18:00 )
8035 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-11-29 |  | Energy |  | 185512920
[13 empty] | 2021-11-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2999 | 578 | 1967 | 0 | 1037 | 407 | 105 | 0 | 0 | 80 | 0 | 0
0:30 | 3061.5 | 512 | 1932 | 0 | 862.5 | 393 | 105.5 | 0 | 0 | 80 | 0 | 0 | Date: | 2021-11-29
1:00 | 3124 | 446 | 1897 | 0 | 688 | 379 | 106 | 0 | 0 | 80 | 0 | 0
1:30 | 3141.5 | 444.5 | 1894.5 | 0 | 514.5 | 364 | 106 | 0 | 0 | 78.5 | 0 | 0 | [8 empty] | Total Energy | 185.5129 | Total Energy Gen 185.513 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.513 MKWHr
2:00 | 3159 | 443 | 1892 | 0 | 341 | 349 | 106 | 0 | 0 | 77 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3143 | 443 | 1858 | 0 | 291.5 | 338.5 | 106 | 0 | 0 | 76 | 0 | 0 | [8 empty] | Energy Requirement | 185.5129
3:00 | 3127 | 443 | 1824 | 0 | 242 | 328 | 106 | 0 | 0 | 75 | 0 | 0
3:30 | 3122 | 443.5 | 1775.5 | 0 | 227.5 | 325.5 | 106 | 0 | 0 | 75 | 0 | 0 | [6 empty] | Shortage
4:00 | 3117 | 444 | 1727 | 0 | 213 | 323 | 106 | 0 | 0 | 75 | 0 | 0
4:30 | 3112 | 443.5 | 1712 | 0 | 213 | 324 | 106.5 | 0 | 0 | 74 | 0 | 0
5:00 | 3107 | 443 | 1697 | 0 | 213 | 325 | 107 | 0 | 0 | 73 | 0 | 0
5:30 | 3107 | 443 | 1726 | 0 | 231.5 | 338.5 | 107 | 0 | 0 | 72 | 0 | 0
6:00 | 3107 | 443 | 1755 | 0 | 250 | 352 | 107 | 0 | 0 | 71 | 0 | 0
6:30 | 3160.5 | 443.5 | 1747 | 0 | 399.5 | 355.5 | 107.5 | 0 | 0 | 70.5 | 4.5 | 0 |  |  |  |  | Coal
7:00 | 3214 | 444 | 1739 | 0 | 549 | 359 | 108 | 0 | 0 | 70 | 9 | 0
7:30 | 3125 | 446.5 | 1648 | 0 | 929.5 | 386.5 | 108 | 0 | 0 | 72 | 26 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3036 | 449 | 1557 | 0 | 1310 | 414 | 108 | 0 | 0 | 74 | 43 | 0
8:30 | 3013.5 | 485.5 | 1565 | 0 | 1464 | 413 | 108 | 0 | 0 | 78 | 59 | 0
9:00 | 2991 | 522 | 1573 | 0 | 1618 | 412 | 108 | 0 | 0 | 82 | 75 | 0
9:30 | 2957 | 583 | 1589.5 | 0 | 1627.5 | 401 | 106 | 0 | 0 | 86 | 88 | 0
10:00 | 2923 | 644 | 1606 | 0 | 1637 | 390 | 104 | 0 | 0 | 90 | 101 | 0
10:30 | 2906.5 | 683.5 | 1631 | 0 | 1638.5 | 390.5 | 104.5 | 0 | 0 | 92.5 | 107.5 | 0
11:00 | 2890 | 723 | 1656 | 0 | 1640 | 391 | 105 | 0 | 0 | 95 | 114 | 0
11:30 | 2944 | 723 | 1703 | 0 | 1745 | 390.5 | 104.5 | 0 | 0 | 95 | 117 | 0
12:00 | 2998 | 723 | 1750 | 0 | 1850 | 390 | 104 | 0 | 0 | 95 | 120 | 0
12:30 | 3023.5 | 722.5 | 1765 | 0 | 1910.5 | 390.5 | 104 | 0 | 0 | 95 | 115.5 | 0
13:00 | 3049 | 722 | 1780 | 0 | 1971 | 391 | 104 | 0 | 0 | 95 | 111 | 0
13:30 | 3049 | 722 | 1780 | 0 | 1971 | 391 | 104 | 0 | 0 | 95 | 111 | 0
14:00 | 3049 | 722 | 1780 | 0 | 1971 | 391 | 104 | 0 | 0 | 95 | 111 | 0
14:30 | 2941.5 | 722.5 | 1690 | 0 | 1878 | 385.5 | 105 | 0 | 0 | 96.5 | 85 | 0
15:00 | 2834 | 723 | 1600 | 0 | 1785 | 380 | 106 | 0 | 0 | 98 | 59 | 0
15:30 | 2914.5 | 723.5 | 1649.5 | 0 | 1694.5 | 380.5 | 89 | 0 | 0 | 97 | 42.5 | 0
16:00 | 2995 | 724 | 1699 | 0 | 1604 | 381 | 72 | 0 | 0 | 96 | 26 | 0
16:30 | 2961 | 723.5 | 1729 | 0 | 1801.5 | 390.5 | 72.5 | 0 | 25 | 98.5 | 13 | 0
17:00 | 2927 | 723 | 1759 | 0 | 1999 | 400 | 73 | 0 | 50 | 101 | 0 | 0
17:30 | 2950 | 723 | 1884.5 | 0 | 2475 | 405 | 89.5 | 0 | 111 | 104 | 0 | 0
18:00 | 2973 | 723 | 2010 | 0 | 2951 | 410 | 106 | 0 | 172 | 107 | 0 | 0
18:30 | 3043 | 723 | 2045 | 0 | 2753.5 | 445 | 106.5 | 0 | 156 | 103.5 | 0 | 0
19:00 | 3113 | 723 | 2080 | 0 | 2556 | 480 | 107 | 0 | 140 | 100 | 0 | 0
19:30 | 3109 | 723 | 2142 | 0 | 2497 | 480 | 100 | 0 | 83 | 99 | 0 | 0
20:00 | 3112 | 723 | 2129 | 0 | 2407 | 480 | 100 | 0 | 24 | 100 | 0 | 0
20:30 | 3147.5 | 723 | 2131 | 0 | 2248 | 478.5 | 100 | 0 | 12 | 98 | 0 | 0
21:00 | 3183 | 723 | 2133 | 0 | 2089 | 477 | 100 | 0 | 0 | 96 | 0 | 0
21:30 | 3190 | 723 | 2111 | 0 | 1898 | 478 | 99.5 | 0 | 0 | 93.5 | 0 | 0
22:00 | 3197 | 723 | 2089 | 0 | 1707 | 479 | 99 | 0 | 0 | 91 | 0 | 0
22:30 | 3125.5 | 723 | 2071.5 | 0 | 1467.5 | 463.5 | 104.5 | 0 | 0 | 88 | 0 | 0
23:00 | 3054 | 723 | 2054 | 0 | 1228 | 448 | 110 | 0 | 0 | 85 | 0 | 0
23:30 | 3026.5 | 650.5 | 2010.5 | 0 | 1132.5 | 427.5 | 107.5 | 0 | 0 | 82.5 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 29.5° C
24:00 | 2999 | 578 | 1967 | 0 | 1037 | 407 | 105 | 0 | 0 | 80 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 185.513 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.513 MKWHr
Note on W13: Author:

## Generation
g | 2021-11-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 66 | 66 | 66 | 66 | 67 | 67 | 68 | 68 | 68 | 64 | 65 | 64 | 64 | 65 | 66 | 32 | 33 | 66 |  | 67 | 60 | 60 | 60 | 59 | 70 | 65 | 1378991
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 |  | 17 | 17 | 17 | 8 | 8 | 8 | 0 | 157172
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 14 | 18 | 19 | 20 | 19 | 7 | 6 | 4 | 0 | [9 empty] | 121500
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 8 |  |  |  |  | 110407
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 75 |  | 51 | 51 | 51 | 51 |  |  | 0 | 465854
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 38 | 80 | 80 | 80 | 80 | 80 | 185 |  | 95 | 95 | 30 |  |  |  | 0 | 923345
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 78 | 78 | 78 | 68 | 78 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1722909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4504500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2875166
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 664200
33 | Ashuganj 225 MW CCPP | 190 | 200 | 187 | 190 | 184 | 200 | 220 | 161 | 162 | 162 | 160 | 182 | 184 | 151 | 151 | 203 | 185 | 218 |  | 218 | 217 | 217 | 218 | 217 | 179 | 180 | 4602000
34 | Ashuganj 450 MW CCPP(South) | 320 | 325 | 310 | 345 | 340 | 325 | 360 | 300 | 300 | 270 | 280 | 270 | 270 | 270 | 265 | 305 | 265 | 265 |  | 275 | 275 | 265 | 285 | 265 | 270 | 265 | 7140000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1091040
36 | Chandpur 150 MW CCPP | 90 | 91 | 90 | 91 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 88 | 91 | 90 | 91 | 88 | 86 |  | 90 | 89 | 90 | 90 | 88 | 91 | 91 | 2129450
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 325 | 327 | 329 | 331 | 335 | 312 | 335 | 363 | 373 | 373 | 341 | 369 | 392 | 376 | 348 | 348 | 343 | 336 |  | 381 | 379 | 379 | 371 | 357 | 356 | 360 | 8601600
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 225 | 225 | 225 | 250 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6419250
41 | Haripur 360MW CCPP(HPL) | [15 empty] | 57 | 120 | 240 |  | 240 | 243 | 243 | 243 | 242 | 242 | 242 | 1794000
42 | RPCL 210MW CCPP | 151 | 158 | 166 | 166 | 166 | 168 | 166 | 166 | 150 | 139 | 129 | 120 | 117 | 115 | 121 | 138 | 136 | 131 |  | 132 | 132 | 135 | 141 | 138 | 138 | 140 | 3361920
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 16 | 30 | 41 | 47 | 49 | 45 | 38 | 26 | 10 | 0 | [9 empty] | 303480
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 980000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 708240
46 | Shajibazar 330 MW CCPP | 142 | 143 | 138 | 140 | 143 | 140 | 143 | 144 | 144 | 142 | 145 | 142 | 143 | 143 | 143 | 143 | 142 | 142 |  | 143 | 143 | 143 | 142 | 168 | 42 | 21 | 3022000
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 33 | 20 | 20 | 33 | 33 | 20 | 20 | 20 | 20 | 31 | 31 | 20 | 20 | 32 | 20 | 33 |  | 33 | 32 | 33 | 32 | 33 | 33 | 33 | 673344
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 10 | 10 | 10 | 50 | 70 | 75 | 75 | 78 | 77 | 77 | 77 | 40 | 40 | 40 | 76 | 77 |  | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 1541760
| Shahjibazar 100 MW GTPP | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1993873
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 192 | 178 | 178 | 178 | 178 | 179 | 179 | 178 | 191 |  | 218 | 218 | 218 | 218 | 217 | 218 | 218 | 4839580
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252900
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 134100
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 14 | 14 | 14 | 47 | 47 | 47 | 47 | 53 | 53 | 50 | 53 | 50 | 50 | 50 | 50 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1106400
56 | Shahjahanulla 25 MW PP | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 13 | 23 | 23 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 532656
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 300 | 305 | 305 | 310 | 330 | 330 | 280 | 285 | 270 | 285 | 290 | 300 | 270 | 290 | 290 | 280 | 280 |  | 290 | 310 | 300 | 290 | 290 | 280 | 285 | 7274000
| Bibiyana South 400 MW | [22 empty] | 57 | 180 | 190 | 190 | 526000
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 17 | 0 | 850261
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 4 | 24 | 24 | 24 | 22 | 24 | 24 | 24 | 24 | 23 | 22 |  | 24 | 24 | 24 | 24 | 24 |  | 0 | 350880
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432144
61 | Narshingdi 22 MW PP (Doreen) | 20 | 20 | 20 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 338508
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509472
63 | Impoprt (Tripura) | 80 | 77 | 75 | 75 | 73 | 71 | 70 | 74 | 82 | 90 | 95 | 95 | 95 | 102 | 98 | 96 | 101 | 107 |  | 100 | 99 | 100 | 96 | 91 | 85 | 80 | 2118720
64 | Malancha, Ctg. EPZ (United) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 9 | 3 | 3 | 2 | 5 | 8 | 5 | 3 | 3 | 3 | 5 |  | 6 | 6 | 8 | 20 | 28 | 30 | 18 | 422880
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 513036
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 233460
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 30 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 28 | 24 | 25 | 25 | 25 | 25 | 25 | 700700
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 208960
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 28 | 25 | 26 | 26 | 26 | 18 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 639540
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 25 | 8 | 25 | 25 | 722000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [16 empty] | 17 | 52 |  | 17 | 17 | 17 |  |  |  | 0 | 95760
| Chowmuhani 113 MW | 36 | 26 | [5 empty] | 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 51 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1047480
| Manikgonj 162MW PP(MPGL) | 162 | 17 |  |  |  | 2 | 37 | 154 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3097440
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [16 empty] | 25 | 52 |  | 52 | 34 | 34 |  |  |  |  | 145920
79 | Kodda 150MW PP | [16 empty] | 40 | 48 |  | 16 | 16 | 16 |  |  |  | 0 | 93600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 4 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 43 |  | 52 | 52 | 52 | 52 | 52 | 8 |  | 441605
| Gazipur 100 MW PP | [16 empty] | 17 | 50 |  | 17 | 17 | 17 | 17 |  |  | 0 | 1164000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25318
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1301405
| Karnaphuli Power Ltd. | [7 empty] | 62 | 108 | 110 | 110 | 110 | 110 | 110 | 110 | 51 | 55 | 103 |  | 110 | 110 | 110 | 110 | 110 | 68 | 17 | 1684430
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [15 empty] | 6 | 23 | 25 |  | 24 | 24 | 25 | 14 |  |  | 0 | 125079
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3619113
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 16 | 87 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 86 | 62 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1813440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 30 | 40 |  | 10 | 10 | 10 |  |  |  | 0 | 78240
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 10 | 10 | 10 | 15 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 1043808
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 50 | 50 | 50 | 32 | 32 | 70 | 102 |  | 32 | 32 | 7 |  |  |  | 0 | 437184
95 | Patenga 50MW PP (Baraka) | 25 | 12 | 12 | 12 | 12 | 13 | 24 | 5 | 22 | 25 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 30 |  | 50 | 50 | 50 | 50 | 49 | 46 | 46 | 677280
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 24 | 45 |  | 17 | 12 | 12 |  |  |  | 0 | 107520
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 15 | 15 | 15 | 15 | 15 | 40 |  | 15 | 15 | 15 |  |  |  | 0 | 171386
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 40 | 55 | 55 | 35 | 17 | 17 | 55 |  | 55 | 55 | 55 | 35 |  |  | 0 | 440232
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 163 | 163 | 110 | 110 | 140 | 163 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3569809
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 13700
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1048680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 16 | 39 |  | 8 | 8 | 8 |  |  |  | 0 | 98400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 16 | 27 | 52 | 53 | 43 | 32 | 52 | 96 |  | 83 | 70 | 69 | 27 |  |  | 0 | 568800
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 12 | 90 | 90 | 90 | 76 | 76 | 76 | 100 | 70 | 40 | 48 | 100 |  | 90 | 90 | 90 | 90 | 50 |  | 0 | 1213440
116 | Chandpur 200MW (Desh energy) | [11 empty] | 2 | 17 | 17 | 17 | 17 | 25 | 58 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 267840
117 | Ashuganj 150MW PP (Midland) | 10 | [5 empty] | 10 | 35 | 100 | 100 | 100 | 100 | 100 | 100 | 40 | 40 | 56 | 118 |  | 132 | 133 | 133 | 133 | 133 | 132 | 133 | 1834981
118 | Bibiyana-III 400 MW CCPP | 399 | 400 | 400 | 399 | 399 | 399 | 399 | 400 | 400 | 374 | 364 | 400 | 402 | 350 | 352 | 377 | 376 | 400 |  | 400 | 400 | 400 | 400 | 328 | 328 | 328 | 9196000
| Jamalpur 115 MW PP (United) | 55 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 45 | 88 |  | 115 | 115 | 115 | 85 | 85 | 50 | 50 | 1320000
| Anwara 300 MW PP (United) | 260 | 165 | 115 | 80 | 80 | 100 | 215 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 288 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 303 | 230 | 6297818
| Juldah unit-2 (Acorn) | [16 empty] | 35 | 80 |  | 20 | 20 | 20 | 10 |  |  | 0 | 145920
| Anlima Energy Ltd. | 34 | 17 | 17 | 17 | 17 | 31 | 88 | 107 | 107 | 108 | 108 | 108 | 108 | 108 | 108 | 70 | 70 | 90 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1992218
| Bhairob 54.5 MW | 17 | 17 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438120
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 12 | 22 | 28 | 32 | 33 | 29 | 25 | 18 | 8 | 0 | [9 empty] | 209888
| Chandpur 115(Doreen) | [11 empty] | 5 | 18 | 18 | 15 | 13 | 9 | 4 | [8 empty] | 87360
120 | Eastern Zone Total | 4753 | 4444 | 4252 | 4130 | 4086 | 4166 | 4565 | 4935 | 5210 | 5214 | 5229 | 5512 | 5653 | 5435 | 5230 | 5207 | 5568 | 6663 |  | 6343 | 6357 | 6205 | 5991 | 5820 | 5439 | 5235 | 128286712
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 28 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 105 |  | 105 | 105 | 105 | 105 | 53 |  | 0 | 863040
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 192 | 193 | 193 | 192 | 192 | 192 | 162 | 162 | 162 | 167 | 167 | 168 | 162 | 142 | 142 | 142 | 142 | 219 |  | 219 | 219 | 219 | 220 | 220 | 222 | 180 | 4394673
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 265779
| Bhola 225 MW CCPP | 68 | 69 | 69 | 69 | 69 | 68 | 69 | 68 | 67 | 67 | 65 | 65 | 65 | 65 | 62 | 65 | 65 | 66 |  | 67 | 67 | 68 | 67 | 68 | 68 | 66 | 1576000
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 17 | 16 | 16 | 15 | 15 | 14 | 13 | 12 | 14 | 14 | 15 | 14 | 13 | 13 | 16 | 20 |  | 20 | 20 | 21 | 21 | 25 | 25 | 19 | 399000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | [8 empty] | 0 | 2432
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 446 | 443 | 443 | 444 | 443 | 443 | 444 | 449 | 522 | 644 | 723 | 723 | 722 | 723 | 723 | 724 | 723 | 723 |  | 723 | 723 | 723 | 723 | 723 | 723 | 578 | 14884363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 300 | 270 | 250 | 250 | 250 | 270 | 280 | 330 | 330 | 310 | 310 | 310 | 310 | 300 | 300 | 300 | 320 | 330 |  | 400 | 400 | 400 | 400 | 400 | 370 | 330 | 8576500
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 78 | 73 | 75 | 82 | 79 | 84 | 82 | 80 | 81 | 80 | 81 | 80 | 80 | 81 | 80 | 80 |  | 80 | 80 | 80 | 77 | 79 | 78 | 77 | 1906909
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 16 |  | 16 | 16 | [5 empty] | 38720
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 0 | 0 | [9 empty] | 34500
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 201 | 196 | 196 | 197 | 198 | 205 | 208 | 180 | 167 | 164 | 167 | 166 | 199 | 173 | 169 | 173 | 178 | 163 |  | 185 | 189 | 188 | 190 | 184 | 180 | 171 | 4622318
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 205 | 198 | 194 | 196 | 200 | 209 | 208 | 193 | 169 | 165 | 175 | 209 | 203 | 191 | 170 | 167 | 177 | 169 |  | 188 | 189 | 196 | 200 | 196 | 186 | 173 | 4809736
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 417 | 417 | 412 | 416 | 414 | 413 | 414 | 301 | 319 | 329 | 338 | 370 | 405 | 343 | 344 | 356 | 298 | 367 |  | 418 | 414 | 416 | 416 | 361 | 332 | 300 | 9005127
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [26 empty] | 0
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 3 | 3 | 3 | 3 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 420240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237096
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 12 | 27 |  | 27 | 27 | 27 |  |  |  | 0 | 84200
166 | Katakhali 50 MW PP (Northern) | [16 empty] | 8 | 24 |  | 24 | [5 empty] | 0 | 65144
167 | Katakhali 50 MW Peaking PP | [16 empty] | 5 | 16 |  | 16 | [6 empty] | 23516
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [11 empty] | 5 | 8 | 8 | 8 | 8 | 25 | 52 |  | 52 | 52 | 52 | 16 |  |  | 0 | 264000
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 41 |  | 41 | [6 empty] | 74280
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 26 | 85 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 35 | 0 | 1787328
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 0 | 80 | 108 | 113 | 113 | 113 | 113 | 113 | 95 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 50 |  | 0 | 1680672
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 34 | 34 | 34 | 34 | 100 | 105 | 105 | 70 | 70 | 100 | 105 |  | 105 | 105 | 105 | 105 | 49 |  | 0 | 1177872
177 | Sympa Solar Power 8MW | [7 empty] | 2 | 3 | 4 | 5 | 7 | 7 | 5 | 4 | 3 | 0 | [9 empty] | 32763
178
178