## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-12-02 | Thursday
|  |  | Date (day): | 2021-12-02 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12491.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13781 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-12-01 | 2021-12-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 362 | 397 | 360 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 338 | 337 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | FGMO & GT-2 S/D due to gas shortage.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 25 | 24 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 72 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 32 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 54 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 28 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 48 | 52 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 195 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 52 | 110 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 94 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
|  | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 0 | 0 | 0 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2122 | 2450 | 2959 | 3331 | 1048 | 1145
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 17 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 62 | 106 | 106 |  | 124 | Low Water Level & Unit 2 & 4,5 U/M.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 34 | 17 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 80 |  | 22 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 40 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 5 | 5 | 11
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 75 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 245 | 300 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 51 | 85 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 20 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 632 | 855 | 1357 | 1367 | 0 | 997
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 100 | 100 | 34 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 184 | 220 | 220 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 270 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 68 | 68 | 127 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 40 | 130 | 125 | 125 |  | 25 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 88 | 90 | 90 |  | 73 | ST Under maint.
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 51 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 102 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 57 | 108 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1054 | 1287 | 1857 | 2083 | 425 | 511
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 109 | 127 | 140 | 140 | 62 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 8 | 24 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 4 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 266 | 290 | 550.6 | 499 | 62 | 8
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 40 | 40 | 40 |  | 30 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 126 | 127 | 144 | 144 |  | 186 | GT-2 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 53 | 60 | 66
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 80 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 65 | 65 | 100 | 100
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 219 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 353 | 400 | 400 |  |  | FGMO
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 50 | 90 | 300 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1560 | 1598 | 1991 | 2018 | 63 | 276
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 709 | 698 | 721 | 721
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 762 | 803 | 876 | 1316 | 0 | 503
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 21 | 20 | 20 |  | 13 | Engine problem
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 65 | 68 | 68 |  | 126 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 84 | 87 | 87 | 87 | 8 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 330 | 430 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 104 | 104 | 110 | 110 |  | 110 | GT-2 Under shut down.
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 594 | 707 | 1015 | 1165 | 8 | 249
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 197 | 183 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 188 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 419 | 361 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 20 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 95 | 100
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1006 | 1228 | 1539 | 1663 | 310 | 89
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 79 | 84 | 84
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 138 | 135 | 142 | 142
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 105 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 258 | 319 | 347 | 339 | 0 | 125
|  | Total |  |  |  |  | 22031 | 20934 | 8254 | 9537 | 12491.6 | 13781 | 1916 | 3903
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7874.9236 | 9099 | 11917.9059 | 13148.0884
| A. |  | 2021-12-01 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 9537 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6127 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9537 | MW
| 3 | Day peak Generation : |  |  | 8254 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9099 | MW
| 4 | Evening peak Generation : |  |  | 9537 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 189.162 | MKWHr | By Solar | 0.76016 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 121.2988 | MKWHr |  | By Oil: | 34.2252 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.5335 | MKWHr |  | By Hydro: | 1.6497 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1916 | MW | Dhaka | 3481 | 3481 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3903 | MW | Chittagong | 1052 | 1052 |  | 0 |  | 18:00 |  | 110
|  |  |  | Total = |  |  | 5819 | MW | Khulna | 1044 | 1044 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 947.52 | MMCFD |  |  | Rajshahi | 890 | 890 |  | 0 |  | 19:00 |  | 102
| 8 | Fuel Cost : | i) Gas : | Taka | 131651210.286 | ii) Oil : | Taka | 244214556.11 | Comilla | 742 | 742 |  | 0 |  | 19:30 |  | 102
|  |  | iii) Coal : |  | 70463865.62 | Total | Taka | 446329632.016 | Mymensingh | 705 | 705 |  | 0 |  | 20:00 |  | 100
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.0895 | MKWHr. | Sylhet | 342 | 342 |  | 0 |  | 21:00 |  | 97
|  | ii) During Peak Demand : |  |  | 114 | MW (E to W) at | 19:00 | hrs | Barisal | 244 | 244 |  | 0 |  | 22:00 |  | 91
|  | iii) Maximum : |  |  | -73 | MW at | 8:00 | hrs | Rangpur | 599 | 599 |  | 0 |  | 23:00 |  | 86
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.2° C |  |  | Total | 9099 | 9099 |  | 0
| B. |  | 2021-12-02 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13781 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
| 4 | Reserve(Generation end) |  |  |  | 4081 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 192.4371 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6013 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.6153 | MKWHr. | ii) HVDC Flow at Peak Time |  | 698 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0794 | MKWHr. | iii) Maximum HVDC Flow : |  | 709 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.77 |  | (b) Today: | 100.57 |  | (c) Rule Curve: |  | 106
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-12-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 372 | 322 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 33 | 0 | 0 | 100 | 0 | 275 | 208 | 68 | 89 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 75 | 140 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 163 | 127 | 20 | 75 | 0 | 218 | 0 | 0 | 10 | 295 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 400 | 55 | 0 | 0 | 0 | 245 | 40 | 17 | 0 | 75 | 0 | 50 | 17 | 0 | 54 | 17 | 60 | 17 | 0 | 0 | 0 |  | 458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 142 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 0 | 170 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 220 | 0 | 0 | 0 |  | 4898 | 2031 | 6929 | 3045 | 458 | 2158 | 0 | 601 | 533 | 59 | 0 | 0 | 75 | 0 | 0 | 100.8
2:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 393 | 322 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 32 | 0 | 0 | 100 | 0 | 310 | 210 | 68 | 92 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 9 | 73 | 138 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 163 | 125 | 40 | 10 | 0 | 218 | 0 | 0 | 10 | 280 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 24 | 0 | 0 | 0 | 135 | 54 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 |  | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 0 | 140 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 0 | 165 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 220 | 0 | 0 | 0 |  | 4527 | 1981 | 6508 | 3072 | 439 | 2069 | 0 | 284 | 512 | 59 | 0 | 0 | 73 | 0 | 0 | 100.8
3:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 345 | 323 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 33 | 0 | 0 | 100 | 0 | 275 | 165 | 68 | 92 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 0 | 9 | 70 | 140 | 0 | 22 | 0 | 41 | 30 | 14 | 0 | 163 | 126 | 40 | 10 | 0 | 218 | 0 | 0 | 0 | 305 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 24 | 0 | 0 | 0 | 100 | 54 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 |  | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 0 | 141 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 0 | 177 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 220 | 0 | 0 | 0 |  | 4270 | 1956 | 6226 | 2922 | 439 | 1984 | 0 | 249 | 503 | 59 | 0 | 0 | 70 | 0 | 0 | 100.79
4:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 371 | 322 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 29 | 25 | 33 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 34 | 0 | 0 | 100 | 0 | 280 | 177 | 35 | 88 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 0 | 9 | 67 | 140 | 0 | 22 | 0 | 41 | 30 | 14 | 0 | 110 | 127 | 40 | 10 | 0 | 218 | 0 | 0 | 0 | 295 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 24 | 0 | 0 | 0 | 100 | 54 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 |  | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 82 | 0 | 140 | 0 | 0 | 0 | 0 | 192 | 0 | 11 | 0 | 172 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 220 | 0 | 0 | 0 |  | 4205 | 1986 | 6191 | 2966 | 439 | 1905 | 0 | 249 | 502 | 63 | 0 | 0 | 67 | 0 | 0 | 100.79
5:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 375 | 322 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 34 | 0 | 0 | 100 | 0 | 275 | 172 | 35 | 90 | 29 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 0 | 9 | 65 | 141 | 0 | 22 | 0 | 41 | 30 | 14 | 0 | 110 | 126 | 40 | 10 | 0 | 218 | 0 | 0 | 0 | 285 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 24 | 0 | 0 | 0 | 100 | 54 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 |  | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 0 | 141 | 0 | 0 | 0 | 0 | 191 | 0 | 11 | 0 | 173 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 220 | 0 | 0 | 0 |  | 4187 | 1940 | 6127 | 2959 | 439 | 1850 | 0 | 249 | 502 | 63 | 0 | 0 | 65 | 0 | 0 | 100.78
6:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 369 | 322 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 30 | 0 | 0 | 100 | 0 | 310 | 158 | 35 | 90 | 28 | 10 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 9 | 66 | 142 | 0 | 22 | 0 | 41 | 30 | 14 | 0 | 163 | 124 | 40 | 10 | 0 | 218 | 0 | 0 | 0 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 399 | 24 | 0 | 0 | 0 | 155 | 54 | 2 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 2 | 60 | 17 | 0 | 0 | 0 |  | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 82 | 0 | 140 | 0 | 0 | 0 | 0 | 195 | 0 | 11 | 0 | 199 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 135 | 0 | 0 | 0 |  | 4372 | 1986 | 6358 | 3037 | 426 | 1934 | 0 | 313 | 502 | 80 | 0 | 0 | 66 | 0 | 0 | 100.77
7:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 390 | 322 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 10 | 11 | 25 | 27 | 25 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 18 | 33 | 0 | 0 | 100 | 0 | 305 | 148 | 35 | 91 | 27 | 10 | 0 | 43 | 0 | 0 | 1 | 22 | 11 | 33 | 9 | 65 | 141 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 163 | 124 | 40 | 40 | 0 | 178 | 0 | 0 | 10 | 280 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 0 | 3 | 398 | 24 | 0 | 0 | 1 | 165 | 54 | 17 | 0 | 9 | 0 | 50 | 5 | 3 | 20 | 17 | 60 | 17 | 2 | 0 | 0 |  | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 82 | 0 | 140 | 0 | 0 | 0 | 0 | 199 | 0 | 21 | 0 | 200 | 0 | 415 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 10 | 300 | 110 | 0 | 0 | 0 |  | 4541 | 2013 | 6554 | 3046 | 426 | 1985 | 0 | 422 | 522 | 80 | 0 | 0 | 65 | 8 | 0 | 100.76
8:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 372 | 322 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 45 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 45 | 18 | 7 | 0 | 0 | 90 | 0 | 275 | 160 | 8 | 90 | 29 | 5 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 9 | 74 | 122 | 0 | 22 | 1 | 40 | 30 | 50 | 0 | 110 | 133 | 52 | 72 | 0 | 218 | 0 | 0 | 10 | 300 | 20 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 10 | 40 | 0 | 20 | 399 | 44 | 0 | 10 | 1 | 245 | 54 | 30 | 0 | 57 | 10 | 50 | 52 | 16 | 104 | 38 | 60 | 17 | 13 | 0 | 0 |  | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 19 | 0 | 8 | 82 | 0 | 138 | 0 | 0 | 0 | 0 | 203 | 0 | 68 | 0 | 175 | 0 | 304 | 50 | 0 | 42 | 0 | 34 | 0 | 1 | 90 | 360 | 108 | 0 | 0 | 2 |  | 4980 | 2195 | 7175 | 3028 | 426 | 1860 | 0 | 1091 | 580 | 72 | 0 | 0 | 74 | 44 | 0 | 100.75
9:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 374 | 323 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 16 | 20 | 0 | 0 | 0 | 35 | 17 | 53 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 38 | 18 | 2 | 0 | 0 | 80 | 0 | 275 | 176 | 8 | 87 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 9 | 82 | 111 | 0 | 22 | 1 | 40 | 30 | 50 | 0 | 110 | 126 | 40 | 72 | 0 | 192 | 0 | 0 | 10 | 290 | 23 | 2 | 0 | 37 | 0 | 0 | 8 | 0 | 16 | 15 | 40 | 0 | 53 | 400 | 75 | 0 | 34 | 2 | 249 | 54 | 51 | 0 | 57 | 10 | 50 | 91 | 34 | 162 | 0 | 70 | 17 | 21 | 0 | 0 |  | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 0 | 8 | 82 | 0 | 137 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 170 | 0 | 290 | 53 | 0 | 109 | 0 | 34 | 0 | 3 | 111 | 360 | 104 | 0 | 0 | 3 |  | 5306 | 2327 | 7633 | 2970 | 550 | 1760 | 0 | 1533 | 579 | 64 | 0 | 16 | 82 | 79 | 0 | 100.74
10:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 336 | 284 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 24 | 32 | 17 | 0 | 0 | 0 | 35 | 17 | 53 | 16 | 25 | 28 | 30 | 33 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 12 | 50 | 18 | 2 | 0 | 0 | 80 | 0 | 280 | 150 | 8 | 90 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 9 | 86 | 107 | 0 | 22 | 2 | 42 | 30 | 50 | 0 | 110 | 130 | 40 | 75 | 0 | 165 | 0 | 0 | 10 | 280 | 23 | 2 | 0 | 45 | 0 | 0 | 8 | 0 | 48 | 18 | 40 | 0 | 70 | 327 | 75 | 0 | 34 | 4 | 245 | 54 | 51 | 0 | 59 | 10 | 50 | 90 | 44 | 162 | 0 | 65 | 17 | 27 | 18 | 0 |  | 709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 81 | 0 | 137 | 0 | 0 | 0 | 0 | 177 | 0 | 63 | 0 | 166 | 0 | 250 | 53 | 0 | 113 | 0 | 34 | 0 | 4 | 113 | 320 | 104 | 0 | 0 | 4 |  | 5253 | 2464 | 7717 | 2802 | 709 | 1739 | 0 | 1619 | 538 | 71 | 0 | 32 | 86 | 103 | 0 | 100.73
11:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 334 | 311 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 24 | 16 | 23 | 0 | 0 | 0 | 35 | 17 | 53 | 19 | 25 | 28 | 30 | 33 | 18 | 0 | 74 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 12 | 50 | 18 | 2 | 0 | 0 | 80 | 0 | 280 | 151 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 9 | 90 | 109 | 0 | 22 | 2 | 42 | 30 | 50 | 0 | 110 | 128 | 40 | 73 | 0 | 165 | 0 | 0 | 10 | 300 | 23 | 2 | 0 | 45 | 0 | 0 | 8 | 0 | 50 | 19 | 40 | 0 | 40 | 399 | 75 | 0 | 34 | 4 | 245 | 54 | 51 | 0 | 58 | 10 | 50 | 91 | 49 | 162 | 0 | 65 | 17 | 29 | 15 | 0 |  | 708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 81 | 0 | 136 | 0 | 0 | 0 | 0 | 173 | 0 | 79 | 0 | 191 | 0 | 402 | 53 | 0 | 70 | 0 | 34 | 0 | 5 | 70 | 320 | 104 | 0 | 0 | 5 |  | 5370 | 2567 | 7937 | 2898 | 708 | 1952 | 0 | 1534 | 537 | 74 | 0 | 16 | 90 | 113 | 0 | 100.72
12:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 362 | 338 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 72 | 16 | 25 | 0 | 0 | 0 | 35 | 17 | 54 | 19 | 25 | 24 | 30 | 33 | 48 | 0 | 75 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 12 | 50 | 18 | 2 | 0 | 0 | 80 | 0 | 305 | 181 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 9 | 98 | 109 | 0 | 22 | 2 | 42 | 30 | 50 | 0 | 130 | 126 | 40 | 72 | 0 | 218 | 0 | 0 | 10 | 300 | 23 | 2 | 0 | 45 | 0 | 0 | 8 | 0 | 52 | 19 | 40 | 0 | 40 | 402 | 75 | 0 | 34 | 4 | 245 | 54 | 51 | 0 | 57 | 10 | 50 | 94 | 50 | 162 | 0 | 65 | 17 | 31 | 0 | 0 |  | 709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 80 | 0 | 138 | 0 | 0 | 0 | 0 | 197 | 0 | 84 | 0 | 187 | 0 | 419 | 53 | 0 | 70 | 0 | 34 | 0 | 6 | 70 | 330 | 104 | 0 | 0 | 5 |  | 5634 | 2620 | 8254 | 3050 | 709 | 2019 | 0 | 1622 | 548 | 75 | 0 | 16 | 98 | 117 | 0 | 100.71
13:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 401 | 336 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 16 | 24 | 0 | 0 | 0 | 35 | 17 | 53 | 19 | 25 | 28 | 30 | 25 | 51 | 0 | 75 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 12 | 50 | 18 | 3 | 0 | 0 | 80 | 0 | 295 | 181 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 9 | 101 | 107 | 0 | 22 | 2 | 42 | 30 | 50 | 0 | 163 | 128 | 50 | 72 | 0 | 218 | 0 | 0 | 10 | 295 | 23 | 2 | 0 | 100 | 0 | 0 | 8 | 0 | 101 | 18 | 40 | 0 | 40 | 402 | 75 | 0 | 34 | 4 | 270 | 54 | 81 | 0 | 58 | 10 | 50 | 103 | 45 | 162 | 0 | 65 | 17 | 28 | 0 | 0 |  | 709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 10 | 0 | 11 | 82 | 0 | 138 | 0 | 0 | 0 | 0 | 200 | 0 | 83 | 0 | 194 | 0 | 340 | 53 | 0 | 70 | 0 | 34 | 0 | 6 | 70 | 340 | 104 | 0 | 0 | 5 |  | 5890 | 2548 | 8438 | 3093 | 709 | 1954 | 0 | 1822 | 560 | 75 | 0 | 16 | 101 | 108 | 0 | 100.7
14:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 354 | 301 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 16 | 24 | 0 | 0 | 0 | 35 | 17 | 53 | 19 | 25 | 28 | 28 | 25 | 34 | 0 | 76 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 3 | 0 | 0 | 80 | 0 | 320 | 181 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 33 | 9 | 99 | 105 | 0 | 22 | 2 | 42 | 30 | 53 | 0 | 130 | 125 | 50 | 72 | 0 | 205 | 0 | 0 | 10 | 270 | 23 | 2 | 0 | 155 | 0 | 0 | 8 | 0 | 105 | 15 | 10 | 0 | 24 | 371 | 75 | 0 | 17 | 3 | 300 | 35 | 68 | 0 | 58 | 0 | 50 | 104 | 39 | 162 | 0 | 65 | 17 | 26 | 0 | 0 |  | 709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 138 | 0 | 0 | 0 | 0 | 182 | 0 | 85 | 0 | 188 | 0 | 335 | 17 | 0 | 35 | 0 | 0 | 0 | 5 | 35 | 340 | 104 | 0 | 0 | 4 |  | 5647 | 2366 | 8013 | 2992 | 709 | 1883 | 0 | 1586 | 558 | 76 | 0 | 16 | 99 | 94 | 0 | 100.69
15:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 358 | 331 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 70 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 26 | 28 | 33 | 16 | 0 | 77 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 3 | 0 | 0 | 80 | 0 | 275 | 181 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 33 | 9 | 102 | 106 | 0 | 22 | 1 | 42 | 30 | 53 | 0 | 163 | 125 | 56 | 72 | 0 | 205 | 0 | 0 | 10 | 270 | 23 | 2 | 0 | 95 | 0 | 0 | 8 | 0 | 80 | 11 | 40 | 0 | 24 | 403 | 55 | 0 | 0 | 2 | 260 | 35 | 90 | 0 | 58 | 0 | 50 | 70 | 28 | 109 | 0 | 65 | 17 | 16 | 0 | 0 |  | 696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 140 | 0 | 0 | 0 | 0 | 179 | 0 | 84 | 0 | 184 | 0 | 419 | 35 | 0 | 80 | 0 | 0 | 0 | 3 | 0 | 340 | 104 | 0 | 0 | 3 |  | 5430 | 2459 | 7889 | 2991 | 696 | 2029 | 0 | 1353 | 561 | 77 | 0 | 16 | 102 | 64 | 0 | 100.68
16:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 403 | 326 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 48 | 16 | 25 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 26 | 28 | 33 | 16 | 0 | 77 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 2 | 0 | 0 | 80 | 0 | 275 | 181 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 9 | 97 | 110 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 126 | 58 | 72 | 0 | 205 | 0 | 0 | 10 | 310 | 23 | 2 | 0 | 95 | 0 | 0 | 8 | 0 | 65 | 6 | 40 | 0 | 24 | 376 | 35 | 0 | 0 | 1 | 260 | 54 | 106 | 0 | 58 | 0 | 52 | 73 | 11 | 108 | 0 | 65 | 17 | 7 | 0 | 0 |  | 697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 140 | 0 | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 196 | 0 | 414 | 35 | 0 | 113 | 0 | 0 | 0 | 2 | 0 | 310 | 104 | 0 | 0 | 0 |  | 5430 | 2470 | 7900 | 3031 | 697 | 2058 | 0 | 1366 | 531 | 77 | 0 | 16 | 97 | 27 | 0 | 100.67
17:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 396 | 333 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 48 | 16 | 24 | 0 | 0 | 0 | 35 | 5 | 55 | 0 | 25 | 26 | 28 | 25 | 16 | 0 | 67 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 4 | 50 | 19 | 3 | 0 | 0 | 100 | 0 | 275 | 186 | 8 | 90 | 29 | 5 | 0 | 51 | 0 | 0 | 12 | 21 | 11 | 33 | 9 | 94 | 120 | 0 | 22 | 0 | 40 | 30 | 53 | 0 | 163 | 131 | 52 | 75 | 0 | 219 | 0 | 0 | 10 | 300 | 24 | 2 | 0 | 110 | 0 | 0 | 8 | 0 | 69 | 0 | 50 | 0 | 43 | 353 | 35 | 0 | 0 | 0 | 300 | 54 | 106 | 17 | 93 | 0 | 54 | 84 | 0 | 124 | 0 | 65 | 17 | 0 | 0 | 2 |  | 696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 11 | 81 | 0 | 140 | 0 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 194 | 0 | 352 | 35 | 0 | 113 | 0 | 10 | 0 | 0 | 10 | 310 | 104 | 0 | 0 | 0 |  | 5582 | 2426 | 8008 | 3025 | 696 | 2000 | 0 | 1577 | 531 | 67 | 0 | 16 | 94 | 0 | 0 | 100.66
18:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 382 | 331 |  | 0 | 270 | 150 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 80 | 64 | 25 | 0 | 0 | 0 | 54 | 42 | 55 | 15 | 25 | 17 | 28 | 25 | 40 | 0 | 78 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 50 | 59 | 50 | 19 | 10 | 0 | 0 | 100 | 0 | 275 | 186 | 8 | 89 | 29 | 5 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 9 | 110 | 120 | 0 | 22 | 0 | 40 | 30 | 53 | 0 | 163 | 129 | 52 | 77 | 0 | 219 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 217 | 0 | 0 | 34 | 0 | 117 | 0 | 100 | 20 | 113 | 352 | 115 | 34 | 48 | 0 | 300 | 54 | 106 | 34 | 106 | 70 | 52 | 104 | 0 | 157 | 0 | 65 | 17 | 0 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 34 | 8 | 22 | 0 | 11 | 80 | 0 | 140 | 0 | 0 | 0 | 0 | 179 | 0 | 87 | 0 | 192 | 0 | 411 | 102 | 0 | 113 | 0 | 100 | 0 | 0 | 100 | 370 | 104 | 0 | 0 | 0 |  | 6603 | 2911 | 9514 | 3015 | 698 | 2072 | 0 | 2753 | 590 | 78 | 0 | 198 | 110 | 0 | 0 | 100.65
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 397 | 337 |  | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 32 | 24 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 30 | 28 | 25 | 52 | 0 | 62 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 4 | 0 | 51 | 0 | 75 | 50 | 19 | 5 | 0 | 0 | 100 | 0 | 270 | 184 | 8 | 88 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 102 | 127 | 0 | 20 | 0 | 40 | 30 | 53 | 0 | 163 | 127 | 53 | 80 | 0 | 219 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 195 | 0 | 0 | 24 | 0 | 110 | 0 | 100 | 51 | 130 | 353 | 115 | 17 | 17 | 0 | 300 | 54 | 85 | 17 | 108 | 20 | 90 | 104 | 0 | 162 | 0 | 65 | 17 | 0 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 0 | 52 | 35 | 22 | 0 | 11 | 79 | 0 | 135 | 0 | 0 | 0 | 0 | 183 | 0 | 87 | 0 | 188 | 0 | 361 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 430 | 104 | 0 | 0 | 0 |  | 6480 | 3057 | 9537 | 3085 | 698 | 2007 | 0 | 2671 | 644 | 62 | 0 | 268 | 102 | 0 | 0 | 100.62
19:30 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 392 | 337 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 16 | 25 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 30 | 28 | 25 | 52 | 0 | 78 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 19 | 0 | 51 | 0 | 51 | 50 | 19 | 8 | 0 | 0 | 100 | 0 | 310 | 203 | 8 | 89 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 102 | 126 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 132 | 52 | 80 | 0 | 219 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 130 | 0 | 0 | 24 | 0 | 70 | 0 | 100 | 51 | 132 | 352 | 115 | 17 | 17 | 0 | 300 | 54 | 17 | 17 | 108 | 0 | 95 | 104 | 0 | 162 | 0 | 65 | 17 | 0 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 25 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 11 | 79 | 0 | 133 | 0 | 0 | 0 | 0 | 187 | 0 | 87 | 0 | 188 | 0 | 411 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 430 | 104 | 0 | 0 | 0 |  | 6300 | 3037 | 9337 | 3154 | 698 | 2093 | 0 | 2394 | 642 | 78 | 0 | 176 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 390 | 226 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 16 | 25 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 78 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 0 | 53 | 50 | 19 | 13 | 0 | 0 | 100 | 0 | 270 | 220 | 8 | 90 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 100 | 136 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 132 | 60 | 80 | 0 | 219 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 130 | 0 | 0 | 24 | 0 | 70 | 0 | 100 | 51 | 133 | 355 | 115 | 17 | 17 | 0 | 300 | 54 | 17 | 17 | 108 | 0 | 100 | 104 | 0 | 162 | 0 | 65 | 17 | 0 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 25 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 134 | 0 | 0 | 0 | 0 | 186 | 0 | 85 | 0 | 191 | 0 | 411 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 430 | 105 | 0 | 0 | 0 |  | 6142 | 3034 | 9176 | 3166 | 698 | 1977 | 0 | 2344 | 644 | 78 | 0 | 169 | 100 | 0 | 0 | 100.63
21:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 364 | 261 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 10 | 25 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 78 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 50 | 50 | 19 | 24 | 0 | 0 | 100 | 0 | 300 | 184 | 8 | 89 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 97 | 132 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 134 | 32 | 80 | 0 | 219 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 80 | 0 | 0 | 0 | 0 | 65 | 0 | 100 | 51 | 127 | 352 | 85 | 0 | 0 | 0 | 260 | 54 | 0 | 17 | 108 | 0 | 114 | 104 | 0 | 162 | 46 | 65 | 17 | 0 | 0 | 0 |  | 697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 131 | 0 | 0 | 0 | 0 | 182 | 0 | 85 | 0 | 186 | 0 | 403 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 430 | 106 | 0 | 0 | 0 |  | 5945 | 2903 | 8848 | 3109 | 697 | 2006 | 0 | 2177 | 640 | 78 | 0 | 44 | 97 | 0 | 0 | 100.62
22:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 363 | 261 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 64 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 20 | 50 | 19 | 31 | 0 | 0 | 100 | 0 | 305 | 184 | 8 | 90 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 91 | 133 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 124 | 32 | 80 | 0 | 219 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 42 | 0 | 100 | 51 | 128 | 352 | 60 | 0 | 0 | 0 | 260 | 54 | 0 | 0 | 108 | 0 | 128 | 104 | 0 | 162 | 70 | 65 | 17 | 0 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 11 | 79 | 0 | 132 | 0 | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 185 | 0 | 360 | 105 | 0 | 113 | 0 | 49 | 0 | 0 | 113 | 430 | 105 | 0 | 0 | 0 |  | 5687 | 2776 | 8463 | 3107 | 698 | 1959 | 0 | 1886 | 641 | 64 | 0 | 17 | 91 | 0 | 0 | 100.61
23:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 352 | 261 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 78 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 100 | 0 | 315 | 188 | 8 | 91 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 33 | 9 | 86 | 127 | 0 | 22 | 0 | 41 | 30 | 53 | 0 | 163 | 125 | 32 | 81 | 0 | 219 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 132 | 352 | 60 | 0 | 0 | 0 | 210 | 54 | 0 | 0 | 98 | 0 | 141 | 104 | 0 | 162 | 17 | 65 | 17 | 0 | 0 | 0 |  | 697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 129 | 0 | 0 | 0 | 0 | 182 | 0 | 85 | 0 | 197 | 0 | 411 | 17 | 0 | 70 | 0 | 0 | 0 | 0 | 70 | 410 | 106 | 0 | 0 | 0 |  | 5239 | 2579 | 7818 | 3133 | 697 | 2024 | 0 | 1182 | 618 | 78 | 0 | 0 | 86 | 0 | 0 | 100.6
24:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 358 | 261 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 100 | 0 | 305 | 185 | 8 | 91 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 9 | 82 | 127 | 0 | 22 | 0 | 41 | 30 | 50 | 0 | 163 | 124 | 32 | 81 | 0 | 219 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 50 | 351 | 45 | 0 | 0 | 0 | 210 | 54 | 0 | 0 | 55 | 0 | 225 | 17 | 0 | 108 | 17 | 65 | 17 | 0 | 0 | 0 |  | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 74 | 0 | 131 | 0 | 0 | 0 | 0 | 182 | 0 | 85 | 0 | 198 | 0 | 414 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 380 | 106 | 0 | 0 | 0 |  | 4977 | 2396 | 7373 | 3207 | 630 | 2013 | 0 | 781 | 585 | 75 | 0 | 0 | 82 | 0 | 0 | 100.6
KWH | 0 | 0 | 0 | 4536000 | 0 | 0 | 0 | 9046010 | 7460000 |  | 0 | 6644750 | 3638516 | 0 | 0 | 423871 | 0 | 0 | 0 | 0 | 910944 | 279360 | 337700 | 0 | 0 | 0 | 998892 | 245247 | 839885 | 307404 | 600000 | 651780 | 718700 | 777300 | 353846 | 0 | 1649738 | 0 | 0 | 0 | 149461 | 0 | 0 | 0 | 0 |  | 123360 | 0 | 177537 | 105000 | 328248 | 984000 | 439968 | 377760 | 0 | 0 | 2234014 | 0 | 7074000 | 4367000 | 535272 | 2125120 | 661248 | 329760 | 0 | 1188992 | 0 | 0 | 488026 | 512712 | 200160 | 692600 | 213770 | 2079360 | 2883840 | 0 | 493992 | 13600 | 981000 | 701880 | 1075200 | 0 | 3701536 | 2949000 | 1039872 | 1448640 | 0 | 4991220 | 0 | 0 | 211860 | 7266000 | 427248 | 113856 | 0 | 1583235 | 0 | 0 | 206400 | 0 | 1030180 | 132435 | 925440 | 249600 | 1344872 | 9114000 | 1504800 | 73284 | 332872 | 26279 | 5675815 | 1238159 | 1056322 | 86640 | 1480080 | 156480 | 1612200 | 1620480 | 319530 | 2770560 | 302345 | 1531527 | 443880 | 198392 | 34560 | 6840 |  | 14615272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1573000 | 410900 | 0 | 0 | 0 | 0 | 112576 | 0 | 178648 | 0 | 0 | 0 | 370560 | 77573 | 394320 | 0 | 220428 | 1947054 | 0 | 3367800 | 0 | 0 | 0 | 0 | 4685236 | 0 | 1321505 | 0 | 4723664 | 0 | 8935709 | 1057632 | 0 | 1621536 | 0 | 688838 | 0 | 34821 | 1291008 | 9218600 | 3158318 | 0 | 0 | 35100 |  | 129163262 | 60040098 | 189203360 | 73199749 | 14615272 | 48099038 | 0 | 33399498 | 14533454 | 1649738 | 0 | 825694 | 2079360 | 760157 | 0
Fuel Cost | 0 | 0 | 0 | 6667920 | 0 | 0 | 0 | 9136470.1 | 7683800 |  | 0 | 7242777.5 | 4038752.76 | 0 | 0 | 3585948.66 | 0 | 0 | 0 | 0 | 8307809.28 | 2748902.4 | 3113594 | 0 | 0 | 0 | 7291911.6 | 1895759.31 | 8281266.1 | 230553 | 450000 | 0 | 0 | 0 | 3421690.82 | 0 | 445429.26 | 0 | 0 | 0 | 1388492.69 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1722108.9 | 1002750 | 2855757.6 | 7793280 | 554359.68 | 1121947.2 | 0 | 0 | 3284000.58 | 0 | 7074000 | 4017640 | 690500.88 | 2443888 | 747210.24 | 461664 | 0 | 2033176.32 | 0 | 0 | 4660648.3 | 651144.24 | 150120 | 1212050 | 160327.5 | 15595200 | 3056870.4 | 0 | 627369.84 | 216784 | 1608840 | 1123008 | 1913856 | 0 | 4219751.04 | 3066960 | 2048547.84 | 2766902.4 | 0 | 8634810.6 | 0 | 0 | 432194.4 | 7338660 | 320436 | 86530.56 | 0 | 11969256.6 | 0 | 0 | 1073280 | 0 | 10136971.2 | 1548165.15 | 7542336 | 2708160 | 9481347.6 | 8476020 | 13723776 | 692533.8 | 2899315.12 | 0 | 42909161.4 | 10784364.89 | 9285070.38 | 864667.2 | 12684285.6 | 1042156.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 84183966.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1777490 | 636895 | 0 | 0 | 0 | 0 | 1107747.84 | 0 | 1581034.8 | 0 | 0 | 0 | 3590726.4 | 752458.1 | 757094.4 | 0 | 166863.996 | 11740735.62 | 0 | 18253476 | 0 | 0 | 0 | 0 | 6184511.52 | 0 | 1982257.5 | 0 | 5526686.88 | 0 | 8846351.91 | 11041678.08 | 0 | 15388376.64 | 0 | 5345382.88 | 0 | 384772.05 | 9540549.12 | 40469654 | 0 | 0 | 0 | 0 |  | 319445239.74 | 229258709.456 | 548703949.196 | 79484628.976 | 84183966.72 | 52166581.31 | 0 | 236302304.07 | 70463865.62 | 445429.26 | 0 | 7912252.04 | 15595200 | 2149721.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 362 | 338 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 72 | 16 | 25 | 0 | 0 | 0 | 35 | 17 | 54 | 19 | 25 | 24 | 30 | 33 | 48 | 0 | 75 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 12 | 50 | 18 | 2 | 0 | 0 | 80 | 0 | 305 | 181 | 8 | 91 | 29 | 5 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 9 | 98 | 109 | 0 | 22 | 2 | 42 | 30 | 50 | 0 | 130 | 126 | 40 | 72 | 0 | 218 | 0 | 0 | 10 | 300 | 23 | 2 | 0 | 45 | 0 | 0 | 8 | 0 | 52 | 19 | 40 | 0 | 40 | 402 | 75 | 0 | 34 | 4 | 245 | 54 | 51 | 0 | 57 | 10 | 50 | 94 | 50 | 162 | 0 | 65 | 17 | 31 | 0 | 0 |  | 709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 80 | 0 | 138 | 0 | 0 | 0 | 0 | 197 | 0 | 84 | 0 | 187 | 0 | 419 | 53 | 0 | 70 | 0 | 34 | 0 | 6 | 70 | 330 | 104 | 0 | 0 | 5 |  | 8254 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 397 | 337 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 32 | 24 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 30 | 28 | 25 | 52 | 0 | 62 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 51 | 0 | 75 | 50 | 19 | 5 | 0 | 0 | 100 | 0 | 270 | 184 | 8 | 88 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 102 | 127 | 0 | 20 | 0 | 40 | 30 | 53 | 0 | 163 | 127 | 53 | 80 | 0 | 219 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 195 | 0 | 0 | 24 | 0 | 110 | 0 | 100 | 51 | 130 | 353 | 115 | 17 | 17 | 0 | 300 | 54 | 85 | 17 | 108 | 20 | 90 | 104 | 0 | 162 | 0 | 65 | 17 | 0 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 0 | 52 | 35 | 22 | 0 | 11 | 79 | 0 | 135 | 0 | 0 | 0 | 0 | 183 | 0 | 87 | 0 | 188 | 0 | 361 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 430 | 104 | 0 | 0 | 0 |  | 9537 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 412 | 300 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 66 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 80 | 100 | 90 | 50 | 20 | 11 | 0 | 0 | 100 | 0 | 360 | 220 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 140 | 0 | 22 | 0 | 40 | 30 | 51 | 0 | 163 | 144 | 66 | 80 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 125 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 320 | 104 | 0 | 162 | 116 | 100 | 17 |  |  |  |  | 721 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 68 | 20 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 27 | 50 | 40 | 52 | 35 | 22 | 0 | 11 | 84 | 0 | 142 | 0 | 0 | 0 | 0 | 220 | 0 | 87 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 110 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 360 | 300 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 66 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 20 | 5 | 0 | 0 | 100 | 0 | 360 | 220 | 68 | 90 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 140 | 0 | 22 | 1.6 | 40 | 30 | 50 | 0 | 163 | 144 | 60 | 80 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 300 | 0 | 100 | 200 | 50 | 149 | 20 | 100 | 200 | 125 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 300 | 104 | 50 | 162 | 116 | 100 | 17 | 30 |  |  |  | 721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 20 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 84 | 0 | 142 | 0 | 0 | 0 | 0 | 200 | 0 | 87 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 110 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 351 | 261 | 0 | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 30 | 20 | 25 | 24 | 28 |  | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 5 | 0 | 0 | 100 | 0 | 305 | 184 | 8 | 90 | 29 | 15 | 0 | 35 | 0 | 0 | 3 | 22 | 0 | 33 | 9 | 74 | 133 | 0 | 22 | 2 | 41 | 30 | 47 | 0 | 140 | 124 | 0 | 71 | 0 | 218 | 0 | 0 | 10 | 300 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 10 | 0 | 46 | 330 | 55 | 0 | 0 | 1 | 230 | 54 | 17 | 0 | 57 | 0 | 300 | 60 | 16 | 133 | 61 | 65 | 17 | 11 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 142 | 0 | 0 | 0 | 0 | 200 | 0 | 63 | 0 | 169 | 0 | 360 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 25 | 320 | 105 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 6127 | 5:00
| Highest Generation |  | 9537 | 19:00
| Day Peak Generation |  | 8254 | 12:00
| Evening Peak Generation |  | 9537 | 19:00
| HVDC Max Flow |  | 709 | 10:00
| HVDC EvPeak Flow |  | 698 | 19:00
| Load factor L.F |  | 82.66%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-12-02
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-12-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8254 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 6013 | MW
Evening Peak Generation : |  | 9537 | MW Hour : | 19:00 | Available Max Generation : |  | 13781 | MW
E.P. Demand (at gen end) : |  | 9537 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9700 | MW
Maximum Generation : |  | 9537 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4081 | MW
Total Gen. (MKWH) : |  | 189.162 | System Load Factor : | 82.66% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -73 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-12-02
Actual : | 100.57 | Ft.(MSL) , | Rule curve : | 106 | Ft.( MSL )
Gas Consumed : | Total = | 947.52 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 131651210.286
: |  | Coal : | 70463865.62 | Oil : | 244214556.11 | Total : | 446329632.016
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3452.4768 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1170.441 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1048.0363 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 946.7619 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 855.7004 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 690.5109 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 390.7222 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 177.9103 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 532.5341 |  |  | 0 | 0%
Total | 0 |  | 9265.094 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan unit-1&2
7) Ashuganj(N)-360 MW.
8) Nutun Bidduit-220 MW GT-2.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Agargaon-Rampura 132 kV Ckt-1 was under shut down from 12:17 to 12:40 for A/M.
b) Agargaon-Rampura 132 kV Ckt-2 was under shut down from 12:43 to 13:04 for A/M.
c) Amnura 132/33 kV T-3 transformer was under shut down from 08:27 to 16:19 for A/M.
d) B.Baria-Shahjibazar 132 kV Ckt-1 was under shut down from 09:02 to 16:31 for A/M.
e) Barapukuria S/S-Barapukuria P/S 230 kV Ckt-1 was under shut down from 08:38 to 17:02 for A/M.
f) Cantonment 132/33 kV T-1 transformer was under shut down from 11:26 to 11:53 for A/M.
g) Cantonment 132/33 kV T-2 transformer was under shut down from 09:16 to 11:19 for A/M.
h) Fenchuganj-Bibiyana 230 kV Ckt-2 was under shut down from 09:10 to 17:28 for A/M.
i) Ghorasal-Ashuganj 132 kV Ckt-1 was under shut down from 09:19 to 17:01 for A/M.
j) Hathazari-Kaptai 132 kV Ckt-2 was under shut down from 08:53 to 16:55 for A/M.
k) Kallyanpur 132/33 kV T-3 transformer was under shut down from 08:13 to 18:40 for A/M.
l) Keraniganj-Aminbazar 132 kV Ckt-1 was under shut down from 10:47 to 12:48 for A/M.
m) Madaripur-Gopalganj(N) 132 kV Ckt-1 &2 were under shut down from 09:18 to 16:54 for A/M.
n) Magura 132/33 kV T-1 transformer was under shut down from 08:25 to 16:21 for A/M.
o) Kabirpur-Manikganj 132 kV Ckt-1 was under shut down from 10:10 to 16:00 for A/M.
p) Sylhet 132/33 kV T-2 transformer was under shut down from 09:27 to 11:25 for A/M.
q) Sylhet-Chatak 132 kV Ckt-2 was under shut down from 11:27 to 12:49 for A/M.
r) Thakurgaon 132/33 kV T-3 transformer was under shut down from 09:05 to 16:55 for A/M.
s) Mirpur-Uttara 132 kV Ckt was under shut down from 09:34 to 15:37 for A/M.
t) Sylhet-Chatak 132 kV Ckt-1 was under shut down from 12:56 to 13:51 for A/M.
u) Sylhet 132/33 kV T-1 transformer was under shut down from 14:29 to 16:15 for D/W.
v) Shyampur-APR 230 kV Ckt was switched on at 17:21.
w) Bibiyana South ST was synchronized at 18:36.
x) Shahjibazar GT-8 was synchronized at 20:44.
y) Hasnabad-APR 230 kV Ckt is under shut down since 07:04(02/12/21) for A/M.
z) Shyampur-APR 230 kV Ckt is under shut down since 06:46(02/12/21) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-12-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4536000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 9046010 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7460000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6644750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3638516 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 423871
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 24 | 337700 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 307404 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 910944
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 998892
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 279360 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 245247 | Low demand.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 839885
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1251780 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 718700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 777300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 52 | 353846
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 1583235 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 110 | 1030180 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 73284 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1620480
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2770560
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 198392
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 0 | 6840
| Dhaka area Total |  |  |  | 5560 | 2450 | 46053176
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 149461 | Low demand.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 132435
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 984000
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 62 | 1649738 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 332872 | Low demand.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 177537 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 105000 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 925440
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 439968 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 377760
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 75 | 328248 | Line O/L
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26279
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 5675815
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1238159
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 85 | 1056322 | Low demand.
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 20 | 156480 | Low demand.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 302345 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 855 | 14057859
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2234014 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4367000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Ashuganj 400 kV Bus S/D
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7074000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 661248 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 329760 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 535272 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1188992
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 1344872 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 88 | 2125120 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 51 | 249600 | Low demand.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 512712
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 200160
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2079360
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 692600
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 488026
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 213770 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 86640 | Low demand.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 108 | 1480080 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443880 | 33 kV feeder fault.
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 34560 | On test
| Cumilla Area Total |  |  |  | 3034 | 1287 | 26341666
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 127 | 2883840 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 493992
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13600
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 24 | 206400 | Low demand.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1504800
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 319530
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 4 | 123360 | Low demand.
| Mymensingh Area Total |  |  |  | 622 | 290 | 5545522
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 981000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 701880 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3701536
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 127 | 2949000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1075200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 113856
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 53 | 1039872 | GT-8 under maint
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1448640
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 65 | 1531527 | Gas shortage
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4991220
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 427248
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7266000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 353 | 9114000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 211860
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 90 | 1612200 | ST synchronization process.
| Sylhet Area Total |  |  |  | 2377 | 1598 | 37165039
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 698 | 14615272
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1057632
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 803 | 15672904
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 410900 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1573000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 87 | 1321505 | Engine problem
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 9218600 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 104 | 3158318
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 707 | 15682323
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 112576
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4685236 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4723664 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 361 | 8935709 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 77573 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 394320
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 220428
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 370560
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 178648
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1621536
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1291008
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35100
| Rajshahi Area Total |  |  |  | 2179 | 1228 | 22646358
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1947054
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 135 | 3367800 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 688838 | Engine problem
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34821
| Rangpur Area Total |  |  |  | 605 | 319 | 6038513
| Total |  |  |  | 20934 | 9537 | 189203360
| Eastern Grid Total |  |  |  | 13975 | 6480 | 129163262
| Western Grid Total |  |  |  | 6959 | 3057 | 60040098
| National Grid Total |  |  |  | 20934 | 9537 | 189203360
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-12-01
(a) ENTIRE EASTERN GRID : |  | 6322 | MW | (b) ENTIRE WESTERN GRID : |  | 2777 | MW
i) Dhaka area |  | 3481 | MW | i) Khulna area |  | 1044 | MW
ii) Chittagong area |  | 1052 | MW | ii) Rajshahi area |  | 890 | MW
iii) Comilla area |  | 742 | MW | iii) Barisal area |  | 244 | MW
iv) Mymensingh area |  | 705 | MW | iv) Rangpur area |  | 599 | MW
v) Sylhet area |  | 342 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9099 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 12:00 | Mymensing | 152 | 18:00 | Jessore | 78 | 18:30
Munsiganj | 64 | 20:00 | Kishoreganj | 88 | 18:00 | Benapol | 38 | 18:00
Sonargaon | 58 | 19:00 | Netrokona | 81 | 18:00 | Jhenida(Old) | 80 | 18:00
Shyampur | 164 | 9:00 | Jamalpur | 94 | 18:00 | Bottail | 94 | 18:00
Bhulta | 165 | 11:00 | Sherpur | 94 | 18:00 | G.K Project | 35 | 18:00
Madanganj | 41 | 10:00 | Srimongal | 38 | 18:00 | Faridpur | 103 | 18:30
Shitalakhya | 106 | 12:00 | Shahjibazar | 83 | 18:00 | Rajbari | 32 | 18:00
Rahim steel | 22 | 23:00 | Fenchuganj | 30 | 17:00 | Madaripur | 63 | 20:00
Matuail | 51 | 10:00 | Kulawara | 30 | 18:00 | Sariatpur | 42 | 20:00
Ghorasal | 60 | 19:00 | Sylhet | 90 | 18:00 | Gopalganj | 66 | 18:00
Narsingdi | 125 | 18:30 | Chatak | 18 | 20:00 | Bagerhat | 66 | 18:30
Haripur (SBU) | 114 | 19:00 | Sunamganj | 30 | 19:00 | Mongla | 42 | 10:00
Sreenagar | 25 | 21:00 | Biani Bazar | 39 | 18:00 | Satkhira | 67 | 18:00
Ullon | 43 | 13:00 | Comilla (S) | 110 | 18:00 | Gallamari | 23 | 13:00
Hasnabad | 60 | 11:00 | Comilla(N) | 79 | 19:30 | Magura | 40 | 18:00
Magbazar | 71 | 13:00 | Chandpur | 42 | 21:00 | Norail | 34 | 18:00
Maniknagar | 56 | 13:00 | Feni | 85 | 18:00 | Chuadanga | 62 | 18:00
Bangabhaban | 8 | 10:00 | Chowmuhani | 128 | 18:00 | Barisal(N) | 26 | 19:00
Motijheel | 21 | 12:00 | Ashuganj | 27 | 23:00 | Barisal (S) | 76 | 18:00
Narinda | 48 | 13:00 | Daudkandi | 92 | 18:00 | Patuakhali | 77 | 21:00
Kazla | 69 | 18:00 | B.Baria | 102 | 19:30 | Bhandaria | 36 | 19:00
Dhanmondi | 145 | 13:00 | Ramganj | 52 | 21:00 | Borguna | 12 | 20:00
Lalbag | 84 | 11:00 | Chaddagram | 23 | 18:00 | Borhan Uddin | 26 | 20:00
Madartek | 51 | 18:00 | PHP | 2 | 2:00 | Ishurdi | 52 | 18:00
Dhaka University | 25 | 12:00 | Kochua | 38 | 19:00 | Ruppur Paromanobik | 3 | 1:00
Aftabnagar | 12 | 18:00 | Madunaghat | 42 | 18:00 | Natore | 87 | 18:00
Fatullah | 52 | 12:00 | Hathazari | 70 | 19:00 | Bogra | 110 | 18:00
Nawabganj | 32 | 21:00 | Khulshi | 132 | 23:00 | Noagaon | 84 | 18:30
Keraniganj | 52 | 18:00 | Halishahar | 88 | 14:00 | Rajshahi | 97 | 18:30
Banani | 45 | 13:00 | Baraulia | 149 | 13:00 | Rajshahi New | 14 | 18:00
Mirpur | 94 | 12:00 | Sikalbaha | 36 | 18:00 | C.Nawabganj | 41 | 12:00
Kalyanpur | 66 | 17:00 | Dohazari | 70 | 18:30 | Amnura | 32 | 18:30
Gulshan | 80 | 13:00 | Cox'sbazar | 83 | 18:30 | Pabna | 68 | 18:00
Uttara | 63 | 13:00 | Chandraghona | 22 | 18:00 | Shahjadpur | 75 | 18:30
Uttara New | 13 | 13:00 | Kaptai | 3.2 | 18:00 | Serajganj | 68 | 18:30
Kamrangirchar | 80 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 40 | 9:00
Savar | 118 | 12:00 | Bakulia | 95 | 18:00 | Joypurhat | 46 | 18:30
Bhasantec | 83 | 18:00 | Julda | 23 | 10:00 | Sherpur(Bogura) | 48 | 18:00
Agargaon | 58 | 13:00 | TK chemical | 23 | 19:30 | Mohastangor | 46 | 18:00
Satmosjid | 75 | 18:00 | Modern Steel | 7 | 10:00 | Bhangura | 20 | 18:00
Tongi | 102 | 11:00 | Shahmirpur | 29 | 18:00 | Rangpur | 96 | 18:30
Kabirpur | 224 | 18:00 | Khagrachhari | 20 | 18:00 | Lalmonirhat | 40 | 18:30
Basundhara | 157 | 18:00 | Matarbari | 24.5 | 17:00 | Saidpur | 82 | 18:30
Purbachal | 55 | 19:30 | Baroiar Hat | 32 | 18:00 | Purbasadipur | 86 | 18:00
Manikganj | 140 | 18:00 | Rangamati | 10 | 18:00 | Thakurgaon | 64 | 18:30
Joydevpur | 67 | 12:00 | Abul Khair 230 | 129 | 6:00 | Palashbari | 87 | 18:00
New Tongi | 222 | 18:30 | BSRM | 152 | 4:00 | Barapukuria | 41 | 19:00
Kodda | 80 | 18:00 | GPH Ispat | 99 | 18:00 | Panchagar | 47 | 18:00
Dhamrai | 82 | 18:30 | Agrabad | 69 | 18:00 | Joldhaka | 29 | 18:00
Rajendrapur | 12 | 18:30 | Goalpara | 24 | 13:00 | Kurigram | 47 | 18:00
Valuka | 84 | 18:00 | Central S/S | 69 | 18:00 | Mithapukur | 24 | 18:00
Tangail | 142 | 18:00 | Noapara | 36 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-12-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 8:00 | 403 | 11:00 | Kaliakoir | 399 | 0.25 | 387 | 0.66667
| Bheramara | 406 | 20:00 | 395 | 13:00 | Bhulta | 374 | 0.33333 | 359 | 0.66667
| Ashuganj(N) | 0 | 0:00 | 0 | 0:00 | Gopalganj | 415 | 0.625 | 404 | 0.75
| Payra | 415 | 8:00 | 407 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 235 | 13:00 | Hathazari | 237 | 21:00 | 220 | 23:00
| Ishurdi | 238 | 5:00 | 226 | 13:00 | Megnaghat | 234 | 19:00 | 230 | 12:00
| Ashuganj | 245 | 19:00 | 235 | 12:00 | Fenchuganj | 246 | 18:00 | 241 | 15:00
| Serajganj | 238 | 19:00 | 232 | 14:00 | Siddhirganj | 232 | 18:00 | 224 | 9:00
| Baghabari | 237 | 4:00 | 228 | 14:00 | Maniknagar | 231 | 18:00 | 223 | 15:00
| Barapukuria | 237 | 3:00 | 233 | 7:00 | Agargaon | 232 | 10:00 | 223 | 12:00
| Bogra | 236 | 21:00 | 228 | 12:00 | Barisal | 247 | 19:00 | 243 | 18:30
| Rajshahi | 234 | 5:00 | 222 | 12:00 | Bhola 225 MW | 250 | 15:00 | 243 | 22:00
| Khulna South | 241 | 5:00 | 223 | 7:00 | AKSML | 241 | 19:00 | 213 | 4:00
| Rampura | 230 | 1:00 | 222 | 15:00 | BSRM | 239 | 18:00 | 213 | 4:00
| Haripur | 232 | 2:00 | 223 | 15:00 | Bibiyana | 244 | 1:00 | 238 | 8:00
| Hasnabad | 232 | 4:00 | 222 | 15:00 | Bhulta | 232 | 8:00 | 224 | 15:00
| Shyampur | 230 | 8:00 | 223 | 11:00 | Ashuganj (S) | 240 | 19:00 | 231 | 12:00
| Aminbazar | 232 | 1:00 | 225 | 2:00 | Kaliakoir | 228 | 15:00 | 223 | 8:00
| Tongi | 228 | 21:00 | 218 | 10:00 | GPH | 240 | 18:00 | 211 | 4:00
| Comilla (N) | 236 | 19:00 | 226 | 15:00 | Jhenaidah | 235 | 5:00 | 220 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 18:00 | 132 | 11:00 | Kachua | 141 | 0.75 | 134 | 0.125
| Munsiganj | 139 | 18:00 | 132 | 11:00 | Madanhat | 142 | 0.70833 | 132 | 0.58333
| Sonargaon | 137 | 19:00 | 132 | 12:00 | Hathazari | 139 | 0.8125 | 131 | 0.041667
| Shyampur | 138 | 8:00 | 133 | 11:00 | Khulshi | 139 | 0.75 | 126 | 0.083333
| Bhulta | 135 | 4:00 | 127 | 12:00 | Halishahar | 139 | 0.75 | 129 | 0.625
| Madanganj | 138 | 18:30 | 132 | 10:00 | Baraulia | 141 | 0.79167 | 127 | 0.083333
| Shitalakhya | 139 | 18:00 | 133 | 10:00 | Sikalbaha | 141 | 0.79167 | 129 | 0.95833
| Rahim steal | 136 | 2:00 | 131 | 15:00 | Dohazari | 137 | 0.77083 | 125 | 0.95833
| Matuail | 136 | 18:00 | 132 | 11:00 | Cox'sbazar | 125 | 0.33333 | 112 | 0.75
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Chandraghona | 141 | 0.75 | 128 | 0.16667
| Narsinghdi | 134 | 1:00 | 130 | 12:00 | Kaptai | 136 | 0.041667 | 136 | 0.041667
| Haripur (SBU) | 136 | 1:00 | 132 | 11:00 | A. Khaer Stl. | 139 | 0.75 | 129 | 0.625
| Sreenagar | 135 | 6:00 | 131 | 11:00 | Bakulia | 139 | 0.33333 | 126 | 0.083333
| Ullon | 134 | 1:00 | 127 | 12:00 | Julda | 139 | 0.79167 | 126 | 0.125
| Hasnabad | 138 | 18:00 | 134 | 10:00 | TK Chemical | 139 | 0.77083 | 131 | 0.20833
| Magbazar | 134 | 8:00 | 127 | 12:00 | Modern Steel | 139 | 0.75 | 125 | 0.16667
| Maniknagar | 135 | 5:00 | 130 | 12:00 | Shahmirpur | 139 | 0.75 | 126 | 0.083333
| Bangabhaban | 135 | 5:00 | 130 | 12:00 | Khagrachhari | 139 | 0.75 | 128 | 0.16667
| Motijheel | 135 | 5:00 | 130 | 12:00 | Matarbari | 123 | 0.33333 | 110 | 0.083333
| Narinda | 135 | 5:00 | 130 | 12:00 | Baroiar Hat | 140 | 18:00 | 132 | 15:00
| Kazla | 135 | 5:00 | 130 | 12:00 | Rangamati | 139 | 18:00 | 128 | 4:00
| Dhanmondi | 136 | 1:00 | 131 | 12:00 | Agrabad | 139 | 18:00 | 124 | 0.125
| Lalbag | 132 | 1:00 | 126 | 12:00 | Goalpara S/S | 136 | 3:00 | 125 | 0.29167
| Madartek | 134 | 1:00 | 128 | 11:00 | Khulna Central S/S | 133 | 6:00 | 125 | 0.29167
| Dhaka University | 133 | 1:00 | 128 | 11:00 | Noapara | 135 | 5:00 | 125 | 0.29167
| Aftabnagar | 134 | 1:00 | 128 | 11:00 | Jessore | 135 | 0.91667 | 124 | 0.54167
| Fatullah | 138 | 1:00 | 134 | 11:00 | Benapol | 137 | 4:00 | 123 | 0.54167
| Nawabganj | 135 | 1:00 | 130 | 12:00 | Jhenida(Old) | 137 | 0.20833 | 128 | 0.29167
| Keraniganj | 136 | 8:00 | 131 | 11:00 | Bottail | 137 | 0.125 | 129 | 0.29167
| Banani | 134 | 2:00 | 127 | 12:00 | G.K Project | 138 | 0.125 | 131 | 0.5
| Mirpur | 132 | 1:00 | 126 | 15:00 | Faridpur | 138 | 0.25 | 133 | 0.625
| Kalyanpur | 132 | 8:00 | 127 | 14:00 | Rajbari | 137 | 0.25 | 131 | 0.5
| Gulshan | 133 | 4:00 | 126 | 15:00 | Madaripur | 144 | 7:00 | 140 | 0.75
| Uttara | 133 | 18:00 | 126 | 12:00 | Shariyatpur S/S | 143 | 0.20833 | 139 | 0.75
| Uttara New | 132 | 1:00 | 126 | 15:00 | Gopalganj | 140 | 4:00 | 138 | 0.75
| Kamrangirchar | 136 | 18:30 | 130 | 11:00 | Bagerhat | 134 | 4:00 | 123 | 0.5
| Savar | 134 | 7:00 | 126 | 15:00 | Mongla | 132 | 2:00 | 123 | 12:00
| Bhasantec | 135 | 1:00 | 130 | 10:00 | Satkhira | 133 | 0.16667 | 124 | 12:00
| Agargaon | 135 | 1:00 | 131 | 11:00 | Gallamari | 140 | 10:00 | 136 | 0.41667
| Satmosjid | 136 | 8:00 | 130 | 14:00 | Magura | 138 | 0.125 | 128 | 0.5
| Tongi | 138 | 18:30 | 129 | 10:00 | Narail | 135 | 2:00 | 126 | 0.54167
| Kabirpur | 136 | 1:00 | 129 | 15:00 | Chuadanga | 138 | 5:00 | 126 | 0.54167
| Basundhara | 137 | 18:00 | 126 | 15:00 | Barisal(N) | 145 | 5:00 | 141 | 12:00
| Purbachal | 140 | 3:00 | 132 | 16:00 | Barisal (S) | 142 | 0.125 | 139 | 0.75
| Manikganj | 139 | 18:00 | 130 | 15:00 | Patuakhali(S) | 141 | 0.375 | 137 | 0.875
| Joydevpur | 137 | 18:30 | 127 | 11:00 | Bhandaria | 142 | 0.25 | 138 | 0.5
| New Tongi | 138 | 18:00 | 123 | 10:00 | Borguna | 142 | 4:00 | 138 | 19:30
| Kodda | 135 | 5:00 | 128 | 12:00 | Jhenaidah(New) | 137 | 3:00 | 129 | 7:00
| Dhamrai | 134 | 19:00 | 118 | 12:00 | Ishurdi | 138 | 5:00 | 131 | 12:00
| Rajendrapur | 137 | 15:00 | 128 | 13:00 | Ruppur Paromanobik | 137 | 1:00 | 131 | 13:00
| Valuka | 131 | 2:00 | 125 | 15:00 | Natore | 139 | 19:00 | 132 | 12:00
| Tangail | 134 | 2:00 | 129 | 12:00 | Bogra | 140 | 19:00 | 133 | 7:00
| Mymensing | 132 | 10:00 | 126 | 17:00 | Noagaon | 137 | 19:00 | 127 | 13:00
| Kishorganj | 133 | 5:00 | 129 | 18:00 | Rajshahi | 138 | 19:00 | 131 | 12:00
| Netrokona | 131 | 1:00 | 126 | 15:00 | Rajshahi New | 138 | 19:00 | 131 | 12:00
| Jamalpur | 138 | 18:00 | 126 | 0:00 | C.Nawabganj | 137 | 1:00 | 130 | 7:00
| Sherpur | 138 | 18:00 | 120 | 6:00 | Amnura | 138 | 18:30 | 128 | 14:00
| Srimongal | 139 | 6:00 | 136 | 11:00 | Pabna | 138 | 5:00 | 131 | 12:00
| Shahjibazar | 136 | 1:00 | 133 | 12:00 | Shahjadpur | 142 | 1:00 | 137 | 13:00
| Fenchuganj | 138 | 22:00 | 136 | 3:00 | Serajganj | 138 | 2:00 | 132 | 12:00
| Khulawara | 137 | 1:00 | 135 | 13:00 | Niyamatpur | 135 | 18:30 | 125 | 8:00
| Sylhet | 135 | 1:00 | 134 | 2:00 | Joypurhat | 138 | 19:00 | 126 | 11:00
| Chatak | 136 | 6:00 | 135 | 1:00 | Sherpur(Bogura) | 139 | 19:00 | 134 | 11:00
| Sunamganj | 133 | 1:00 | 132 | 17:00 | Mohastangor | 138 | 19:00 | 132 | 14:00
| Biani Bazar | 135 | 1:00 | 133 | 11:00 | Bangura | 140 | 5:00 | 133 | 12:00
| Comilla(s) | 128 | 3:00 | 124 | 12:00 | Rangpur | 136 | 21:00 | 128 | 12:00
| Comilla(n) | 143 | 19:00 | 137 | 16:00 | Lalmonirhat | 133 | 5:00 | 128 | 12:00
| Chandpur | 141 | 18:00 | 136 | 12:00 | Saidpur | 134 | 4:00 | 127 | 18:00
| Feni | 140 | 18:30 | 130 | 2:00 | Purbasadipur | 133 | 3:00 | 126 | 18:00
| Chowmuhani | 138 | 18:00 | 133 | 16:00 | Thakurgaon | 131 | 2:00 | 121 | 18:00
| Ashuganj | 139 | 1:00 | 136 | 23:00 | Palashbari | 135 | 19:00 | 128 | 5:00
| Daudkandi | 138 | 18:00 | 133 | 15:00 | Barapukuria | 137 | 0.125 | 133 | 0.29167
| B.Baria | 135 | 1:00 | 131 | 13:00 | Panchagar | 136 | 0.20833 | 122 | 0.75
| Ramganj | 140 | 21:00 | 134 | 2:00 | Joldhaka | 134 | 0.20833 | 125 | 0.75
| Chaddagram | 141 | 18:00 | 134 | 2:00 | Kurigram | 136 | 0.875 | 126 | 0.75
| PHP | 140 | 18:00 | 129 | 2:00 | Mithapukur | 137 | 0.16667 | 130 | 0.29167

## L-Curve
Date | 2021-12-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 320 | 4977 | 2396 | 7373 |  |  |  | QF-LDC-11
0:30 | 216 | 4937.5 | 2213.5 | 7151 | Date: | 2021-12-01
1:00 | 112 | 4898 | 2031 | 6929
1:30 | 118.5 | 4712.5 | 2006 | 6718.5
2:00 | 125 | 4527 | 1981 | 6508
2:30 | 185.5 | 4398.5 | 1968.5 | 6367 | [5 empty] | Gen. at Eve. Peak | 9537 | 9537 MW (19:00 )
3:00 | 246 | 4270 | 1956 | 6226 | [6 empty] | 19:00
3:30 | 255 | 4237.5 | 1971 | 6208.5 | [5 empty] | Gen. at Day Peak | 8254 | 8254 MW (12:00 )
4:00 | 264 | 4205 | 1986 | 6191 | [6 empty] | 12:00
4:30 | 248 | 4196 | 1963 | 6159 | [5 empty] | Highest Generation | 9537
5:00 | 232 | 4187 | 1940 | 6127 | [6 empty] | 19:00
5:30 | 203 | 4279.5 | 1963 | 6242.5
6:00 | 174 | 4372 | 1986 | 6358
6:30 | 167.5 | 4456.5 | 1999.5 | 6456
7:00 | 161 | 4541 | 2013 | 6554
7:30 | 117 | 4760.5 | 2104 | 6864.5
8:00 | 73 | 4980 | 2195 | 7175
8:30 | 148.5 | 5143 | 2261 | 7404
9:00 | 224 | 5306 | 2327 | 7633
9:30 | 340 | 5279.5 | 2395.5 | 7675
10:00 | 456 | 5253 | 2464 | 7717
10:30 | 510 | 5311.5 | 2515.5 | 7827
11:00 | 564 | 5370 | 2567 | 7937
11:30 | 501 | 5502 | 2593.5 | 8095.5
12:00 | 438 | 5634 | 2620 | 8254
12:30 | 325 | 5762 | 2584 | 8346
13:00 | 212 | 5890 | 2548 | 8438
13:30 | 279 | 5768.5 | 2457 | 8225.5
14:00 | 346 | 5647 | 2366 | 8013
14:30 | 439 | 5538.5 | 2412.5 | 7951
15:00 | 532 | 5430 | 2459 | 7889
15:30 | 518 | 5430 | 2464.5 | 7894.5
16:00 | 504 | 5430 | 2470 | 7900
16:30 | 420 | 5506 | 2448 | 7954
17:00 | 336 | 5582 | 2426 | 8008
17:30 | 195 | 6092.5 | 2668.5 | 8761
18:00 | 54 | 6603 | 2911 | 9514
18:30 | 84 | 6541.5 | 2984 | 9525.5
19:00 | 114 | 6480 | 3057 | 9537
19:30 | 170 | 6300 | 3037 | 9337
20:00 | 190 | 6142 | 3034 | 9176 |  |  |  | Executive Engineer
20:30 | 188 | 6043.5 | 2968.5 | 9012 |  |  |  | Network Operation Division
21:00 | 186 | 5945 | 2903 | 8848
21:30 | 231 | 5816 | 2839.5 | 8655.5
22:00 | 276 | 5687 | 2776 | 8463 |  |  |  |  | Page 6 of 7
22:30 | 303 | 5463 | 2677.5 | 8140.5
23:00 | 330 | 5239 | 2579 | 7818
23:30 | 325 | 5108 | 2487.5 | 7595.5
24:00 | 320 | 4977 | 2396 | 7373
9537 MW (19:00 )
8254 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-12-01 |  | Energy |  | 189203360
[13 empty] | 2021-12-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3207 | 630 | 2013 | 0 | 781 | 585 | 75 | 0 | 0 | 82 | 0 | 0
0:30 | 3126 | 544 | 2085.5 | 0 | 691 | 559 | 67 | 0 | 0 | 78.5 | 0 | 0 | Date: | 2021-12-01
1:00 | 3045 | 458 | 2158 | 0 | 601 | 533 | 59 | 0 | 0 | 75 | 0 | 0
1:30 | 3058.5 | 448.5 | 2113.5 | 0 | 442.5 | 522.5 | 59 | 0 | 0 | 74 | 0 | 0 | [8 empty] | Total Energy | 189.2034 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3072 | 439 | 2069 | 0 | 284 | 512 | 59 | 0 | 0 | 73 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2997 | 439 | 2026.5 | 0 | 266.5 | 507.5 | 59 | 0 | 0 | 71.5 | 0 | 0 | [8 empty] | Energy Requirement | 189.2034
3:00 | 2922 | 439 | 1984 | 0 | 249 | 503 | 59 | 0 | 0 | 70 | 0 | 0
3:30 | 2944 | 439 | 1944.5 | 0 | 249 | 502.5 | 61 | 0 | 0 | 68.5 | 0 | 0 | [6 empty] | Shortage
4:00 | 2966 | 439 | 1905 | 0 | 249 | 502 | 63 | 0 | 0 | 67 | 0 | 0
4:30 | 2962.5 | 439 | 1877.5 | 0 | 249 | 502 | 63 | 0 | 0 | 66 | 0 | 0
5:00 | 2959 | 439 | 1850 | 0 | 249 | 502 | 63 | 0 | 0 | 65 | 0 | 0
5:30 | 2998 | 432.5 | 1892 | 0 | 281 | 502 | 71.5 | 0 | 0 | 65.5 | 0 | 0
6:00 | 3037 | 426 | 1934 | 0 | 313 | 502 | 80 | 0 | 0 | 66 | 0 | 0
6:30 | 3041.5 | 426 | 1959.5 | 0 | 367.5 | 512 | 80 | 0 | 0 | 65.5 | 4 | 0 |  |  |  |  | Coal
7:00 | 3046 | 426 | 1985 | 0 | 422 | 522 | 80 | 0 | 0 | 65 | 8 | 0
7:30 | 3037 | 426 | 1922.5 | 0 | 756.5 | 551 | 76 | 0 | 0 | 69.5 | 26 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3028 | 426 | 1860 | 0 | 1091 | 580 | 72 | 0 | 0 | 74 | 44 | 0
8:30 | 2999 | 488 | 1810 | 0 | 1312 | 579.5 | 68 | 0 | 8 | 78 | 61.5 | 0
9:00 | 2970 | 550 | 1760 | 0 | 1533 | 579 | 64 | 0 | 16 | 82 | 79 | 0
9:30 | 2886 | 629.5 | 1749.5 | 0 | 1576 | 558.5 | 67.5 | 0 | 24 | 84 | 91 | 0
10:00 | 2802 | 709 | 1739 | 0 | 1619 | 538 | 71 | 0 | 32 | 86 | 103 | 0
10:30 | 2850 | 708.5 | 1845.5 | 0 | 1576.5 | 537.5 | 72.5 | 0 | 24 | 88 | 108 | 0
11:00 | 2898 | 708 | 1952 | 0 | 1534 | 537 | 74 | 0 | 16 | 90 | 113 | 0
11:30 | 2974 | 708.5 | 1985.5 | 0 | 1578 | 542.5 | 74.5 | 0 | 16 | 94 | 115 | 0
12:00 | 3050 | 709 | 2019 | 0 | 1622 | 548 | 75 | 0 | 16 | 98 | 117 | 0
12:30 | 3071.5 | 709 | 1986.5 | 0 | 1722 | 554 | 75 | 0 | 16 | 99.5 | 112.5 | 0
13:00 | 3093 | 709 | 1954 | 0 | 1822 | 560 | 75 | 0 | 16 | 101 | 108 | 0
13:30 | 3093 | 709 | 1954 | 0 | 1822 | 560 | 75 | 0 | 16 | 101 | 108 | 0
14:00 | 3093 | 709 | 1954 | 0 | 1822 | 560 | 75 | 0 | 16 | 101 | 108 | 0
14:30 | 3042 | 702.5 | 1991.5 | 0 | 1587.5 | 560.5 | 76 | 0 | 16 | 101.5 | 86 | 0
15:00 | 2991 | 696 | 2029 | 0 | 1353 | 561 | 77 | 0 | 16 | 102 | 64 | 0
15:30 | 3011 | 696.5 | 2043.5 | 0 | 1359.5 | 546 | 77 | 0 | 16 | 99.5 | 45.5 | 0
16:00 | 3031 | 697 | 2058 | 0 | 1366 | 531 | 77 | 0 | 16 | 97 | 27 | 0
16:30 | 3028 | 696.5 | 2029 | 0 | 1471.5 | 531 | 72 | 0 | 16 | 95.5 | 13.5 | 0
17:00 | 3025 | 696 | 2000 | 0 | 1577 | 531 | 67 | 0 | 16 | 94 | 0 | 0
17:30 | 3020 | 697 | 2036 | 0 | 2165 | 560.5 | 72.5 | 0 | 107 | 102 | 0 | 0
18:00 | 3015 | 698 | 2072 | 0 | 2753 | 590 | 78 | 0 | 198 | 110 | 0 | 0
18:30 | 3050 | 698 | 2039.5 | 0 | 2712 | 617 | 70 | 0 | 233 | 106 | 0 | 0
19:00 | 3085 | 698 | 2007 | 0 | 2671 | 644 | 62 | 0 | 268 | 102 | 0 | 0
19:30 | 3154 | 698 | 2093 | 0 | 2394 | 642 | 78 | 0 | 176 | 102 | 0 | 0
20:00 | 3166 | 698 | 1977 | 0 | 2344 | 644 | 78 | 0 | 169 | 100 | 0 | 0
20:30 | 3137.5 | 697.5 | 1991.5 | 0 | 2260.5 | 642 | 78 | 0 | 106.5 | 98.5 | 0 | 0
21:00 | 3109 | 697 | 2006 | 0 | 2177 | 640 | 78 | 0 | 44 | 97 | 0 | 0
21:30 | 3108 | 697.5 | 1982.5 | 0 | 2031.5 | 640.5 | 71 | 0 | 30.5 | 94 | 0 | 0
22:00 | 3107 | 698 | 1959 | 0 | 1886 | 641 | 64 | 0 | 17 | 91 | 0 | 0
22:30 | 3120 | 697.5 | 1991.5 | 0 | 1534 | 629.5 | 71 | 0 | 8.5 | 88.5 | 0 | 0
23:00 | 3133 | 697 | 2024 | 0 | 1182 | 618 | 78 | 0 | 0 | 86 | 0 | 0
23:30 | 3170 | 663.5 | 2018.5 | 0 | 981.5 | 601.5 | 76.5 | 0 | 0 | 84 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.2° C
24:00 | 3207 | 630 | 2013 | 0 | 781 | 585 | 75 | 0 | 0 | 82 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2021-12-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 59 | 59 | 59 | 63 | 63 | 80 | 80 | 72 | 64 | 71 | 74 | 75 | 75 | 76 | 77 | 77 | 67 | 78 |  | 62 | 78 | 78 | 78 | 64 | 78 | 75 | 1649738
2 | Karnaphuli Hydro PP Unit-4 & 5 | 0
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 17 | 17 | 17 | 17 | 8 | 8 | 0 | 149461
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 10 | 15 | 18 | 19 | 19 | 18 | 15 | 11 | 6 | 0 | [9 empty] | 132435
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 34 | 17 |  | 0 | 177537
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 10 | 34 | 34 | 34 | 34 | 34 | 17 |  |  |  | 48 |  | 17 | 17 | 17 |  |  |  | 0 | 332872
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 37 | 45 | 45 | 45 | 100 | 155 | 95 | 95 | 110 | 217 |  | 195 | 130 | 130 | 80 | 15 |  | 0 | 1583235
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 68 | 68 | 35 | 35 | 35 | 35 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 535272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4536000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2234014
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 28 | 27 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 661248
33 | Ashuganj 225 MW CCPP | 208 | 210 | 165 | 177 | 172 | 158 | 148 | 160 | 176 | 150 | 151 | 181 | 181 | 181 | 181 | 181 | 186 | 186 |  | 184 | 203 | 220 | 184 | 184 | 188 | 185 | 4367000
34 | Ashuganj 450 MW CCPP(South) | 275 | 310 | 275 | 280 | 275 | 310 | 305 | 275 | 275 | 280 | 280 | 305 | 295 | 320 | 275 | 275 | 275 | 275 |  | 270 | 310 | 270 | 300 | 305 | 315 | 305 | 7074000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 20 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 329760
36 | Chandpur 150 MW CCPP | 89 | 92 | 92 | 88 | 90 | 90 | 91 | 90 | 87 | 90 | 91 | 91 | 91 | 90 | 90 | 90 | 90 | 89 |  | 88 | 89 | 90 | 89 | 90 | 91 | 91 | 2125120
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 372 | 393 | 345 | 371 | 375 | 369 | 390 | 372 | 374 | 336 | 334 | 362 | 401 | 354 | 358 | 403 | 396 | 382 |  | 397 | 392 | 390 | 364 | 363 | 352 | 358 | 9046010
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6644750
41 | Haripur 360MW CCPP(HPL) | 322 | 322 | 323 | 322 | 322 | 322 | 322 | 322 | 323 | 284 | 311 | 338 | 336 | 301 | 331 | 326 | 333 | 331 |  | 337 | 337 | 226 | 261 | 261 | 261 | 261 | 7460000
42 | RPCL 210MW CCPP | 140 | 138 | 140 | 140 | 141 | 142 | 141 | 122 | 111 | 107 | 109 | 109 | 107 | 105 | 106 | 110 | 120 | 120 |  | 127 | 126 | 136 | 132 | 133 | 127 | 127 | 2883840
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 16 | 34 | 44 | 49 | 50 | 45 | 39 | 28 | 11 | 0 | [9 empty] | 319530
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 40 |  | 40 | 42 | 42 | 42 | 41 | 41 | 41 | 981000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 701880
46 | Shajibazar 330 MW CCPP | 127 | 125 | 126 | 127 | 126 | 124 | 124 | 133 | 126 | 130 | 128 | 126 | 128 | 125 | 125 | 126 | 131 | 129 |  | 127 | 132 | 132 | 134 | 124 | 125 | 124 | 2949000
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 52 | 40 | 40 | 40 | 40 | 50 | 50 | 56 | 58 | 52 | 52 |  | 53 | 52 | 60 | 32 | 32 | 32 | 32 | 1039872
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 10 | 10 | 10 | 10 | 10 | 40 | 72 | 72 | 75 | 73 | 72 | 72 | 72 | 72 | 72 | 75 | 77 |  | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 1448640
| Shahjibazar 100 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1531527
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 218 | 178 | 218 | 192 | 165 | 165 | 218 | 218 | 205 | 205 | 205 | 219 | 219 |  | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 4991220
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 211860
54 | Hobiganj 11MW PP Cofidence-E | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 113856
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 14 | 14 | 14 | 14 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 1075200
56 | Shahjahanulla 25 MW PP | 20 | 5 |  |  |  |  | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 427248
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 280 | 305 | 295 | 285 | 300 | 280 | 300 | 290 | 280 | 300 | 300 | 295 | 270 | 270 | 310 | 300 | 300 |  | 280 | 310 | 300 | 290 | 280 | 290 | 280 | 7266000
| Bibiyana South 400 MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 54 | 52 |  | 90 | 95 | 100 | 114 | 128 | 141 | 225 | 1612200
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 10 | 45 | 53 | 53 | 53 | 54 | 53 | 53 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 17 | 0 | 839885
59 | Tangail Palli Power Gen 22 MW | [19 empty] | 4 | 19 | 18 | 24 | 24 | 24 | 24 | 123360
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439968
61 | Narshingdi 22 MW PP (Doreen) | 19 | [5 empty] | 11 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 |  | 15 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 307404
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 493992
63 | Impoprt (Tripura) | 75 | 73 | 70 | 67 | 65 | 66 | 65 | 74 | 82 | 86 | 90 | 98 | 101 | 99 | 102 | 97 | 94 | 110 |  | 102 | 102 | 100 | 97 | 91 | 86 | 82 | 2079360
64 | Malancha, Ctg. EPZ (United) | 33 | 32 | 33 | 34 | 34 | 30 | 33 | 7 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 10 |  | 5 | 8 | 13 | 24 | 31 | 33 | 33 | 377760
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512712
66 | Feni 11 MW PP (Doreen) | 11 | [5 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 200160
67 | Jangalia 33MW PP (Summit) | 33 | 33 |  |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 692600
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 213770
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 29 | 28 | 28 | 27 | 28 | 28 | 28 | 28 | 24 | 28 | 28 | 26 | 26 | 26 | 17 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 651780
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 718700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 25 | 25 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 777300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [16 empty] | 17 | 34 |  | 17 | 17 | 17 | 17 |  |  | 0 | 86640
| Chowmuhani 113 MW | 75 | [5 empty] | 9 | 57 | 57 | 59 | 58 | 57 | 58 | 58 | 58 | 58 | 93 | 106 |  | 108 | 108 | 108 | 108 | 108 | 98 | 55 | 1480080
| Manikgonj 162MW PP(MPGL) | 54 | [5 empty] | 20 | 104 | 162 | 162 | 162 | 162 | 162 | 162 | 109 | 108 | 124 | 157 |  | 162 | 162 | 162 | 162 | 162 | 162 | 108 | 2770560
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [10 empty] | 18 | 48 | 51 | 34 | 16 | 16 | 16 | 40 |  | 52 | 52 |  |  |  |  | 0 | 353846
79 | Kodda 150MW PP | [8 empty] | 16 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 64 |  | 32 | 16 | 16 | 10 |  |  | 0 | 279360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [6 empty] | 1 | 8 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 12 | 43 |  | 52 | 52 | 52 | 52 | 52 | 8 |  | 488026
| Gazipur 100 MW PP | [17 empty] | 34 |  | 17 | 17 | 17 |  |  |  | 0 | 73284
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26279
| Jodiac Power | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1238159
| Karnaphuli Power Ltd. | 17 |  |  |  |  | 2 | 17 | 30 | 51 | 51 | 51 | 51 | 81 | 68 | 90 | 106 | 106 | 106 |  | 85 | 17 | 17 |  |  |  | 0 | 1056322
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 20 | 17 | 23 | 25 | 24 | 24 | 25 | 25 | 24 | 25 |  | 24 | 25 | 25 | 25 | 24 |  | 0 | 337700
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3638516
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | [5 empty] | 5 | 52 | 91 | 90 | 91 | 94 | 103 | 104 | 70 | 73 | 84 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 17 | 1620480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 10 | 50 | [7 empty] | 0 | 105000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1188992
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 3 | 24 | 24 | 24 | 72 | 102 | 102 | 70 | 48 | 48 | 80 |  | 102 | 64 | 64 | 64 | 32 |  | 0 | 910944
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 24 | 45 | 38 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 984000
96 | Chattogram 108 MW PP (ECPV) | [8 empty] | 10 | 12 | 12 | 12 | 12 |  |  |  | 4 | 59 |  | 75 | 51 | 53 | 50 | 20 |  | 0 | 328248
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 |  | 55 | 15 | 15 | 15 |  |  | 0 | 423871
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 5 | 42 |  | 17 | 17 | 17 | 17 |  |  | 0 | 245247
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 110 | 110 | 163 | 163 | 110 | 110 | 110 | 110 | 130 | 163 | 130 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3701536
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 13600
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 998892
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 |  | 24 | 24 | 24 |  |  |  | 0 | 206400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 0 | 16 | 48 | 50 | 52 | 101 | 105 | 80 | 65 | 69 | 117 |  | 110 | 70 | 70 | 65 | 42 |  | 0 | 1030180
115 | Juldah 100 MW PP Unit-3 (Acorn) | [5 empty] | 5 | 10 | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 40 | 40 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 925440
116 | Chandpur 200MW (Desh energy) | [17 empty] | 20 |  | 51 | 51 | 51 | 51 | 51 |  | 0 | 249600
117 | Ashuganj 150MW PP (Midland) | 10 | [5 empty] | 3 | 20 | 53 | 70 | 40 | 40 | 40 | 24 | 24 | 24 | 43 | 113 |  | 130 | 132 | 133 | 127 | 128 | 132 | 50 | 1344872
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 398 | 399 | 398 | 399 | 398 | 399 | 400 | 327 | 399 | 402 | 402 | 371 | 403 | 376 | 353 | 352 |  | 353 | 352 | 355 | 352 | 352 | 352 | 351 | 9114000
| Jamalpur 115 MW PP (United) | 55 | 24 | 24 | 24 | 24 | 24 | 24 | 44 | 75 | 75 | 75 | 75 | 75 | 75 | 55 | 35 | 35 | 115 |  | 115 | 115 | 115 | 85 | 60 | 60 | 45 | 1504800
| Anwara 300 MW PP (United) | 245 | 135 | 100 | 100 | 100 | 155 | 165 | 245 | 249 | 245 | 245 | 245 | 270 | 300 | 260 | 260 | 300 | 300 |  | 300 | 300 | 300 | 260 | 260 | 210 | 210 | 5675815
| Juldah unit-2 (Acorn) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  |  | 70 |  | 20 | 0 |  |  |  |  | 0 | 156480
| Anlima Energy Ltd. | 17 |  |  |  |  | 2 | 17 | 38 | [14 empty] | 46 | 70 | 17 | 17 | 302345
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443880
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 13 | 21 | 27 | 29 | 31 | 28 | 26 | 16 | 7 | 0 | [9 empty] | 198392
| Chandpur 115(Doreen) | [9 empty] | 18 | 15 | [14 empty] | 0 | 34560
| Kanchan Purbachal Power Generation Ltd. | [15 empty] | 0 | 2 | [9 empty] | 6840
120 | Eastern Zone Total | 4898 | 4527 | 4270 | 4205 | 4187 | 4372 | 4541 | 4980 | 5306 | 5253 | 5370 | 5634 | 5890 | 5647 | 5430 | 5430 | 5582 | 6603 |  | 6480 | 6300 | 6142 | 5945 | 5687 | 5239 | 4977 | 129163262
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 50 | 53 | 53 | 53 | 53 | 53 | 17 | 35 | 35 | 35 | 102 |  | 105 | 105 | 105 | 105 | 105 | 17 | 0 | 1057632
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 135 | 110 | 108 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 105 | 106 | 105 | 106 | 106 | 3158318
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 21 | 68 |  | 63 | 79 | 84 | 83 | 85 | 84 | 85 | 87 | 87 |  | 87 | 87 | 85 | 85 | 85 | 85 | 85 | 1321505
| Bhola 225 MW CCPP | 65 | 68 | 69 | 69 | 68 | 69 | 68 | 68 | 68 | 65 | 65 | 64 | 62 | 62 | 64 | 67 | 65 | 65 |  | 65 | 66 | 66 | 68 | 68 | 68 | 69 | 1573000
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 16 | 16 | 16 | 16 | 15 | 14 | 14 | 13 | 13 | 12 | 12 | 15 | 15 | 14 | 15 | 20 |  | 21 | 24 | 25 | 25 | 25 | 25 | 24 | 410900
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 458 | 439 | 439 | 439 | 439 | 426 | 426 | 426 | 550 | 709 | 708 | 709 | 709 | 709 | 696 | 697 | 696 | 698 |  | 698 | 698 | 698 | 697 | 698 | 697 | 630 | 14615272
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 310 | 290 | 280 | 280 | 280 | 280 | 300 | 360 | 360 | 320 | 320 | 330 | 340 | 340 | 340 | 310 | 310 | 370 |  | 430 | 430 | 430 | 430 | 430 | 410 | 380 | 9218600
149
150 | Barapukuria TPP Unit-1 | 81 | 82 | 82 | 82 | 81 | 82 | 82 | 82 | 82 | 81 | 81 | 80 | 82 | 80 | 81 | 81 | 81 | 80 |  | 79 | 79 | 80 | 79 | 79 | 79 | 74 | 1947054
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 142 | 140 | 141 | 140 | 141 | 140 | 140 | 138 | 137 | 137 | 136 | 138 | 138 | 138 | 140 | 140 | 140 | 140 |  | 135 | 133 | 134 | 131 | 132 | 129 | 131 | 3367800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 43 |  |  |  |  | 112576
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 0 | 0 | [9 empty] | 35100
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 181 | 181 | 183 | 192 | 191 | 195 | 199 | 203 | 187 | 177 | 173 | 197 | 200 | 182 | 179 | 180 | 180 | 179 |  | 183 | 187 | 186 | 182 | 180 | 182 | 182 | 4685236
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 165 | 177 | 172 | 173 | 199 | 200 | 175 | 170 | 166 | 191 | 187 | 194 | 188 | 184 | 196 | 194 | 192 |  | 188 | 188 | 191 | 186 | 185 | 197 | 198 | 4723664
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 345 | 360 | 330 | 357 | 312 | 410 | 415 | 304 | 290 | 250 | 402 | 419 | 340 | 335 | 419 | 414 | 352 | 411 |  | 361 | 411 | 411 | 403 | 360 | 411 | 414 | 8935709
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 0 |  |  |  | 15 | 18 | 19 | 19 | 22 | 22 | 22 | 10 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 394320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220428
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 8 |  | 35 | 34 | 34 |  |  |  |  | 77573
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 3 | 25 | 25 | 25 | 25 | 25 |  |  |  | 2 | 34 |  | 52 | 52 | 52 | 43 | 16 |  | 0 | 370560
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 75 |  | 100 | 25 | 25 |  |  |  |  | 178648
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 1 | 42 | 109 | 113 | 70 | 70 | 70 | 35 | 80 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 1621536
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 10 | 90 | 111 | 113 | 70 | 70 | 70 | 35 |  |  | 10 | 100 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 1291008
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 34 | 34 | 34 | 34 | 34 | 34 |  |  |  | 10 | 100 |  | 105 | 105 | 105 | 104 | 49 |  | 0 | 688838
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 3 | 4 | 5 | 6 | 6 | 5 | 3 | 2 | 0 | [9 empty] | 34821
178
178