## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-07-01 | Monday
|  | Date (day): | 2019-07-01 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13232 | MW |  |  | (b) At Evening Peak Hour : |  | 14733 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-06-30 | 2019-07-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 |  | 15
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 139 | 138 | 140 | 140
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 150 | 0 | 0 |  | 365 | Under maint. |  | 30/06/2019
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 69 | 40 | 70 | 70 | 8
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 72 | 108 | 108
5 | Haripur GT PP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 280 | 250 | 412 | 412 |  |  | FGMO
| Haripur 110 MW PP(NEPC) |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Contract expired
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 304 | 304 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 330 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 87 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 297 | 290 | 300 | 300
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 96 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 78 | 20 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 90 | 90 | 120 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 72 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 35 | 33 | 33 | 33 |  |  | Test
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 92 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 48 | 48 | 49 | 49
21 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 96 | 140 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 35 | 35 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 57 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW (Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW (Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 49 | 49 | 50 | 50
30 | Tongi 80 MW GT PP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 250 | 300 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 20 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| Dhaka area Total |  |  |  |  | 6039 | 5803 | 3131 | 3462 | 3757 | 4457 | 388 | 440
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas Shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 3.48 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 46 | 46 | 46
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 37 | 75 | 75 |  | 155 | Low water lavel
42 | Sikalbaha 60MW TPP |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 206 | 211 | 220 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
45 | Sikalbaha 51 MW PP(Engine) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 24 | 32 | 33 |  | 18 | Engine problem
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 17 | 105 | 105
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 84 | 85 | 85
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 60 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 31 | 85 | 100 | 100
| Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 0 | 0 | 5.1 | 0 | 3 | 0
| Anwara 300 MW PP (United) |  | HFO | United Group | 300 MW | 0 | 0 | 178 | 249 | 300 | 300
| Chattogram area Total |  |  |  |  | 1866 | 1786 | 906.58 | 1280 | 1540 | 1533 | 260 | 213
53 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 125 | 125 | 125 | 125 | 10
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
54 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 199 | 221 | 221
55 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 120 | 330 | 360 | 360
56 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 290 | 360 | 360
57 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 |  | 45 | Gas Line problem.
58 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 55 | 55 | 55
59 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
60 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 199 | 78 | 78 | 190 | 5 |  | Gas shortage
61 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 40 | 40 |  | 11 | Engine problem
62 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 145 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 97 | 140 | 140
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 177 | 177 | 200 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 134 | 152 | 190
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 11 | 21 | 20 | 20
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1779 | 1851 | 2019 | 2419 | 278 | 56
73 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 146 | 145 | 150 | 150 |  | 52 | GT-1 Under maint.
74 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95 MW PP |  | HFO | IPP | 12*8.924 | 95 | 95 | 86 | 84 | 85 | 85 |  | 10 | Engine problem
76 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 2 | 0
77 | United Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 184 | 200 | 200
78 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 85 | 90 | 100 | 100 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 441.4 | 525 | 559 | 557 | 0 | 62
79 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 53 | 53 | 54 | 54
80 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 29 | 57 | 70 | 70
81 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
82 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 151 | 155 | 150 | 150 |  |  | GT-1 Under maint
83 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
84 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 49 | 44 | 44
85 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
86 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 32 | 66 | 66 |  |  | FGMO
87 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 86 | 86
88 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 45 | 46 | 46
89 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 75 | 122 | 120 | 130
90 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 15 | 19
91 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 48 | 47 | 47
92 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
93 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 320 | 341 | 341
| Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 0 | 0 | 249 | 204 | 285 | 285 |  |  | On test
94 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1302 | 1379 | 1584 | 1598 | 0 | 0
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 16 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 920 | 930 | 930
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 104 | 115 | 115 | 115
97 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 40
98 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | St Under maint
99 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 59 | 0 | 60
100 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
101 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 99 | 0 | 100
103 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 105 | 105
104 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 87 | 52 | 105 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1200 | 1406 | 1295 | 1541 | 0 | 410
105 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
106 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
107 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 30 | 33 | 33
108 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 173 | 172 | 172 | 172
109 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 307 | 407 | 410 | 436 | 0 | 0
110 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
111 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
112 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 32 | 0 | 35
113 | Amnura 50 MW PP |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 40 | 40 | 40 |  | 10 | Engine problem
114 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 32 | 43 | 32 | 43 |  | 7 | Engine problem
115 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 47
116 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 154 | 191 | 220 | 220 |  |  | FGMO
117 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 145 | 156 | 220 | 220 |  |  | FGMO
118 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 156 | 198 | 220 | 220 |  |  | FGMO
119 | Sirajgonj 400 MW CCPP Unit-4 (Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 370 | 350 | 414 | 414
120 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 36
121 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
122 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 13 | 15 | 14 | 14
123 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
124 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 41 | 51 | 52 | 52
125 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 47 | 95 | 100 | 100
126 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
127 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 108 | 108 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1160 | 1489 | 1795 | 1884 | 0 | 117
128 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint.
129 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 250 | 250
130 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 17
131 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 18
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 20 | 1 | 23 | 23
| Rangpur Area Total |  |  |  |  | 564 | 484 | 219 | 233 | 273 | 308 | 0 | 85
| Total |  |  |  |  | 18539 | 17996 | 10445.98 | 12032 | 13232 | 14733 | 926 | 1383
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9995.3929 | 11513 | 12661.238 | 14097.4924
A. |  | 2019-06-30 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 12035 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8642.6 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12032 | MW
3 | Day peak Generation : |  |  | 10445.98 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11513 | MW
4 | Evening peak Generation : |  |  | 12032 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 264.2643 | MKWHr | By Solar | 0.14655 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 153.1201 | MKWHr |  | By Oil: | 79.3766 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.8577 | MKWHr |  | By Hydro: | 0.848 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 926 | MW | Dhaka | 4185 | 4185 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1383 | MW | Chittagong | 1191 | 1191 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2309 | MW | Khulna | 1370 | 1370 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1328.43 | MMCFD |  |  | Rajshahi | 1272 | 1272 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 104918324.642 | ii) Oil : | Taka | 526651779.53 | Comilla | 1048 | 1048 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 18750722 | Total | Taka | 650320826.172 | Mymensingh | 963 | 963 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.8435 | MKWHr. | Sylhet | 480 | 480 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -260 | MW (E to W) at | 21:00 | hrs | Barisal | 322 | 322 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -280 | MW at | 22:00 | hrs | Rangpur | 682 | 682 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.1° C |  |  | Total | 11513 | 11513 |  | 0
B. |  | 2019-07-01 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 36.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14733 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | 2133 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 276.6706 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9010.9 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0916 | MKWHr. | ii) HVDC Flow at Peak Time |  | 920 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8237 | MKWHr. | iii) Maximum HVDC Flow : |  | 927 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 77.78 |  | (b) Today: | 78.01 |  | (c) Rule Curve: |  | 84
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-06-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Haripur 110 MW PP(NEPC) | Haripur GT PP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Banco Energy 54MW | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW (Summit) | Rupganj 33 MW (Summit) | Gazipur 52 MW PP | Tongi 80 MW GT PP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 139 | 0 | 190 | 0 | 102 | 69 | 347 | 351 | 0 | 0 | 350 | 260 | 100 | 50 | 55 | 0 | 0 | 0 | 0 | 50 | 93 | 140 | 46 | 72 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 0 | 34 | 100 | 0 | 16 | 208 | 0 | 133 | 0 | 0 | 16 | 84 | 51 | 75 | 96 | 43 | 18 | 36 | 125 | 0 | 0 | 0 | 161 | 217 | 199 | 142 | 0 | 56 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 146 | 149 | 84 | 22 | 0 | 53 | 57 | 50 | 46 | 0 | 96 | 61 | 82 | 46 | 108 | 0 | 48 | 10 | 310 | 24 | 11 | 0 | 145 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 180 | 150 | 293 | 85 | 105 | 35 | 0 | 241 |  | 927 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 52 | 0 | 172 | 37 | 110 | 0 | 0 | 60 | 50 | 0 | 90 | 40 | 43 | 37 | 51 | 28 | 22 | 14 | 11 | 0 | 0 | 200 | 17 | 18 | 197 | 0 | 193 | 0 | 95 | 100 | 212 | 0 | 417 | 105 | 0 | 108 | 87 | 32 |  | 7932 | 3681 | 11613 | 3799 | 927 | 2375 | 3524 | 200 | 34 | 608 | 146 | 0 | 0 | 77.68
2:00 | 70 | 139 | 0 | 190 | 0 | 102 | 50 | 327 | 352 | 0 | 0 | 330 | 255 | 100 | 40 | 30 | 0 | 0 | 0 | 0 | 26 | 93 | 140 | 20 | 72 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 0 | 35 | 100 | 0 | 16 | 204 | 0 | 132 | 0 | 0 | 16 | 50 | 51 | 88 | 96 | 45 | 18 | 37 | 125 | 0 | 0 | 0 | 342 | 182 | 199 | 142 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 144 | 150 | 84 | 22 | 0 | 53 | 57 | 50 | 46 | 0 | 95 | 63 | 82 | 45 | 109 | 0 | 48 | 10 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 178 | 150 | 294 | 86 | 105 | 35 | 0 | 241 |  | 926 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 52 | 0 | 172 | 34 | 110 | 0 | 0 | 60 | 50 | 0 | 90 | 40 | 43 | 0 | 51 | 28 | 22 | 14 | 11 | 0 | 0 | 200 | 17 | 18 | 183 | 0 | 179 | 0 | 95 | 50 | 204 | 0 | 360 | 105 | 0 | 108 | 87 | 32 |  | 7937 | 3497 | 11434 | 3888 | 926 | 2256 | 3448 | 200 | 35 | 537 | 144 | 0 | 0 | 77.7
3:00 | 70 | 139 | 0 | 190 | 0 | 106 | 50 | 329 | 354 | 0 | 0 | 330 | 240 | 70 | 20 | 30 | 0 | 0 | 0 | 0 | 16 | 72 | 140 | 20 | 72 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 0 | 34 | 100 | 0 | 16 | 204 | 0 | 130 | 0 | 0 | 16 | 50 | 51 | 88 | 96 | 46 | 18 | 37 | 125 | 0 | 0 | 0 | 309 | 182 | 199 | 142 | 0 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 140 | 152 | 84 | 22 | 0 | 53 | 57 | 50 | 46 | 0 | 95 | 53 | 82 | 46 | 108 | 0 | 48 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 177 | 150 | 296 | 86 | 105 | 35 | 0 | 241 |  | 926 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 36 | 0 | 173 | 33 | 80 | 0 | 0 | 60 | 50 | 0 | 90 | 40 | 43 | 0 | 51 | 28 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 182 | 0 | 180 | 0 | 97 | 47 | 202 | 0 | 360 | 105 | 0 | 108 | 87 | 32 |  | 7765 | 3407 | 11172 | 3848 | 926 | 2275 | 3269 | 200 | 34 | 480 | 140 | 0 | 0 | 77.72
4:00 | 70 | 139 | 0 | 190 | 0 | 106 | 50 | 328 | 351 | 0 | 0 | 330 | 278 | 65 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 50 | 98 | 0 | 72 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 0 | 34 | 100 | 0 | 16 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 88 | 96 | 46 | 18 | 38 | 125 | 0 | 0 | 15 | 305 | 182 | 199 | 142 | 0 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 140 | 152 | 84 | 22 | 0 | 53 | 57 | 50 | 46 | 0 | 96 | 62 | 82 | 46 | 110 | 0 | 48 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 194 | 0 | 110 | 0 | 100 | 177 | 150 | 294 | 86 | 105 | 35 | 0 | 241 |  | 927 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 36 | 0 | 173 | 36 | 80 | 0 | 0 | 60 | 0 | 0 | 90 | 12 | 43 | 0 | 52 | 28 | 22 | 15 | 8 | 0 | 0 | 199 | 0 | 0 | 182 | 0 | 178 | 0 | 96 | 0 | 199 | 0 | 360 | 90 | 0 | 108 | 86 | 38 |  | 7556 | 3268 | 10824 | 3861 | 927 | 2266 | 3093 | 199 | 34 | 304 | 140 | 0 | 0 | 77.74
5:00 | 70 | 139 | 0 | 190 | 0 | 106 | 50 | 334 | 353 | 0 | 0 | 330 | 258 | 35 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 7 | 95 | 0 | 72 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 0 | 33 | 50 | 0 | 0 | 35 | 100 | 0 | 16 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 96 | 46 | 18 | 40 | 125 | 0 | 0 | 15 | 316 | 181 | 199 | 142 | 0 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 138 | 151 | 84 | 22 | 0 | 53 | 57 | 48 | 46 | 0 | 95 | 59 | 82 | 46 | 109 | 0 | 48 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 194 | 0 | 105 | 0 | 100 | 178 | 150 | 296 | 86 | 105 | 35 | 0 | 241 |  | 918 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 3 | 0 | 173 | 36 | 48 | 0 | 0 | 60 | 0 | 0 | 90 | 12 | 24 | 0 | 52 | 28 | 22 | 14 | 8 | 0 | 0 | 199 | 0 | 0 | 190 | 0 | 186 | 0 | 95 | 0 | 201 | 0 | 360 | 90 | 0 | 108 | 86 | 38 |  | 7220 | 3191 | 10411 | 3884 | 918 | 2286 | 2700 | 199 | 35 | 251 | 138 | 0 | 0 | 77.76
6:00 | 70 | 139 | 0 | 190 | 0 | 106 | 50 | 327 | 325 | 0 | 0 | 330 | 271 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 47 | 17 | 18 | 17 | 22 | 25 | 32 | 4 | 33 | 8 | 0 | 0 | 35 | 100 | 0 | 16 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 10 | 46 | 18 | 40 | 125 | 0 | 0 | 0 | 320 | 183 | 199 | 142 | 0 | 56 | 0 | 35 | 0 | 0 | 25 | 0 | 0 | 33 | 20 | 116 | 150 | 48 | 0 | 0.3 | 53 | 57 | 50 | 46 | 0 | 0 | 63 | 82 | 46 | 108 | 0 | 46 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0.6 | 100 | 100 | 80 | 260 | 86 | 105 | 33 | 0.2 | 241 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 29 | 32 | 0 | 0 | 60 | 0 | 0 | 70 | 12 | 0 | 0 | 8 | 0 | 22 | 15 | 8 | 0 | 0 | 199 | 0 | 0 | 182 | 0 | 178 | 0 | 97 | 0 | 197 | 0 | 300 | 90 | 0 | 108 | 87 | 23 |  | 6174.1 | 2826 | 9000.1 | 3675 | 920 | 2174 | 1778 | 199 | 35 | 102 | 116 | 1.1 | 0 | 77.78
7:00 | 70 | 139 | 0 | 190 | 0 | 106 | 50 | 335 | 285 | 0 | 0 | 330 | 290 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 72 | 0 | 47 | 17 | 18 | 17 | 22 | 25 | 32 | 16 | 33 | 8 | 0 | 0 | 35 | 100 | 0 | 16 | 216 | 0 | 135 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 46 | 18 | 36 | 125 | 0 | 0 | 0 | 320 | 203 | 199 | 142 | 0 | 56 | 0 | 35 | 0 | 0 | 8 | 13 | 0 | 33 | 20 | 110 | 150 | 8 | 0 | 0.4 | 53 | 57 | 22 | 20 | 0 | 0 | 62 | 40 | 46 | 120 | 0 | 22 | 10 | 310 | 8 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 5.6 | 100 | 90 | 80 | 200 | 86 | 104 | 17 | 1.6 | 241 |  | 919 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 25 | 16 | 0 | 0 | 55 | 0 | 0 | 70 | 12 | 0 | 0 | 8 | 0 | 22 | 15 | 8 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 160 | 0 | 96 | 0 | 187 | 0 | 260 | 90 | 0 | 108 | 86 | 4 |  | 5925.6 | 2717 | 8642.6 | 3641 | 919 | 1985 | 1659 | 200 | 35 | 86 | 110 | 7.6 | 0 | 77.79
8:00 | 70 | 140 | 0 | 190 | 0 | 107 | 50 | 347 | 284 | 0 | 0 | 330 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 72 | 0 | 47 | 17 | 18 | 17 | 12 | 25 | 32 | 33 | 33 | 10 | 0 | 0 | 35 | 100 | 0 | 16 | 217 | 0 | 139 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 46 | 19 | 6 | 125 | 0 | 0 | 0 | 310 | 204 | 199 | 142 | 0 | 54 | 0 | 35 | 0 | 0 | 8 | 14 | 5 | 33 | 20 | 102 | 148 | 8 | 0 | 1 | 53 | 57 | 22 | 20 | 0 | 10 | 61 | 40 | 46 | 123 | 0 | 45 | 10 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 4.92 | 90 | 52 | 84 | 249 | 86 | 105 | 17 | 3.12 | 240 |  | 919 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 16 | 16 | 0 | 0 | 60 | 0 | 0 | 70 | 12 | 0 | 0 | 8 | 0 | 22 | 15 | 8 | 0 | 0 | 200 | 0 | 0 | 197 | 0 | 162 | 0 | 97 | 0 | 185 | 0 | 320 | 90 | 0 | 108 | 52 | 7 |  | 5930.04 | 2752 | 8682.04 | 3711 | 919 | 2028 | 1592 | 200 | 35 | 86 | 102 | 9.04 | 0 | 77.79
9:00 | 70 | 139 | 0 | 190 | 0 | 104 | 50 | 361 | 285 | 0 | 0 | 330 | 255 | 2 | 0 | 0 | 13 | 0 | 0 | 0 | 7 | 32 | 16 | 12 | 72 | 0 | 47 | 30 | 37 | 17 | 12 | 25 | 32 | 33 | 33 | 41 | 0 | 0 | 35 | 100 | 0 | 16 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 31 | 46 | 19 | 9 | 125 | 0 | 0 | 20 | 320 | 182 | 199 | 142 | 0 | 50 | 0 | 35 | 0 | 0 | 25 | 19 | 5 | 33 | 20 | 96 | 148 | 43 | 22 | 1.6 | 53 | 47 | 45 | 38 | 0 | 11 | 61 | 83 | 46 | 110 | 0 | 46 | 10 | 305 | 16 | 11 | 0 | 35 | 0 | 0 | 7 | 0 | 17 | 10.65 | 100 | 120 | 146 | 299 | 86 | 105 | 17 | 3.38 | 241 |  | 920 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 16 | 16 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 8 | 0 | 22 | 15 | 8 | 0 | 0 | 199 | 0 | 0 | 203 | 0 | 199 | 0 | 95 | 0 | 209 | 0 | 320 | 90 | 0 | 108 | 52 | 12 |  | 6415.63 | 2805 | 9220.63 | 3856 | 920 | 2103 | 1930 | 199 | 35 | 66 | 96 | 15.63 | 0 | 77.79
10:00 | 70 | 139 | 0 | 190 | 0 | 101 | 50 | 280 | 263 | 0 | 0 | 330 | 278 | 44 | 0 | 0 | 35 | 0 | 0 | 0 | 50 | 32 | 48 | 50 | 72 | 0 | 48 | 54 | 55 | 35 | 16 | 25 | 32 | 33 | 33 | 49 | 0 | 0 | 36 | 100 | 0 | 16 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 83 | 38 | 16 | 2 | 125 | 0 | 0 | 20 | 285 | 185 | 199 | 142 | 0 | 50 | 0 | 35 | 0 | 0 | 25 | 18 | 5 | 33 | 19 | 102 | 147 | 87 | 22 | 1.1 | 53 | 47 | 47 | 46 | 0 | 12 | 61 | 81 | 44 | 110 | 0 | 44 | 10 | 290 | 16 | 11 | 0 | 107 | 0 | 0 | 19 | 0 | 100 | 16.47 | 100 | 178 | 145 | 297 | 86 | 105 | 17 | 5.15 | 240 |  | 921 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 10 | 16 | 0 | 0 | 55 | 0 | 0 | 47 | 12 | 43 | 0 | 8 | 0 | 22 | 15 | 8 | 0 | 0 | 199 | 0 | 0 | 183 | 0 | 181 | 0 | 92 | 0 | 190 | 0 | 280 | 90 | 0 | 108 | 52 | 8 |  | 6852.72 | 2778 | 9630.72 | 3702 | 921 | 2011 | 2542 | 199 | 36 | 95 | 102 | 22.72 | 0 | 0
11:00 | 70 | 140 | 0 | 190 | 0 | 101 | 60 | 280 | 344 | 0 | 0 | 330 | 271 | 68 | 0 | 0 | 35 | 0 | 0 | 0 | 58 | 50 | 96 | 70 | 35 | 0 | 43 | 54 | 55 | 35 | 16 | 25 | 31 | 33 | 33 | 49 | 0 | 0 | 35 | 100 | 0 | 20 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 31 | 32 | 16 | 2 | 125 | 0 | 0 | 35 | 360 | 184 | 199 | 140 | 0 | 50 | 0 | 35 | 0 | 0 | 30 | 21 | 5 | 33 | 19 | 120 | 148 | 87 | 22 | 2.1 | 53 | 20 | 47 | 43 | 10 | 60 | 49 | 82 | 44 | 74 | 0 | 44 | 10 | 280 | 16 | 11 | 0 | 111 | 0 | 0 | 79 | 0 | 132 | 19.24 | 90 | 179 | 140 | 200 | 86 | 105 | 17 | 1.85 | 177 |  | 920 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 26 | 16 | 0 | 0 | 55 | 0 | 0 | 47 | 12 | 43 | 0 | 26 | 0 | 18 | 13 | 8 | 0 | 0 | 199 | 0 | 0 | 189 | 0 | 187 | 0 | 92 | 0 | 196 | 0 | 370 | 90 | 0 | 108 | 87 | 12 |  | 6964.19 | 2985 | 9949.19 | 3686 | 920 | 2200 | 2623 | 199 | 35 | 143 | 120 | 23.19 | 0 | 0
12:00 | 70 | 139 | 0 | 190 | 0 | 101 | 69 | 280 | 304 | 0 | 0 | 300 | 297 | 90 | 0 | 0 | 35 | 0 | 0 | 0 | 72 | 92 | 96 | 78 | 35 | 0 | 48 | 54 | 55 | 35 | 16 | 25 | 31 | 33 | 33 | 49 | 0 | 0 | 35 | 100 | 0 | 25 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 31 | 32 | 16 | 2 | 125 | 0 | 0 | 120 | 360 | 184 | 199 | 140 | 0 | 51 | 0 | 35 | 0 | 0 | 52 | 21 | 5 | 33 | 11 | 126 | 146 | 86 | 22 | 2.4 | 53 | 29 | 47 | 43 | 100 | 151 | 61 | 81 | 44 | 75 | 0 | 42 | 10 | 290 | 16 | 11 | 0 | 250 | 0 | 0 | 100 | 0 | 149 | 3.48 | 100 | 177 | 140 | 249 | 85 | 105 | 17 | 5.1 | 178 |  | 919 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 26 | 16 | 0 | 0 | 55 | 0 | 0 | 47 | 12 | 32 | 0 | 41 | 0 | 19 | 13 | 8 | 0 | 0 | 199 | 0 | 0 | 154 | 0 | 145 | 0 | 92 | 0 | 156 | 0 | 370 | 90 | 0 | 108 | 87 | 20 |  | 7559.98 | 2886 | 10445.98 | 3807 | 919 | 2238 | 2968 | 199 | 35 | 143 | 126 | 10.98 | 0 | 0
13:00 | 70 | 138 | 0 | 190 | 0 | 106 | 66 | 280 | 304 | 0 | 0 | 300 | 265 | 90 | 0 | 0 | 35 | 0 | 0 | 0 | 72 | 92 | 96 | 100 | 34 | 0 | 48 | 54 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 49 | 0 | 0 | 34 | 100 | 0 | 25 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 31 | 34 | 16 | 6 | 100 | 0 | 0 | 150 | 360 | 183 | 150 | 140 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 21 | 5 | 33 | 12 | 142 | 147 | 86 | 22 | 0.8 | 53 | 51 | 47 | 43 | 100 | 151 | 49 | 80 | 44 | 110 | 0 | 44 | 10 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 177 | 140 | 150 | 85 | 105 | 17 | 2.02 | 178 |  | 920 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 28 | 16 | 0 | 0 | 55 | 0 | 0 | 47 | 12 | 43 | 0 | 41 | 0 | 21 | 13 | 8 | 0 | 0 | 199 | 0 | 0 | 175 | 0 | 167 | 0 | 92 | 0 | 177 | 0 | 370 | 90 | 0 | 108 | 87 | 8 |  | 7534.82 | 2964 | 10498.82 | 3826 | 920 | 2193 | 3019 | 199 | 34 | 143 | 142 | 22.82 | 0 | 0
14:00 | 70 | 139 | 0 | 190 | 0 | 102 | 65 | 250 | 302 | 0 | 0 | 300 | 291 | 84 | 0 | 0 | 35 | 0 | 0 | 0 | 70 | 92 | 96 | 60 | 34 | 0 | 19 | 54 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 49 | 0 | 0 | 34 | 100 | 0 | 25 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 31 | 38 | 18 | 4 | 100 | 0 | 0 | 220 | 360 | 183 | 128 | 142 | 0 | 50 | 0 | 35 | 0 | 0 | 52 | 22 | 5 | 33 | 12 | 150 | 146 | 86 | 22 | 1.4 | 53 | 51 | 47 | 46 | 100 | 154 | 60 | 50 | 45 | 109 | 0 | 45 | 10 | 270 | 24 | 11 | 0 | 300 | 0 | 102 | 100 | 0 | 149 | 19 | 100 | 140 | 100 | 150 | 85 | 105 | 18 | 0 | 178 |  | 920 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 28 | 16 | 0 | 0 | 55 | 0 | 0 | 47 | 12 | 34 | 0 | 41 | 0 | 21 | 14 | 8 | 0 | 0 | 199 | 0 | 0 | 181 | 0 | 179 | 0 | 92 | 0 | 188 | 0 | 340 | 90 | 0 | 108 | 86 | 3 |  | 7516.4 | 2950 | 10466.4 | 3923 | 920 | 2094 | 2983 | 199 | 34 | 143 | 150 | 20.4 | 0 | 0
15:00 | 70 | 139 | 0 | 190 | 0 | 102 | 65 | 250 | 304 | 0 | 0 | 300 | 273 | 87 | 0 | 0 | 35 | 0 | 0 | 0 | 40 | 101 | 96 | 60 | 34 | 0 | 23 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 49 | 0 | 0 | 34 | 95 | 0 | 25 | 219 | 0 | 142 | 0 | 0 | 16 | 0 | 0 | 10 | 31 | 39 | 18 | 4 | 125 | 0 | 0 | 300 | 330 | 185 | 128 | 142 | 0 | 50 | 0 | 35 | 0 | 0 | 52 | 22 | 5 | 33 | 7 | 110 | 143 | 85 | 22 | 1.6 | 53 | 69 | 47 | 42 | 100 | 157 | 60 | 78 | 45 | 124 | 0 | 42 | 10 | 315 | 24 | 0 | 0 | 208 | 0 | 102 | 100 | 0 | 149 | 0 | 90 | 140 | 100 | 250 | 85 | 105 | 17 | 0.9 | 180 |  | 919 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 16 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 34 | 0 | 50 | 0 | 21 | 15 | 8 | 0 | 0 | 199 | 0 | 0 | 195 | 0 | 193 | 0 | 92 | 0 | 202 | 0 | 380 | 90 | 0 | 108 | 87 | 9 |  | 7606.5 | 3039 | 10645.5 | 4178 | 919 | 2195 | 2866 | 199 | 34 | 142 | 110 | 2.5 | 0 | 0
16:00 | 70 | 139 | 0 | 190 | 0 | 102 | 64 | 270 | 300 | 0 | 0 | 330 | 253 | 90 | 0 | 0 | 35 | 0 | 0 | 0 | 50 | 100 | 140 | 86 | 34 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 49 | 0 | 0 | 35 | 95 | 0 | 25 | 206 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 40 | 54 | 39 | 18 | 3 | 125 | 0 | 0 | 300 | 345 | 183 | 78 | 100 | 0 | 50 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 134 | 143 | 85 | 22 | 1.2 | 53 | 69 | 47 | 43 | 100 | 154 | 37 | 80 | 44 | 110 | 0 | 42 | 10 | 310 | 16 | 11 | 0 | 208 | 0 | 102 | 120 | 0 | 149 | 2 | 90 | 162 | 108 | 292 | 85 | 105 | 17 | 3.5 | 230 |  | 920 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 10 | 0 | 173 | 27 | 48 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 34 | 0 | 49 | 0 | 21 | 14 | 8 | 0 | 0 | 199 | 0 | 0 | 196 | 0 | 196 | 0 | 92 | 0 | 203 | 0 | 405 | 90 | 0 | 108 | 87 | 3 |  | 7842.7 | 3111 | 10953.7 | 4180 | 920 | 2197 | 3086 | 199 | 35 | 196 | 134 | 6.7 | 0 | 0
17:00 | 70 | 139 | 0 | 190 | 0 | 22 | 64 | 280 | 304 | 0 | 0 | 330 | 274 | 32 | 10 | 15 | 35 | 0 | 0 | 0 | 95 | 16 | 140 | 100 | 34 | 0 | 47 | 54 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 49 | 0 | 0 | 36 | 95 | 0 | 25 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 40 | 90 | 42 | 18 | 6 | 125 | 0 | 0 | 300 | 340 | 188 | 78 | 95 | 0 | 53 | 0 | 10 | 0 | 0 | 16 | 22 | 8 | 33 | 20 | 134 | 144 | 85 | 22 | 0.3 | 53 | 20 | 11 | 10 | 100 | 153 | 31 | 10 | 10 | 110 | 0 | 13 | 10 | 270 | 16 | 11 | 0 | 250 | 0 | 102 | 140 | 0 | 92 | 1.4 | 90 | 177 | 130 | 201 | 95 | 105 | 17 | 0.7 | 247 |  | 920 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 28 | 0 | 173 | 27 | 48 | 0 | 0 | 55 | 0 | 0 | 46 | 12 | 34 | 0 | 8 | 0 | 21 | 15 | 8 | 0 | 0 | 199 | 0 | 0 | 182 | 0 | 186 | 0 | 62 | 0 | 189 | 0 | 350 | 53 | 0 | 108 | 34 | 5 |  | 7351.4 | 2878 | 10229.4 | 3991 | 920 | 1776 | 2957 | 199 | 36 | 214 | 134 | 2.4 | 0 | 0
18:00 | 70 | 139 | 0 | 190 | 50 | 22 | 65 | 270 | 279 | 0 | 0 | 330 | 255 | 7 | 15 | 15 | 35 | 0 | 0 | 0 | 45 | 16 | 140 | 100 | 34 | 0 | 47 | 54 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 49 | 0 | 0 | 36 | 100 | 0 | 14 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 88 | 46 | 18 | 2 | 125 | 0 | 0 | 290 | 280 | 182 | 78 | 96 | 0 | 54 | 0 | 10 | 0 | 0 | 16 | 22 | 8 | 33 | 20 | 124 | 145 | 85 | 22 | 0.2 | 53 | 42 | 13 | 10 | 100 | 152 | 32 | 10 | 10 | 110 | 17 | 12 | 10 | 300 | 24 | 11 | 0 | 250 | 0 | 103 | 140 | 0 | 70 | 0.4 | 40 | 200 | 80 | 200 | 95 | 105 | 17 | 0.25 | 231 |  | 921 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 20 | 43 | 0 | 173 | 23 | 48 | 0 | 0 | 55 | 0 | 10 | 46 | 12 | 8 | 0 | 8 | 0 | 22 | 15 | 8 | 0 | 0 | 199 | 0 | 0 | 181 | 0 | 186 | 0 | 22 | 0 | 189 | 0 | 300 | 53 | 0 | 108 | 34 | 5 |  | 7150.85 | 2804 | 9954.85 | 4005 | 921 | 1687 | 2706 | 199 | 36 | 276 | 124 | 0.85 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 139 | 0 | 190 | 50 | 50 | 66 | 250 | 305 | 0 | 0 | 330 | 273 | 9 | 15 | 19 | 33 | 0 | 0 | 0 | 8 | 102 | 140 | 100 | 35 | 0 | 18 | 54 | 55 | 30 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 36 | 100 | 0 | 25 | 205 | 0 | 130 | 0 | 0 | 24 | 56 | 83 | 13 | 84 | 46 | 18 | 9 | 125 | 0 | 0 | 300 | 310 | 184 | 78 | 96 | 0 | 55 | 0 | 10 | 0 | 50 | 16 | 22 | 8 | 33 | 20 | 142 | 143 | 85 | 22 | 0 | 53 | 42 | 15 | 18 | 100 | 154 | 32 | 55 | 10 | 122 | 17 | 44 | 10 | 290 | 24 | 11 | 0 | 262 | 0 | 103 | 140 | 0 | 70 | 0 | 100 | 200 | 95 | 250 | 94 | 105 | 17 | 0 | 249 |  | 920 | 10 | 0 | 0 | 115 | 0 | 0 | 0 | 37 | 78 | 0 | 172 | 28 | 110 | 0 | 0 | 55 | 50 | 31 | 90 | 25 | 8 | 37 | 27 | 25 | 22 | 15 | 11 | 0 | 0 | 199 | 16 | 17 | 184 | 0 | 189 | 0 | 89 | 9 | 191 | 0 | 350 | 53 | 0 | 108 | 50 | 1 |  | 7737 | 3322 | 11059 | 4092 | 920 | 1949 | 3001 | 199 | 36 | 720 | 142 | 0 | 0 | 0
19:30 | 70 | 139 | 0 | 190 | 50 | 95 | 66 | 250 | 304 | 0 | 0 | 330 | 273 | 80 | 70 | 55 | 34 | 0 | 0 | 0 | 40 | 102 | 140 | 100 | 35 | 0 | 18 | 54 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 37 | 100 | 0 | 25 | 204 | 0 | 130 | 0 | 0 | 24 | 82 | 85 | 60 | 84 | 46 | 18 | 2 | 125 | 0 | 0 | 310 | 310 | 182 | 78 | 96 | 0 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 128 | 149 | 84 | 22 | 0 | 53 | 57 | 46 | 49 | 100 | 151 | 33 | 79 | 44 | 110 | 18 | 48 | 10 | 310 | 24 | 11 | 0 | 300 | 0 | 103 | 182 | 0 | 149 | 0 | 100 | 200 | 150 | 249 | 95 | 105 | 17 | 0 | 249 |  | 920 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 72 | 0 | 172 | 22 | 110 | 0 | 0 | 55 | 50 | 33 | 95 | 40 | 16 | 38 | 50 | 35 | 22 | 15 | 11 | 0 | 0 | 199 | 16 | 17 | 191 | 0 | 195 | 0 | 95 | 100 | 189 | 0 | 350 | 78 | 0 | 108 | 87 | 1 |  | 8470 | 3554 | 12024 | 4119 | 920 | 2155 | 3696 | 199 | 37 | 770 | 128 | 0 | 0 | 0
20:00 | 70 | 139 | 0 | 190 | 50 | 102 | 66 | 250 | 303 | 0 | 0 | 330 | 250 | 68 | 70 | 55 | 34 | 0 | 0 | 0 | 72 | 102 | 140 | 100 | 35 | 0 | 42 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 0 | 37 | 100 | 0 | 25 | 205 | 0 | 130 | 0 | 0 | 24 | 84 | 85 | 60 | 84 | 46 | 18 | 11 | 125 | 0 | 0 | 310 | 275 | 181 | 78 | 96 | 0 | 55 | 0 | 23 | 0 | 50 | 48 | 22 | 8 | 33 | 21 | 128 | 148 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 151 | 20 | 79 | 44 | 109 | 17 | 47 | 10 | 270 | 24 | 11 | 0 | 292 | 0 | 103 | 170 | 0 | 149 | 0 | 100 | 188 | 147 | 205 | 90 | 105 | 17 | 0 | 249 |  | 919 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 41 | 68 | 0 | 172 | 26 | 110 | 0 | 0 | 55 | 50 | 33 | 95 | 40 | 43 | 39 | 50 | 35 | 22 | 15 | 11 | 0 | 0 | 199 | 16 | 17 | 185 | 0 | 182 | 0 | 96 | 100 | 193 | 0 | 350 | 105 | 0 | 108 | 53 | 1 |  | 8328 | 3560 | 11888 | 4017 | 919 | 2126 | 3693 | 199 | 37 | 769 | 128 | 0 | 0 | 77.5
21:00 | 70 | 138 | 0 | 190 | 150 | 72 | 40 | 250 | 304 | 0 | 0 | 330 | 290 | 87 | 96 | 55 | 33 | 0 | 0 | 0 | 100 | 102 | 140 | 20 | 35 | 0 | 48 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 0 | 37 | 100 | 0 | 25 | 211 | 0 | 130 | 0 | 0 | 24 | 84 | 68 | 60 | 85 | 46 | 18 | 26 | 125 | 0 | 0 | 330 | 290 | 199 | 78 | 97 | 0 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 134 | 145 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 155 | 32 | 81 | 45 | 122 | 18 | 48 | 10 | 320 | 24 | 11 | 0 | 300 | 0 | 20 | 184 | 0 | 149 | 0 | 100 | 177 | 145 | 204 | 90 | 105 | 17 | 0 | 249 |  | 920 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 59 | 0 | 172 | 30 | 110 | 0 | 0 | 55 | 50 | 32 | 95 | 40 | 43 | 37 | 51 | 35 | 22 | 15 | 11 | 0 | 0 | 199 | 16 | 17 | 191 | 0 | 156 | 0 | 95 | 99 | 198 | 0 | 350 | 105 | 0 | 108 | 52 | 1 |  | 8497 | 3535 | 12032 | 4186 | 920 | 2155 | 3662 | 199 | 37 | 739 | 134 | 0 | 0 | 77.5
22:00 | 70 | 139 | 0 | 190 | 150 | 72 | 40 | 250 | 306 | 0 | 0 | 330 | 290 | 92 | 96 | 55 | 34 | 0 | 0 | 0 | 100 | 102 | 140 | 20 | 36 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 0 | 38 | 100 | 0 | 25 | 212 | 0 | 133 | 0 | 0 | 24 | 84 | 68 | 60 | 90 | 46 | 19 | 33 | 125 | 0 | 0 | 335 | 300 | 202 | 78 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 0 | 33 | 21 | 122 | 146 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 154 | 32 | 80 | 46 | 119 | 18 | 48 | 10 | 325 | 24 | 11 | 0 | 300 | 0 | 0 | 175 | 0 | 149 | 0 | 100 | 177 | 135 | 201 | 90 | 105 | 17 | 0 | 249 |  | 920 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 65 | 0 | 172 | 38 | 110 | 0 | 0 | 55 | 50 | 32 | 95 | 40 | 43 | 37 | 52 | 34 | 22 | 15 | 11 | 0 | 0 | 195 | 17 | 17 | 198 | 0 | 162 | 0 | 95 | 99 | 205 | 0 | 350 | 105 | 0 | 108 | 86 | 1 |  | 8435 | 3600 | 12035 | 4220 | 920 | 2177 | 3668 | 195 | 38 | 695 | 122 | 0 | 0 | 77.5
23:00 | 70 | 139 | 0 | 190 | 150 | 73 | 40 | 250 | 305 | 0 | 0 | 330 | 287 | 92 | 96 | 55 | 34 | 0 | 0 | 0 | 100 | 102 | 140 | 20 | 35 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 0 | 38 | 100 | 0 | 0 | 214 | 0 | 130 | 0 | 0 | 24 | 84 | 68 | 60 | 90 | 46 | 18 | 38 | 125 | 0 | 0 | 325 | 290 | 203 | 78 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 0 | 33 | 21 | 124 | 147 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 156 | 32 | 80 | 46 | 118 | 16 | 48 | 10 | 325 | 24 | 11 | 0 | 300 | 0 | 0 | 175 | 0 | 149 | 0 | 100 | 177 | 135 | 201 | 81 | 105 | 17 | 0 | 249 |  | 919 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 60 | 0 | 172 | 37 | 110 | 0 | 0 | 55 | 50 | 33 | 91 | 40 | 43 | 37 | 52 | 34 | 22 | 15 | 11 | 0 | 0 | 194 | 17 | 17 | 200 | 0 | 165 | 0 | 95 | 99 | 207 | 0 | 350 | 105 | 0 | 108 | 87 | 1 |  | 8384 | 3590 | 11974 | 4206 | 919 | 2181 | 3632 | 194 | 38 | 680 | 124 | 0 | 0 | 77.5
24:00 | 70 | 139 | 0 | 190 | 150 | 73 | 40 | 290 | 305 | 0 | 0 | 330 | 275 | 93 | 70 | 55 | 34 | 0 | 0 | 0 | 100 | 102 | 142 | 20 | 36 | 0 | 47 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 0 | 36 | 100 | 0 | 14 | 203 | 0 | 140 | 0 | 0 | 25 | 84 | 68 | 60 | 90 | 46 | 19 | 33 | 125 | 0 | 0 | 310 | 275 | 183 | 78 | 100 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 5 | 33 | 21 | 136 | 148 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 154 | 33 | 80 | 46 | 121 | 15 | 47 | 10 | 300 | 24 | 11 | 0 | 285 | 0 | 0 | 175 | 0 | 149 | 0 | 100 | 178 | 135 | 200 | 81 | 105 | 17 | 0 | 249 |  | 920 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 33 | 60 | 0 | 172 | 35 | 110 | 0 | 0 | 60 | 50 | 33 | 84 | 40 | 43 | 37 | 52 | 34 | 22 | 15 | 11 | 0 | 0 | 194 | 17 | 18 | 198 | 0 | 170 | 0 | 93 | 99 | 204 | 0 | 350 | 105 | 0 | 108 | 86 | 1 |  | 8326 | 3553 | 11879 | 4207 | 920 | 2146 | 3580 | 194 | 36 | 660 | 136 | 0 | 0 | 77.5
KWH | 1661000 | 3486800 | 0 | 4551750 | 627800 | 2125409 | 1354752 | 7282690 | 7367000 | 0 | 0 | 7885875 | 6672175 | 1484160 | 648912 | 501078 | 621418 | 0 | 0 | 0 | 1231680 | 1599552 | 2446560 | 1257635 | 1205760 | 0 | 1056720 | 1154520 | 1155809 | 750040 | 433116 | 600000 | 708660 | 714700 | 797000 | 1073388 | 0 | 0 | 848000 | 2400000 | 0 | 459095 | 4921548 | 0 | 3226500 | 0 | 0 | 450720 | 646696 | 621171 | 886200 | 1584960 | 1032960 | 435552 | 446880 | 2975686 | 0 | 0 | 7527000 | 7527000 | 4607000 | 3546181 | 2967040 | 0 | 3849500 | 0 | 731092 | 0 | 138504 | 993115 | 439992 | 150840 | 803800 | 408770 | 3823680 | 3464280 | 1860480 | 428076 | 14300 | 1270000 | 1292120 | 1038000 | 1004256 | 1385206 | 2350000 | 1173312 | 1649280 | 975240 | 2774970 | 65000 | 967600 | 250740 | 7532250 | 503784 | 218880 | 0 | 4586616 | 0 | 711042 | 3069600 | 0 | 2662560 | 102735 | 2261760 | 3988320 | 3069450 | 5637000 | 2055600 | 2488800 | 521050 | 29520 | 5499927 |  | 22091636 | 80100 | 0 | 0 | 2287680 | 0 | 0 | 0 | 401760 | 608896 | 0 | 4205243 | 651694 | 1440960 | 0 | 0 | 1360000 | 432208 | 194808 | 1544092 | 551950 | 674996 | 255200 | 821760 | 334960 | 505920 | 344268 | 214866 | 0 | 0 | 4857700 | 126000 | 136000 | 4777154 | 0 | 4469200 | 0 | 2140423 | 762240 | 4917036 | 0 | 8372000 | 2194080 | 0 | 2603520 | 1799280 | 299520 |  | 187807195 | 76457150 | 264264345 | 98996583 | 22091636 | 54123566 | 71409670 | 4857700 | 848000 | 7966955 | 3823680 | 146555 | 0
Fuel Cost | 1428460 | 2998648 | 0 | 3914505 | 401792 | 1721581.29 | 1273466.88 | 4442440.9 | 4493870 | 0 | 0 | 5283536.25 | 101350338.25 | 9320524.8 | 4334732.16 | 3061586.58 | 403921.7 | 0 | 0 | 0 | 7698000 | 10541047.68 | 23658235.2 | 8011134.95 | 7222502.4 | 0 | 7048322.4 | 8231727.6 | 7223806.25 | 4702750.8 | 324837 | 450000 | 0 | 0 | 0 | 10154250.48 | 0 | 0 | 0 | 2640000 | 0 | 4347629.65 | 3248221.68 | 0 | 3710475 | 0 | 0 | 3961828.8 | 6964915.92 | 6043993.83 | 5485578 | 10238841.6 | 6755558.4 | 370219.2 | 0 | 2707874.26 | 0 | 0 | 4666740 | 5193630 | 3224900 | 2446864.89 | 2848358.4 | 0 | 3310570 | 0 | 599495.44 | 0 | 1501383.36 | 7368913.3 | 338793.84 | 113130 | 618926 | 306577.5 | 26153971.2 | 2598210 | 17097811.2 | 329618.52 | 0 | 1320800 | 1343804.8 | 996480 | 903830.4 | 1080460.68 | 1645000 | 1337575.68 | 1764729.6 | 1072764 | 3163465.8 | 83200 | 899868 | 233188.2 | 4820640 | 377838 | 166348.8 | 0 | 33298832.16 | 0 | 12123266.1 | 21947640 | 0 | 0 | 0 | 0 | 37250908.8 | 28668663 | 4904190 | 0 | 0 | 0 | 0 | 0 |  | 112667343.6 | 2334915 | 0 | 0 | 18964867.2 | 0 | 0 | 0 | 4523817.6 | 7172794.88 | 0 | 2901617.67 | 645177.06 | 10663104 | 0 | 0 | 1428000 | 4948781.6 | 2088341.76 | 13835064.32 | 4774367.5 | 6007464.4 | 2717880 | 8151859.2 | 3942479.2 | 556512 | 323611.92 | 162653.562 | 0 | 0 | 18750722 | 4060980 | 3640720 | 3248464.72 | 0 | 3128440 | 0 | 0 | 13209619.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 534292542.58 | 254849598.392 | 789142140.972 | 72491678.032 | 112667343.6 | 32426646.61 | 439217476.86 | 18750722 | 0 | 87434302.67 | 26153971.2 | 0 | 0
Yesterday Day Peak | 70 | 139 | 0 | 190 | 0 | 101 | 69 | 280 | 304 | 0 | 0 | 300 | 297 | 90 | 0 | 0 | 35 | 0 | 0 | 0 | 72 | 92 | 96 | 78 | 35 | 0 | 48 | 54 | 55 | 35 | 16 | 25 | 31 | 33 | 33 | 49 | 0 | 0 | 35 | 100 | 0 | 25 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 31 | 32 | 16 | 2 | 125 | 0 | 0 | 120 | 360 | 184 | 199 | 140 | 0 | 51 | 0 | 35 | 0 | 0 | 52 | 21 | 5 | 33 | 11 | 126 | 146 | 86 | 22 | 2.4 | 53 | 29 | 47 | 43 | 100 | 151 | 61 | 81 | 44 | 75 | 0 | 42 | 10 | 290 | 16 | 11 | 0 | 250 | 0 | 0 | 100 | 0 | 149 | 3.48 | 100 | 177 | 140 | 249 | 85 | 105 | 17 | 5.1 | 178 |  | 919 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 26 | 16 | 0 | 0 | 55 | 0 | 0 | 47 | 12 | 32 | 0 | 41 | 0 | 19 | 13 | 8 | 0 | 0 | 199 | 0 | 0 | 154 | 0 | 145 | 0 | 92 | 0 | 156 | 0 | 370 | 90 | 0 | 108 | 87 | 20 |  | 10445.98 | DayPeak
Yesterday Evening Peak | 70 | 138 | 0 | 190 | 150 | 72 | 40 | 250 | 304 | 0 | 0 | 330 | 290 | 87 | 96 | 55 | 33 | 0 | 0 | 0 | 100 | 102 | 140 | 20 | 35 | 0 | 48 | 54 | 55 | 35 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 0 | 37 | 100 | 0 | 25 | 211 | 0 | 130 | 0 | 0 | 24 | 84 | 68 | 60 | 85 | 46 | 18 | 26 | 125 | 0 | 0 | 330 | 290 | 199 | 78 | 97 | 0 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 134 | 145 | 84 | 22 | 0 | 53 | 57 | 50 | 49 | 100 | 155 | 32 | 81 | 45 | 122 | 18 | 48 | 10 | 320 | 24 | 11 | 0 | 300 | 0 | 20 | 184 | 0 | 149 | 0 | 100 | 177 | 145 | 204 | 90 | 105 | 17 | 0 | 249 |  | 920 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 59 | 0 | 172 | 30 | 110 | 0 | 0 | 55 | 50 | 32 | 95 | 40 | 43 | 37 | 51 | 35 | 22 | 15 | 11 | 0 | 0 | 199 | 16 | 17 | 191 | 0 | 156 | 0 | 95 | 99 | 198 | 0 | 350 | 105 | 0 | 108 | 52 | 1 |  | 12032 | EvPeak
Forecast for Evening | 70 | 140 | 0 | 190 | 0 | 108 | 70 | 412 | 360 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 33 | 0 | 90 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 225 | 0 | 130 | 0 | 0 | 33 | 85 | 68 | 100 | 100 | 46 | 21 | 20 | 125 | 0 | 0 | 360 | 360 | 221 | 190 | 140 | 0 | 55 | 0 | 40 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 190 | 150 | 85 | 22 | 0 | 54 | 70 | 51 | 44 | 163 | 150 | 66 | 86 | 46 | 130 | 19 | 47 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 100 | 100 | 105 |  | 300 |  | 930 | 46 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 60 | 40 | 172 | 33 | 110 | 26 | 0 | 60 | 50 | 35 | 100 | 40 | 43 | 47 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 250 | 17 | 18 | 220 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 105 | 23
Forecast for Day | 70 | 140 | 0 | 190 | 0 | 108 | 70 | 412 | 360 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 33 | 0 | 90 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 35 | 100 | 0 | 25 | 220 | 0 | 130 | 0 | 0 | 32 | 85 | 68 | 100 | 100 | 46 | 21 | 10 | 125 | 0 | 0 | 360 | 360 | 221 | 78 | 140 | 0 | 55 | 0 | 40 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 152 | 150 | 85 | 22 | 2 | 54 | 70 | 51 | 44 | 163 | 150 | 66 | 86 | 46 | 120 | 15 | 47 | 10 | 341 | 25 | 11 | 0 | 100 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 285 | 100 | 100 | 105 | 3 | 300 |  | 930 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 172 | 33 | 110 | 0 | 0 | 60 | 50 | 0 | 100 | 40 | 32 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 220 | 0 | 220 | 0 | 95 | 0 | 220 | 0 | 414 | 105 | 0 | 100 | 105 | 23
Generation at 08:00(Today) | 70 | 139 | 0 | 190 | 0 | 73 | 50 | 290 | 305 | 0 | 0 | 330 | 277 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 7 | 60 | 0 | 35 | 0 | 47 | 54 | 55 | 30 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 0 | 37 | 100 | 0 | 25.5 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 51 | 46 | 16 | 11 | 125 | 0 | 0 | 310 | 275 | 184 | 78 | 100 | 0 | 52 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 106 | 147 | 84 | 22 | 1.1 | 53 | 57 | 50 | 49 | 10 | 154 | 32 | 50 | 44 | 120 | 15 | 45 | 10 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 16 | 1.8 | 100 | 177 | 135 | 201 | 84 | 88 | 17 | 1.5 | 232 | 0 | 493 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 23 | 48 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 10 | 0 | 22 | 16 | 8 | 0 | 0 | 194 | 0 | 0 | 145 | 0 | 147 | 0 | 97 | 0 | 188 | 0 | 320 | 105 | 0 | 108 | 86 | 0 | 0
199
| Minimum Generation |  | 8642.6 | 7:00
| Highest Generation |  | 12035 | 22:00
| Day Peak Generation |  | 10445.98 | 12:00
| Evening Peak Generation |  | 12032 | 21:00
| HVDC Max Flow |  | 927 | 1:00
| HVDC EvPeak Flow |  | 920 | 21:00
| Load factor L.F |  | 91.49%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-07-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-06-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10445.98 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9010.9 | MW
Evening Peak Generation : |  | 12032 | MW Hour : | 21:00 | Available Max Generation : |  | 14733 | MW
E.P. Demand (at gen end) : |  | 12032 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12600 | MW
Maximum Generation : |  | 12035 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2133 | MW
Total Gen. (MKWH) : |  | 264.2643 | System Load Factor : | 91.49% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -280 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-07-01
Actual : | 78.01 | Ft.(MSL) , | Rule curve : | 84 | Ft.( MSL )
Gas Consumed : | Total = | 1328.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104918324.642
|  | Coal : | 18750722 | Oil : | 526651779.53 | Total : | 650320826.172
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4481.6698 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1527.8853 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1369.6241 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1237.8157 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1118.4612 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 902.5683 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 499.6923 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 232.2553 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 696.1293 |  |  | 0 | 0%
Total | 0 |  | 12066.1014 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 & 2. | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-7 & 3.
3) Sikalbaha ST 60 MW
4) Bheramara 410 MW.
5) Siddhirganj ST
6) Ashuganj #4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Bagerhat 132/33 kV T1 & T3 transformers tripped at 06:08 from 33 kV end showing E/F due to 33 kV PBS Rampal |  |  |  |  | About 40 MW power interruption occurred under Bagerhat S/S
feeder fault and were switched on at 06:17, 06:18 respectively. |  |  |  |  | area from 06:08 to 06:17.
b) Ashuganj (N) 450 MW CCPP GT was synchronized at 08:54.
c) Ashuganj (N) 450 MW CCPP ST was synchronized at 11:23.
d) Shahjibazar 330 MW CCPP GT-2 & ST was synchronized 10:03
e) Kushiara CCPP GT was synchronized at 10:54.
f) Sikalbaha-Madunaghat 132 kV Ckt was under shut down from 10:54 to 13:11 for D/W.
g) Pabna 132/33 kV T3 transformer was under shut down from 10:12 to 15:05 due to oil leakage maintenance
of buchholz relay.
h) Feni 132/33 kV T2 transformer was under shut down from 13:11 to 21:36 due to replacing 33 kV O/C relay.
i) Kaptai-Hathazari 132 kV both Ckt tripped at 14:09 showing Dist. E/F R-phase relay and was switched on at 14:39.
j) Madunaghat 132/33 kV T1 transformer was under shut down from 17:20 to 17:30 due to 33 kV B-phase
CB pole maintenance.
k) Madunaghat 132/33 kV T2 transformer tripped at 17:24 showing winding temperature high and was switched on |  |  |  |  | About 45 MW power interruption occurred under Madunaghat S/S
at 21:12. |  |  |  |  | area from 17:24 to 21:12.
l) Jamalpur 132/33 kV T2 transformer was switched on at 15:18.
m) Chapai Nawabganj 132/33 kV T2 transformer was switched on at 18:20.
n) Ghorasal unit-7 was shut down at 07:12(01/07/2019) to couple STG.
o) Nator 132/33 kV T4 transformer tripped at 02:55(01/07/2019) showing O/C relay at 33 kV end and |  |  |  |  | About 10 MW power interruption occurred under Nator S/S
was switched on at 03:01(01/07/2019) |  |  |  |  | area from 02:55 to 03:01(01/07/2019).
p) Sirajganj unit-1 STG tripped at 02:08(01/07/2019) due to HVDC breaker open.
q) Bheramara HVDC Block-1 was shut down at 06:18(01/07/2019) due to red hat maintenance at 230 kV end.
r) Aminbazar-Saver 132 kV Ckt-2 & Main Bus were shut down at 06:06 (01/07/2019) for C/M.
s) Madunaghat 132/33 kV T1 transformer was shut down at 05:45(01/07/2019) due to 33 kV B-phase
CB pole maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-06-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1661000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 138 | 3486800
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4551750
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 150 | 627800 | Synchronized at 17:02.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 40 | 1354752 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 2125409 | Gas shortage
5 | Haripur GT PP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 250 | 7282690 | Gas shortage
7 | Haripur 110 MW PP(NEPC) |  | IPP | 8*15 | 110 | 0 | 0 | Contract Expired
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 304 | 7367000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 7885875 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 87 | 1484160 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 290 | 6672175 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 648912
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 501078
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 20 | 1257635 | Low demand
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 433116
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1231680
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 33 | 621418 | test
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1599552
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 1056720
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1154520
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 140 | 2446560
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1155809
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 750040 | Engine problem
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 35 | 1205760 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1308660 | Engine problem
28 | Maona 33 MW (Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 714700
29 | Rupganj 33 MW (Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 797000
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 49 | 1073388
31 | Tongi 80 MW GT PP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 4586616
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 20 | 711042 | Low demand
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2662560
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2488800
| Dhaka area Total |  |  |  | 5803 | 3462 | 72904977
38 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
39 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 459095
40 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 102735
41 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 1032960
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 848000 | Low water level
43 | Sikalbaha 60MW TPP |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 211 | 4921548 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3226500
46 | Sikalbaha 51 MW PP(Engine) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 24 | 450720 | Engine problem
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 521050 | Low demand
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 84 | 646696
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 621171
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 60 | 886200 | Low demand
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2261760
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 435552
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 446880
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1584960 | Engine problem
| Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 0 | 0 | 29520
| Anwara 300 MW PP (United) |  | United Group | 300 MW | 0 | 249 | 5499927 | on test
| Chattogram area Total |  |  |  | 1786 | 1280 | 26375274
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 125 | 2975686 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4607000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7527000 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7527000 | Machine problem
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas Line maint.
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 3849500
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 78 | 3546181 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 731092 | Machine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 145 | 3069450
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 138504
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 97 | 2967040 | ST under maint.
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 177 | 3988320 | Low demand
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 439992
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 150840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 3823680 | Load restricted from India.
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 803800
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 993115
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 408770
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1851 | 47546970
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3464280 | GT-1 under maint.
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 428076
76 | Jamalpur 95 MW PP |  | IPP | 12*8.924 | 95 | 84 | 1860480 | Engine problem
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14300
78 | United Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 184 | 3069600 | Engine problem
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 90 | 2055600 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 525 | 10892336
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 53 | 1270000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1292120
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 1385206 | Machine problem
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 155 | 2350000 | FGMO & ST Under maint
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1038000
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1004256
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 218880
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 1173312 | GT-9 under maint.
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1649280
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 45 | 975240
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 122 | 2774970 | FGMO
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 65000
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 48 | 967600
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 503784
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7532250 | FGMO
| Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 0 | 204 | 5637000 | On test
95 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250740
| Sylhet Area Total |  |  |  | 1549 | 1379 | 30087638
96 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 16 | 80100 | Low demand
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 920 | 22091636
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
97 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2287680
98 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 401760
99 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
100 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 59 | 608896
101 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
102 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Engine problem
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
103 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 99 | 762240
104 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2194080
105 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 52 | 1799280 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1406 | 30225672
106 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1440960
107 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
108 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 651694
109 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 172 | 4205243 | FGMO
110 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 2140423
| Barisal Area Total |  |  |  | 462 | 407 | 8438320
111 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1360000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
112 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 432208
113 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 32 | 194808
114 | Amnura 50 MW PP |  | QRPP | 7*7.79 | 50 | 40 | 551950 | Engine problem
115 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 674996 | Engine problem
116 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 255200
117 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 191 | 4777154 | FGMO
118 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 156 | 4469200 | FGMO
119 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 198 | 4917036 | FGMO
120 | Sirajgonj 400 MW CCPP Unit-4 (Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 350 | 8372000 | frequency control.
121 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 334960
122 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 505920
123 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 15 | 344268
124 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 214866
125 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 51 | 821760
126 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 1544092
127 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
128 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 108 | 2603520
| Rajshahi Area Total |  |  |  | 2070 | 1489 | 32373938
129 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
130 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4857700
131 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 126000
132 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 136000
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 1 | 299520 | On test
| Rangpur Area Total |  |  |  | 484 | 233 | 5419220
| Total |  |  |  | 17996 | 12032 | 264264345
| Eastern Grid Total |  |  |  | 12666 | 8497 | 187807195
| Western Grid Total |  |  |  | 5330 | 3535 | 76457150
| National Grid Total |  |  |  | 17996 | 12032 | 264264345
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-06-30
| (a) ENTIRE EASTERN GRID : |  | 7867 | MW | (b) ENTIRE WESTERN GRID : |  | 3646 | MW
| i) Dhaka area |  | 4185 | MW | i) Khulna area |  | 1370 | MW
| ii) Chittagong area |  | 1191 | MW | ii) Rajshahi area |  | 1272 | MW
| iii) Comilla area |  | 1048 | MW | iii) Barisal area |  | 322 | MW
| iv) Mymensingh area |  | 963 | MW | iv) Rangpur area |  | 682 | MW
| v) Sylhet area |  | 480 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11513 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 130 | 900 | Jamalpur | 142 | 2200 | Jessore | 116 | 2200
2 | Munsiganj | 128 | 2100 | Sherpur | 96 | 100 | Benapol | 114 | 1930
3 | Sonargaon | 72 | 2000 | Srimongal | 38 | 1930 | Jhenida | 130 | 1930
4 | Shyampur | 200 | 2400 | Shahjibazar | 124 | 2200 | Bottail | 58 | 2000
5 | Bhulta | 195 | 2200 | Fenchuganj | 50 | 2200 | G.K Project | 178 | 1930
6 | Madanganj | 67 | 1930 | Kulawara | 42 | 2300 | Faridpur | 116 | 2200
7 | Shitalakhya | 117 | 1600 | Sylhet | 142 | 2100 | Madaripur | 97 | 2200
8 | Rahim steel | 4 | 2100 | Chatak | 34 | 2100 | Sariatpur | 96 | 1930
9 | Matuail | 102 | 1200 | Sunamganj | 36 | 2100 | Gopalganj | 32 | 1100
10 | Ghorasal | 92 | 1930 | Biani Bazar | 49 | 2200 | Bagerhat | 103 | 2200
11 | Narsingdi | 146 | 2000 | Comilla (S) | 150 | 1400 | Mongla | 51 | 1300
12 | Haripur (SBU) | 106 | 1200 | Comilla(N) | 153 | 2000 | Satkhira | 55 | 2000
13 | Ullon | 92 | 2000 | Chandpur | 103 | 2400 | Gallamari | 87 | 2000
14 | Hasnabad | 207 | 2000 | Feni | 138 | 2200 | Magura | 110 | 1900
15 | Magbazar | 147 | 1500 | Chowmuhani | 162 | 2400 | Chuadanga | 101 | 2200
16 | Maniknagar | 120 | 1500 | Ashuganj | 56 | 2400 | Barisal | 52 | 1900
17 | Bangabhaban | 38 | 1200 | Daudkandi | 135 | 2100 | Barisal (N) | 43 | 2100
18 | Narinda | 96 | 1500 | B.Baria | 142 | 2200 | Patuakhali | 28 | 100
19 | Dhanmondi | 160 | 1200 | Ramganj | 83 | 1900 | Bhandaria | 21 | 2200
20 | Lalbag | 97 | 1600 | Madunaghat | 55 | 1930 | Borhan Uddin | 36 | 100
21 | Madartek | 63 | 2300 | Hathazari | 109 | 1930 | Ishurdi | 66 | 1930
22 | Mirpur | 115 | 1900 | Khulshi | 206 | 1600 | Ruppur Paromanobik | 2 | 900
23 | Kalyanpur | 123 | 1900 | Halishahar | 153 | 1600 | Natore | 128 | 2100
24 | Gulshan | 174 | 1600 | Baraulia | 158 | 200 | Bogra | 248 | 2100
25 | Uttara | 90 | 1700 | Sikalbaha | 40 | 1900 | Noagaon | 124 | 100
26 | Uttara New | 19 | 1700 | Dohazari | 104 | 1900 | Rajshahi | 176 | 2000
27 | Kamrangirchar | 76 | 1930 | Cox'sbazar | 90 | 100 | C.Nawabganj | 81 | 2300
28 | Savar | 148 | 1200 | Chandraghona | 24 | 100 | Amnura | 38 | 100
29 | Bhasantec | 176 | 1600 | Kaptai | 4.5 | 1930 | Pabna | 117 | 2200
30 | Agargaon | 65 | 1300 | A. Khaer Stl. | 20 | 900 | Shahjadpur | 105 | 2100
31 | Satmosjid | 114 | 1900 | Bakulia | 119 | 2000 | Serajganj | 119 | 2100
32 | Tongi | 163 | 1500 | Julda | 21 | 900 | Niyamatpur | 63 | 200
33 | Kabirpur | 232 | 1600 | TK chemical | 4.2 | 1400 | Joypurhat | 49 | 100
34 | Basundhara | 122 | 2100 | Modern Steel | 15 | 2000 | Mohastangor | 16 | 2000
35 | Manikganj | 102 | 2100 | Shahmirpur | 34 | 100 | Rangpur | 137 | 2000
36 | Joydevpur | 233 | 1930 | Khagrachhari | 21 | 1930 | Lalmonirhat | 90 | 2200
37 | New Tongi | 105 | 1930 | Matarbari | 29 | 2200 | Saidpur | 112 | 2000
38 | Korda | 249 | 1600 | Baroiar Hat | 38 | 1900 | Purbasadipur | 100 | 2000
39 | Dhamrai | 65 | 2100 | Rangamati | 12 | 1900 | Thakurgaon | 68 | 100
40 | Valuka | 108 | 1600 | Abul Khair 230 | 106 | 1100 | Palashbari | 115 | 2100
41 | Tangail | 208 | 2200 | BSRM | 106 | 1600 | Barapukuria | 50 | 1930
42 | Mymensing | 234 | 2100 | Goalpara | 28 | 1930 | Panchagar | 41 | 1930
43 | Kishorganj | 124 | 2000 | Central (S) | 87 | 2300 | Joldhaka | 20 | 1930
44 | Netrokona | 107 | 2000 | Noapara | 97 | 1930
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-06-30
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 391 | 13:00 | 381 | 21:00 | Kaliakoir | 368 | 2:00 | 360
2 | Bheramara | 392 | 6:00 | 384 | 24:00 | Bhulta | 386 | 20:00 | 372
3 | Ashuganj(N) | 392 | 4:00 | 375 | 8:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 8:00
1 | Ghorasal | 232 | 1:00 | 230 | 7:00 | Hathazari | 222 | 19:30 | 215
2 | Ishurdi | 235 | 3:00 | 220 | 21:00 | Megnaghat | 222 | 4:00 | 220
3 | Ashuganj | 238 | 4:00 | 234 | 10:00 | Fenchuganj | 234 | 13:00 | 228
4 | Serajganj | 233 | 18:00 | 225 | 21:00 | Siddhirganj | 223 | 2:00 | 216
5 | Baghabari | 231 | 6:00 | 221 | 21:00 | Maniknagar | 221 | 20:00 | 215
6 | Barapukuria | 233 | 5:00 | 219 | 23:00 | Old Airport | 220 | 3:00 | 213
7 | Bogra | 226 | 5:00 | 209 | 22:00 | Barisal | 236 | 20:00 | 223
8 | Khulna South | 230 | 5:00 | 207 | 21:00 | AKSML | 221 | 20:00 | 214
9 | Rampura | 222 | 4:00 | 217 | 15:00 | BSRM | 224 | 20:00 | 216
10 | Haripur | 220 | 1:00 | 215 | 9:00 | Bibiyana | 232 | 14:00 | 226
11 | Hasnabad | 222 | 20:00 | 215 | 10:00 | Bhulta | 223 | 2:00 | 217
12 | Aminbazar | 220 | 3:00 | 215 | 12:00 | Ashuganj (S) | 237 | 5:00 | 232
13 | Tongi | 225 | 1:00 | 216 | 8:00 | Kaliakoir | 226 | 20:00 | 218
14 | Comilla (N) | 228 | 5:00 | 224 | 15:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 131 | 1930 | 127 | 800 | Hathazari | 136 | 1000 | 128
2 | Munsiganj | 134 | 2000 | 127 | 1200 | Khulshi | 130 | 400 | 125
3 | Megnaghat | 131 | 2400 | 127 | 800 | Halishahar | 134 | 500 | 129
4 | Shyampur | 134 | 2000 | 129 | 1600 | Baraulia | 131 | 1930 | 125
5 | Bhulta | 126 | 2000 | 116 | 1200 | Sikalbaha | 135 | 2000 | 130
6 | Madanganj | 136 | 2000 | 127 | 600 | Dohazari | 132 | 500 | 129
7 | Shitalakhya | 139 | 2000 | 128 | 800 | Cox'sbazar | 128 | 1700 | 120
8 | Rahim steal | 132 | 2000 | 127 | 900 | Chandraghona | 133 | 2000 | 129
9 | Matuail | 131 | 2000 | 125 | 1000 | Kaptai | 132 | 800 | 129
10 | Ghorasal | 138 | 100 | 135 | 2300 | A. Khaer Stl. | 130 | 1900 | 126
11 | Narsinghdi | 125 | 600 | 119 | 1200 | Bakulia | 133 | 1930 | 128
12 | Haripur (SBU) | 132 | 2000 | 127 | 900 | Julda | 134 | 1930 | 129
13 | Ullon | 134 | 600 | 126 | 1600 | TK Chemical | 134 | 1930 | 129
14 | Hasnabad | 134 | 1800 | 128 | 1200 | Modern Steel | 133 | 100 | 129
15 | Magbazar | 125 | 600 | 127 | 1200 | Shahmirpur | 134 | 1930 | 128
16 | Maniknagar | 133 | 600 | 129 | 1200 | Khagrachhari | 131 | 2000 | 127
17 | Bangabhaban | 133 | 600 | 129 | 1200 | Matarbari | 129 | 900 | 122
18 | Narinda | 133 | 600 | 129 | 1200 | Baroiar Hat | 130 | 1930 | 123
19 | Dhanmondi | 134 | 600 | 126 | 1600 | Rangamati | 132 | 2000 | 127
20 | Lalbag | 131 | 500 | 124 | 1200 | Goalpara | 137 | 1830 | 122
21 | Madartek | 134 | 500 | 127 | 1500 | Central s/s | 136 | 1800 | 121
22 | Mirpur | 135 | 300 | 128 | 1600 | Noapara | 132 | 1830 | 116
23 | Kalyanpur | 135 | 200 | 130 | 1100 | Jessore | 126 | 1800 | 110
24 | Gulshan | 134 | 500 | 126 | 1600 | Benapol | 128 | 1830 | 105
25 | Uttara | 132 | 300 | 125 | 1200 | Jhenida | 134 | 500 | 116
26 | Uttara New | 134 | 100 | 129 | 700 | Bottail | 139 | 1800 | 125
27 | Kamrangirchar | 131 | 100 | 126 | 800 | G.K Project | 132 | 700 | 120
28 | Savar | 133 | 300 | 127 | 1100 | Faridpur | 135 | 1900 | 124
29 | Bhasantec | 135 | 300 | 129 | 1200 | Madaripur | 141 | 1930 | 130
30 | Agargaon | 137 | 500 | 131 | 1200 | Sariatpur | 134 | 1800 | 121
31 | Satmosjid | 136 | 200 | 130 | 1600 | Gopalganj | 132 | 1800 | 122
32 | Tongi | 137 | 2300 | 130 | 800 | Bagerhat | 134 | 1800 | 114
33 | Kabirpur | 133 | 500 | 126 | 2100 | Mongla | 136 | 1800 | 121
34 | Basundhara | 133 | 2400 | 120 | 1600 | Satkhira | 128 | 1830 | 103
35 | Manikganj | 140 | 2400 | 130 | 800 | Gallamari | 123 | 1830 | 96
36 | Joydevpur | 141 | 600 | 132 | 900 | Magura | 138 | 1830 | 130
37 | New Tongi | 135 | 2000 | 128 | 800 | Chuadanga | 136 | 700 | 128
38 | Kodda | 138 | 2000 | 128 | 700 | Barisal | 135 | 800 | 124
39 | Dhamrai | 131 | 500 | 126 | 2100 | Barisal (N) | 139 | 1900 | 130
40 | Valuka | 131 | 600 | 110 | 2100 | Patuakhali | 135 | 900 | 122
41 | Tangail | 132 | 600 | 120 | 2100 | Bhandaria | 130 | 1830 | 112
42 | Mymensing | 131 | 600 | 115 | 2100 | Ishurdi | 138 | 1800 | 126
43 | Kishorganj | 132 | 700 | 120 | 2100 | Ruppur Paromanobik | 136 | 1830 | 128
44 | Netrokona | 131 | 400 | 116 | 2100 | Natore | 138 | 1900 | 122
45 | Jamalpur | 137 | 400 | 131 | 800 | Bogra | 134 | 600 | 121
46 | Sherpur | 136 | 500 | 129 | 800 | Noagaon | 130 | 1830 | 114
47 | Srimongal | 136 | 600 | 132 | 1900 | Rajshahi | 129 | 100 | 122
48 | Shahjibazar | 135 | 500 | 130 | 2100 | C.Nawabganj | 126 | 1900 | 119
49 | Fenchuganj | 135 | 800 | 132 | 200 | Amnura | 133 | 1900 | 120
50 | Khulawara | 134 | 700 | 130 | 100 | Pabna | 136 | 1800 | 124
51 | Sylhet | 135 | 800 | 131 | 1800 | Shahjadpur | 140 | 600 | 132
52 | Chatak | 134 | 700 | 130 | 100 | Serajganj | 133 | 500 | 124
53 | Sunamganj | 134 | 700 | 128 | 100 | Niyamatpur | 129 | 1830 | 113
54 | Biani Bazar | 136 | 800 | 128 | 2200 | Joypurhat | 129 | 1830 | 115
55 | Comilla(s) | 124 | 800 | 120 | 1900 | Mohastangor | 132 | 600 | 119
56 | Comilla(n) | 135 | 1830 | 132 | 1500 | Rangpur | 130 | 600 | 111
57 | Chandpur | 135 | 700 | 132 | 1400 | Lalmonirhat | 125 | 500 | 103
58 | Feni | 128 | 2000 | 122 | 2200 | Saidpur | 131 | 600 | 111
59 | Chowmuhani | 127 | 700 | 120 | 2200 | Purbasadipur | 130 | 500 | 110
60 | Ashuganj | 136 | 800 | 131 | 2100 | Thakurgaon | 125 | 600 | 104
61 | Daudkandi | 133 | 2000 | 125 | 1500 | Palashbari | 130 | 600 | 112
62 | B.Baria | 134 | 600 | 126 | 2200 | Barapukuria | 133 | 500 | 119

## L-Curve
Date | 2019-06-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 160 | 8326 | 3553 | 11879 |  |  |  | QF-LDC-12
0:30 | 210 | 8129 | 3617 | 11746 | Date: | 2019-06-30
1:00 | 260 | 7932 | 3681 | 11613
1:30 | 220 | 7934.5 | 3589 | 11523.5
2:00 | 180 | 7937 | 3497 | 11434
2:30 | 145 | 7851 | 3452 | 11303 | [5 empty] | Gen. at Eve. Peak | 12032 | 12032 MW (21:00 )
3:00 | 110 | 7765 | 3407 | 11172 | [6 empty] | 21:00
3:30 | 95 | 7660.5 | 3337.5 | 10998 | [5 empty] | Gen. at Day Peak | 10445.98 | 10445.98 MW (12:00 )
4:00 | 80 | 7556 | 3268 | 10824 | [6 empty] | 12:00
4:30 | 60 | 7388 | 3229.5 | 10617.5 | [5 empty] | Highest Generation | 12035
5:00 | 40 | 7220 | 3191 | 10411 | [6 empty] | 22:00
5:30 | 140 | 6697.05 | 3008.5 | 9705.55
6:00 | 240 | 6174.1 | 2826 | 9000.1
6:30 | 192 | 6049.85 | 2771.5 | 8821.35
7:00 | 144 | 5925.6 | 2717 | 8642.6
7:30 | 192 | 5927.82 | 2734.5 | 8662.32
8:00 | 240 | 5930.04 | 2752 | 8682.04
8:30 | 310 | 6172.835 | 2778.5 | 8951.335
9:00 | 380 | 6415.63 | 2805 | 9220.63
9:30 | 420 | 6634.175 | 2791.5 | 9425.675
10:00 | 460 | 6852.72 | 2778 | 9630.72
10:30 | 390 | 6908.455 | 2881.5 | 9789.955
11:00 | 320 | 6964.19 | 2985 | 9949.19
11:30 | 300 | 7262.085 | 2935.5 | 10197.585
12:00 | 280 | 7559.98 | 2886 | 10445.98
12:30 | 235 | 7547.4 | 2925 | 10472.4
13:00 | 190 | 7534.82 | 2964 | 10498.82
13:30 | 165 | 7525.61 | 2957 | 10482.61
14:00 | 140 | 7516.4 | 2950 | 10466.4
14:30 | 120 | 7561.45 | 2994.5 | 10555.95
15:00 | 100 | 7606.5 | 3039 | 10645.5
15:30 | 175 | 7724.6 | 3075 | 10799.6
16:00 | 250 | 7842.7 | 3111 | 10953.7
16:30 | 315 | 7597.05 | 2994.5 | 10591.55
17:00 | 380 | 7351.4 | 2878 | 10229.4
17:30 | 380 | 7251.125 | 2841 | 10092.125
18:00 | 380 | 7150.85 | 2804 | 9954.85
18:30 | 375 | 7443.925 | 3063 | 10506.925
19:00 | 370 | 7737 | 3322 | 11059
19:30 | 60 | 8470 | 3554 | 12024
20:00 | 140 | 8328 | 3560 | 11888 |  |  |  | Executive Engineer
20:30 | 200 | 8412.5 | 3547.5 | 11960 |  |  |  | Network Operation Division
21:00 | 260 | 8497 | 3535 | 12032
21:30 | 270 | 8466 | 3567.5 | 12033.5
22:00 | 280 | 8435 | 3600 | 12035 |  |  |  |  | Page 6 of 7
22:30 | 230 | 8409.5 | 3595 | 12004.5
23:00 | 180 | 8384 | 3590 | 11974
23:30 | 170 | 8355 | 3571.5 | 11926.5
24:00 | 160 | 8326 | 3553 | 11879
12032 MW (21:00 )
10445.98 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-06-30 |  | Energy | 264264345
[10 empty] | 2019-06-30 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4207 | 920 | 2146 | 3580 | 194 | 36 | 660 | 0 | 136
0:30 | 4003 | 923.5 | 2260.5 | 3552 | 197 | 35 | 634 | 0 | 141 | Date: | 2019-06-30
1:00 | 3799 | 927 | 2375 | 3524 | 200 | 34 | 608 | 0 | 146
1:30 | 3843.5 | 926.5 | 2315.5 | 3486 | 200 | 34.5 | 572.5 | 0 | 145 | [7 empty] | Total Energy | 264.2643 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3888 | 926 | 2256 | 3448 | 200 | 35 | 537 | 0 | 144 | [7 empty] | Energy not Served | 0
2:30 | 3868 | 926 | 2265.5 | 3358.5 | 200 | 34.5 | 508.5 | 0 | 142 | [7 empty] | Energy Requirement | 264.2643
3:00 | 3848 | 926 | 2275 | 3269 | 200 | 34 | 480 | 0 | 140
3:30 | 3854.5 | 926.5 | 2270.5 | 3181 | 199.5 | 34 | 392 | 0 | 140 | [6 empty] | Shortage
4:00 | 3861 | 927 | 2266 | 3093 | 199 | 34 | 304 | 0 | 140
4:30 | 3872.5 | 922.5 | 2276 | 2896.5 | 199 | 34.5 | 277.5 | 0 | 139
5:00 | 3884 | 918 | 2286 | 2700 | 199 | 35 | 251 | 0 | 138
5:30 | 3779.5 | 919 | 2230 | 2239 | 199 | 35 | 176.5 | 0 | 127
6:00 | 3675 | 920 | 2174 | 1778 | 199 | 35 | 102 | 0 | 116
6:30 | 3658 | 919.5 | 2079.5 | 1718.5 | 199.5 | 35 | 94 | 0 | 113 |  |  |  |  | Coal
7:00 | 3641 | 919 | 1985 | 1659 | 200 | 35 | 86 | 0 | 110
7:30 | 3676 | 919 | 2006.5 | 1625.5 | 200 | 35 | 86 | 0 | 106 |  |  |  | Oil |  |  |  | ,
8:00 | 3711 | 919 | 2028 | 1592 | 200 | 35 | 86 | 0 | 102
8:30 | 3783.5 | 919.5 | 2065.5 | 1761 | 199.5 | 35 | 76 | 0 | 99
9:00 | 3856 | 920 | 2103 | 1930 | 199 | 35 | 66 | 0 | 96
9:30 | 3779 | 920.5 | 2057 | 2236 | 199 | 35.5 | 80.5 | 0 | 99
10:00 | 3702 | 921 | 2011 | 2542 | 199 | 36 | 95 | 0 | 102
10:30 | 3694 | 920.5 | 2105.5 | 2582.5 | 199 | 35.5 | 119 | 0 | 111
11:00 | 3686 | 920 | 2200 | 2623 | 199 | 35 | 143 | 0 | 120
11:30 | 3746.5 | 919.5 | 2219 | 2795.5 | 199 | 35 | 143 | 0 | 123
12:00 | 3807 | 919 | 2238 | 2968 | 199 | 35 | 143 | 0 | 126
12:30 | 3816.5 | 919.5 | 2215.5 | 2993.5 | 199 | 34.5 | 143 | 0 | 134
13:00 | 3826 | 920 | 2193 | 3019 | 199 | 34 | 143 | 0 | 142
13:30 | 3826 | 920 | 2193 | 3019 | 199 | 34 | 143 | 0 | 142
14:00 | 3826 | 920 | 2193 | 3019 | 199 | 34 | 143 | 0 | 142
14:30 | 4002 | 919.5 | 2194 | 2942.5 | 199 | 34 | 142.5 | 0 | 126
15:00 | 4178 | 919 | 2195 | 2866 | 199 | 34 | 142 | 0 | 110
15:30 | 4179 | 919.5 | 2196 | 2976 | 199 | 34.5 | 169 | 0 | 122
16:00 | 4180 | 920 | 2197 | 3086 | 199 | 35 | 196 | 0 | 134
16:30 | 4085.5 | 920 | 1986.5 | 3021.5 | 199 | 35.5 | 205 | 0 | 134
17:00 | 3991 | 920 | 1776 | 2957 | 199 | 36 | 214 | 0 | 134
17:30 | 3998 | 920.5 | 1731.5 | 2831.5 | 199 | 36 | 245 | 0 | 129
18:00 | 4005 | 921 | 1687 | 2706 | 199 | 36 | 276 | 0 | 124
18:30 | 4048.5 | 920.5 | 1818 | 2853.5 | 199 | 36 | 498 | 0 | 133
19:00 | 4092 | 920 | 1949 | 3001 | 199 | 36 | 720 | 0 | 142
19:30 | 4119 | 920 | 2155 | 3696 | 199 | 37 | 770 | 0 | 128
20:00 | 4017 | 919 | 2126 | 3693 | 199 | 37 | 769 | 0 | 128
20:30 | 4101.5 | 919.5 | 2140.5 | 3677.5 | 199 | 37 | 754 | 0 | 131
21:00 | 4186 | 920 | 2155 | 3662 | 199 | 37 | 739 | 0 | 134
21:30 | 4203 | 920 | 2166 | 3665 | 197 | 37.5 | 717 | 0 | 128
22:00 | 4220 | 920 | 2177 | 3668 | 195 | 38 | 695 | 0 | 122
22:30 | 4213 | 919.5 | 2179 | 3650 | 194.5 | 38 | 687.5 | 0 | 123
23:00 | 4206 | 919 | 2181 | 3632 | 194 | 38 | 680 | 0 | 124
23:30 | 4206.5 | 919.5 | 2163.5 | 3606 | 194 | 37 | 670 | 0 | 130 | Max Temp. in Dhaka |  | 35.1° C
24:00 | 4207 | 920 | 2146 | 3580 | 194 | 36 | 660 | 0 | 136
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-06-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 34 | 35 | 34 | 34 | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 35 | 34 | 34 | 34 | 35 | 36 | 36 |  | 36 | 37 | 37 | 37 | 38 | 38 | 36 | 848000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 14 |  | 25 | 25 | 25 | 25 | 25 | 0 | 14 | 459095
| Teknaf Solartech 20MW |  |  |  |  | 0 | 0.6 | 5.6 | 4.92 | 10.65 | 16.47 | 19.24 | 3.48 | 20 | 19 | 0 | 2 | 1.4 | 0.4 |  | 0 | [6 empty] | 102735
6 | Sikalbaha 225MW (Gas) | 208 | 204 | 204 | 205 | 204 | 205 | 216 | 217 | 204 | 206 | 205 | 206 | 205 | 206 | 219 | 206 | 206 | 204 |  | 205 | 204 | 205 | 211 | 212 | 214 | 203 | 4921548
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 133 | 132 | 130 | 130 | 130 | 130 | 135 | 139 | 130 | 130 | 130 | 130 | 130 | 130 | 142 | 140 | 130 | 130 |  | 130 | 130 | 130 | 130 | 133 | 130 | 140 | 3226500
10 | Sikalbaha GT 150MW (Oil) | [26 empty] | 0
| Dohazari Peaking | 51 | 51 | 51 | 17 | 0 | [11 empty] | 0 | 17 |  | 83 | 85 | 85 | 68 | 68 | 68 | 68 | 621171
12 | Hathazari peaking | 84 | 50 | 50 | 0 | [13 empty] | 0 |  | 56 | 82 | 84 | 84 | 84 | 84 | 84 | 646696
| Baraka Sikalbaha PL | 35 | 35 | 35 | 35 | 35 | 33 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 521050
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 50 | 50 | 50 | 50 | 0 | 0 |  | 138504
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP |  |  |  | 0 | 33 | 33 | 34 | 0 | 13 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 33 | 34 | 34 | 33 | 34 | 34 | 34 | 621418
18 | Summit Gazipur -2 | 145 | 195 | 145 | 145 | 0 |  |  |  | 35 | 107 | 111 | 250 | 300 | 300 | 208 | 208 | 250 | 250 |  | 262 | 300 | 292 | 300 | 300 | 300 | 285 | 4586616
19 | Ashuganj 195MW Modular | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 150 | 128 | 128 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 3546181
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1661000
21 | Ghorasal Repowered CCPP Unit-3 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 140 | 139 | 139 | 140 | 139 | 138 | 139 | 139 | 139 | 139 | 139 |  | 139 | 139 | 139 | 138 | 139 | 139 | 139 | 3486800
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4551750
24
25 | Ghorasal 365 MW CCPP Unit-7 | [16 empty] | 0 | 50 |  | 50 | 50 | 50 | 150 | 150 | 150 | 150 | 627800
26
28 | Ashuganj ST: Unit- 3 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 100 | 100 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2975686
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK
33 | Ashuganj CCPP 225 MW | 217 | 182 | 182 | 182 | 181 | 183 | 203 | 204 | 182 | 185 | 184 | 184 | 183 | 183 | 185 | 183 | 188 | 182 |  | 184 | 182 | 181 | 199 | 202 | 203 | 183 | 4607000
34 | Ashuganj CCPP(South) | 161 | 342 | 309 | 305 | 316 | 320 | 320 | 310 | 320 | 285 | 360 | 360 | 360 | 360 | 330 | 345 | 340 | 280 |  | 310 | 310 | 275 | 290 | 300 | 290 | 275 | 7527000
| Ashuganj CCPP(North) |  |  | 0 | 15 | 15 | 0 |  |  | 20 | 20 | 35 | 120 | 150 | 220 | 300 | 300 | 300 | 290 |  | 300 | 310 | 310 | 330 | 335 | 325 | 310 | 7527000
35 | Ashuganj (Precision) 55MW | 56 | 55 | 56 | 56 | 56 | 56 | 56 | 54 | 50 | 50 | 50 | 51 | 54 | 50 | 50 | 50 | 53 | 54 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 3849500
36 | Chandpur CCPP | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 140 | 140 | 140 | 142 | 142 | 100 | 95 | 96 |  | 96 | 96 | 96 | 97 | 100 | 100 | 100 | 2967040
37 | Tongi 80 MW GT PP
38 | Haripur GT PP
39 | Haripur 412 MW CCPP | 347 | 327 | 329 | 328 | 334 | 327 | 335 | 347 | 361 | 280 | 280 | 280 | 280 | 250 | 250 | 270 | 280 | 270 |  | 250 | 250 | 250 | 250 | 250 | 250 | 290 | 7282690
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7885875
41 | Haripur 360MW CCPP(HPL) | 351 | 352 | 354 | 351 | 353 | 325 | 285 | 284 | 285 | 263 | 344 | 304 | 304 | 302 | 304 | 300 | 304 | 279 |  | 305 | 304 | 303 | 304 | 306 | 305 | 305 | 7367000
42 | Mymensingh RPCL 210MW | 149 | 150 | 152 | 152 | 151 | 150 | 150 | 148 | 148 | 147 | 148 | 146 | 147 | 146 | 143 | 143 | 144 | 145 |  | 143 | 149 | 148 | 145 | 146 | 147 | 148 | 3464280
43 | Haripur 110 MW PP(NEPC)
44 | Fenchugonj CCPP-1 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1270000
45 | Fenchugonj CCPP-2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 47 | 47 | 20 | 29 | 51 | 51 | 69 | 69 | 20 | 42 |  | 42 | 57 | 57 | 57 | 57 | 57 | 57 | 1292120
46 | Shajibazar 330 MW | 96 | 95 | 95 | 96 | 95 | 0 |  | 10 | 11 | 12 | 60 | 151 | 151 | 154 | 157 | 154 | 153 | 152 |  | 154 | 151 | 151 | 155 | 154 | 156 | 154 | 2350000
47 | Shahjibazar GT: Unit- 8, 9 | 61 | 63 | 53 | 62 | 59 | 63 | 62 | 61 | 61 | 61 | 49 | 61 | 49 | 60 | 60 | 37 | 31 | 32 |  | 32 | 33 | 20 | 32 | 32 | 32 | 33 | 1173312
48 | Shahjibazar 86MW | 82 | 82 | 82 | 82 | 82 | 82 | 40 | 40 | 83 | 81 | 82 | 81 | 80 | 50 | 78 | 80 | 10 | 10 |  | 55 | 79 | 79 | 81 | 80 | 80 | 80 | 1649280
49 | Shahjibazar (EPL) 50MW | 46 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 45 | 45 | 44 | 10 | 10 |  | 10 | 44 | 44 | 45 | 46 | 46 | 46 | 975240
50 | Sylhet GT 150 MW | 108 | 109 | 108 | 110 | 109 | 108 | 120 | 123 | 110 | 110 | 74 | 75 | 110 | 109 | 124 | 110 | 110 | 110 |  | 122 | 110 | 109 | 122 | 119 | 118 | 121 | 2774970
51 | Sylhet GT 20 MW | [16 empty] | 0 | 17 |  | 17 | 18 | 17 | 18 | 18 | 16 | 15 | 65000
52 | Sylhet (EPL) 50MW | 48 | 48 | 48 | 48 | 48 | 46 | 22 | 45 | 46 | 44 | 44 | 42 | 44 | 45 | 42 | 42 | 13 | 12 |  | 44 | 48 | 47 | 48 | 48 | 48 | 47 | 967600
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250740
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 218880
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 48 | 50 | 22 | 22 | 45 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 11 | 13 |  | 15 | 46 | 50 | 50 | 50 | 50 | 50 | 1038000
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 16 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 503784
57 | Summit Bibiana- 2 | 310 | 290 | 300 | 290 | 310 | 290 | 310 | 310 | 305 | 290 | 280 | 290 | 280 | 270 | 315 | 310 | 270 | 300 |  | 290 | 310 | 270 | 320 | 325 | 325 | 300 | 7532250
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 17 |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 750040
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 450720
60 | Barabkunda (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 16 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 19 | 18 | 19 | 435552
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 12 | 12 | 16 | 16 | 16 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 433116
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 0 |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 428076
63 | Tripura | 146 | 144 | 140 | 140 | 138 | 116 | 110 | 102 | 96 | 102 | 120 | 126 | 142 | 150 | 110 | 134 | 134 | 124 |  | 142 | 128 | 128 | 134 | 122 | 124 | 136 | 3823680
64 | Malancha, Ctg. EPZ (United) | 36 | 37 | 37 | 38 | 40 | 40 | 36 | 6 | 9 | 2 | 2 | 2 | 6 | 4 | 4 | 3 | 6 | 2 |  | 9 | 2 | 11 | 26 | 33 | 38 | 33 | 446880
65 | Feni (Doreen) 22MW | 21 | 21 | 22 | 22 | 22 | 0 | 13 | 14 | 19 | 18 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 439992
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 5 | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 0 |  | 5 | 150840
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803800
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 11 | 12 | 12 | 7 | 20 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 408770
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 |  | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 708660
71 | Maona 33 MW (Summit) | 33 | 33 | 33 | 33 | 0 | 4 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 714700
72 | Rupganj 33 MW (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 797000
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 106 | 106 | 106 | 106 | 106 | 107 | 104 | 101 | 101 | 101 | 106 | 102 | 102 | 102 | 22 | 22 |  | 50 | 95 | 102 | 72 | 72 | 73 | 73 | 2125409
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 26 | 16 | 7 | 0 |  |  |  | 7 | 50 | 58 | 72 | 72 | 70 | 40 | 50 | 95 | 45 |  | 8 | 40 | 72 | 100 | 100 | 100 | 100 | 1231680
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 8 | 8 | 10 | 41 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 1073388
79 | Kodda 150MW PP | 140 | 140 | 140 | 98 | 95 | 32 | 16 | 16 | 16 | 48 | 96 | 96 | 96 | 96 | 96 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 142 | 2446560
80 | Jamalpur 95MW | 84 | 84 | 84 | 84 | 84 | 48 | 8 | 8 | 43 | 87 | 87 | 86 | 86 | 86 | 85 | 85 | 85 | 85 |  | 85 | 84 | 84 | 84 | 84 | 84 | 84 | 1860480
81 | Lakdhanvi 52 MW | 52 | 52 | 52 | 52 | 52 | 25 | 8 | 8 | 25 | 25 | 30 | 52 | 52 | 52 | 52 | 52 | 16 | 16 |  | 16 | 52 | 48 | 52 | 52 | 52 | 52 | 993115
| Gazipur 100 MW | 105 | 105 | 105 | 105 | 105 | 105 | 104 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2488800
| Kaptai Solar |  |  |  |  | 0 | 0.2 | 1.6 | 3.12 | 3.38 | 5.15 | 1.85 | 5.1 | 2.02 | 0 | 0.9 | 3.5 | 0.7 | 0.25 |  | 0 | [6 empty] | 29520
82 | Madanganj 102 PP(Summit) | 50 | 40 | 20 | 0 | [11 empty] | 0 | 10 | 15 |  | 15 | 70 | 70 | 96 | 96 | 96 | 70 | 648912
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 46 | 20 | 20 | 0 |  |  |  | 0 | 12 | 50 | 70 | 78 | 100 | 60 | 60 | 86 | 100 | 100 |  | 100 | 100 | 100 | 20 | 20 | 20 | 20 | 1257635
86 | Meghnaghat CCPP(Summit) | 260 | 255 | 240 | 278 | 258 | 271 | 290 | 298 | 255 | 278 | 271 | 297 | 265 | 291 | 273 | 253 | 274 | 255 |  | 273 | 273 | 250 | 290 | 290 | 287 | 275 | 6672175
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 70 | 65 | 35 | 0 |  | 0 | 2 | 44 | 68 | 90 | 90 | 84 | 87 | 90 | 32 | 7 |  | 9 | 80 | 68 | 87 | 92 | 92 | 93 | 1484160
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 69 | 66 | 65 | 65 | 64 | 64 | 65 |  | 66 | 66 | 66 | 40 | 40 | 40 | 40 | 1354752
90 | Ashuganj (United) 53MW
91 | Juldah (Acorn) | 75 | 88 | 88 | 88 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 10 |  | 13 | 60 | 60 | 60 | 60 | 60 | 60 | 886200
92 | Fenchuganj (EPL) 44MW | 46 | 46 | 46 | 46 | 46 | 46 | 20 | 20 | 38 | 46 | 43 | 43 | 43 | 46 | 42 | 43 | 10 | 10 |  | 18 | 49 | 49 | 49 | 49 | 49 | 49 | 1004256
93 | Ashuganj (Midland) 51MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 |  | 10 | 35 | 23 | 35 | 35 | 35 | 35 | 731092
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 72 | 50 | 7 | 0 |  | 7 | 32 | 32 | 50 | 92 | 92 | 92 | 101 | 100 | 16 | 16 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1599552
95 | Patenga 50MW | 43 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 38 | 32 | 32 | 34 | 38 | 39 | 39 | 42 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1032960
96 | Chattogram ECPV 108 MW | 96 | 96 | 96 | 96 | 96 | 10 | 12 | 12 | 31 | 83 | 31 | 31 | 31 | 31 | 31 | 54 | 90 | 88 |  | 84 | 84 | 84 | 85 | 90 | 90 | 90 | 1584960
97 | Katpotti 52 MW PP (Sinha) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 43 | 48 | 48 | 19 | 23 | 47 | 47 | 47 |  | 18 | 18 | 42 | 48 | 47 | 47 | 47 | 1056720
98 | Bosila 108MW PP(CLC) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 35 | 35 | 34 | 34 | 34 | 34 | 34 | 34 |  | 35 | 35 | 35 | 35 | 36 | 35 | 36 | 1205760
99 | Madanganj-55 MW PP(Summit) | 55 | 30 | 30 | 15 | 0 | [10 empty] | 0 | 15 | 15 |  | 19 | 55 | 55 | 55 | 55 | 55 | 55 | 501078
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 18 | 18 | 18 | 37 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1155809
101 | Kushiara 163 MW CCPP GT | [10 empty] | 10 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1385206
102 | Sarishabari (Solar) |  |  |  |  | 0 | 0.3 | 0.4 | 1 | 1.6 | 1.1 | 2.1 | 2.4 | 0.8 | 1.4 | 1.6 | 1.2 | 0.3 | 0.2 |  | 0 | [6 empty] | 14300
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 30 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1154520
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | [13 empty] | 102 | 102 | 102 | 102 | 103 |  | 103 | 103 | 103 | 20 |  |  |  | 711042
106 | United Mymensingh PPL | 194 | 194 | 194 | 194 | 194 | 36 | 16 | 7 | 7 | 19 | 79 | 100 | 100 | 100 | 100 | 120 | 140 | 140 |  | 140 | 182 | 170 | 184 | 175 | 175 | 175 | 3069600
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 149 | 149 | 149 | 110 | 105 | 0 |  |  | 17 | 100 | 132 | 149 | 149 | 149 | 149 | 149 | 92 | 70 |  | 70 | 149 | 149 | 149 | 149 | 149 | 149 | 2662560
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 90 | 100 | 100 | 100 | 90 | 90 | 90 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2261760
116 | Chandpur Desh 200MW | 180 | 178 | 177 | 177 | 178 | 100 | 90 | 52 | 120 | 178 | 179 | 177 | 177 | 140 | 140 | 162 | 177 | 200 |  | 200 | 200 | 188 | 177 | 177 | 177 | 178 | 3988320
117 | Midland 150MW | 150 | 150 | 150 | 150 | 150 | 80 | 80 | 84 | 146 | 145 | 140 | 140 | 140 | 100 | 100 | 108 | 130 | 80 |  | 95 | 150 | 147 | 145 | 135 | 135 | 135 | 3069450
118 | Bibiyana-3 285 MW | 293 | 294 | 296 | 294 | 296 | 260 | 200 | 249 | 299 | 297 | 200 | 249 | 150 | 150 | 250 | 292 | 201 | 200 |  | 250 | 249 | 205 | 204 | 201 | 201 | 200 | 5637000
| United Jamalpur PPL | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 85 | 85 | 85 | 85 | 95 | 95 |  | 94 | 95 | 90 | 90 | 90 | 81 | 81 | 2055600
| Anwara United | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 240 | 241 | 240 | 177 | 178 | 178 | 178 | 180 | 230 | 247 | 231 |  | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 5499927
120 | Eastern Zone Total | 7932 | 7937 | 7765 | 7556 | 7220 | 6174.1 | 5925.6 | 5930.04 | 6415.63 | 6852.72 | 6964.19 | 7559.98 | 7534.82 | 7516.4 | 7606.5 | 7842.7 | 7351.4 | 7150.85 |  | 7737 | 8470 | 8328 | 8497 | 8435 | 8384 | 8326 | 187807195
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 16 | 16 | 16 | 19 | 66 | 99 | 104 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 99 | 2287680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 41 | 41 | 35 | 35 | 35 | 0 | [10 empty] | 0 | 20 |  | 37 | 41 | 41 | 40 | 40 | 33 | 33 | 401760
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 53 | 53 |  | 53 | 78 | 105 | 105 | 105 | 105 | 105 | 2194080
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 80 | 80 | 48 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 48 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1440960
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 95 | 95 | 97 | 96 | 95 | 97 | 96 | 97 | 95 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 62 | 22 |  | 89 | 95 | 96 | 95 | 95 | 95 | 93 | 2140423
| Bhola CCPP 194MW | 172 | 172 | 173 | 173 | 173 | 173 | 173 | 172 | 172 | 172 | 172 | 173 | 172 | 173 | 173 | 173 | 173 | 173 |  | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 4205243
140 | Bhola (Venture) 33MW | 37 | 34 | 33 | 36 | 36 | 29 | 25 | 16 | 16 | 10 | 26 | 26 | 28 | 28 | 20 | 27 | 27 | 23 |  | 28 | 22 | 26 | 30 | 38 | 37 | 35 | 651694
141 | Bangla Trak Noapara | 100 | 50 | 47 | 0 | [15 empty] | 9 | 100 | 100 | 99 | 99 | 99 | 99 | 762240
142 | Noapara (KZA) 40MW
143 | Gopalganj Peaking | 52 | 52 | 36 | 36 | 3 | 0 | [9 empty] | 10 | 28 | 43 |  | 78 | 72 | 68 | 59 | 65 | 60 | 60 | 608896
144 | Bheramara GT-1,2,3 | [19 empty] | 10 | 16 | 16 | 16 | 16 | 16 | 0 | 80100
145 | Madhumati Power Plant | 87 | 87 | 87 | 86 | 86 | 87 | 86 | 52 | 52 | 52 | 87 | 87 | 87 | 86 | 87 | 87 | 34 | 34 |  | 50 | 87 | 53 | 52 | 86 | 87 | 86 | 1799280
146 | Bheramara HVDC | 927 | 926 | 926 | 927 | 918 | 920 | 919 | 919 | 920 | 921 | 920 | 919 | 920 | 920 | 919 | 920 | 920 | 921 |  | 920 | 920 | 919 | 920 | 920 | 919 | 920 | 22091636
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 200 | 200 | 200 | 199 | 199 | 199 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 195 | 194 | 194 | 4857700
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 60 | 1360000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 50 | 50 | 0 | [15 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 432208
157 | Sirajgonj Unit-1 225MW (Gas) | 197 | 183 | 182 | 182 | 190 | 182 | 187 | 197 | 203 | 183 | 189 | 154 | 175 | 181 | 195 | 196 | 182 | 181 |  | 184 | 191 | 185 | 191 | 198 | 200 | 198 | 4777154
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 193 | 179 | 180 | 178 | 186 | 178 | 160 | 162 | 199 | 181 | 187 | 145 | 167 | 179 | 193 | 196 | 186 | 186 |  | 189 | 195 | 182 | 156 | 162 | 165 | 170 | 4469200
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 212 | 204 | 202 | 199 | 201 | 197 | 187 | 185 | 209 | 190 | 196 | 156 | 177 | 188 | 202 | 203 | 189 | 189 |  | 191 | 189 | 193 | 198 | 205 | 207 | 204 | 4917036
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 417 | 360 | 360 | 360 | 360 | 300 | 260 | 320 | 320 | 280 | 370 | 370 | 370 | 340 | 380 | 405 | 350 | 300 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8372000
161 | Bera Peaking | [16 empty] | 0 | 10 |  | 31 | 33 | 33 | 32 | 32 | 33 | 33 | 194808
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 19 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 505920
163 | Bogra (EPL) | 14 | 14 | 14 | 15 | 14 | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 13 | 14 | 15 | 14 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 344268
164 | Ullapara (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 214866
165 | Amnura 50MW | 40 | 40 | 40 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 25 | 40 | 40 | 40 | 40 | 40 | 40 | 551950
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 24 | 0 |  |  |  | 43 | 43 | 32 | 43 | 34 | 34 | 34 | 34 | 8 |  | 8 | 16 | 43 | 43 | 43 | 43 | 43 | 674996
167 | Katakhali Peaking | 37 | 0 | [15 empty] | 0 |  | 37 | 38 | 39 | 37 | 37 | 37 | 37 | 255200
168 | Santahar Peaking | 28 | 28 | 28 | 28 | 28 | 0 | [11 empty] | 0 |  | 25 | 35 | 35 | 35 | 34 | 34 | 34 | 334960
169 | Rajlanka 52 MW | 51 | 51 | 51 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 26 | 41 | 41 | 41 | 50 | 49 | 8 | 8 |  | 27 | 50 | 50 | 51 | 52 | 52 | 52 | 821760
170 | Chapainawabganj-100 MW | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 70 | 50 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 46 | 46 |  | 90 | 95 | 95 | 95 | 95 | 91 | 84 | 1544092
171 | Paramount Baghabari
172 | Confidence Bogura-2 (CPBL) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2603520
173 | Rangpur GT | 17 | 17 | 0 | [16 empty] | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 126000
175 | Saidpur GT | 18 | 18 | 0 | [16 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 136000
176 | Confidence Rangpur | 32 | 32 | 32 | 38 | 38 | 23 | 4 | 7 | 12 | 8 | 12 | 20 | 8 | 3 | 9 | 3 | 5 | 5 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 299520
177
178
178 | Western Zone Total | 3681 | 3497 | 3407 | 3268 | 3191 | 2826 | 2717 | 2752 | 2805 | 2778 | 2985 | 2886 | 2964 | 2950 | 3039 | 3111 | 2878 | 2804 | 0 | 3322 | 3554 | 3560 | 3535 | 3600 | 3590 | 3553 | 76457150