## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-12-05 | Sunday
|  |  | Date (day): | 2021-12-05 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11580.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12926 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-12-04 | 2021-12-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 67 | 400 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 212 | 300 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 140 | 140 | 140 | 165 |  | FGMO & GT-2 S/D due to gas shortage.
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 25 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 24 | 24 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 18 | 18 | 18
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 95 | 60 | 95 | 115 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 25 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 160 | 260 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 25 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 27 | 25 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 52 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 5 | 0 | 30 | 0
|  | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 26 | 0 | 0 | 0 |  |  | On test
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 1665 | 2408 | 3037 | 3424 | 943 | 1145
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 72 | 73 | 80 | 80 |  | 150 | Low Water Level & Unit 2 & 4,5 U/M.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 51 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 80 |  | 22 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 3 | 5 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 280 | 300 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 51 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 60 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 50 | 105 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 662 | 1061 | 1331 | 1341 | 0 | 1023
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 130 | 130 | 130 | 130
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 300 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 187 | 180 | 180 | 180
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 33 | 125 | 123 | 132 |  | 18 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 15 | 34 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 93 | 103 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 30 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 7 | 9 | 9 | 9
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 58 | 116 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 28 | 0 | 0 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1027 | 1310 | 1687 | 1922 | 264 | 819
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 158 | 139 | 160 | 160 | 42 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 32 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 24 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 299 | 330 | 570.6 | 519 | 42 | 8
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 42 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 130 | 130 |  | 200 | Under maint.
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 50 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 33 |  | 33 | GT-9 Under maint.
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 77 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 80 | 80 | 80 | 80
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 198 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 20 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 383 | 383
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1138 | 1136 | 1272 | 1276 | 0 | 1061
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 656 | 704 | 653 | 701
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 673 | 809 | 808 | 1296 | 0 | 503
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 26 | 20 | 23 |  | 10 | Engine problem
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 60 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 52 | 94 | 70 | 72 | 23 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 470 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 109 | 110 | 110 | 110 |  | 110 | GT-1 Under maint.
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 560 | 760 | 995 | 1150 | 23 | 249
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 27 | 27 |  | 23 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 0 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 199 | 181 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 201 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 394 | 358 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 20 | 35 |  | 15 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 24 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 95 | 100
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 50 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 944 | 1277 | 1539 | 1663 | 310 | 89
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 79 | 80 | 82
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 133 | 134 | 140 | 140 | 134 |  | Coal shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 49 | 105 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 267 | 318 | 341 | 335 | 134 | 125
|  | Total |  |  |  |  | 22031 | 20934 | 7235 | 9409 | 11580.6 | 12926 | 1716 | 5022
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6925.1153 | 9006 | 11084.5875 | 12372.3622
| A. |  | 2021-12-04 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 9409 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5694 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9409 | MW
| 3 | Day peak Generation : |  |  | 7235 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9006 | MW
| 4 | Evening peak Generation : |  |  | 9409 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 178.0462 | MKWHr | By Solar | 0.29013 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 103.6823 | MKWHr |  | By Oil: | 42.6779 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.6993 | MKWHr |  | By Hydro: | 1.6317 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1716 | MW | Dhaka | 3413 | 3413 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 5022 | MW | Chittagong | 1059 | 1059 |  | 0 |  | 18:00 |  | 106
|  |  |  | Total = |  |  | 6738 | MW | Khulna | 1028 | 1028 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 848.05 | MMCFD |  |  | Rajshahi | 873 | 873 |  | 0 |  | 19:00 |  | 103
| 8 | Fuel Cost : | i) Gas : | Taka | 109977577.13 | ii) Oil : | Taka | 297246908.78 | Comilla | 752 | 752 |  | 0 |  | 19:30 |  | 102
|  |  | iii) Coal : |  | 71062820.35 | Total | Taka | 478287306.26 | Mymensingh | 692 | 692 |  | 0 |  | 20:00 |  | 100
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.005 | MKWHr. | Sylhet | 335 | 335 |  | 0 |  | 21:00 |  | 98
|  | ii) During Peak Demand : |  |  | 221 | MW (E to W) at | 19:00 | hrs | Barisal | 253 | 253 |  | 0 |  | 22:00 |  | 94
|  | iii) Maximum : |  |  | 20 | MW at | 8:00 | hrs | Rangpur | 601 | 601 |  | 0 |  | 23:00 |  | 85
| 10 | Maximum Temperature in Dhaka was |  |  |  | 26.7° C |  |  | Total | 9006 | 9006 |  | 0
| B. |  | 2021-12-05 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 22.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12926 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8100 | MW
| 4 | Reserve(Generation end) |  |  |  | 3326 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 181.6605 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6053 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.0124 | MKWHr. | ii) HVDC Flow at Peak Time |  | 704 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0525 | MKWHr. | iii) Maximum HVDC Flow : |  | 705 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.42 |  | (b) Today: | 100.28 |  | (c) Rule Curve: |  | 105.64
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-12-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 384 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 13 | 25 | 28 | 25 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 21 | 37 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 18 | 22 | 8 | 33 | 9 | 73 | 203 | 0 | 20 | 0 | 42 | 30 | 50 | 0 | 163 | 0 | 35 | 80 | 0 | 192 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 50 | 0 | 60 | 0 | 0 | 0 | 210 | 54 | 0 | 0 | 59 | 0 | 400 | 55 | 0 | 162 | 17 | 70 | 17 | 0 | 0 | 0 |  | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 135 | 0 | 0 | 0 | 0 | 195 | 0 | 63 | 0 | 214 | 0 | 350 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 112 | 0 | 0 | 0 |  | 4288 | 2053 | 6341 | 2775 | 384 | 1600 | 0 | 841 | 588 | 80 | 0 | 0 | 73 | 0 | 0 | 100.44
2:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 387 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 13 | 25 | 28 | 25 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 37 | 0 | 0 | 130 | 0 | 315 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 9 | 68 | 206 | 0 | 20 | 0 | 42 | 30 | 50 | 0 | 130 | 0 | 35 | 80 | 0 | 191 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 50 | 0 | 0 | 0 | 210 | 54 | 0 | 0 | 57 | 0 | 400 | 17 | 0 | 162 | 17 | 70 | 17 | 0 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 135 | 0 | 0 | 0 | 0 | 194 | 0 | 82 | 0 | 207 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 112 | 0 | 0 | 0 |  | 4199 | 1977 | 6176 | 2787 | 374 | 1584 | 0 | 735 | 548 | 80 | 0 | 0 | 68 | 0 | 0 | 100.44
3:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 390 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 25 | 28 | 25 | 33 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 40 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 9 | 68 | 214 | 0 | 20 | 0 | 43 | 30 | 50 | 0 | 130 | 0 | 35 | 80 | 0 | 191 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 30 | 0 | 0 | 0 | 210 | 54 | 0 | 0 | 26 | 0 | 400 | 17 | 0 | 90 | 17 | 70 | 13 | 0 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 135 | 0 | 0 | 0 | 0 | 192 | 0 | 82 | 0 | 207 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 112 | 0 | 0 | 0 |  | 3972 | 1951 | 5923 | 2782 | 374 | 1583 | 0 | 509 | 528 | 79 | 0 | 0 | 68 | 0 | 0 | 100.43
4:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 402 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 25 | 25 | 25 | 33 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 40 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 9 | 65 | 215 | 0 | 20 | 0 | 43 | 30 | 50 | 0 | 130 | 0 | 35 | 80 | 0 | 191 | 18 | 0 | 10 | 0 | 22 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 175 | 54 | 0 | 0 | 26 | 0 | 400 | 0 | 0 | 35 | 17 | 70 | 17 | 0 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 135 | 0 | 0 | 0 | 0 | 193 | 0 | 58 | 0 | 204 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 112 | 0 | 0 | 0 |  | 3864 | 1916 | 5780 | 2789 | 374 | 1560 | 0 | 396 | 518 | 78 | 0 | 0 | 65 | 0 | 0 | 100.43
5:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 406 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 25 | 25 | 25 | 33 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 40 | 0 | 0 | 130 | 0 | 310 | 0 | 182 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 9 | 64 | 215 | 0 | 20 | 0 | 43 | 30 | 50 | 0 | 130 | 0 | 35 | 80 | 0 | 191 | 18 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 100 | 54 | 0 | 0 | 26 | 0 | 400 | 0 | 0 | 35 | 0 | 70 | 17 | 0 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 135 | 0 | 0 | 0 | 0 | 195 | 0 | 53 | 0 | 204 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 111 | 0 | 0 | 0 |  | 3784 | 1910 | 5694 | 2803 | 374 | 1555 | 0 | 304 | 517 | 77 | 0 | 0 | 64 | 0 | 0 | 100.42
6:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 320 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 25 | 24 | 25 | 33 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 40 | 0 | 0 | 130 | 0 | 320 | 0 | 182 | 0 | 29 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 9 | 64 | 215 | 0 | 20 | 0 | 43 | 30 | 50 | 0 | 163 | 0 | 35 | 80 | 0 | 191 | 18 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 110 | 54 | 8 | 0 | 31 | 0 | 400 | 6 | 0 | 38 | 13 | 70 | 17 | 0 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 135 | 0 | 0 | 0 | 0 | 197 | 0 | 53 | 0 | 204 | 0 | 400 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 320 | 111 | 0 | 0 | 0 |  | 3777 | 1992 | 5769 | 2728 | 374 | 1635 | 0 | 354 | 537 | 77 | 0 | 0 | 64 | 0 | 0 | 100.42
7:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 332 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 52 | 13 | 25 | 26 | 25 | 33 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 21 | 0 | 0 | 130 | 0 | 310 | 0 | 182 | 0 | 29 | 55 | 0 | 43 | 0 | 0 | 4 | 22 | 8 | 33 | 9 | 63 | 218 | 0 | 20 | 0 | 43 | 30 | 50 | 0 | 110 | 0 | 35 | 77 | 0 | 171 | 18 | 0 | 10 | 0 | 15 | 8 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 195 | 54 | 61 | 0 | 57 | 0 | 400 | 46 | 1 | 130 | 62 | 70 | 17 | 0 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 135 | 0 | 0 | 0 | 0 | 198 | 0 | 53 | 0 | 201 | 0 | 330 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 10 | 320 | 111 | 0 | 0 | 1 |  | 4228 | 2009 | 6237 | 2706 | 374 | 1489 | 0 | 994 | 534 | 72 | 0 | 0 | 63 | 5 | 0 | 0
8:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 410 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 54 | 0 | 55 | 13 | 25 | 26 | 25 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 39 | 21 | 2 | 0 | 0 | 130 | 0 | 365 | 0 | 182 | 0 | 29 | 55 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 9 | 70 | 218 | 0 | 20 | 0 | 43 | 30 | 50 | 0 | 163 | 0 | 35 | 78 | 0 | 211 | 18 | 0 | 10 | 0 | 15 | 5 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 0 | 18 | 0 | 90 | 0 | 0 | 1 | 260 | 54 | 51 | 0 | 59 | 0 | 400 | 78 | 4 | 152 | 50 | 70 | 17 | 2 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 18 | 0 | 11 | 81 | 0 | 133 | 0 | 0 | 0 | 0 | 206 | 0 | 52 | 0 | 200 | 0 | 305 | 18 | 0 | 111 | 0 | 49 | 0 | 1 | 35 | 330 | 111 | 0 | 0 | 0 |  | 4609 | 2126 | 6735 | 2877 | 374 | 1493 | 0 | 1290 | 544 | 70 | 0 | 0 | 70 | 17 | 0 | 100.41
9:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 401 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 54 | 0 | 55 | 13 | 25 | 26 | 25 | 25 | 0 | 0 | 69 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 41 | 21 | 2 | 0 | 0 | 130 | 0 | 365 | 0 | 182 | 0 | 29 | 55 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 33 | 9 | 81 | 216 | 0 | 17 | 1 | 42 | 30 | 47 | 0 | 130 | 0 | 30 | 77 | 0 | 217 | 18 | 0 | 10 | 0 | 15 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 75 | 0 | 115 | 0 | 0 | 2 | 280 | 54 | 51 | 0 | 59 | 0 | 400 | 94 | 13 | 162 | 50 | 70 | 17 | 7 | 0 | 0 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 132 | 0 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 194 | 0 | 284 | 53 | 0 | 113 | 0 | 49 | 0 | 3 | 35 | 340 | 111 | 0 | 0 | 1 |  | 4774 | 2165 | 6939 | 2824 | 374 | 1441 | 0 | 1559 | 552 | 69 | 0 | 0 | 81 | 39 | 0 | 100.4
10:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 398 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 54 | 0 | 55 | 15 | 25 | 26 | 25 | 25 | 0 | 0 | 77 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 48 | 18 | 2 | 0 | 0 | 130 | 0 | 350 | 0 | 182 | 0 | 29 | 55 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 33 | 7 | 87 | 195 | 0 | 17 | 1 | 42 | 30 | 44 | 0 | 130 | 0 | 30 | 78 | 0 | 218 | 18 | 0 | 10 | 0 | 20 | 4 | 0 | 95 | 0 | 0 | 0 | 0 | 2 | 9 | 10 | 0 | 80 | 0 | 75 | 0 | 0 | 4 | 280 | 54 | 51 | 0 | 58 | 0 | 400 | 94 | 17 | 162 | 50 | 70 | 17 | 13 | 18 | 15 |  | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 133 | 0 | 0 | 0 | 0 | 175 | 0 | 53 | 0 | 192 | 0 | 335 | 53 | 0 | 50 | 0 | 49 | 0 | 4 | 35 | 300 | 111 | 0 | 0 | 1 |  | 4793 | 2082 | 6875 | 2782 | 374 | 1490 | 0 | 1470 | 513 | 77 | 0 | 0 | 87 | 49 | 0 | 100.4
11:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 25 | 0 | 0 | 0 | 54 | 17 | 55 | 15 | 25 | 25 | 25 | 25 | 12 | 0 | 79 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 18 | 2 | 0 | 0 | 130 | 0 | 280 | 0 | 177 | 0 | 29 | 20 | 0 | 43 | 0 | 0 | 9 | 19 | 5 | 33 | 7 | 90 | 172 | 0 | 17 | 1 | 43 | 30 | 50 | 0 | 130 | 0 | 30 | 77 | 0 | 218 | 18 | 0 | 10 | 0 | 20 | 4 | 0 | 95 | 0 | 0 | 0 | 48 | 30 | 8 | 50 | 0 | 30 | 0 | 75 | 0 | 0 | 2 | 280 | 54 | 51 | 0 | 59 | 0 | 400 | 94 | 17 | 162 | 50 | 70 | 17 | 8 | 27 | 40 |  | 485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 134 | 0 | 0 | 0 | 0 | 183 | 0 | 52 | 0 | 209 | 0 | 403 | 53 | 0 | 50 | 0 | 49 | 0 | 5 | 35 | 300 | 111 | 0 | 0 | 1 |  | 4437 | 2286 | 6723 | 2316 | 485 | 1521 | 48 | 1545 | 514 | 79 | 0 | 16 | 90 | 42 | 0 | 100.39
12:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 |  | 0 | 270 | 140 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 102 | 48 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 25 | 0 | 72 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 2 | 0 | 0 | 130 | 0 | 280 | 0 | 187 | 0 | 29 | 20 | 0 | 43 | 0 | 0 | 30 | 19 | 5 | 33 | 7 | 93 | 158 | 0 | 17 | 1 | 43 | 30 | 47 | 0 | 163 | 0 | 30 | 77 | 0 | 218 | 18 | 0 | 10 | 0 | 20 | 2 | 0 | 160 | 0 | 25 | 0 | 27 | 52 | 10 | 50 | 15 | 33 | 0 | 75 | 0 | 0 | 5 | 280 | 54 | 51 | 0 | 58 | 0 | 400 | 104 | 24 | 162 | 50 | 80 | 17 | 5 | 28 | 26 |  | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 133 | 0 | 0 | 0 | 0 | 199 | 0 | 52 | 0 | 208 | 0 | 394 | 17 | 0 | 50 | 0 | 49 | 0 | 5 | 35 | 320 | 109 | 0 | 0 | 1 |  | 4791 | 2444 | 7235 | 2329 | 656 | 1550 | 52 | 1797 | 533 | 72 | 0 | 48 | 93 | 51 | 0 | 100.39
13:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 |  | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 25 | 0 | 77 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 48 | 21 | 5 | 0 | 0 | 130 | 0 | 275 | 0 | 180 | 0 | 29 | 20 | 0 | 43 | 0 | 0 | 46 | 21 | 5 | 33 | 7 | 95 | 144 | 0 | 17 | 1 | 43 | 30 | 50 | 0 | 163 | 0 | 30 | 77 | 0 | 218 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 249 | 0 | 86 | 0 | 0 | 85 | 8 | 62 | 18 | 65 | 0 | 85 | 0 | 0 | 2 | 280 | 54 | 51 | 0 | 58 | 0 | 400 | 104 | 14 | 162 | 50 | 80 | 17 | 0 | 0 | 38 |  | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 82 | 0 | 131 | 0 | 0 | 0 | 0 | 206 | 0 | 52 | 0 | 208 | 0 | 393 | 17 | 0 | 50 | 0 | 49 | 0 | 5 | 35 | 330 | 110 | 0 | 0 | 0 |  | 5051 | 2466 | 7517 | 2318 | 657 | 1554 | 86 | 2021 | 543 | 77 | 0 | 98 | 95 | 30 | 0 | 100.38
14:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 |  | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 64 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 25 | 0 | 64 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 45 | 21 | 3 | 0 | 0 | 130 | 0 | 280 | 0 | 180 | 0 | 29 | 30 | 0 | 43 | 0 | 0 | 52 | 22 | 5 | 33 | 7 | 97 | 138 | 0 | 17 | 1 | 41 | 30 | 50 | 0 | 130 | 0 | 30 | 77 | 0 | 190 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 270 | 0 | 0 | 0 | 0 | 90 | 3 | 70 | 34 | 65 | 0 | 85 | 0 | 0 | 1 | 280 | 54 | 51 | 0 | 58 | 0 | 400 | 104 | 10 | 162 | 50 | 80 | 17 | 6 | 0 | 38 |  | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 134 | 0 | 0 | 0 | 0 | 178 | 0 | 52 | 0 | 191 | 0 | 350 | 17 | 0 | 50 | 0 | 49 | 0 | 4 | 35 | 330 | 110 | 0 | 0 | 0 |  | 4914 | 2377 | 7291 | 2243 | 656 | 1486 | 0 | 2074 | 544 | 64 | 0 | 64 | 97 | 25 | 0 | 100.48
15:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 31 |  | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 64 | 25 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 25 | 25 | 25 | 25 | 0 | 74 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 46 | 21 | 2 | 0 | 0 | 130 | 0 | 280 | 0 | 180 | 0 | 29 | 43 | 0 | 43 | 0 | 0 | 52 | 22 | 5 | 33 | 7 | 94 | 141 | 0 | 17 | 1 | 43 | 30 | 50 | 0 | 130 | 0 | 30 | 78 | 0 | 185 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 260 | 0 | 0 | 0 | 0 | 70 | 2 | 70 | 34 | 65 | 0 | 85 | 0 | 0 | 1 | 280 | 54 | 51 | 0 | 58 | 0 | 400 | 104 | 4 | 162 | 50 | 80 | 12 | 3 | 0 | 44 |  | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 130 | 0 | 0 | 0 | 0 | 167 | 0 | 52 | 0 | 164 | 0 | 388 | 17 | 0 | 50 | 0 | 49 | 0 | 3 | 35 | 310 | 110 | 0 | 0 | 0 |  | 4906 | 2352 | 7258 | 2205 | 657 | 1567 | 0 | 2019 | 520 | 74 | 0 | 64 | 94 | 14 | 0 | 100.48
16:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 31 |  | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 97 | 0 | 102 | 64 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 25 | 25 | 25 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 3 | 0 | 46 | 21 | 2 | 0 | 0 | 130 | 0 | 290 | 0 | 180 | 0 | 29 | 43 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 8 | 96 | 140 | 0 | 20 | 0 | 43 | 30 | 50 | 0 | 130 | 0 | 30 | 77 | 0 | 185 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 260 | 0 | 0 | 0 | 0 | 70 | 1 | 70 | 17 | 65 | 0 | 85 | 0 | 5 | 0 | 300 | 54 | 51 | 0 | 57 | 10 | 400 | 104 | 1 | 162 | 50 | 80 | 17 | 1 | 0 | 53 |  | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 135 | 0 | 0 | 0 | 0 | 168 | 0 | 53 | 0 | 163 | 0 | 357 | 17 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 300 | 110 | 0 | 0 | 0 |  | 5006 | 2284 | 7290 | 2323 | 656 | 1534 | 0 | 2014 | 515 | 30 | 0 | 64 | 96 | 5 | 0 | 100.48
17:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 6 | 28 |  | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 97 | 0 | 102 | 98 | 25 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 25 | 25 | 25 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 15 | 30 | 22 | 49 | 21 | 2 | 0 | 0 | 130 | 0 | 355 | 0 | 180 | 0 | 29 | 52 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 8 | 101 | 140 | 0 | 20 | 0 | 43 | 30 | 53 | 0 | 163 | 0 | 30 | 77 | 0 | 198 | 18 | 0 | 10 | 0 | 23 | 5 | 0 | 260 | 0 | 0 | 9 | 0 | 75 | 0 | 70 | 32 | 65 | 0 | 90 | 9 | 25 | 0 | 300 | 54 | 60 | 0 | 99 | 70 | 400 | 104 | 0 | 162 | 60 | 80 | 17 | 0 | 0 | 19 |  | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 63 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 9 | 22 | 0 | 11 | 80 | 0 | 133 | 0 | 0 | 0 | 0 | 192 | 0 | 52 | 0 | 185 | 0 | 411 | 30 | 0 | 35 | 0 | 80 | 0 | 0 | 70 | 330 | 110 | 0 | 0 | 0 |  | 5389 | 2517 | 7906 | 2453 | 657 | 1634 | 0 | 2345 | 543 | 30 | 0 | 124 | 101 | 0 | 0 | 100.47
18:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 36 | 66 |  | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 95 | 0 | 102 | 149 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 17 | 25 | 33 | 25 | 0 | 71 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 100 | 48 | 50 | 21 | 2 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 54 | 0 | 43 | 0 | 38 | 52 | 22 | 11 | 33 | 9 | 106 | 140 | 0 | 20 | 0 | 43 | 30 | 53 | 0 | 163 | 0 | 30 | 77 | 0 | 198 | 18 | 0 | 10 | 0 | 24 | 11 | 47 | 260 | 0 | 90 | 60 | 92 | 118 | 0 | 100 | 34 | 85 | 0 | 115 | 74 | 68 | 0 | 300 | 54 | 86 | 34 | 114 | 100 | 400 | 104 | 0 | 162 | 101 | 80 | 17 | 0 | 0 | 0 |  | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 59 | 26 | 0 | 0 | 0 | 0 | 43 | 0 | 72 | 0 | 34 | 0 | 52 | 35 | 22 | 0 | 11 | 78 | 0 | 133 | 0 | 0 | 0 | 0 | 200 | 0 | 93 | 10 | 210 | 0 | 318 | 95 | 0 | 90 | 0 | 105 | 0 | 0 | 90 | 440 | 110 | 0 | 0 | 0 |  | 6315 | 3036 | 9351 | 2466 | 705 | 1627 | 239 | 3093 | 651 | 71 | 0 | 393 | 106 | 0 | 0 | 100.47
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 67 | 212 |  | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 95 | 0 | 102 | 149 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 73 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 50 | 50 | 50 | 21 | 3 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 56 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 103 | 139 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 30 | 77 | 0 | 198 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 260 | 0 | 0 | 32 | 25 | 149 | 0 | 100 | 34 | 125 | 0 | 115 | 105 | 51 | 0 | 300 | 54 | 110 | 0 | 116 | 60 | 400 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 | 0 |  | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 0 | 43 | 0 | 98 | 0 | 50 | 0 | 52 | 35 | 22 | 0 | 11 | 79 | 0 | 134 | 0 | 0 | 0 | 0 | 181 | 0 | 94 | 0 | 201 | 0 | 358 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 470 | 110 | 0 | 0 | 0 |  | 6245 | 3164 | 9409 | 2482 | 704 | 1817 | 25 | 3130 | 683 | 73 | 0 | 392 | 103 | 0 | 0 | 100.46
19:30 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 193 | 293 |  | 0 | 270 | 140 | 0 | 0 | 15 | 0 | 0 | 95 | 0 | 102 | 149 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 73 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 30 | 50 | 21 | 3 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 56 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 102 | 141 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 30 | 77 | 0 | 198 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 260 | 0 | 0 | 32 | 0 | 149 | 0 | 100 | 17 | 125 | 0 | 115 | 17 | 17 | 0 | 300 | 54 | 110 | 0 | 116 | 10 | 400 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 | 0 |  | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 26 | 0 | 0 | 0 | 0 | 43 | 0 | 55 | 0 | 50 | 0 | 52 | 35 | 22 | 0 | 11 | 78 | 0 | 133 | 0 | 0 | 0 | 0 | 182 | 0 | 94 | 0 | 184 | 0 | 363 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 470 | 102 | 0 | 0 | 0 |  | 6122 | 3104 | 9226 | 2597 | 705 | 1895 | 0 | 2841 | 681 | 73 | 0 | 332 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 187 | 293 |  | 0 | 270 | 140 | 0 | 0 | 15 | 0 | 0 | 95 | 0 | 102 | 149 | 24 | 0 | 0 | 0 | 54 | 35 | 35 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 75 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 25 | 50 | 21 | 4 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 100 | 139 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 30 | 77 | 0 | 198 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 260 | 0 | 0 | 32 | 0 | 149 | 0 | 100 | 17 | 125 | 0 | 115 | 17 | 17 | 0 | 300 | 54 | 110 | 0 | 116 | 10 | 400 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 | 0 |  | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 50 | 0 | 52 | 0 | 22 | 0 | 11 | 78 | 0 | 134 | 0 | 0 | 0 | 0 | 182 | 0 | 94 | 0 | 185 | 0 | 356 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 470 | 110 | 0 | 0 | 0 |  | 6039 | 3012 | 9051 | 2589 | 705 | 1897 | 0 | 2816 | 682 | 75 | 0 | 187 | 100 | 0 | 0 | 100.46
21:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 298 | 342 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 102 | 100 | 25 | 0 | 0 | 0 | 54 | 17 | 55 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 77 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 3 | 98 | 141 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 30 | 77 | 0 | 198 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 145 | 0 | 0 | 0 | 0 | 120 | 0 | 100 | 17 | 130 | 0 | 115 | 0 | 17 | 0 | 300 | 54 | 110 | 0 | 116 | 0 | 400 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 | 0 |  | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 134 | 0 | 0 | 0 | 0 | 188 | 0 | 97 | 0 | 190 | 0 | 353 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 470 | 103 | 0 | 0 | 0 |  | 5896 | 2925 | 8821 | 2705 | 705 | 1941 | 0 | 2512 | 683 | 77 | 0 | 100 | 98 | 0 | 0 | 100.46
22:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 348 | 352 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 77 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 16 | 0 | 0 | 130 | 0 | 295 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 9 | 94 | 142 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 7 | 30 | 78 | 0 | 198 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 70 | 0 | 100 | 17 | 133 | 0 | 95 | 0 | 0 | 0 | 300 | 54 | 68 | 0 | 116 | 0 | 389 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 | 0 |  | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 79 | 0 | 133 | 0 | 0 | 0 | 0 | 179 | 0 | 88 | 0 | 189 | 0 | 359 | 70 | 0 | 70 | 0 | 75 | 0 | 0 | 70 | 450 | 100 | 0 | 0 | 0 |  | 5579 | 2707 | 8286 | 2744 | 705 | 1959 | 0 | 1981 | 662 | 77 | 0 | 64 | 94 | 0 | 0 | 100.34
23:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 378 | 352 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 20 | 0 | 0 | 130 | 0 | 275 | 0 | 180 | 0 | 29 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 33 | 9 | 85 | 145 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 130 | 91 | 30 | 78 | 0 | 199 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 93 | 0 | 75 | 0 | 0 | 0 | 300 | 54 | 34 | 0 | 116 | 0 | 400 | 55 | 0 | 162 | 69 | 80 | 17 | 0 | 0 | 0 |  | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 133 | 0 | 0 | 75 | 0 | 174 | 0 | 88 | 0 | 162 | 0 | 337 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 410 | 111 | 0 | 0 | 0 |  | 5221 | 2517 | 7738 | 2900 | 705 | 1922 | 0 | 1428 | 622 | 76 | 0 | 0 | 85 | 0 | 0 | 100.33
24:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 397 | 357 |  | 0 | 270 | 140 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 26 | 21 | 30 | 0 | 0 | 130 | 0 | 265 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 22 | 0 | 33 | 9 | 81 | 153 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 130 | 122 | 30 | 78 | 0 | 197 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 75 | 0 | 0 | 0 | 300 | 54 | 34 | 0 | 104 | 0 | 400 | 54 | 0 | 162 | 69 | 80 | 17 | 0 | 0 | 0 |  | 551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 77 | 0 | 135 | 0 | 0 | 0 | 0 | 178 | 0 | 87 | 0 | 172 | 0 | 302 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 390 | 107 | 0 | 0 | 0 |  | 5185 | 2241 | 7426 | 2873 | 551 | 1895 | 0 | 1348 | 602 | 76 | 0 | 0 | 81 | 0 | 0 | 100.33
KWH | 0 | 0 | 0 | 4536000 | 0 | 0 | 0 | 5804030 | 1880000 |  | 0 | 6510550 | 3490647 | 0 | 0 | 447150 | 0 | 0 | 868000 | 0 | 1115856 | 1044480 | 343346 | 0 | 0 | 0 | 1073880 | 496261 | 965531 | 364680 | 600000 | 612360 | 738900 | 752700 | 334560 | 0 | 1631672 | 0 | 0 | 0 | 216815 | 0 | 0 | 0 | 0 |  | 381120 | 0 | 76578 | 153240 | 148800 | 1027200 | 484512 | 365760 | 0 | 0 | 3115598 | 0 | 7587000 | 0 | 4365818 | 0 | 668952 | 1185600 | 0 | 1121812 | 0 | 93600 | 725006 | 479412 | 179640 | 816200 | 219410 | 2052480 | 4102080 | 0 | 420048 | 4250 | 1003000 | 690960 | 1214400 | 0 | 3690245 | 143000 | 760608 | 1870080 | 0 | 4802650 | 413000 | 0 | 252720 | 0 | 497880 | 191904 | 15744 | 2973272 | 0 | 201833 | 170400 | 176177 | 1133860 | 65475 | 1252800 | 294240 | 1517157 | 0 | 1936800 | 228000 | 217454 | 16350 | 6297818 | 1292307 | 1280470 | 18240 | 1766520 | 214080 | 9586700 | 1897920 | 107510 | 3489120 | 1371218 | 1802545 | 434880 | 58306 | 76800 | 251640 |  | 13012363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7168 | 0 | 1545000 | 446600 | 0 | 0 | 0 | 0 | 94411 | 0 | 203620 | 0 | 152802 | 0 | 534720 | 75584 | 510960 | 0 | 251400 | 1916945 | 0 | 3290200 | 0 | 0 | 80500 | 0 | 4727736 | 0 | 1576571 | 27840 | 4929591 | 0 | 8691491 | 860160 | 0 | 1469760 | 0 | 1077753 | 0 | 30982 | 1021920 | 9492200 | 2733027 | 0 | 0 | 7260 |  | 119277617 | 58768564 | 178046181 | 63775996 | 13012363 | 39906281 | 421594 | 40660876 | 14699345 | 1631672 | 0 | 1595441 | 2052480 | 290133 | 0
Fuel Cost | 0 | 0 | 0 | 6667920 | 0 | 0 | 0 | 5862070.3 | 1936400 |  | 0 | 7096499.5 | 3874618.17 | 0 | 0 | 3782889 | 0 | 0 | 1501640 | 0 | 10176606.72 | 10277683.2 | 3165650.12 | 0 | 0 | 0 | 7839324 | 3836097.53 | 9520135.66 | 273510 | 450000 | 0 | 0 | 0 | 3235195.2 | 0 | 440551.44 | 0 | 0 | 0 | 2014211.35 | 0 | 0 | 0 | 0 |  | 0 | 0 | 742806.6 | 1463442 | 1294560 | 8135424 | 610485.12 | 1086307.2 | 0 | 0 | 4579929.06 | 0 | 7587000 | 0 | 5631905.22 | 0 | 755915.76 | 1659840 | 0 | 1918298.52 | 0 | 945360 | 6923807.3 | 608853.24 | 134730 | 1428350 | 164557.5 | 15393600 | 4348204.8 | 0 | 533460.96 | 67745 | 1644920 | 1105536 | 2161632 | 0 | 4206879.3 | 148720 | 1498397.76 | 3571852.8 | 0 | 8308584.5 | 904470 | 0 | 515548.8 | 0 | 373410 | 145847.04 | 267805.44 | 22477936.32 | 0 | 3374647.76 | 886080 | 2945679.44 | 11157182.4 | 765402.75 | 10210320 | 3192504 | 10695956.85 | 0 | 17663616 | 2154600 | 1894024.34 | 0 | 47611504.08 | 11255993.97 | 11255331.3 | 182035.2 | 15139076.4 | 1425772.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 74951210.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75120.64 | 0 | 1745850 | 692230 | 0 | 0 | 0 | 0 | 929004.24 | 0 | 1802037 | 0 | 2065883.04 | 0 | 5181436.8 | 733164.8 | 981043.2 | 0 | 190309.8 | 11559178.35 | 0 | 17832884 | 0 | 0 | 94185 | 0 | 6240611.52 | 0 | 2364856.5 | 473558.4 | 5767621.47 | 0 | 8604576.09 | 8980070.4 | 0 | 13948022.4 | 0 | 8363363.28 | 0 | 342351.1 | 7551988.8 | 41670758 | 0 | 0 | 0 | 0 |  | 347106851.72 | 223141315.71 | 570248167.43 | 63675089.83 | 74951210.88 | 46302487.3 | 7061691.04 | 274680041.26 | 71062820.35 | 440551.44 | 0 | 15505176.48 | 15393600 | 1175498.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 |  | 0 | 270 | 140 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 102 | 48 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 25 | 25 | 25 | 0 | 72 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 2 | 0 | 0 | 130 | 0 | 280 | 0 | 187 | 0 | 29 | 20 | 0 | 43 | 0 | 0 | 30 | 19 | 5 | 33 | 7 | 93 | 158 | 0 | 17 | 1 | 43 | 30 | 47 | 0 | 163 | 0 | 30 | 77 | 0 | 218 | 18 | 0 | 10 | 0 | 20 | 2 | 0 | 160 | 0 | 25 | 0 | 27 | 52 | 10 | 50 | 15 | 33 | 0 | 75 | 0 | 0 | 5 | 280 | 54 | 51 | 0 | 58 | 0 | 400 | 104 | 24 | 162 | 50 | 80 | 17 | 5 | 28 | 26 |  | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 133 | 0 | 0 | 0 | 0 | 199 | 0 | 52 | 0 | 208 | 0 | 394 | 17 | 0 | 50 | 0 | 49 | 0 | 5 | 35 | 320 | 109 | 0 | 0 | 1 |  | 7235 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 67 | 212 | 0 | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 95 | 0 | 102 | 149 | 24 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 29 | 25 | 33 | 25 | 0 | 73 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 50 | 50 | 50 | 21 | 3 | 0 | 0 | 130 | 0 | 300 | 0 | 180 | 0 | 29 | 56 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 103 | 139 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 30 | 77 | 0 | 198 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 260 | 0 | 0 | 32 | 25 | 149 | 0 | 100 | 34 | 125 | 0 | 115 | 105 | 51 | 0 | 300 | 54 | 110 | 0 | 116 | 60 | 400 | 104 | 0 | 162 | 105 | 80 | 17 | 0 | 0 | 0 |  | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 0 | 43 | 0 | 98 | 0 | 50 | 0 | 52 | 35 | 22 | 0 | 11 | 79 | 0 | 134 | 0 | 0 | 0 | 0 | 181 | 0 | 94 | 0 | 201 | 0 | 358 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 470 | 110 | 0 | 0 | 0 |  | 9409 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 412 | 320 | 0 | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 95 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 25 | 33 | 51 | 0 | 80 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 80 | 100 | 90 | 50 | 21 | 10 | 0 | 0 | 130 | 0 | 360 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 160 | 0 | 22 | 0 | 43 | 30 | 51 | 0 | 163 | 130 | 33 | 80 | 0 | 220 | 18 | 0 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 132 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 383 | 104 | 0 | 162 | 116 | 80 | 17 |  |  |  |  | 701 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 65 | 23 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 27 | 50 | 40 | 52 | 35 | 22 | 0 | 11 | 82 | 0 | 140 | 0 | 0 | 0 | 0 | 220 | 0 | 72 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 110 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 400 | 300 | 0 | 0 | 270 | 140 | 0 | 0 | 55 | 0 | 0 | 60 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 30 | 25 | 33 | 51 | 0 | 80 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 20 | 5 | 0 | 0 | 130 | 0 | 360 | 0 | 180 | 0 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 160 | 0 | 22 | 1.6 | 43 | 30 | 50 | 0 | 163 | 130 | 30 | 80 | 0 | 220 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 0 | 100 | 200 | 50 | 149 | 20 | 100 | 200 | 123 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 383 | 104 | 50 | 162 | 116 | 80 | 17 | 30 |  |  |  | 653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 27 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 80 | 0 | 140 | 0 | 0 | 0 | 0 | 200 | 0 | 70 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 110 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 372 | 312 | 0 | 0 | 270 | 140 | 0 | 0 | 5 | 0 | 0 | 60 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 54 | 17 | 55 | 18 | 25 | 27 | 25 |  | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 21 | 2 | 0 | 0 | 130 | 0 | 285 | 0 | 180 | 0 | 26 | 55 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 9 | 78 | 169 | 0 | 20 | 1 | 43 | 30 | 44 | 0 | 130 | 130 | 30 | 78 | 0 | 172 | 18 | 0 | 10 | 0 | 22 | 5 | 0 | 35 | 0 | 0 | 7 | 0 | 17 | 8 | 60 | 0 | 50 | 0 | 60 | 0 | 0 | 1 | 283 | 54 | 51 | 0 | 59 | 0 | 350 | 104 | 7 | 150 | 68 | 70 | 17 | 4 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 22 | 0 | 8 | 78 | 0 | 136 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 176 | 0 | 382 | 28 | 0 | 80 | 0 | 40 | 0 | 1 | 35 | 300 | 144 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5694 | 5:00
| Highest Generation |  | 9409 | 19:00
| Day Peak Generation |  | 7235 | 12:00
| Evening Peak Generation |  | 9409 | 19:00
| HVDC Max Flow |  | 705 | 18:00
| HVDC EvPeak Flow |  | 704 | 19:00
| Load factor L.F |  | 78.85%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-12-05
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-12-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7235 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 6053 | MW
Evening Peak Generation : |  | 9409 | MW Hour : | 19:00 | Available Max Generation : |  | 12926 | MW
E.P. Demand (at gen end) : |  | 9409 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9600 | MW
Maximum Generation : |  | 9409 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3326 | MW
Total Gen. (MKWH) : |  | 178.0462 | System Load Factor : | 78.85% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 20 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-12-05
Actual : | 100.28 | Ft.(MSL) , | Rule curve : | 105.64 | Ft.( MSL )
Gas Consumed : | Total = | 848.05 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 109977577.13
: |  | Coal : | 71062820.35 | Oil : | 297246908.78 | Total : | 478287306.26
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3428.0562 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1161.9597 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1040.4057 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 939.8559 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 849.4656 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 685.4792 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 388.1366 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 176.6208 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 528.6524 |  |  | 0 | 0%
Total | 0 |  | 9198.6321 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Summit Bibiyana-2
|  |  |  | 2) Ghorasal-3,4,7 |  | 11) Summit Bibiyana-3
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-2
6) Raozan unit-1&2
7) Ashuganj(N)-360 MW.
8) Nutun Bidduit-220 MW GT-1
9) chandpur-163 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Rajshahi 230/132 kV T-01 transformer was under shut down from 08:30 to 16:54 for A/M.
b) Kishoreganj 132/33 kV T-3 transformer was under shut down from 08:35 to 12:05 for C/M.
c) Hathazari-Baroirhat 132 kV Ckt-1 was under shut down from 08:56 to 16:10 for A/M.
d) Maniknagar-Matual 132 kV Ckt was under shut down from 09:10 to 16:12 for A/M.
e) Meghnaghat-Aminbazar 230 kV Ckt-1 was under shut down from 09:21 to 13:39 for A/M.
f) Kishoreganj 132/33 kV T-1 transformer along with its 33 kV Bus was under shut down from 09:12 to 14:48 for A/M.
g) Cumilla(N) 230/132 kV T-02 transformer was under shut down from 09:29 to 14:22 for A/M.
h) Jamalpur 33 kV Bus of 132/33 kV T-1 transformer was under shut down from 09:38 to 10:05 for A/M.
i) Kodda 132/33 kV T-1 & T-2 transformers along with their 33 kV Bus were under shut down from 08:49 to 17:17 for | [5 empty] | About 40 MW power interruption occurred under
PBS work. | [5 empty] | Kodda S/S area from 08:49 to 17:17.
j) Bheramara HVDC-Bahrampur 400 KV Ckt-02 & Bay 10C01 were under shut down from 09:35 to 16:17 for A/M.
k) Mymensingh 132/33 kV T-1 transformer was under shut down from 09:38 to 16:28 for A/M.
l) Ghorashal-Narshingdi 132 kV Ckt-2 was under shut down from 10:17 to 15:45 for A/M.
m) Netrokona 132/33 kV T-1 transformer along with its 33 kV Bus was under shut down from 10:03 to 11:21 for A/M.
n) BSRM-Mirsharai 230 kV Ckt-1 is under shut down since 11:35 for A/M.
o) Tongi 230/132 kV T-02 transformer was under shut down from 09:55 to 15:46 for A/M.
p) Bogura 230/132 kV T-02 transformer is under shut down since11:07 for D/W.
q) Barapukuria-Saidpur 132 kV Ckt-2 was under shut down from 08:14 to 16:55 for A/M.
r) Halishahar 132/33 kV T-1 transformer was under shut down from 10:39 to 16:54 for GIS work.
s) Naogaon-Niyamatpur 132 kV Ckt was under shut down from 08:34 to 16:32 for A/M. | [5 empty] | About 10 MW power interruption occurred under
Niyamatpur S/S area from 08:34 to 16:32.
t) Haripur 412 MW CCPP tripped at 10:21 due to gas system problem and was synchronized at 16:42(GT) & 18:57(ST).
u) Haripur 360 MW CCPP GT & ST were synchronized at 14:33 & 17:57 respectively.
v) Shajibazar 330 MW GT-1 was synchronized at 21:59.
w) Sirajganj unit-1 was synchronized at 22:00 and was shutdown at 23:00.
x) Natun Biddut GT-1 was synchronized at 01:00(05/12/2021).
y) Kallyanpur-Lalbag 132 kV Ckt-1 is under shut down since 07:10(05/12/2021) for A/M.
z) Barishal(N)-Barishal(S) 132 kV Ckt-1 is under shut down since 07:21(05/12/2021) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-12-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4536000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 67 | 5804030 | (GT sync. At 16:42)
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 212 | 1880000 | Load increaing
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6510550 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3490647 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 447150
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 24 | 343346 | Low demand.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 364680 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 95 | 868000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1115856
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1073880
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1044480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 496261
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 965531 | 33 kV feeder fault.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1212360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 738900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 752700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 334560 | 33 kV Feeder SD
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 2973272 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 201833 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 176177 | Low demand.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1133860
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 228000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1897920
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3489120
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 58306
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 0 | 251640 | On test
| Dhaka area Total |  |  |  | 5560 | 2408 | 42389059
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 216815 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 65475
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1027200
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 73 | 1631672 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 51 | 217454 | High Voltage.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 76578 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 153240 | High Voltage.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1252800
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 484512 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 3 | 365760
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 148800 | Line O/L
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 16350
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 6297818
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1292307
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1280470
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 214080 | High Voltage.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 105 | 1371218 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1061 | 16112549
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 130 | 3115598 | Engine problem
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under Maint.
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Ashuganj 400 kV Bus S/D
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7587000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 668952 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1185600
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 180 | 4365818 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1121812
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 1517157 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 93600
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 34 | 294240 | High Voltage.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 479412
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 179640
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 103 | 2052480
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 816200
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 725006
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 219410 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 15744 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 18240 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 116 | 1766520
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 434880 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 76800 | On test
| Cumilla Area Total |  |  |  | 3034 | 1310 | 26734109
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 139 | 4102080 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 420048
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4250
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 32 | 170400 | High Voltage.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1936800
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 107510
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 381120
| Mymensingh Area Total |  |  |  | 622 | 330 | 7122208
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1003000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 690960 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3690245
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 143000 | GT-2 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1214400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 191904
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 760608 | GT-9 under maint
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1870080
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 80 | 1802545 | On test
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 198 | 4802650
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 413000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 497880
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | under Maint.
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252720
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9586700
| Sylhet Area Total |  |  |  | 2377 | 1136 | 26919692
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 704 | 13012363
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 7168 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 27840 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 860160
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 809 | 13907531
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 446600 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1545000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 94 | 1576571 | Engine problem
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 470 | 9492200 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 2733027
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 760 | 15793398
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 94411 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 152802
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 80500 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 181 | 4727736 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 201 | 4929591 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 358 | 8691491 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 75584 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 510960
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 251400
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 534720
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 203620
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1469760
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1021920
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 7260
| Rajshahi Area Total |  |  |  | 2179 | 1277 | 22751755
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1916945
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 134 | 3290200
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 1077753
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30982
| Rangpur Area Total |  |  |  | 605 | 318 | 6315880
| Total |  |  |  | 20934 | 9409 | 178046181
| Eastern Grid Total |  |  |  | 13975 | 6245 | 119277617
| Western Grid Total |  |  |  | 6959 | 3164 | 58768564
| National Grid Total |  |  |  | 20934 | 9409 | 178046181
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-12-04
(a) ENTIRE EASTERN GRID : |  | 6251 | MW | (b) ENTIRE WESTERN GRID : |  | 2755 | MW
i) Dhaka area |  | 3413 | MW | i) Khulna area |  | 1028 | MW
ii) Chittagong area |  | 1059 | MW | ii) Rajshahi area |  | 873 | MW
iii) Comilla area |  | 752 | MW | iii) Barisal area |  | 253 | MW
iv) Mymensingh area |  | 692 | MW | iv) Rangpur area |  | 601 | MW
v) Sylhet area |  | 335 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9006 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 91 | 12:00 | Mymensing | 135 | 18:00 | Jessore | 79 | 18:00
Munsiganj | 62 | 19:00 | Kishoreganj | 90 | 19:30 | Benapol | 40 | 18:00
Sonargaon | 49 | 11:00 | Netrokona | 80 | 18:00 | Jhenida(Old) | 84 | 18:30
Shyampur | 172 | 11:00 | Jamalpur | 92 | 18:00 | Bottail | 96 | 18:00
Bhulta | 161 | 18:30 | Sherpur | 90 | 18:00 | G.K Project | 36 | 18:00
Madanganj | 34 | 22:00 | Srimongal | 36 | 18:00 | Faridpur | 102 | 19:00
Shitalakhya | 92 | 18:30 | Shahjibazar | 74 | 19:00 | Rajbari | 36 | 18:00
Rahim steel | 19 | 7:00 | Fenchuganj | 28 | 17:00 | Madaripur | 62 | 18:00
Matuail | 54 | 10:00 | Kulawara | 28 | 18:00 | Sariatpur | 40 | 18:00
Ghorasal | 57 | 18:30 | Sylhet | 84 | 19:30 | Gopalganj | 63 | 18:00
Narsingdi | 125 | 19:00 | Chatak | 17 | 18:00 | Bagerhat | 78 | 19:30
Haripur (SBU) | 111 | 18:00 | Sunamganj | 30 | 18:30 | Mongla | 34 | 11:00
Sreenagar | 26 | 21:00 | Biani Bazar | 40 | 18:00 | Satkhira | 77 | 18:00
Ullon | 46 | 18:00 | Comilla (S) | 106 | 18:00 | Gallamari | 40 | 13:00
Hasnabad | 61 | 14:00 | Comilla(N) | 81 | 21:00 | Magura | 40 | 18:00
Magbazar | 64 | 13:00 | Chandpur | 45 | 19:30 | Norail | 36 | 18:00
Maniknagar | 48 | 13:00 | Feni | 80 | 18:30 | Chuadanga | 64 | 18:00
Bangabhaban | 5 | 11:00 | Chowmuhani | 133 | 20:00 | Barisal(N) | 29 | 18:00
Motijheel | 17 | 13:00 | Ashuganj | 23 | 13:00 | Barisal (S) | 76 | 18:30
Narinda | 46 | 13:00 | Daudkandi | 92 | 19:30 | Patuakhali | 76 | 21:00
Kazla | 72 | 18:00 | B.Baria | 98 | 19:00 | Bhandaria | 36 | 18:00
Dhanmondi | 126 | 13:00 | Ramganj | 52 | 18:00 | Borguna | 12 | 18:30
Lalbag | 83 | 13:00 | Chaddagram | 29 | 18:00 | Borhan Uddin | 31 | 20:00
Madartek | 50 | 18:00 | PHP | 3 | 18:00 | Ishurdi | 55 | 18:00
Dhaka University | 22 | 12:00 | Kochua | 38 | 18:00 | Ruppur Paromanobik | 2 | 1:00
Aftabnagar | 12 | 18:00 | Madunaghat | 40 | 13:00 | Natore | 89 | 18:00
Fatullah | 49 | 15:00 | Hathazari | 75 | 18:30 | Bogra | 110 | 19:00
Nawabganj | 32 | 21:00 | Khulshi | 167 | 13:00 | Noagaon | 79 | 18:00
Keraniganj | 52 | 18:00 | Halishahar | 76 | 9:00 | Rajshahi | 97 | 19:30
Banani | 41 | 18:00 | Baraulia | 119 | 0:00 | Rajshahi New | 14 | 18:00
Mirpur | 90 | 18:30 | Sikalbaha | 25 | 15:00 | C.Nawabganj | 41 | 19:00
Kalyanpur | 66 | 18:00 | Dohazari | 66 | 17:00 | Amnura | 36 | 8:00
Gulshan | 68 | 12:00 | Cox'sbazar | 79 | 21:00 | Pabna | 82 | 18:00
Uttara | 56 | 13:00 | Chandraghona | 20 | 18:00 | Shahjadpur | 69 | 18:30
Uttara New | 11 | 18:00 | Kaptai | 3 | 17:00 | Serajganj | 56 | 18:00
Kamrangirchar | 80 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 42 | 18:00
Savar | 136 | 18:00 | Bakulia | 94 | 18:00 | Joypurhat | 44 | 18:00
Bhasantec | 88 | 18:00 | Julda | 21 | 13:00 | Sherpur(Bogura) | 46 | 18:00
Agargaon | 55 | 13:00 | TK chemical | 24 | 18:00 | Mohastangor | 40 | 18:00
Satmosjid | 76 | 13:00 | Modern Steel | 0 | 1:00 | Bhangura | 20 | 18:00
Tongi | 96 | 18:00 | Shahmirpur | 38 | 18:30 | Rangpur | 98 | 18:00
Kabirpur | 176 | 18:30 | Khagrachhari | 20 | 18:00 | Lalmonirhat | 40 | 18:00
Basundhara | 150 | 18:00 | Matarbari | 26 | 17:00 | Saidpur | 80 | 18:00
Purbachal | 54 | 20:00 | Baroiar Hat | 38 | 18:00 | Purbasadipur | 86 | 19:30
Manikganj | 133 | 18:00 | Rangamati | 10 | 18:00 | Thakurgaon | 69 | 18:00
Joydevpur | 66 | 12:00 | Abul Khair 230 | 15 | 18:30 | Palashbari | 80 | 19:00
New Tongi | 191 | 18:30 | BSRM | 164 | 7:00 | Barapukuria | 41 | 18:00
Kodda | 84 | 12:00 | GPH Ispat | 17 | 12:00 | Panchagar | 47 | 18:00
Dhamrai | 79 | 19:00 | Agrabad | 66 | 18:00 | Joldhaka | 28 | 18:00
Rajendrapur | 12 | 19:00 | Goalpara | 20 | 13:00 | Kurigram | 51 | 18:00
Valuka | 102 | 18:00 | Central S/S | 54 | 21:00 | Mithapukur | 24 | 18:00
Tangail | 134 | 19:30 | Noapara | 36 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-12-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 414 | 3:00 | 404 | 11:00 | Kaliakoir | 408 | 0.125 | 396 | 0.41667
| Bheramara | 403 | 7:00 | 393 | 12:00 | Bhulta | 380 | 0.125 | 359 | 0.41667
| Ashuganj(N) | 0 | 1:00 | 0 | 1:00 | Gopalganj | 413 | 0.625 | 400 | 0.75
| Payra | 413 | 1:00 | 406 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 238 | 1:00 | Hathazari | 244 | 17:00 | 236 | 11:00
| Ishurdi | 237 | 3:00 | 230 | 12:00 | Megnaghat | 238 | 14:00 | 234 | 1:00
| Ashuganj | 248 | 13:00 | 242 | 10:00 | Fenchuganj | 247 | 1:00 | 242 | 10:00
| Serajganj | 240 | 18:30 | 229 | 9:00 | Siddhirganj | 235 | 6:00 | 228 | 11:00
| Baghabari | 239 | 3:00 | 231 | 7:00 | Maniknagar | 236 | 6:00 | 22 | 13:00
| Barapukuria | 237 | 21:00 | 223 | 9:00 | Agargaon | 235 | 3:00 | 226 | 11:00
| Bogra | 234 | 5:00 | 230 | 12:00 | Barisal | 246 | 18:00 | 240 | 21:00
| Rajshahi | 238 | 19:00 | 225 | 12:00 | Bhola 225 MW | 249 | 3:00 | 244 | 18:00
| Khulna South | 239 | 4:00 | 228 | 7:00 | AKSML | 241 | 18:00 | 228 | 4:00
| Rampura | 232 | 1:00 | 227 | 11:00 | BSRM | 241 | 18:00 | 227 | 5:00
| Haripur | 234 | 1:00 | 223 | 10:00 | Bibiyana | 246 | 19:00 | 239 | 5:00
| Hasnabad | 236 | 4:00 | 226 | 9:00 | Bhulta | 234 | 2:00 | 225 | 11:00
| Shyampur | 233 | 1:00 | 225 | 11:00 | Ashuganj (S) | 244 | 18:30 | 236 | 11:00
| Aminbazar | 236 | 1:00 | 226 | 2:00 | Kaliakoir | 237 | 13:00 | 227 | 10:00
| Tongi | 235 | 13:00 | 225 | 10:00 | GPH | 243 | 18:00 | 227 | 5:00
| Comilla (N) | 238 | 18:00 | 230 | 10:00 | Jhenaidah | 233 | 1:00 | 224 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 1:00 | 132 | 11:00 | Kachua | 141 | 0.29167 | 136 | 0.41667
| Munsiganj | 140 | 14:00 | 133 | 11:00 | Madanhat | 141 | 0.20833 | 137 | 0.041667
| Sonargaon | 139 | 13:00 | 132 | 10:00 | Hathazari | 141 | 0.25 | 138 | 0.041667
| Shyampur | 141 | 18:00 | 135 | 11:00 | Khulshi | 138 | 0.75 | 130 | 0.16667
| Bhulta | 134 | 2:00 | 123 | 14:00 | Halishahar | 140 | 0.75 | 136 | 0.041667
| Madanganj | 139 | 13:00 | 131 | 11:00 | Baraulia | 142 | 0.29167 | 136 | 0
| Shitalakhya | 141 | 19:00 | 133 | 10:00 | Sikalbaha | 140 | 0.25 | 132 | 0.16667
| Rahim steal | 138 | 1:00 | 130 | 10:00 | Dohazari | 137 | 0.375 | 130 | 0.8125
| Matuail | 137 | 1:00 | 132 | 11:00 | Cox'sbazar | 125 | 0.375 | 109 | 0.83333
| Ghorasal | 142 | 20:00 | 138 | 1:00 | Chandraghona | 141 | 0.75 | 137 | 0.16667
| Narsinghdi | 136 | 1:00 | 133 | 19:00 | Kaptai | 140 | 0.54167 | 137 | 0.041667
| Haripur (SBU) | 138 | 1:00 | 133 | 11:00 | A. Khaer Stl. | 142 | 0.41667 | 136 | 0.125
| Sreenagar | 138 | 2:00 | 133 | 10:00 | Bakulia | 142 | 0.75 | 133 | 0.041667
| Ullon | 136 | 5:00 | 128 | 11:00 | Julda | 138 | 0.45833 | 135 | 0.041667
| Hasnabad | 140 | 1:00 | 135 | 10:00 | TK Chemical | 141 | 0.75 | 135 | 0.041667
| Magbazar | 135 | 1:00 | 129 | 11:00 | Modern Steel | 139 | 0.79167 | 132 | 0.20833
| Maniknagar | 137 | 1:00 | 130 | 11:00 | Shahmirpur | 140 | 0.77083 | 134 | 0.041667
| Bangabhaban | 137 | 1:00 | 130 | 11:00 | Khagrachhari | 141 | 0.75 | 136 | 0.16667
| Motijheel | 137 | 1:00 | 130 | 11:00 | Matarbari | 124 | 0.375 | 109 | 0.8125
| Narinda | 137 | 1:00 | 130 | 11:00 | Baroiar Hat | 142 | 18:00 | 136 | 1:00
| Kazla | 137 | 1:00 | 130 | 11:00 | Rangamati | 141 | 18:00 | 136 | 4:00
| Dhanmondi | 138 | 5:00 | 130 | 11:00 | Agrabad | 141 | 18:00 | 131 | 0.20833
| Lalbag | 135 | 2:00 | 128 | 11:00 | Goalpara S/S | 138 | 19:00 | 130 | 0.29167
| Madartek | 135 | 1:00 | 128 | 11:00 | Khulna Central S/S | 137 | 6:00 | 130 | 0.5
| Dhaka University | 136 | 6:00 | 129 | 11:00 | Noapara | 136 | 3:00 | 127 | 0.29167
| Aftabnagar | 136 | 1:00 | 129 | 10:00 | Jessore | 135 | 0.083333 | 129 | 0.29167
| Fatullah | 141 | 6:00 | 134 | 11:00 | Benapol | 136 | 4:00 | 127 | 0.54167
| Nawabganj | 139 | 2:00 | 134 | 11:00 | Jhenida(Old) | 137 | 0.25 | 132 | 0.5
| Keraniganj | 138 | 18:00 | 133 | 10:00 | Bottail | 138 | 0.16667 | 131 | 0.5
| Banani | 136 | 6:00 | 130 | 11:00 | G.K Project | 138 | 0.79167 | 133 | 0.5
| Mirpur | 136 | 2:00 | 128 | 10:00 | Faridpur | 137 | 0.083333 | 132 | 0.75
| Kalyanpur | 136 | 1:00 | 130 | 9:00 | Rajbari | 138 | 0.20833 | 131 | 0.75
| Gulshan | 135 | 1:00 | 129 | 11:00 | Madaripur | 143 | 4:00 | 138 | 0.77083
| Uttara | 136 | 3:00 | 128 | 11:00 | Shariyatpur S/S | 144 | 0.20833 | 137 | 0.83333
| Uttara New | 136 | 1:00 | 129 | 9:00 | Gopalganj | 142 | 3:00 | 136 | 0.75
| Kamrangirchar | 138 | 2:00 | 133 | 9:00 | Bagerhat | 135 | 18:00 | 127 | 0.29167
| Savar | 135 | 7:00 | 130 | 9:00 | Mongla | 135 | 9:00 | 127 | 23:00
| Bhasantec | 137 | 1:00 | 131 | 10:00 | Satkhira | 135 | 0.16667 | 129 | 12:00
| Agargaon | 138 | 1:00 | 132 | 11:00 | Gallamari | 142 | 4:00 | 135 | 0.75
| Satmosjid | 138 | 8:00 | 130 | 9:00 | Magura | 138 | 0.25 | 132 | 0.5
| Tongi | 142 | 13:00 | 133 | 18:30 | Narail | 137 | 3:00 | 128 | 0.29167
| Kabirpur | 139 | 1:00 | 134 | 10:00 | Chuadanga | 136 | 1:00 | 130 | 0.29167
| Basundhara | 138 | 18:30 | 130 | 10:00 | Barisal(N) | 143 | 1:00 | 138 | 18:00
| Purbachal | 141 | 16:00 | 136 | 17:00 | Barisal (S) | 143 | 0.25 | 138 | 0.70833
| Manikganj | 141 | 7.00 | 133 | 10:00 | Patuakhali(S) | 142 | 0.16667 | 135 | 0.70833
| Joydevpur | 140 | 20:00 | 131 | 10:00 | Bhandaria | 145 | 0.375 | 135 | 0.75
| New Tongi | 139 | 19:00 | 129 | 10:00 | Borguna | 143 | 6:00 | 137 | 18:00
| Kodda | 137 | 3:00 | 129 | 19:00 | Jhenaidah(New) | 138 | 2:00 | 131 | 7:00
| Dhamrai | 137 | 14:00 | 125 | 11:00 | Ishurdi | 137 | 3:00 | 133 | 12:00
| Rajendrapur | 136 | 1:00 | 129 | 11:00 | Ruppur Paromanobik | 137 | 5:00 | 132 | 11:00
| Valuka | 134 | 2:00 | 128 | 18:00 | Natore | 139 | 20:00 | 133 | 12:00
| Tangail | 139 | 14:00 | 132 | 17:00 | Bogra | 139 | 19:30 | 133 | 13:00
| Mymensing | 136 | 5:00 | 133 | 18:00 | Noagaon | 135 | 3:00 | 130 | 12:00
| Kishorganj | 136 | 6:00 | 133 | 12:00 | Rajshahi | 139 | 20:00 | 131 | 12:00
| Netrokona | 135 | 2:00 | 131 | 7:00 | Rajshahi New | 141 | 19:00 | 131 | 12:00
| Jamalpur | 140 | 18:00 | 132 | 5:00 | C.Nawabganj | 140 | 19:00 | 128 | 11:00
| Sherpur | 139 | 17:00 | 130 | 5:00 | Amnura | 138 | 18:00 | 128 | 11:00
| Srimongal | 139 | 13:00 | 137 | 10:00 | Pabna | 137 | 2:00 | 132 | 12:00
| Shahjibazar | 137 | 1:00 | 134 | 11:00 | Shahjadpur | 142 | 1:00 | 137 | 12:00
| Fenchuganj | 139 | 8:00 | 136 | 11:00 | Serajganj | 138 | 1:00 | 134 | 17:00
| Khulawara | 137 | 1:00 | 135 | 11:00 | Niyamatpur | 136 | 4:00 | 128 | 7:00
| Sylhet | 135 | 1:00 | 134 | 12:00 | Joypurhat | 136 | 2:00 | 130 | 11:00
| Chatak | 136 | 1:00 | 135 | 10:00 | Sherpur(Bogura) | 138 | 3:00 | 133 | 12:00
| Sunamganj | 135 | 9:00 | 133 | 17:00 | Mohastangor | 138 | 19:30 | 132 | 12:00
| Biani Bazar | 136 | 6:00 | 133 | 17:00 | Bangura | 140 | 3:00 | 135 | 12:00
| Comilla(s) | 127 | 2:00 | 123 | 14:00 | Rangpur | 134 | 19:30 | 125 | 11:00
| Comilla(n) | 144 | 18:00 | 139 | 10:00 | Lalmonirhat | 135 | 4:00 | 123 | 13:00
| Chandpur | 141 | 6:00 | 136 | 10:00 | Saidpur | 134 | 6:00 | 122 | 13:00
| Feni | 142 | 18:00 | 137 | 10:00 | Purbasadipur | 133 | 4:00 | 121 | 13:00
| Chowmuhani | 140 | 1:00 | 136 | 16:00 | Thakurgaon | 131 | 4:00 | 120 | 12:00
| Ashuganj | 140 | 1:00 | 136 | 11:00 | Palashbari | 135 | 1:00 | 129 | 12:00
| Daudkandi | 140 | 7:00 | 135 | 10:00 | Barapukuria | 136 | 0.041667 | 123 | 0.375
| B.Baria | 137 | 7:00 | 132 | 11:00 | Panchagar | 133 | 0.16667 | 121 | 0.54167
| Ramganj | 139 | 6:00 | 136 | 10:00 | Joldhaka | 134 | 0.16667 | 122 | 0.5
| Chaddagram | 142 | 7:00 | 138 | 5:00 | Kurigram | 133 | 0.125 | 124 | 0.54167
| PHP | 141 | 7:00 | 135 | 5:00 | Mithapukur | 136 | 0.83333 | 129 | 0.5

## L-Curve
Date | 2021-12-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 114 | 5185 | 2241 | 7426 |  |  |  | QF-LDC-11
0:30 | 164 | 4736.5 | 2147 | 6883.5 | Date: | 2021-12-04
1:00 | 214 | 4288 | 2053 | 6341
1:30 | 205 | 4243.5 | 2015 | 6258.5
2:00 | 196 | 4199 | 1977 | 6176
2:30 | 218 | 4085.5 | 1964 | 6049.5 | [5 empty] | Gen. at Eve. Peak | 9409 | 9409 MW (19:00 )
3:00 | 240 | 3972 | 1951 | 5923 | [6 empty] | 19:00
3:30 | 265 | 3918 | 1933.5 | 5851.5 | [5 empty] | Gen. at Day Peak | 7235 | 7235 MW (12:00 )
4:00 | 290 | 3864 | 1916 | 5780 | [6 empty] | 12:00
4:30 | 305 | 3824 | 1913 | 5737 | [5 empty] | Highest Generation | 9409
5:00 | 320 | 3784 | 1910 | 5694 | [6 empty] | 19:00
5:30 | 354 | 3780.5 | 1951 | 5731.5
6:00 | 388 | 3777 | 1992 | 5769
6:30 | 208 | 4002.5 | 2000.5 | 6003
7:00 | 28 | 4228 | 2009 | 6237
7:30 | 24 | 4418.5 | 2067.5 | 6486
8:00 | 20 | 4609 | 2126 | 6735
8:30 | 103.5 | 4691.5 | 2145.5 | 6837
9:00 | 187 | 4774 | 2165 | 6939
9:30 | 329.5 | 4783.5 | 2123.5 | 6907
10:00 | 472 | 4793 | 2082 | 6875
10:30 | 463 | 4615 | 2184 | 6799
11:00 | 454 | 4437 | 2286 | 6723
11:30 | 497 | 4614 | 2365 | 6979
12:00 | 540 | 4791 | 2444 | 7235
12:30 | 492 | 4921 | 2455 | 7376
13:00 | 444 | 5051 | 2466 | 7517
13:30 | 410 | 4982.5 | 2421.5 | 7404
14:00 | 376 | 4914 | 2377 | 7291
14:30 | 458 | 4910 | 2364.5 | 7274.5
15:00 | 540 | 4906 | 2352 | 7258
15:30 | 505 | 4956 | 2318 | 7274
16:00 | 470 | 5006 | 2284 | 7290
16:30 | 455.5 | 5197.5 | 2400.5 | 7598
17:00 | 441 | 5389 | 2517 | 7906
17:30 | 265.5 | 5852 | 2776.5 | 8628.5
18:00 | 90 | 6315 | 3036 | 9351
18:30 | 155.5 | 6280 | 3100 | 9380
19:00 | 221 | 6245 | 3164 | 9409
19:30 | 226 | 6122 | 3104 | 9226
20:00 | 132 | 6039 | 3012 | 9051 |  |  |  | Executive Engineer
20:30 | 143 | 5967.5 | 2968.5 | 8936 |  |  |  | Network Operation Division
21:00 | 154 | 5896 | 2925 | 8821
21:30 | 186.5 | 5737.5 | 2816 | 8553.5
22:00 | 219 | 5579 | 2707 | 8286 |  |  |  |  | Page 6 of 7
22:30 | 221 | 5400 | 2612 | 8012
23:00 | 223 | 5221 | 2517 | 7738
23:30 | 168.5 | 5203 | 2379 | 7582
24:00 | 114 | 5185 | 2241 | 7426
9409 MW (19:00 )
7235 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-12-04 |  | Energy |  | 178046181
[13 empty] | 2021-12-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2873 | 551 | 1895 | 0 | 1348 | 602 | 76 | 0 | 0 | 81 | 0 | 0
0:30 | 2824 | 467.5 | 1747.5 | 0 | 1094.5 | 595 | 78 | 0 | 0 | 77 | 0 | 0 | Date: | 2021-12-04
1:00 | 2775 | 384 | 1600 | 0 | 841 | 588 | 80 | 0 | 0 | 73 | 0 | 0
1:30 | 2781 | 379 | 1592 | 0 | 788 | 568 | 80 | 0 | 0 | 70.5 | 0 | 0 | [8 empty] | Total Energy | 178.0462 | Total Energy Gen 178.046 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 178.046 MKWHr
2:00 | 2787 | 374 | 1584 | 0 | 735 | 548 | 80 | 0 | 0 | 68 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2784.5 | 374 | 1583.5 | 0 | 622 | 538 | 79.5 | 0 | 0 | 68 | 0 | 0 | [8 empty] | Energy Requirement | 178.0462
3:00 | 2782 | 374 | 1583 | 0 | 509 | 528 | 79 | 0 | 0 | 68 | 0 | 0
3:30 | 2785.5 | 374 | 1571.5 | 0 | 452.5 | 523 | 78.5 | 0 | 0 | 66.5 | 0 | 0 | [6 empty] | Shortage
4:00 | 2789 | 374 | 1560 | 0 | 396 | 518 | 78 | 0 | 0 | 65 | 0 | 0
4:30 | 2796 | 374 | 1557.5 | 0 | 350 | 517.5 | 77.5 | 0 | 0 | 64.5 | 0 | 0
5:00 | 2803 | 374 | 1555 | 0 | 304 | 517 | 77 | 0 | 0 | 64 | 0 | 0
5:30 | 2765.5 | 374 | 1595 | 0 | 329 | 527 | 77 | 0 | 0 | 64 | 0 | 0
6:00 | 2728 | 374 | 1635 | 0 | 354 | 537 | 77 | 0 | 0 | 64 | 0 | 0
6:30 | 2717 | 374 | 1562 | 0 | 674 | 535.5 | 74.5 | 0 | 0 | 63.5 | 2.5 | 0 |  |  |  |  | Coal
7:00 | 2706 | 374 | 1489 | 0 | 994 | 534 | 72 | 0 | 0 | 63 | 5 | 0
7:30 | 2791.5 | 374 | 1491 | 0 | 1142 | 539 | 71 | 0 | 0 | 66.5 | 11 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2877 | 374 | 1493 | 0 | 1290 | 544 | 70 | 0 | 0 | 70 | 17 | 0
8:30 | 2850.5 | 374 | 1467 | 0 | 1424.5 | 548 | 69.5 | 0 | 0 | 75.5 | 28 | 0
9:00 | 2824 | 374 | 1441 | 0 | 1559 | 552 | 69 | 0 | 0 | 81 | 39 | 0
9:30 | 2803 | 374 | 1465.5 | 0 | 1514.5 | 532.5 | 73 | 0 | 0 | 84 | 44 | 0
10:00 | 2782 | 374 | 1490 | 0 | 1470 | 513 | 77 | 0 | 0 | 87 | 49 | 0
10:30 | 2549 | 429.5 | 1505.5 | 24 | 1507.5 | 513.5 | 78 | 0 | 8 | 88.5 | 45.5 | 0
11:00 | 2316 | 485 | 1521 | 48 | 1545 | 514 | 79 | 0 | 16 | 90 | 42 | 0
11:30 | 2322.5 | 570.5 | 1535.5 | 50 | 1671 | 523.5 | 75.5 | 0 | 32 | 91.5 | 46.5 | 0
12:00 | 2329 | 656 | 1550 | 52 | 1797 | 533 | 72 | 0 | 48 | 93 | 51 | 0
12:30 | 2323.5 | 656.5 | 1552 | 69 | 1909 | 538 | 74.5 | 0 | 73 | 94 | 40.5 | 0
13:00 | 2318 | 657 | 1554 | 86 | 2021 | 543 | 77 | 0 | 98 | 95 | 30 | 0
13:30 | 2318 | 657 | 1554 | 86 | 2021 | 543 | 77 | 0 | 98 | 95 | 30 | 0
14:00 | 2318 | 657 | 1554 | 86 | 2021 | 543 | 77 | 0 | 98 | 95 | 30 | 0
14:30 | 2261.5 | 657 | 1560.5 | 43 | 2020 | 531.5 | 75.5 | 0 | 81 | 94.5 | 22 | 0
15:00 | 2205 | 657 | 1567 | 0 | 2019 | 520 | 74 | 0 | 64 | 94 | 14 | 0
15:30 | 2264 | 656.5 | 1550.5 | 0 | 2016.5 | 517.5 | 52 | 0 | 64 | 95 | 9.5 | 0
16:00 | 2323 | 656 | 1534 | 0 | 2014 | 515 | 30 | 0 | 64 | 96 | 5 | 0
16:30 | 2388 | 656.5 | 1584 | 0 | 2179.5 | 529 | 30 | 0 | 94 | 98.5 | 2.5 | 0
17:00 | 2453 | 657 | 1634 | 0 | 2345 | 543 | 30 | 0 | 124 | 101 | 0 | 0
17:30 | 2459.5 | 681 | 1630.5 | 119.5 | 2719 | 597 | 50.5 | 0 | 258.5 | 103.5 | 0 | 0
18:00 | 2466 | 705 | 1627 | 239 | 3093 | 651 | 71 | 0 | 393 | 106 | 0 | 0
18:30 | 2474 | 704.5 | 1722 | 132 | 3111.5 | 667 | 72 | 0 | 392.5 | 104.5 | 0 | 0
19:00 | 2482 | 704 | 1817 | 25 | 3130 | 683 | 73 | 0 | 392 | 103 | 0 | 0
19:30 | 2597 | 705 | 1895 | 0 | 2841 | 681 | 73 | 0 | 332 | 102 | 0 | 0
20:00 | 2589 | 705 | 1897 | 0 | 2816 | 682 | 75 | 0 | 187 | 100 | 0 | 0
20:30 | 2647 | 705 | 1919 | 0 | 2664 | 682.5 | 76 | 0 | 143.5 | 99 | 0 | 0
21:00 | 2705 | 705 | 1941 | 0 | 2512 | 683 | 77 | 0 | 100 | 98 | 0 | 0
21:30 | 2724.5 | 705 | 1950 | 0 | 2246.5 | 672.5 | 77 | 0 | 82 | 96 | 0 | 0
22:00 | 2744 | 705 | 1959 | 0 | 1981 | 662 | 77 | 0 | 64 | 94 | 0 | 0
22:30 | 2822 | 705 | 1940.5 | 0 | 1704.5 | 642 | 76.5 | 0 | 32 | 89.5 | 0 | 0
23:00 | 2900 | 705 | 1922 | 0 | 1428 | 622 | 76 | 0 | 0 | 85 | 0 | 0
23:30 | 2886.5 | 628 | 1908.5 | 0 | 1388 | 612 | 76 | 0 | 0 | 83 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 26.7° C
24:00 | 2873 | 551 | 1895 | 0 | 1348 | 602 | 76 | 0 | 0 | 81 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 178.046 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 178.046 MKWHr
Note on W13: Author:

## Generation
g | 2021-12-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 80 | 80 | 79 | 78 | 77 | 77 | 72 | 70 | 69 | 77 | 79 | 72 | 77 | 64 | 74 | 30 | 30 | 71 |  | 73 | 73 | 75 | 77 | 77 | 76 | 76 | 1631672
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 8 | 8 |  | 0 | 216815
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 12 | 9 | 8 | 10 | 8 | 3 | 2 | 1 | [10 empty] | 65475
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 15 | 51 |  | 17 | [5 empty] | 0 | 76578
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [15 empty] | 5 | 25 | 68 |  | 51 | 17 | 17 | 17 |  |  | 0 | 217454
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 47 | [8 empty] | 15744
14 | Titas 50 MW Peaking PP | [17 empty] | 38 |  | 50 | 50 | [5 empty] | 93600
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [15 empty] | 97 | 97 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 94 | 868000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 20 | 55 | 95 | 95 | 95 | 160 | 249 | 270 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 145 | 15 |  | 0 | 2973272
19 | Ashuganj 195MW PP (APSCL-United) | 180 | 180 | 180 | 180 | 182 | 182 | 182 | 182 | 182 | 182 | 177 | 187 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4365818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4536000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3115598
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 668952
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 300 | 315 | 300 | 300 | 310 | 320 | 310 | 365 | 365 | 350 | 280 | 280 | 275 | 280 | 280 | 290 | 355 | 300 |  | 300 | 300 | 300 | 300 | 295 | 275 | 265 | 7587000
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 20 | 20 | 20 | 30 | 43 | 43 | 52 | 54 |  | 56 | 56 | 55 | 55 | 55 | 56 | 55 | 1185600
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 384 | 387 | 390 | 402 | 406 | 320 | 332 | 410 | 401 | 398 | [6 empty] | 6 | 36 |  | 67 | 193 | 187 | 298 | 348 | 378 | 397 | 5804030
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6510550
41 | Haripur 360MW CCPP(HPL) | [14 empty] | 31 | 31 | 28 | 66 |  | 212 | 293 | 293 | 342 | 352 | 352 | 357 | 1880000
42 | RPCL 210MW CCPP | 203 | 206 | 214 | 215 | 215 | 215 | 218 | 218 | 216 | 195 | 172 | 158 | 144 | 138 | 141 | 140 | 140 | 140 |  | 139 | 141 | 139 | 141 | 142 | 145 | 153 | 4102080
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 4 | 13 | 17 | 17 | 24 | 14 | 10 | 4 | 1 | 0 | [9 empty] | 107510
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 | 43 | 43 | 41 | 43 | 43 | 43 | 43 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1003000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 690960
46 | Shajibazar 330 MW CCPP | [23 empty] | 7 | 91 | 122 | 143000
47 | Shahjibazar GTPP Unit- 8 & 9 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 760608
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 80 | 77 | 78 | 77 | 78 | 77 | 77 | 77 | 77 | 78 | 77 | 77 | 77 |  | 77 | 77 | 77 | 77 | 78 | 78 | 78 | 1870080
| Shahjibazar 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1802545
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 192 | 191 | 191 | 191 | 191 | 191 | 171 | 211 | 217 | 218 | 218 | 218 | 218 | 190 | 185 | 185 | 198 | 198 |  | 198 | 198 | 198 | 198 | 198 | 199 | 197 | 4802650
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 413000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252720
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 10 | 8 | 8 | 8 | 5 | 5 | 4 | 4 | 2 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 191904
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 44 | 50 | 47 | 50 | 50 | 50 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1214400
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 15 | 20 | 20 | 20 | 16 | 16 | 16 | 21 | 23 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 497880
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 389 | 400 | 400 | 9586700
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 0 |  |  |  | 52 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 965531
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 0 | 11 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 381120
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 484512
61 | Narshingdi 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 364680
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 420048
63 | Impoprt (Tripura) | 73 | 68 | 68 | 65 | 64 | 64 | 63 | 70 | 81 | 87 | 90 | 93 | 95 | 97 | 94 | 96 | 101 | 106 |  | 103 | 102 | 100 | 98 | 94 | 85 | 81 | 2052480
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 40 | 40 | 40 | 40 | 21 | 2 | 2 | 2 | 2 | 2 | 5 | 3 | 2 | 2 | 2 | 2 |  | 3 | 3 | 4 | 0 | 16 | 20 | 30 | 365760
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 479412
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 179640
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816200
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 |  | 9 | 9 | 9 | 3 | 9 | 9 | 9 | 219410
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 25 | 25 | 24 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 612360
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 738900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 752700
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [17 empty] | 34 | [7 empty] | 0 | 18240
| Chowmuhani 113 MW | 59 | 57 | 26 | 26 | 26 | 31 | 57 | 59 | 59 | 58 | 59 | 58 | 58 | 58 | 58 | 57 | 99 | 114 |  | 116 | 116 | 116 | 116 | 116 | 116 | 104 | 1766520
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 90 | 35 | 35 | 38 | 130 | 152 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3489120
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [10 empty] | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 334560
79 | Kodda 150MW PP | [10 empty] | 16 | 48 | 98 | 64 | 64 | 64 | 98 | 149 |  | 149 | 149 | 149 | 100 | 64 |  | 0 | 1044480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 18 | 52 | 0 |  |  |  | 4 | 8 | 8 | 8 | 9 | 30 | 46 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 725006
| Gazipur 100 MW PP | [16 empty] | 9 | 74 |  | 105 | 17 | 17 |  |  |  | 0 | 228000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 2 | 5 | 2 | 1 | 1 | 0 | [10 empty] | 16350
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1292307
| Karnaphuli Power Ltd. | [5 empty] | 8 | 61 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 60 | 86 |  | 110 | 110 | 110 | 110 | 68 | 34 | 34 | 1280470
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 13 | 24 | 25 | 25 | 24 | 25 | 25 | 25 | 24 | 25 | 24 |  | 24 | 24 | 24 | 25 |  |  | 0 | 343346
86 | Meghnaghat CCPP ( Summit) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3490647
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 55 | 17 | 17 | 0 | 0 | 6 | 46 | 78 | 94 | 94 | 94 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 55 | 54 | 1897920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [15 empty] | 3 | 30 | 100 |  | 50 | 10 | 10 |  |  |  | 0 | 153240
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 1121812
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 24 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 48 | 16 | 16 | 1115856
95 | Patenga 50MW PP (Baraka) | 50 | 35 | 25 | 25 | 25 | 25 | 35 | 39 | 41 | 48 | 50 | 50 | 48 | 45 | 46 | 46 | 49 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 26 | 1027200
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 22 | 48 |  | 50 | 30 | 25 |  |  |  | 0 | 148800
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 25 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 15 | 15 |  |  |  | 0 | 447150
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 35 | 17 |  |  | 0 | 496261
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 163 | 110 | 163 | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 130 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3690245
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [10 empty] | 4250
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1073880
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko) | [11 empty] | 25 | 86 |  |  |  |  | 90 | [7 empty] | 0 | 201833
106 | Mymensingh 200 MW PP (United) | [16 empty] | 9 | 60 |  | 32 | 32 | 32 |  |  |  | 0 | 170400
112 | Aurahati 100MW PP (Aggreko) | [10 empty] | 48 | 27 | [5 empty] | 92 |  | 25 | [5 empty] | 0 | 176177
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 2 | 30 | 52 | 85 | 90 | 70 | 70 | 75 | 118 |  | 149 | 149 | 149 | 120 | 70 |  | 0 | 1133860
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | 20 | 0 |  |  |  | 50 | 10 | 10 | 10 | 50 | 50 | 62 | 70 | 70 | 70 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1252800
116 | Chandpur 200MW (Desh energy) | [11 empty] | 15 | 18 | 34 | 34 | 17 | 32 | 34 |  | 34 | 17 | 17 | 17 | 17 |  | 0 | 294240
117 | Ashuganj 150MW PP (Midland) | 50 | 10 | 10 | 0 |  |  |  | 18 | 75 | 80 | 30 | 33 | 65 | 65 | 65 | 65 | 65 | 85 |  | 125 | 125 | 125 | 130 | 133 | 93 | 50 | 1517157
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 60 | 50 | 30 | 30 | 30 | 30 | 60 | 90 | 115 | 75 | 75 | 75 | 85 | 85 | 85 | 85 | 90 | 115 |  | 115 | 115 | 115 | 115 | 95 | 75 | 75 | 1936800
| Anwara 300 MW PP (United) | 210 | 210 | 210 | 175 | 100 | 110 | 195 | 260 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6297818
| Juldah unit-2 (Acorn) | [15 empty] | 10 | 70 | 100 |  | 60 | 10 | 10 |  |  |  | 0 | 214080
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 0 | 13 | 62 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 101 |  | 105 | 105 | 105 | 105 | 105 | 69 | 69 | 1371218
| Bhairob 54.5 MW | 17 | 17 | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 12 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434880
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 2 | 7 | 13 | 8 | 5 |  | 6 | 3 | 1 | 0 | [9 empty] | 58306
| Chandpur 115(Doreen) | [9 empty] | 18 | 27 | 28 | [14 empty] | 76800
| Kanchan Purbachal Power Generation Ltd. | [9 empty] | 15 | 40 | 26 | 38 | 38 | 44 | 53 | 19 | [8 empty] | 0 | 251640
120 | Eastern Zone Total | 4288 | 4199 | 3972 | 3864 | 3784 | 3777 | 4228 | 4609 | 4774 | 4793 | 4437 | 4791 | 5051 | 4914 | 4906 | 5006 | 5389 | 6315 |  | 6245 | 6122 | 6039 | 5896 | 5579 | 5221 | 5185 | 119277617
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 18 | 53 | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 30 | 95 |  | 105 | 105 | 105 | 105 | 70 | 17 | 17 | 860160
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 112 | 112 | 112 | 112 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 109 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 102 | 110 | 103 | 100 | 111 | 107 | 2733027
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 63 | 82 | 82 | 58 | 53 | 53 | 53 | 52 | 53 | 53 | 52 | 52 | 52 | 52 | 52 | 53 | 52 | 93 |  | 94 | 94 | 94 | 97 | 88 | 88 | 87 | 1576571
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 63 | 63 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 63 | 59 |  | 60 | 63 | 62 | 60 | 61 | 65 | 65 | 1545000
140 | Bhola 33 MW PP (Venture) | 17 | 19 | 15 | 16 | 15 | 16 | 15 | 14 | 15 | 15 | 14 | 14 | 19 | 19 | 18 | 16 | 21 | 26 |  | 26 | 26 | 27 | 25 | 22 | 24 | 23 | 446600
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 10 | [7 empty] | 0 | 27840
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 5 | [8 empty] | 7168
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 384 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 374 | 485 | 656 | 657 | 656 | 657 | 656 | 657 | 705 |  | 704 | 705 | 705 | 705 | 705 | 705 | 551 | 13012363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 370 | 330 | 310 | 300 | 300 | 320 | 320 | 330 | 340 | 300 | 300 | 320 | 330 | 330 | 310 | 300 | 330 | 440 |  | 470 | 470 | 470 | 470 | 450 | 410 | 390 | 9492200
149
150 | Barapukuria TPP Unit-1 | 83 | 83 | 83 | 83 | 82 | 82 | 79 | 81 | 80 | 80 | 80 | 80 | 82 | 80 | 80 | 80 | 80 | 78 |  | 79 | 78 | 78 | 79 | 79 | 79 | 77 | 1916945
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 133 | 132 | 133 | 134 | 133 | 131 | 134 | 130 | 135 | 133 | 133 |  | 134 | 133 | 134 | 134 | 133 | 133 | 135 | 3290200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 43 |  | 43 | 43 | [5 empty] | 94411
| Sirajgonj 6.55 MW Solar | [6 empty] | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | [10 empty] | 7260
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [23 empty] | 0 | 75 | 0 | 80500
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 195 | 194 | 192 | 193 | 195 | 197 | 198 | 206 | 180 | 175 | 183 | 199 | 206 | 178 | 167 | 168 | 192 | 200 |  | 181 | 182 | 182 | 188 | 179 | 174 | 178 | 4727736
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 214 | 207 | 207 | 204 | 204 | 204 | 201 | 200 | 194 | 192 | 209 | 208 | 208 | 191 | 164 | 163 | 185 | 210 |  | 201 | 184 | 185 | 190 | 189 | 162 | 172 | 4929591
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 346 | 346 | 346 | 346 | 400 | 330 | 305 | 284 | 335 | 403 | 394 | 393 | 350 | 388 | 357 | 411 | 318 |  | 358 | 363 | 356 | 353 | 359 | 337 | 302 | 8691491
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251400
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 34 |  | 50 | 50 | 50 |  |  |  | 0 | 152802
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [16 empty] | 9 | 35 |  | 35 | 35 | [5 empty] | 75584
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 14 | 52 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 52 |  | 52 | 52 | 52 | 52 | 24 |  | 0 | 534720
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 72 |  | 98 | 55 | 38 |  |  |  |  | 203620
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 0 |  |  | 0 | 5 | 87 | 111 | 113 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 35 | 90 |  | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 1469760
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 90 |  | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 1021920
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 35 | 80 | 105 |  | 105 | 105 | 105 | 105 | 75 | 34 | 34 | 1077753
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 30982
178
178