## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:October 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-10-01 |  | 2021-09-01 |  | 2020-10-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13482 | 2021-10-11 | 13509 | 2021-09-11 | 12759 | 2021-11-10 | 13792 | 2021-04-27
|  |  | 21:00 |  | 20:00 |  | 19:00 |  | 20:00
2 | Minimum Generation (MW) | 7486 | 2021-10-22 | 8491 | 2021-09-17 | 6045 | 23/10/20 | - | -
|  |  | 19:30 |  | 1:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13482 | 2021-10-11 | 13509 | 2021-09-11 | 12759 | 2020-10-11 | 13792 | 2021-04-27
|  |  | 21:00 |  | 20:00 |  | 19:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 11987 | 2021-10-14 | 11723 | 2021-09-05 | 10723 | 13/10/20 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13482 | 2021-10-11 | 13509 | 2021-09-11 | 12759 | 11'/10/20 | 14097 | 2021-04-27
|  |  | 21:00 |  | 20:00 |  | 19:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 12110.3871 |  | 12742.17 |  | 11755.29 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 10238.1935 |  | 10804.67 |  | 9551.77 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 733 | 2021-10-27 | 729 | 2021-09-26 | 933 | 28/10/2020 | 956 | 27/3/2019
|  |  | 22:00 |  | 3:30 |  | 15:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 160 | 2021-10-10 | 180 | 2021-09-05 | 178 | 14/10/2020 | 194 | 12/06/19
|  |  | 18:00 |  | 18:30 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 0 |  | 0 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1492.9513 |  | 1586.2 |  | 3604.39 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 83.4403 |  | 134.3 |  | 123.11
22 | Net Generation of BPDB (MKWH) | 1409.5109 |  | 1451.9 |  | 3481.28
23 | Net Generation of IPP (MKWH) | 5175.3075 |  | 5324.06 |  | 2428.85
24 | Net Generation of REB (MKWH) | 147.564 |  | 141.32 |  | 145.86
24 | Net Generation of Rental Power Plant (MKWH) | 437.4456 |  | 490.11 |  | 540.71
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7169.8281 |  | 7407.4 |  | 6596.69 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 4548.5962 |  | 4494.93 |  | 4215.06 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 480.4616 |  | 614.19 |  | 467.31 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1701.026 |  | 1887.48 |  | 1436.16 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 111.4727 |  | 104.88 |  | 85.06 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 20.1353 |  | 23.22 |  | 6.32 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 391.5767 |  | 417.01 |  | 509.89 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 617.2962 |  | 600.37 |  | 765.29 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 78.4655 |  | 81.01 |  | 78.85 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:October 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13482 | 2021-10-11 | 21:00
Generation Period
| Dhaka | MW | 4596
| Chattogram | MW | 1338
| Cumilla | MW | 1283
| Mymensingh | MW | 957
| Sylhet | MW | 572
a) | Total supply in East zone | MW | 8746
| Khulna | MW | 1592
| Barisal | MW | 402
| Rajshahi | MW | 1360
| Rangpur | MW | 737
b) | Total supply in West zone | MW | 4091
c) | Total supply in both zone ( a+b) | MW | 12837
Ref: | 27.21.0000.603.16.087.20.447 | Date: 18/10/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 620 | 2021-09-06 | 22:00
| b) Ishurdi end | MW | 272 | 2021-09-14 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 650 | 2021-09-15 | 12:00 |  |  | 1.7815
| b) Ishurdi end | MW | 240 | 2021-09-03 | 19:30
19 | Daily Maximum Energy Export through EWI/NO-1 | [6 empty] | 0 | Ghorashal
| a) Ghorashal end | MKWH | - | - |  |  |  | 0
| b) Ishurdi end | MKWH | - | - |  |  |  | 0
20 | Daily Maximum Energy Import through EWI/ NO-1 | [6 empty] | 0
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 24.09 |  |  |  |  | #REF! | Imp | Exp
| b) Ishurdi end | MKWH | 34.64 |  |  |  |  | #REF! | #REF! | 0
22 | Total Energy Import through EWI/ NO-1 | [6 empty] | #REF! | #REF! | 0
| a) Ghorashal end | MKWH | 33.61 |  |  |  |  | 0
| b) Ishurdi end | MKWH | 23.39 |  |  |  |  | 0
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  |  |  | 0 |  |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 | [6 empty] | 0 |  |  |  | 2.955
| a) Ashuganj end | MW | 410 | 2021-09-03 | 21:00 |  |  | 0
| b)Serajganj end | MW | 250 | 2021-09-14 | 10:00 |  |  |  | #REF! | 0
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 240 | 2021-09-14 | 10:00
| b)Sirajganj end | MW | 370 | 2021-09-03 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.002 | 2021-09-10 |  |  | 2366 | 4.732
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 3.954 | 2021-09-10 |  |  | 2370 | 4.74
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 60.18
| b)Sirajganj end | MKWH | 20.64
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 20.33
| b)Sirajganj end | MKWH | 60.82 |  |  |  |  | 132.822 | 132822000 | 0.01099 | 1.099
30 | Transmission loss of EWI /NO-2 | % | 0.181 |  |  |  |  | 134.298 | 134298000
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken | [7 empty] | 1.099 | 1476000 | 0.01099 | 1.099
from the calculation of GMD, PGCB, Ishwardi. | [8 empty] | 1.099
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken | [10 empty] | 420
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65 | 0.83636
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74 | 0.81127
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
| 2nd East-West Interconnector Loss: |  |  |  |  | 99387644.47
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578 |  | 96795991.85
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062 |  | 2308363.67
| Difference (-) : | 3516000 |  |  |  | 2239112.76
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV transformers T-1&T-2 | 2021-10-03 06:05 | 2021-10-03 06:45 | 0:40 | E/O | Due to 33 kV feeder fault | 88 | 58.6667 | Power interruption
Mymensingh | 132/33 kV transformers T-1&T-2 | 2021-10-06 17:59 | 2021-10-06 18:08 | 0:09 | E/O | Due to bursting of 33 kV feeder
| 132/33 kV transformers T-1 | 2021-10-17 09:08 | 2021-10-17 09:25 | 0:17 | T | Tripped showing O/C relay | 175 | 49.5833 | Power interruption 09:25 to 9:25
| 132/33 kV transformers T-2 | 2021-10-17 09:08 | 2021-10-17 09:26 | 0:18 | T
| 132/33 kV transformers T-3 | 2021-10-17 09:08 | 2021-10-17 09:36 | 0:28 | T
Sherpur | 132/33 kV transformers T-5 | 2021-10-17 17:30 | 2021-10-17 17:30 | 0:00 | T | Tripped showing O/C & E/F relay at 33 kV side | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformers T-3 | 2021-10-21 09:46 | 2021-10-21 17:50 | 8:04 | T | Tripped showing O/C& E/F relay | 30 | 242 | Power interruption
Cantonment | 132/33 kV transformers T-1 | 2021-10-31 16:19 | 2021-10-31 19:01 | 2:42 | T | Tripped showing buchholz relay at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 12:38 |  | Unserved Energy: |  | 350.25
Dhaka (South) Grid Circle :
Bhulta | Bhulta-Rampura 230 kV line-4 | 2021-10-01 13:04 | 2021-10-01 13:29 | 0:25 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Siddhirganj | 132/33 kV transformers T-1&T-2 | 2021-10-03 12:02 | 2021-10-03 12:24 | 0:22 | T | Tripped showing O/C relay | 60 | 22 | Power interruption
Bhulta | 132/33 kV transformer T-2 | 2021-10-06 06:45 | 2021-10-06 07:50 | 1:05 | E/O | Due to red-hot maint | 0 | 0 | No interruption | 0:00
Hasnabad | 33 kV Bus | 2021-10-14 12:54 | 2021-10-14 13:05 | 0:11 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Moghbazar | 132/33 kV transformer T-2 | 2021-10-17 14:31 | 2021-10-17 23:13 | 8:42 | T | Tripped showing E/F & O/C relay at 33 kV side | 0 | 0
Nawabganj | 132/33 kV transformer T-1 | 2021-10-17 15:23 | 2021-10-17 17:06 | 1:43 | E/O | Due to red-hot maint at 33 kV PBS feeder | 18 | 30.9 | Power interruption
Haripur | 230/132 kV transformer T-1 | 2021-10-23 07:18 | 2021-10-23 07:39 | 0:21 | T | Tripped showing lockout relay | 0 | 0 | No interruption
| 132 kV Breaker | 2021-10-25 09:31 | 2021-10-25 11:15 | 1:44 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 0:25 |  | Unserved Energy: |  | 52.9
Chattogram Grid Circle :
Chandraghona | 132/33 kV transformer T-2 | 2021-10-02 08:17 | 2021-10-02 10:17 | 2:00 | T | Tripped showing main protection relay | 0 | 0 | No interruption
GPH isat | 230/132 kV transformer T-1 | 2021-10-03 12:44 | 2021-10-03 12:44 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T-1 | 2021-10-13 06:10 | 2021-10-13 07:30 | 1:20 | E/O | Due to red-hot maint at 33 kV isolator | 0 | 0 | No interruption
Halishahar | 132/33 kV transformers T-1 & T2 | 2021-10-15 17:12 | 2021-10-15 17:49 | 0:37 | T | Due to bad weather | 46 | 28.3667 | Power interruption
Halishahar | 132/33 kV transformers T-1,&T-3 | 2021-10-21 21:45 | 2021-10-21 22:08 | 0:23 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformers T-2 | 2021-10-21 21:45 | 2021-10-21 22:19 | 0:34 | T |  | 64 | 36.2667 | Power interruption
|  |  | Total : | 4:54 |  | Unserved Energy: |  | 64.6333
Cumilla Grid Circle :
Cumilla(N) | 132/33 kV transformers T-3 | 2021-10-02 17:54 | 2021-10-02 18:26 | 0:32 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformers T-4 | 2021-10-02 17:54 | 2021-10-02 18:09 | 0:15 | T |  | 0 | 0 | No interruption
Comilla(S) | 132/33 kV transformers T-3 | 2021-10-06 08:57 | 2021-10-06 09:41 | 0:44 | E/O | Due to bursting of PT at 33 kV side | 36 | 26.4 | Power interruption
| 132/33 kV transformers T-4 | 2021-10-06 08:57 | 2021-10-06 16:28 | 7:31 | E/O
Shahjibazar | 132/33 kV transformer T-2 | 2021-10-13 16:03 | 2021-10-13 16:49 | 0:46 | T | Tripped showing E/F relay at 33 kV side | 30 | 23 | Power interruption
Biyanibazar | 132/33 kV transformers T-1 & T2 | 2021-10-15 07:00 | 2021-10-15 07:30 | 0:30 | T | Tripped showing E/F relay | 50 | 25 | Power interruption
Chowmuhani | 132/33 kV transformers T-2 | 2021-10-15 17:17 | 2021-10-15 17:26 | 0:09 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Dohazari | 132/33 kV transformers T-1 & T2 | 2021-10-15 16:21 | 2021-10-15 17:02 | 0:41 | T | Due to bad weather | 26 | 17.7667 | Power interruption
Cumilla(N) | 132/33 kV transformers T-3 | 2021-10-16 08:29 | 2021-10-16 10:11 | 1:42 | E/O | Due to red-hot maint at PBS Bus | 50 | 85 | Power interruption
| 132/33 kV transformers T-3 & T4 | 2021-10-16 15:58 | 2021-10-16 16:36 | 0:38 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T-2 | 2021-10-19 14:38 | 2021-10-19 15:55 | 1:17 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Feni | 132/33 kV transformer T-2 | 2021-10-20 14:47 | 2021-10-20 16:05 | 1:18 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T-1 & 33 kV Bus | 2021-10-21 06:35 | 2021-10-21 08:53 | 2:18 | E/O | Due to red-hot maint | 20 | 46 | Power interruption
|  |  | Total : | 18:21 |  |  |  | 223.1667
Khulna Grid Circle :
Barishal(N) | 230/132 kV transformer T-02 | 2021-10-01 21:50 | 2021-10-01 23:06 | 1:16 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Jhenaidah | 230/132 kV transformer T-2 | 2021-10-03 14:12 | 2021-10-03 15:25 | 1:13 | T | Tripped showing Diff. relay | 10 | 12.1667 | Power interruption
Patuakhali | 132/33 kV transformers T-1 | 2021-10-07 18:10 | 2021-10-07 18:22 | 0:12 | T | Tripped showing O/C & E/F relay | 46 | 9.2 | Power interruption
| 132/33 kV transformers T-2 | 2021-10-07 18:10 | 2021-10-07 20:36 | 2:26 | T
Goalpara | 132/33 kV transformer T-6 | 2021-10-11 12:52 | 2021-10-11 13:14 | 0:22 | T | Tripped showing Buchholz. relay | 26 | 9.5333 | Power interruption
| 132/33 kV transformer T-6 | 2021-10-12 08:20 | 2021-10-12 09:25 | 1:05 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Benapole | 132/33 kV transformers T-1 & T2 | 2021-10-17 21:36 | 2021-10-17 22:03 | 0:27 | T | Tripped showing E/F relay at 33 kV side | 50 | 22.5 | Power interruption
Shariatpur | 33 kV Bus-2 | 2021-10-22 08:29 | 2021-10-22 10:14 | 1:45 | E/O | Due to red-hot maint at 33 kV Bus | 10 | 15.8333 | Power interruption 08:29 to 10:04
Norail | 132/33 kV transformer T-1 | 2021-10-22 15:04 | 2021-10-22 16:00 | 0:56 | E/O | Due to red-hot maint at 33 kV Bus | 8 | 7.4667 | Power interruption
Bagerhat | 132/33 kV transformers T-1 | 2021-10-23 07:12 | 2021-10-23 13:21 | 6:09 | T | Due to red-hot maint |  |  | Power interruption
| 132/33 kV transformers T-2 | 2021-10-23 07:12 | 2021-10-23 11:16 | 4:04 | T |  | 20 | 123
Norail | 132/33 kV transformer T-2 | 2021-10-24 06:25 | 2021-10-24 08:35 | 2:10 | E/O | Due to red-hot maint at 33 kV Bus | 12 | 26 | Power interruption
Bagerhat | 132/33 kV transformer T-3 | 2021-10-29 22:48 | 2021-10-30 00:06 | 1:18 | E/O | Due to red-hot maint at 33 kV Bus | 45 | 58.5 | Power interruption
Gollamari | 132/33 kV transformers T-1 & T2 | 2021-10-30 15:58 | 2021-10-30 16:12 | 0:14 | E/O | Due to 33 kV feeder fault | 18 | 18 | Power interruption 15:58 to 16:58
|  |  | Total : | 23:37 |  | Unserved Energy: |  | 302.2
HVDC Grid Circle : Nil
|  |  | Total : | 0:00 |  |  |  | 0
Bogura Grid Circle:
Purbasadipur | 132/33 kV transformers T-2 | 2021-10-06 02:14 | 2021-10-06 03:20 | 1:06 | E/O |  | 45 | 75.75 | Power interruption 2:14 to 3:20
| 132/33 kV transformers T-3 | 2021-10-06 02:14 | 2021-10-06 03:55 | 1:41 | E/O | Due to fire occurred at capacitor bank
Palashbari | 132/33 kV transformers T-2 | 2021-10-08 09:10 | 2021-10-08 10:25 | 1:15 | E/O | Due to red-hot maint | 24 | 30 | Power interruption
Pabna | 132/33 kV transformer T-1 | 2021-10-13 15:51 | 2021-10-13 16:01 | 0:10 | T | Tripped showing E/F relay at 33 kV side | 5 | 0.83333 | Power interruption
Natore | 132/33 kV transformer T-4 | 2021-10-16 02:46 | 2021-10-16 03:24 | 0:38 | T | Due to bad weather | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T-3 | 2021-10-21 09:37 | 2021-10-21 09:52 | 0:15 | T | Tripped showing E/F relay at 33 kV side | 25 | 6.25 | Power interruption
| 132/33 kV transformer T-1 | 2021-10-22 07:02 | 2021-10-22 08:15 | 1:13 | E/O | Due to red-hot maint | 27 | 32.85 | Power interruption
Natore | 132/33 kV transformers T-1 & T2 | 2021-10-22 15:35 | 2021-10-22 16:32 | 0:57 | T | Tripped showing E/F relay at 33 kV side | 31 | 29.45 | Power interruption
|  |  | Total : | 7:15 |  |  |  | 175.1333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 67:10 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Lalbagh | Lalbagh-Kallyanpur 132 kkV Ckt-1 | 2021-10-02 06:05 | 2021-10-02 07:04 | 0:59 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Aminbazar | Aminbazar-Bosila 132 kV Ckt | 2021-10-03 10:44 | 2021-10-03 11:18 | 0:34 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
RPCL | RPCL-Tangail 132 kV Ckt-2 | 2021-10-03 12:32 | 2021-10-03 13:05 | 0:33 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2021-10-03 14:36 | 2021-10-03 14:38 | 0:02 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-1 | 2021-10-05 00:30 | 2021-10-05 00:42 | 0:12 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV Ckt-2 | 2021-10-09 17:40 | 2021-10-09 18:26 | 0:46 | T | Tripped showing remote.protection. relay. | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2021-10-10 12:58 | 2021-10-10 13:12 | 0:14 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV Ckt-1 | 2021-10-21 11:30 | 2021-10-21 11:44 | 0:14 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-1 | 2021-10-22 17:37 | 2021-10-22 17:48 | 0:11 | T | Tripped showing TCSR relay. | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV Ckt-1 | 2021-10-31 18:04 | 2021-10-31 22:28 | 4:24 | T | Tripped showing Diff.& E/F relay. | 0 | 0 | No interruption
|  |  | Total : | 4:24 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Haripur 230 kV Ckt-1 | 2021-10-01 13:04 | 2021-10-01 18:26 | 5:22 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-1 | 2021-10-01 18:38 | 2021-10-01 18:50 | 0:12 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur 360 MW Ckt-1 | 2021-10-03 15:02 | 2021-10-03 16:51 | 1:49 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV Ckt-1 | 2021-10-10 14:46 | 2021-10-10 15:10 | 0:24 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
| Bashundhara-Rampura 132 kV both Ckts | 2021-10-10 14:04 | 2021-10-10 14:18 | 0:14 | T |  | 85 | 19.8333 | Power interruption
| Bashundhara-Banani 132 kV Ckt | 2021-10-10 14:46 | 2021-10-10 15:11 | 0:25 | T | Tripped showing Dist. Z1 relay | 44 | 18.3333 | Power interruption
Fatulla | Fatulla-Shyampur(N) 132 kV Ckt-2 | 2021-10-13 15:41 | 2021-10-13 15:50 | 0:09 | T | Tripped showing Dist.& O/C relay | 0 | 0 | No interruption
| Fatulla-Brahmangaon P/S 132 kV Ckt | 2021-10-13 14:22 | 2021-10-13 16:14 | 1:52 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 | 2021-10-18 14:36 | 2021-10-18 14:54 | 0:18 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-1 | 2021-10-27 16:46 | 2021-10-27 16:46 | 0:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Shyampur | Shyampur-Fatulla-132 kV Ckt-1 | 2021-10-27 18:07 | 2021-10-27 18:26 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Madanganj | Madanganj-Char saidpur 132 kV Ckt-2 | 2021-10-28 09:30 | 2021-10-28 20:52 | 11:22 | T | Tripped showing O/C & E/F. relay |  |  | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 | 2021-10-30 13:50 | 2021-10-30 19:02 | 5:12 | T | Tripped showing Diff.& E/F relay | 0 | 0 | No interruption
|  |  | Total : | 27:38 |  | Unserved Energy: |  | 38.1667
Chattogram Grid Circle :
AKMS | AKMS-Hathazari 230 kV Ckt | 2021-10-02 08:30 | 2021-10-02 08:37 | 0:07 | E/O | Due to CB spring discharge | 0 | 0 | No interruption
Hathazari | Hathazari-Abul Khair 230 kV Ckt-1 | 2021-10-05 12:25 | 2021-10-05 13:59 | 1:34 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV Ckt-2 | 2021-10-06 06:23 | 2021-10-06 07:18 | 0:55 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV Ckt-2 | 2021-10-08 04:10 | 2021-10-08 07:18 | 3:08 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Rangamati | Rangamati -Khagrachari132 kV Ckt-1 | 2021-10-08 05:43 | 2021-10-08 05:43 |  | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2021-10-08 12:32 | 2021-10-08 14:50 | 2:18 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-2 | 2021-10-12 12:53 | 2021-10-12 13:09 | 0:16 | T | Tripped showing Dist. relay | 30 | 8 | Power interruption
| Dohazari-Cox's Bazar 132 kV Ckt-2 | 2021-10-12 01:56 | 2021-10-12 02:24 | 0:28 | T |  | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV Ckt-1 | 2021-10-15 16:38 | 2021-10-15 16:59 | 0:21 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV Ckt | 2021-10-15 17:11 | 2021-10-15 17:38 | 0:27 | T |  | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-intermediate 230 kV Ckt | 2021-10-15 17:42 | 2021-10-15 18:01 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-1 | 2021-10-16 10:47 | 2021-10-16 11:03 | 0:16 | T | Tripped showing Dist.& E/F relay | 0 | 0 | No interruption
Rangamati | Rangamati -Khagrachari132 kV Ckt-2 | 2021-10-20 06:35 | 2021-10-20 06:50 | 0:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV both Ckts | 2021-10-20 18:28 | 2021-10-20 18:43 | 0:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
T.K.chemical | T.K.chemical-Sikalbaha (N) 132 kV Ckt | 2021-10-27 12:16 | 2021-10-27 12:30 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
BSRM | BSRM-Abul Khair 230 kV Ckt | 2021-10-30 13:19 | 2021-10-30 22:47 | 9:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 20:21 |  | Unserved Energy: |  | 8
Cumilla Grid Circle :
Fenchuganj | Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-3 | 2021-10-02 03:55 | 2021-10-02 05:16 | 1:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-2 | 2021-10-02 05:05 | 2021-10-02 05:15 | 0:10 | T | Tripped showing Dist.A .relay | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV Ckt | 2021-10-03 10:07 | 2021-10-03 10:18 | 0:11 | T | Tripped showing Dist.B-phase .relay | 19 | 3.4833 | Power interruption
Sylhet | Sylhet-Chatak 132 kV Ckt-1 | 2021-10-03 10:34 | 2021-10-03 12:39 | 2:05 | T | Tripped showing Dist. relay | 10 | 20.8333 | Power interruption
Cumilla(N) | Cumilla(N)-Megnaghat 230 Ckt-1 | 2021-10-05 12:24 | 2021-10-05 12:50 | 0:26 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-10-08 00:35 | 2021-10-08 00:50 | 0:15 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-2 | 2021-10-10 10:31 | 2021-10-10 14:49 | 4:18 | E/O | Due to DC ground fault at Bteaker | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-10-11 19:16 | 2021-10-11 19:46 | 0:30 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-10-12 18:33 | 2021-10-12 18:33 | 0:00 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt-2 | 2021-10-13 06:04 | 2021-10-13 07:38 | 1:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV Ckt-2 | 2021-10-13 04:56 | 2021-10-13 06:18 | 1:22 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-10-13 23:53 | 2021-10-14 00:09 | 0:16 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-10-14 12:59 | 2021-10-14 13:05 | 0:06 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-10-15 05:15 | 2021-10-15 06:12 | 0:57 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-10-16 12:05 | 2021-10-16 19:59 | 7:54 | T |  | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-10-16 20:06 | 2021-10-16 20:09 | 0:03 | T |  | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-10-16 21:53 | 2021-10-16 22:21 | 0:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 & 2 | 2021-10-17 22:04 | 2021-10-17 22:17 | 0:13 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV Ckt-2 | 2021-10-30 06:22 | 2021-10-30 06:22 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2021-10-30 15:41 | 2021-10-30 16:09 | 0:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 22:37 |  | Unserved Energy: |  | 24.3167
Khulna Grid Circle :
Barisal | Barisal-Bhola 230 kV Ckt-2 | 2021-10-03 13:55 | 2021-10-03 14:26 | 0:31 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2021-10-03 17:33 | 2021-10-03 17:39 | 0:06 | T | Tripped showing Dist. relay | 45 | 4.5 | Power interruption
| Barisal-Bhola 230 kV Ckt-1 | 2021-10-11 10:42 | 2021-10-11 17:12 | 6:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bhola | Bhola-Barishal (N) kV 230 kV Ckts-1 | 2021-10-15 09:26 | 2021-10-15 20:12 | 10:46 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Bhola-Barishal (N) kV 230 kV Ckts-2 | 2021-10-15 09:26 | 2021-10-15 20:21 | 10:55 | T |  | 0 | 0 | No interruption
Gopalganj (N) | Gopalganj (N)-Madaripur 132 kV Ckt-3 | 2021-10-27 23:51 | 2021-10-28 00:32 | 0:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Gopalganj (N)-Madaripur 132 kV Ckt-4 | 2021-10-27 23:51 | 2021-10-28 00:19 | 0:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Gopalganj (N)-Faridpur 132 kV Ckt | 2021-10-27 23:51 | 2021-10-28 00:29 | 0:38 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Gopalganj (N)-Gopalganj (O) 132 kV Ckt-1 | 2021-10-27 23:55 | 2021-10-28 00:47 | 0:52 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Gopalganj (N)-Gopalganj (O) 132 kV Ckt-2 | 2021-10-27 23:55 | 2021-10-28 00:58 | 1:03 | T |  | 0 | 0 | No interruption
|  |  | Total : | 32:30 |  | Unserved Energy: |  | 4.5
HVDC Grid Circle :
Bheramara | Bheramara-Bharampur 400 kV Ckt-3 | 2021-10-15 11:34 | 2021-10-15 11:40 | 0:06 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:06 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Sherpur | Sherpur(Bogura) 33 kV full Bus | 2021-10-02 08:30 | 2021-10-02 10:40 | 2:10 | E/O | Due to red hot maint | 40 | 86.6667 | Power interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV Ckt-1 | 2021-10-03 06:46 | 2021-10-03 07:27 | 0:41 | T | Tripped showing Dist.C-phase relay | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-1 | 2021-10-03 09:56 | 2021-10-03 12:34 | 2:38 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| Natore-Bogura 132 kV line-1 | 2021-10-03 15:33 | 2021-10-03 15:43 | 0:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Sherpur(Bogura) | Sherpur(Bogura) -Bogura(O)132 kV Ckt-1 | 2021-10-04 08:28 | 2021-10-04 09:08 | 0:40 | E/O | Due to PT burst | 42 | 28 | Power interruption
Thakurgaon | Thakurgaon-Thakurgaon P.P &132 kV Ckts | 2021-10-20 08:34 | 2021-10-20 09:16 | 0:42 | T | Due to bad weather | 59 | 41.3 | Power interruption
| Thakurgaon-Panchuagar 132 kV Ckt | 2021-10-20 08:34 | 2021-10-20 09:16 | 0:42 | T
Rangpur | Rangpur-Lalmonirhat 132 kV Ckt | 2021-10-27 07:51 | 2021-10-27 10:40 | 2:49 | T | Tripped showing Dist. Z1 relay | 30 | 84.5 | No interruption
|  |  | Total : | 10:32 |  | Unserved Energy: |  | 240.4667
Others :
Maniknagar | Maniknagar-Narinda 132 kV Ckt-2 | 2021-10-18 07:17 | 2021-10-18 07:17 | 0:00 | T | Tripped showing main pro.& Pilot wire prot.relay | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 118:08 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: October2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka | 132/33 kV transformer T-1 | 2021-10-01 08:31 | 2021-10-01 12:32 | 4:01 | S/O | Due to C/M work | 50 | 200.8333 | Power interruption
Aminbazar | 230/132 kV transformer T-01 | 2021-10-03 10:02 | 2021-10-03 17:20 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2021-10-04 09:37 | 2021-10-04 10:52 | 1:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-10-04 10:56 | 2021-10-04 12:00 | 1:04 | S/O
Kabirpur | 132/33 kV transformer T2 | 2021-10-04 12:45 | 2021-10-04 17:47 | 5:02 | S/O | Due to A/M work | 10 | 50.3333 | Power interruption
Manikganj | 132 kV main bus-1 | 2021-10-04 08:46 | 2021-10-04 14:38 | 5:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-3 | 2021-10-04 08:29 | 2021-10-04 10:43 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-1 | 2021-10-04 10:17 | 2021-10-04 15:02 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV main bus-A | 2021-10-04 10:17 | 2021-10-04 15:35 | 5:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-10-06 07:34 | 2021-10-06 10:32 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-2 | 2021-10-06 06:45 | 2021-10-06 07:50 | 1:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-01 | 2021-10-07 09:28 | 2021-10-07 15:30 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2021-10-07 08:11 | 2021-10-07 20:03 | 11:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-2 | 2021-10-07 09:06 | 2021-10-07 10:17 | 1:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 | 2021-10-08 08:30 | 2021-10-08 17:13 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-10-09 08:55 | 2021-10-09 17:35 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-10-10 09:49 | 2021-10-10 16:36 | 6:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | 132 kV bus coupler | 2021-10-11 10:15 | 2021-10-11 11:55 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2021-10-12 09:20 | 2021-10-12 17:15 | 7:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 400/132 kV transformer ATR-03 | 2021-10-14 09:00 | 2021-10-14 09:00 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-3 | 2021-10-14 08:25 | 2021-10-14 22:30 | 14:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-10-15 00:10 | 2021-10-15 12:55 | 12:45 | S/O | Due to abnormal sound of 132 kV R-phase CT | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-10-15 15:10 | 2021-10-15 17:40 | 2:30 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-10-15 18:38 | 2021-10-15 18:38 | 0:00 | S/O |  | 0 | 0 | No interruption
Aminbazar | 400/230 kV transformer AT-02 | 2021-10-16 09:33 | 2021-10-16 09:33 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 | 2021-10-16 11:28 | 2021-10-16 14:49 | 3:21 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-10-16 09:45 | 2021-10-16 11:18 | 1:33 | S/O |  | 0 | 0 | No interruption
Sherur | 132/33 kV transformer T-1 | 2021-10-16 08:54 | 2021-10-16 16:54 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2021-10-16 09:36 | 2021-10-16 16:14 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2021-10-17 08:28 | 2021-10-17 17:16 | 8:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-3 | 2021-10-17 22:06 | 2021-10-17 23:34 | 1:28 | S/O | Due to loop changing | 45 | 66 | Power interruption
Sherur | 132/33 kV transformer T-1 | 2021-10-18 08:45 | 2021-10-18 16:29 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-10-19 09:36 | 2021-10-19 15:45 | 6:09 | S/O |  | 0 | 0 | No interruption
Sherur | 132/33 kV transformers T-1 | 2021-10-20 08:27 | 2021-10-20 13:28 | 5:01 | S/O | Due to D/W work
| 132/33 kV transformer T-2 | 2021-10-20 08:27 | 2021-10-20 13:29 | 5:02 |  |  | 35 | 176.1667 | Power interruption
Kaliakoir | 400 kV Bus | 2021-10-21 11:34 | 2021-10-21 12:12 | 0:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-10-23 09:42 | 2021-10-23 17:38 | 7:56 | S/O | Due to installation work at 33 kV side | 0 | 0 | No interruption
Sherur | 132/33 kV transformer T-2 | 2021-10-24 09:10 | 2021-10-24 15:01 | 5:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus | 2021-10-25 12:07 | 2021-10-25 14:54 | 2:47 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sherur | 132/33 kV transformer T-2 | 2021-10-25 09:06 | 2021-10-25 16:27 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-10-26 08:50 | 2021-10-26 16:21 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 400/132 kV transformer ATR-3 | 2021-10-27 09:47 | 2021-10-27 16:06 | 6:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2021-10-27 07:40 | 2021-10-27 17:22 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 400/132 kV transformer ATR-2 | 2021-10-27 16:29 | 2021-10-27 16:29 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2021-10-28 07:45 | 2021-10-28 07:45 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformers T-1 | 2021-10-28 09:59 | 2021-10-28 10:09 | 0:10 | S/O | Due to D/W work | 10 | 1.6667 | Power interruption
| 132/33 kV transformers T-1 | 2021-10-28 10:30 | 2021-10-28 10:38 | 0:08
Sherur | 132/33 kV transformer T-3 | 2021-10-30 08:51 | 2021-10-30 16:50 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-10-31 08:35 | 2021-10-31 16:39 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 241:12 |  | Unserved Energy: |  | 495
Dhaka (South) Grid Circle :
Madanganj | 132 kV main Bus-1 | 2021-10-02 12:38 | 2021-10-02 13:54 | 1:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | 132/33 kV transformer T1 | 2021-10-04 08:27 | 2021-10-04 09:54 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Fatullah | 132/33 kV transformer GT1 | 2021-10-10 09:42 | 2021-10-10 17:40 | 7:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T1 | 2021-10-19 12:29 | 2021-10-19 13:49 | 1:20 | S/O | Due to high temperature | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-19 13:50 | 2021-10-19 17:04 | 3:14 | S/O |  | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformers T-02 |  | 2021-10-21 20:06 |  | S/O | After maint.work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T3 | 2021-10-23 20:28 | 2021-10-23 21:08 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-10-24 07:58 | 2021-10-24 07:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T1 | 2021-10-29 09:41 | 2021-10-29 11:35 | 1:54 | S/O | Due to C/M work | 0 | 0
Shyampur (O) | 132/33 kV transformer T4 | 2021-10-30 09:06 | 2021-10-30 09:06 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 17:49 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Bakulia | 132/33 kv transformer T-3 |  | 2021-10-04 15:30 |  | S/O | After maintenance work | 0 | 0 | Power interruption
Khagrachari | 132/33 kV transformer T-1 | 2021-10-05 10:01 | 2021-10-05 13:41 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirsharai | 230/132 kV transformer T02 | 2021-10-09 11:55 | 2021-10-09 13:10 | 1:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2021-10-09 13:27 | 2021-10-09 13:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
j) GPH Ispat | 230/132 kV transformer T02 | 2021-10-10 13:03 | 2021-10-10 17:56 | 4:53 | S/O | for safey work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2021-10-14 06:27 | 2021-10-14 06:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | Power interruption
Dohazari | 132/33 kV transformer T2 | 2021-10-14 10:02 | 2021-10-14 11:48 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Barulia | 132 kV main Bus | 2021-10-16 07:22 | 2021-10-16 07:22 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | 132/33 kV transformer T1 | 2021-10-19 09:49 | 2021-10-19 11:54 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-20 10:30 | 2021-10-20 11:30 | 1:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T2 | 2021-10-22 07:26 | 2021-10-22 07:26 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-10-22 12:20 | 2021-10-22 16:28 | 4:08 | S/O | Due to D/W work | 5 | 20.6667 | Power interruption
j) GPH Ispat | 230/132 kV transformers T1 & T2 | 2021-10-23 08:28 | 2021-10-23 12:38 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T1 | 2021-10-25 06:15 | 2021-10-25 07:53 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | 132/33 kV transformer T1 | 2021-10-28 12:38 | 2021-10-28 13:37 | 0:59 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-28 09:58 | 2021-10-28 12:30 | 2:32 | S/O |  | 0 | 0 | No interruption
Sikalbaha | 230/132 kV transformer T01 | 2021-10-29 10:13 | 2021-10-29 13:47 | 3:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2021-10-29 14:21 | 2021-10-29 17:03 | 2:42 | S/O | Due to D/W work | 0 | 0
Halishahar | 132/33 kV transformer T1 | 2021-10-30 07:17 | 2021-10-30 07:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 34:22 |  | Unserved Energy : |  | 20.6667
Cumilla Grid Circle :
Kulaura | 132/33 kV transformer T-1 | 2021-10-05 13:32 | 2021-10-05 14:26 | 0:54 | S/O | Due to C/M work | 20 | 18 | Power interruption
Chowmuhani | 33 kV Bus | 2021-10-07 19:52 | 2021-10-07 20:26 | 0:34 | S/O | Due to C/M work | 50 | 28.3333 | Power interruption
Shajibazar | 132/33 kV transformer T2 | 2021-10-09 09:02 | 2021-10-09 17:03 | 8:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer T2 with 33 kV bus-2 | 2021-10-15 06:53 | 2021-10-15 06:58 | 0:05 | S/O | Due to C/M work | 35 | 2.9167 | Power interruption
Mohastanghor | 132/33 kV transformer T2 | 2021-10-09 09:02 | 2021-10-09 17:03 | 8:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus coupler | 2021-10-22 09:17 | 2021-10-22 12:08 | 2:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformers T1 | 2021-10-22 08:24 | 2021-10-22 11:47 | 3:23 | S/O | Due to C/M work | 0 | 0 | Power interruption 08:24 to 11:35
| 132/33 kV transformers T2 | 2021-10-22 08:24 | 2021-10-22 11:35 | 3:11 | S/O |  | 35 | 111.4167
B.Baria | 132/33 kV transformer T1 | 2021-10-23 07:14 | 2021-10-23 17:48 | 10:34 | S/O | Due to C/M work | 25 | 94.1667 | Power interruption 07:14 to 11:00
Cumilla (S) | 132/33 kV transformer T1 | 2021-10-24 01:30 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T1 | 2021-10-25 08:30 | 2021-10-25 13:29 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-25 14:40 | 2021-10-25 17:22 | 2:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T3 | 2021-10-26 08:46 | 2021-10-26 11:02 | 2:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-26 11:02 | 2021-10-26 13:12 | 2:10 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2021-10-26 11:30 | 2021-10-26 14:01 | 2:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirshari | 230/132 kV transformer T2 | 2021-10-27 11:33 | 2021-10-27 15:25 |  | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T2 | 2021-10-27 16:12 |  |  | S/O | Due to auxiliary supply problem | 0 | 0 | No interruption
| 230 kV bus-1 | 2021-10-28 14:43 | 2021-10-28 16:57 | 3:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformers T2 & T3 | 2021-10-29 08:20 | 2021-10-29 11:52 | 3:32 | S/O | Due to D/W work | 20 | 70.6667 | No interruption
Beanibazar | 132/33 kV transformer T1 | 2021-10-30 09:27 | 2021-10-30 14:25 | 4:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirshari | 230/132 kV transformer T1 |  | 2021-10-30 12:36 |  | S/O | After maint.work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer T2 | 2021-10-30 14:40 | 2021-10-30 16:58 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T1 | 2021-10-31 07:14 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T3 | 2021-10-31 11:50 | 2021-10-31 11:58 | 0:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformers T1 | 2021-10-31 09:20 | 2021-10-31 11:49 | 2:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-31 11:52 | 2021-10-31 13:52 | 2:00 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 45:15 |  | Unserved Energy : |  | 325.5
Khulna Grid Circle :
Bagerhat | 132/33 kV transformer T1 | 2021-10-01 07:36 | 2021-10-01 08:19 | 0:43 | S/O | Due to C/M work | 14 | 10.0333 | Power interruption
Shariatpur | 132/33 kV transformer T2 | 2021-10-01 08:36 | 2021-10-01 10:06 | 1:30 | S/O | Due to C/M work | 15 | 22.5 | Power interruption
Noapara | 33 kV Bus | 2021-10-04 07:28 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(N) | 230/132 kV transformer T-01 | 2021-10-05 14:42 | 2021-10-05 16:14 | 1:32 | S/O | Due to protection test | 0 | 0 | No interruption
| 230/132 kV transformer T-02 | 2021-10-05 16:22 | 2021-10-05 16:54 | 0:32 | S/O |  | 0 | 0 | No interruption
Bhola | 230/111 kV transformer T-01 | 2021-10-07 15:07 | 2021-10-07 16:38 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | 230/111 kV auxiliary transformer | 2021-10-08 10:35 | 2021-10-08 12:00 | 1:25 | S/O | Due to internal work | 0 | 0 | No interruption
Satkhira | 132 kV full Bus | 2021-10-09 07:04 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T1 | 2021-10-09 07:37 |  |  | S/O | Due to A/M work | 0 | 0
Goalpara | 132/33 kV transformer T6 | 2021-10-09 10:48 | 2021-10-09 12:22 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T4 | 2021-10-09 11:43 | 2021-10-09 12:32 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T1 | 2021-10-10 08:25 | 2021-10-10 16:47 | 8:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T5 | 2021-10-11 07:14 |  |  | S/O | Due to A/M work | 0 | 0
| 132/33 kV transformer T5 | 2021-10-12 08:23 | 2021-10-12 16:56 | 8:33 | S/O | Due to A/M work | 0 | 0
Shariatpur | 132/33 kV transformer T2 | 2021-10-12 08:36 | 2021-10-12 16:16 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus | 2021-10-13 11:10 | 2021-10-13 17:21 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 | 2021-10-14 08:55 | 2021-10-14 09:24 | 0:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-10-14 09:38 | 2021-10-14 14:40 | 5:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | 132/33 kV transformer T2 & 33 kV Bus | 2021-10-15 07:12 |  |  | S/O | Due to C/M work | 40 | 0 | Power interruption
Gopalganj | 132/33 kV transformer T3 | 2021-10-17 07:03 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T4 | 2021-10-17 07:44 |  |  | S/O | Due to A/M work | 0 | 0
Barishal(N) | 132/33 kV transformer T5 | 2021-10-18 08:36 | 2021-10-18 10:39 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T1 | 2021-10-18 08:46 | 2021-10-18 17:20 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T2 | 2021-10-18 08:06 | 2021-10-18 14:04 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T2 | 2021-10-19 08:10 | 2021-10-19 09:25 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T3 | 2021-10-20 07:41 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T6 | 2021-10-20 16:50 | 2021-10-20 17:24 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T2 | 2021-10-21 07:25 |  |  | S/O | Due to A/M work | 0 | 0
Noapara | 132/33 kV transformer T1 | 2021-10-22 08:12 | 2021-10-22 12:35 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Barguna | 132/33 kV transformer T1 | 2021-10-23 08:13 | 2021-10-23 17:51 | 9:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-10-23 08:21 | 2021-10-23 15:02 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T5 | 2021-10-23 12:21 | 2021-10-23 13:45 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Barguna | 132/33 kV transformer T2 | 2021-10-25 08:12 | 2021-10-25 16:36 | 8:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T2 | 2021-10-25 08:24 | 2021-10-25 12:40 | 4:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformersT1 & T3 | 2021-10-27 06:53 | 2021-10-27 09:01 | 2:08 | S/O | Due to A/M work | 20 | 42.6667 | Power interruption
Noapara | 132/33 kV transformer T4 | 2021-10-27 08:46 | 2021-10-27 13:13 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV transformer T4 | 2021-10-28 09:39 | 2021-10-28 11:42 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132 kV capacitor Bank | 2021-10-28 08:09 | 2021-10-28 18:45 | 10:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T4 | 2021-10-28 08:19 | 2021-10-28 12:47 | 4:28 | S/O | Due to A/M work | 0 | 0
Banapole | 132/33 kV transformer T1 | 2021-10-29 09:32 | 2021-10-29 16:06 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T1 | 2021-10-30 07:18 |  |  | S/O | Due to A/M work | 0 | 0
Benapol | 132/33 kV transformer T1 | 2021-10-30 09:06 | 2021-10-30 15:20 | 6:14 | S/O | Due to A/M work | 0 | 0
Bhandaria | 132/33 kV transformer T1 | 2021-10-30 09:32 | 2021-10-30 10:52 | 1:20 | S/O | Due to C/M work | 5 | 6.6667 | Power interruption
Panchagarh | 132/33 kV transformer T2 | 2021-10-30 08:15 | 2021-10-30 16:15 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 144:53 |  | Unserved Energy : |  | 81.8667
HVDC Grid Circle
Ishurdi | 132/33 kV transformer T1 | 2021-10-04 09:45 | 2021-10-04 12:45 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | HVDC pole-2 | 2021-10-06 13:40 | 2021-10-06 13:48 | 6:05 | S/O | Due to C/M work | 0 | 0 | No interruption
b) HVDC Bheramara | HVDC Bheramara-400 kV filter 10CF26 | 2021-10-10 08:28 | 2021-10-10 16:45 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara20DF11 230 kV filter | 2021-10-11 08:25 | 2021-10-11 17:04 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC pole-2 | 2021-10-11 11:32 | 2021-10-11 17:15 | 5:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara 230 kV 20DF31 filter | 2021-10-12 08:00 | 2021-10-12 16:26 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara-20DF12 kV filter | 2021-10-13 08:18 | 2021-10-13 15:49 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara-20DF32 kV filter | 2021-10-14 08:18 | 2021-10-14 16:42 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T2 | 2021-10-16 08:21 | 2021-10-16 09:10 | 0:49 | S/O | Due to isolator maint.at 33 kV PBS feeder | 15 | 12.25 | Power interruption
| 132/33 kV transformer T1 & 33 kV Bus | 2021-10-19 21:22 | 2021-10-19 21:48 | 0:18 | S/O | Due to C/M work | 31 | 9.3 | Power interruption
| HVDC Bheramara-400 kV 10DCF42 kV filter | 2021-10-26 07:27 | 2021-10-26 10:05 | 7:06 | S/O |  | 0 | 0 | No interruption
HVDC Bheramara | b) HVDC Bheramara-230 kV filter 20df13 | 2021-10-27 10:32 | 2021-10-27 12:55 | 2:23 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 66:41 |  | Unserved Energy : |  | 21.55
Bogura Grid Circle:
Lalmonirhat | 132/33 kV transformer T2 | 2021-10-02 08:15 | 2021-10-02 15:55 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T3 | 2021-10-02 09:20 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformers T3 & T4 | 2021-10-02 14:47 | 2021-10-02 15:25 | 0:38 | S/O | Due to C/M work | 40 | 25.3333 | Power interruption
Niyamatpur | 132/33 kV transformer T2 | 2021-10-03 07:41 | 2021-10-03 08:10 | 0:29 | S/O | Due to C/M work | 8 | 3.8667 | Power interruption
Bogura | 230/132 kV transformer T01 | 2021-10-03 08:16 | 2021-10-03 17:21 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV transformer T2 | 2021-10-03 08:25 | 2021-10-03 14:30 |  |  |  | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T01 | 2021-10-04 08:25 | 2021-10-04 15:55 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T3 |  | 2021-10-04 14:53 |  |  | After maintenance | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-10-04 15:10 |  |  | S/O | Due to CT change | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T2 | 2021-10-04 16:16 | 2021-10-04 17:50 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV transformer T3 | 2021-10-05 08:20 | 2021-10-05 15:45 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T02 | 2021-10-05 08:19 | 2021-10-05 16:35 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T1 | 2021-10-06 08:22 | 2021-10-06 15:26 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T2 | 2021-10-06 13:07 | 2021-10-06 13:25 | 0:18 | S/O | Due to 33 kV maint. By NESCO | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T02 | 2021-10-06 08:27 | 2021-10-06 15:33 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T03 | 2021-10-07 08:15 | 2021-10-07 15:25 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T2 | 2021-10-07 08:10 | 2021-10-07 15:30 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV transformer T1 | 2021-10-07 12:30 | 2021-10-07 14:35 | 2:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-07 15:15 | 2021-10-07 17:15 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T2 | 2021-10-09 07:20 | 2021-10-09 09:18 | 1:58 | S/O | Due to C/M work | 6 | 11.8 | Power interruption
Palashbari | 132/33 kV transformer T1 | 2021-10-09 08:10 | 2021-10-09 15:11 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T03 | 2021-10-09 08:20 | 2021-10-09 14:18 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T2 | 2021-10-09 11:02 | 2021-10-09 11:45 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T2 | 2021-10-10 08:10 | 2021-10-10 14:15 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T4 |  | 2021-10-10 16:38 |  | S/O | After main.work | 0 | 0 | No interruption
Natore | 132/33 kV transformers T1 & T2 | 2021-10-11 06:16 | 2021-10-11 07:35 | 1:19 | S/O | Due to A/M work | 47 | 61.8833 | Power interruption
Palashbari | 132/33 kV transformer T3 | 2021-10-11 08:05 | 2021-10-11 14:15 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T3 | 2021-10-11 09:15 | 2021-10-11 18:18 | 9:03 | S/O | Due to A/M work at 33 kV side | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T3 | 2021-10-12 08:14 | 2021-10-12 14:45 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 | 2021-10-13 08:20 | 2021-10-13 12:56 | 4:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T4 | 2021-10-13 08:10 | 2021-10-13 14:25 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T1 | 2021-10-13 08:21 | 2021-10-13 16:28 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T2 | 2021-10-14 08:21 | 2021-10-14 08:39 | 0:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T4 | 2021-10-14 08:17 | 2021-10-14 14:10 | 5:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T2 | 2021-10-14 09:14 | 2021-10-14 15:11 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T1 | 2021-10-16 08:15 | 2021-10-16 16:21 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T3 | 2021-10-16 08:50 | 2021-10-16 16:10 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T3 | 2021-10-17 07:24 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T1 | 2021-10-17 08:11 | 2021-10-17 15:09 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T4 | 2021-10-17 08:20 | 2021-10-17 15:35 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T1 | 2021-10-17 08:25 | 2021-10-17 15:40 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T2 | 2021-10-18 10:57 | 2021-10-18 11:39 | 0:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T1 | 2021-10-18 08:35 | 2021-10-18 15:45 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T3 | 2021-10-19 08:30 | 2021-10-19 10:05 | 1:35 | S/O | Due to C/M work | 20 | 31.6667 | Power interruption
Saidpur | 132/33 kV transformer T5 |  | 2021-10-19 22:30 |  |  | After main.work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T2 | 2021-10-21 08:34 | 2021-10-21 15:25 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T2 | 2021-10-21 08:14 | 2021-10-21 15:25 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T3 | 2021-10-21 08:15 | 2021-10-21 15:28 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T1 | 2021-10-21 09:40 | 2021-10-21 15:20 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T1 | 2021-10-22 09:15 | 2021-10-22 14:10 | 4:55 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-10-22 14:17 | 2021-10-22 16:25 | 2:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T4 | 2021-10-23 07:26 | 2021-10-23 08:48 | 1:22 | S/O | Due to C/M work | 15 | 20.5 | Power interruption
C.nawabganj | 132/33 kV transformer T3 | 2021-10-23 11:28 | 2021-10-23 12:26 | 0:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T2 | 2021-10-23 08:56 | 2021-10-23 16:34 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Mohastanghor | 132/33 kV transformer T2 | 2021-10-23 09:32 | 2021-10-23 15:01 | 5:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T1 | 2021-10-23 08:25 | 2021-10-23 14:22 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T3 | 2021-10-23 08:30 | 2021-10-23 13:44 | 5:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Mohastanghor | 132/33 kV transformer T1 | 2021-10-23 15:02 | 2021-10-23 16:57 | 1:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T4 | 2021-10-24 08:06 | 2021-10-24 15:15 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T4 | 2021-10-24 08:29 | 2021-10-24 14:05 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T1 | 2021-10-24 08:16 | 2021-10-24 15:07 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T3 | 2021-10-24 08:45 | 2021-10-24 17:32 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-10-25 12:30 | 2021-10-25 14:30 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T1 | 2021-10-26 08:20 | 2021-10-26 16:40 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Jaldhaka | 132 kV Bus-A | 2021-10-26 09:26 | 2021-10-26 16:00 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T3 | 2021-10-26 11:39 | 2021-10-26 13:45 | 2:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T2 | 2021-10-26 08:13 | 2021-10-26 16:39 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T1 | 2021-10-27 08:18 | 2021-10-27 15:05 | 6:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T1 | 2021-10-28 08:17 | 2021-10-28 16:56 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T2 | 2021-10-28 08:10 | 2021-10-28 15:04 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchagar | 132/33 kV transformer T1 | 2021-10-28 08:06 | 2021-10-28 17:50 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T1 | 2021-10-29 08:34 | 2021-10-29 15:07 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T2 | 2021-10-30 08:22 | 2021-10-30 15:10 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T2 | 2021-10-30 08:42 | 2021-10-30 16:18 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T3 | 2021-10-30 12:40 | 2021-10-30 14:16 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(O) | 132 kV main Bus | 2021-10-31 07:01 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T2 | 2021-10-31 09:12 | 2021-10-31 16:17 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T3 | 2021-10-31 08:14 | 2021-10-31 17:26 | 9:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Palshbari | 132/33 kV transformer T2 & 33 kV Bus | 2021-10-31 10:10 | 2021-10-31 15:30 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchagarh | 132/33 kV transformer T2 | 2021-10-31 08:13 | 2021-10-31 16:01 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 400:17 |  | Unserved Energy : |  | 155.05
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 950:29 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-10-01 09:05 | 2021-10-01 17:25 | 8:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-10-02 07:24 | 2021-10-02 17:35 | 10:11 | S/O
Tongi | Tongi-Kodda 300 MW P/P 230 kV Ckt | 2021-10-02 09:21 | 2021-10-02 17:02 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-10-03 07:09 | 2021-10-03 07:09 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV Ckt | 2021-10-03 08:52 | 2021-10-03 17:58 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kodda 300 MW P/P 230 kV Ckt | 2021-10-03 09:08 | 2021-10-03 16:17 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV Ckt-1 | 2021-10-03 08:34 | 2021-10-03 11:54 | 3:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Agargaon | Agargaon-Aminbazar 132 kV Ckt-2 | 2021-10-03 14:53 | 2021-10-03 16:22 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda P/P | Kodda P/P-Tongi 230 kV Ckt | 2021-10-04 09:09 | 2021-10-04 16:54 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2021-10-04 09:35 | 2021-10-04 15:55 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV Ckt | 2021-10-04 10:56 | 2021-10-04 16:29 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-1 | 2021-10-04 12:04 | 2021-10-04 12:50 | 0:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bhaluka-Mymensingh 132 kV Ckt-2 | 2021-10-04 12:58 | 2021-10-04 13:25 | 0:27 | S/O |  | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-10-04 16:18 | 2021-10-04 16:31 | 0:13 | S/O | Due to winding temperature high | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2021-10-05 10:28 | 2021-10-05 15:19 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | JoydevpurGhorasal 132 kV Ckt-2 | 2021-10-05 13:04 | 2021-10-06 20:34 | 31:30 | S/O | Due to PT maintenance | 0 | 0 | No interruption | 1489 | 2532.32
Mirpur | Mirpur-Uttara 3rd phase 132 kV Ckt | 2021-10-05 08:53 | 2021-10-05 21:03 | 12:10 | S/O | Due to A/M work | 0 | 0 | No interruption | 40 | 482.5
Mymensingh | Mymensingh S/S-RPCL 132 Ckt-2 | 2021-10-07 07:28 | 2021-10-07 07:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt | 2021-10-07 09:34 | 2021-10-07 15:56 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Kaliakoir 230 kV Ckt | 2021-10-09 08:40 | 2021-10-09 16:24 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd phase 132 kV Ckt | 2021-10-09 09:55 | 2021-10-09 21:03 | 11:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-10-09 09:05 | 2021-10-09 16:31 | 7:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-10-10 09:24 | 2021-10-10 16:27 | 7:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt | 2021-10-10 08:49 | 2021-10-10 16:01 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Bosila CLC 132 kV Ckt | 2021-10-10 14:34 | 2021-10-10 14:57 | 0:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda P/P | Kodda P/P-Jodevpur 132 kV Ckt-1 | 2021-10-11 09:12 | 2021-10-11 16:26 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt | 2021-10-11 09:17 | 2021-10-11 17:02 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-10-11 09:31 | 2021-10-11 16:38 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2021-10-12 11:23 | 2021-10-12 16:47 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-1 | 2021-10-12 10:25 | 2021-10-12 17:15 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt | 2021-10-12 10:44 | 2021-10-12 17:38 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-10-13 08:41 | 2021-10-13 18:14 | 9:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2021-10-13 11:55 | 2021-10-13 14:36 | 2:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-10-14 08:22 | 2021-10-14 14:27 | 6:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kalikoir 230 kV Ckt-2 | 2021-10-16 09:46 | 2021-10-16 16:26 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-10-16 11:28 | 2021-10-16 14:49 | 3:21 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kabirpur-Manikganj 132 kV Ckt-1 | 2021-10-16 09:45 | 2021-10-16 11:18 | 1:33 | S/O |  | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2021-10-16 09:03 | 2021-10-16 18:08 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-10-16 09:18 | 2021-10-16 16:13 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-2 | 2021-10-17 10:04 | 2021-10-17 16:50 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2021-10-17 09:56 | 2021-10-17 15:29 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2021-10-17 08:26 | 2021-10-17 15:37 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-2 | 2021-10-18 09:50 | 2021-10-18 18:18 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-1 | 2021-10-18 09:22 | 2021-10-18 17:09 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-1 | 2021-10-19 10:49 | 2021-10-19 15:28 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd 132 kV Ckt | 2021-10-19 12:31 | 2021-10-19 16:12 | 3:41 | S/O | Due to protection test | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-2 | 2021-10-20 09:35 | 2021-10-20 09:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-2 | 2021-10-21 09:20 | 2021-10-21 16:52 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 132 kV Ckt-1 | 2021-10-21 10:14 | 2021-10-21 16:27 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2021-10-23 09:05 | 2021-10-23 17:21 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminabazar 132 kV Ckt-1 | 2021-10-24 07:22 | 2021-10-24 07:22 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2021-10-24 09:00 | 2021-10-24 17:27 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminabazar 132 kV Ckt-2 | 2021-10-25 07:23 | 2021-10-25 17:06 | 9:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2021-10-25 09:00 | 2021-10-25 16:43 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2021-10-26 08:38 | 2021-10-26 17:34 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd 132 kV Ckt | 2021-10-26 09:07 | 2021-10-26 16:08 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2021-10-26 09:15 | 2021-10-26 15:23 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd 132 kV Ckt | 2021-10-27 08:47 | 2021-10-27 16:32 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2021-10-27 09:40 | 2021-10-27 16:04 | 6:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensingh-Bhaluka 132 kV Ckt-2 | 2021-10-27 17:15 | 2021-10-27 17:43 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2021-10-28 07:41 | 2021-10-28 17:25 | 9:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd 132 kV Ckt | 2021-10-28 09:02 | 2021-10-28 15:55 | 6:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-10-30 09:20 | 2021-10-30 16:53 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-10-30 09:35 | 2021-10-30 16:49 | 7:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-10-31 08:58 | 2021-10-31 17:24 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi P.S 132 kV Ckt | 2021-10-31 09:09 | 2021-10-31 13:10 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 423:48 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2021-10-01 10:11 | 2021-10-01 15:15 | 5:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Bramongaon 132 kV line | 2021-10-01 10:29 | 2021-10-01 15:14 | 4:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-2 | 2021-10-02 07:12 | 2021-10-02 09:53 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Narsingdi 132 kV line-1 & 2 | 2021-10-03 11:36 | 2021-10-03 17:11 | 5:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV line | 2021-10-06 10:11 | 2021-10-06 15:47 | 5:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Madanganj 100 MW P/P 132 kV Ckt | 2021-10-09 11:25 | 2021-10-09 15:32 | 4:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj GT-2 P/P 132 kV Ckt | 2021-10-12 12:29 | 2021-10-12 13:25 | 0:56 | S/O | Due to project work | 0 | 0 | No interruption
Madanganj | Madanganj-Charsayedpur 132 kV Ckt-1 |  | 2021-10-19 18:10 |  |  | New connection | 0 | 0 | No interruption
| Madanganj-Charsayedpur 132 kV Ckt-2 |  | 2021-10-19 18:13 |  |  |  | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-1 | 2021-10-20 08:10 | 2021-10-20 15:38 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV Ckt | 2021-10-23 08:30 | 2021-10-23 08:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Shyampur-Hasnabad 230 kV Ckt | 2021-10-23 08:29 | 2021-10-23 08:29 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-2 | 2021-10-23 08:27 | 2021-10-23 15:35 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sonargaon-Haripur 132 kV Ckt-1 | 2021-10-25 08:30 | 2021-10-25 15:26 | 6:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sonargaon-Haripur 132 kV Ckt-1 | 2021-10-26 08:46 | 2021-10-26 16:36 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sonargaon-Haripur 132 kV Ckt-2 | 2021-10-27 08:23 | 2021-10-27 15:24 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-1 |  | 2021-10-28 13:07 |  | S/O | After maint.work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 kV Ckt-2 | 2021-10-28 08:40 | 2021-10-28 15:39 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 72:06 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Rangamati | Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-02 08:23 | 2021-10-02 15:22 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-03 08:57 | 2021-10-03 15:37 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-04 08:52 | 2021-10-04 15:43 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-05 08:53 | 2021-10-05 16:07 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulshi | Kulshi-Bakulia 132 kV Ckt | 2021-10-06 08:54 | 2021-10-06 14:39 | 5:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-06 08:41 | 2021-10-06 15:34 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha(O)-Sikalbaha new 132 kV Ckt-1 | 2021-10-06 09:02 | 2021-10-06 17:12 | 8:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-10-07 06:50 | 2021-10-07 06:50 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha(O)-Sikalbaha new 132 kV Ckt-2 | 2021-10-07 08:32 | 2021-10-07 17:07 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV Ckt |  | 2021-10-07 08:58 |  | S/O | After maint.work | 0 | 0 | No interruption
Kulshi | Kulshi-Bakulia 132 kV Ckt | 2021-10-07 08:47 | 2021-10-07 13:13 | 4:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kv Ckt-1 | 2021-10-07 09:03 | 2021-10-07 09:03 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-07 08:40 | 2021-10-07 15:33 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Anawara 300 MW kV Ckt-1 & 2 | 2021-10-08 08:22 | 2021-10-08 15:29 | 7:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-09 08:45 | 2021-10-09 16:14 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV Ckt | 2021-10-10 07:13 | 2021-10-10 08:36 | 1:23 | S/O | Due to D/W work | 30 | 41.5 | Power interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-1 | 2021-10-10 07:57 | 2021-10-10 13:51 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati kV Ckt-2 | 2021-10-11 08:43 | 2021-10-11 15:17 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-11 09:24 | 2021-10-11 16:41 | 7:17 | S/O |  | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-10-12 06:35 | 2021-10-12 18:52 | 12:17 | S/O |  | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV Ckt-1 | 2021-10-12 09:17 | 2021-10-12 16:22 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 | 2021-10-13 08:33 | 2021-10-13 15:33 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 | 2021-10-14 08:15 | 2021-10-14 15:32 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulshi | Kulshi-Madunaghat 132 kV Ckt-1 | 2021-10-14 11:27 | 2021-10-14 13:59 | 2:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.k.chemical 132 kV Ckt | 2021-10-14 09:34 | 2021-10-14 09:34 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-1 | 2021-10-15 15:36 | 2021-10-15 16:14 | 0:38 | S/O | Due to wire removing | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-1 | 2021-10-16 06:27 | 2021-10-16 06:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV Ckt | 2021-10-16 08:46 | 2021-10-16 08:46 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 | 2021-10-16 08:28 | 2021-10-16 08:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV Ckt | 2021-10-16 08:46 | 2021-10-16 08:46 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kulshi | Kulshi-Madunaghat 132 kV Ckt-1 | 2021-10-16 15:21 | 2021-10-16 16:32 | 1:11 | S/O | Due to tree trimming | 0 | 0 | No interruption
Hathazari | Hathazari-Sikalbaha 230 kV Ckt-1 | 2021-10-17 10:18 | 2021-10-17 17:12 | 6:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-2 | 2021-10-18 09:35 | 2021-10-18 17:03 | 7:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-10-19 07:02 | 2021-10-19 10:45 | 3:43 | S/O | Due to A/M work | 11 | 40.8833 | Power interruption
Hathazari | Hathazari-Rampur 230 kV Bay-1 | 2021-10-19 10:09 | 2021-10-19 17:34 | 7:25 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Rampur 230 kV Bay-1 | 2021-10-20 10:01 | 2021-10-20 12:58 | 2:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2021-10-21 12:07 | 2021-10-21 12:07 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2021-10-22 10:48 | 2021-10-22 10:48 | 0:00 | S/O | Due to GI wire remove from line | 0 | 0 | No interruption
| Hathazari-Rampur 230 kV Bay-1 | 2021-10-23 10:05 | 2021-10-23 14:27 | 4:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Rampur 230 kV Ckt-2 | 2021-10-23 14:29 | 2021-10-23 15:51 | 1:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona -Rangamati 132 kV Ckt-1 | 2021-10-24 08:34 | 2021-10-24 15:31 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Sikalbaha 230 kV Ckt-1 | 2021-10-24 09:58 | 2021-10-24 11:32 | 1:34 | S/O |  | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-2 | 2021-10-24 11:32 | 2021-10-24 12:32 | 1:00 | S/O |  | 0 | 0 | No interruption
Halishar | Halishar-Khulshi 132 kV Ckt-3 | 2021-10-25 10:40 | 2021-10-25 12:30 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona -Rangamati 132 kV Ckt-1 | 2021-10-25 08:51 | 2021-10-25 15:39 | 6:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-GPH 230 kV Ckt | 2021-10-26 06:50 | 2021-10-26 06:50 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2021-10-28 08:31 | 2021-10-28 16:44 | 8:13 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madunaghat-Chandraghona 132 kV Ckt-2 | 2021-10-29 09:06 | 2021-10-29 09:06 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-1 | 2021-10-30 08:37 | 2021-10-30 08:37 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV Ckt-2 | 2021-10-30 09:26 | 2021-10-30 15:32 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt | 2021-10-31 10:08 | 2021-10-31 11:56 | 1:48 | S/O | Due to tree trimming | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV Ckt-2 | 2021-10-31 08:26 | 2021-10-31 10:55 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 213:06 |  | Unserved Energy: |  | 82.3833
Cumilla Grid Circle :
Ashuganj | Ashuganj-B.Baria 132 kV line-2 | 2021-10-02 03:55 | 2021-10-02 11:00 | 7:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur Desh P/P | Chandpur Desh P/P-Chandpur S/S 132 kV Ckt-1 & 2 | 2021-10-05 07:33 | 2021-10-05 14:09 | 6:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur P/S 132 kV Ckt-1 & 2 | 2021-10-09 07:05 | 2021-10-09 14:33 | 7:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-10-14 11:37 | 2021-10-14 17:54 | 6:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2021-10-18 08:23 | 2021-10-18 10:06 | 1:43 | S/O |  | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-10-25 12:40 | 2021-10-25 13:36 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-10-25 13:36 | 2021-10-25 14:40 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj(S)-Ghorashal 230 kV Ckt-1 | 2021-10-28 06:22 | 2021-10-28 10:21 | 3:59 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj(S)-Ashuganj 230 kV Ckt-1 | 2021-10-28 06:03 | 2021-10-28 10:00 | 3:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2021-10-31 10:25 | 2021-10-31 21:17 | 10:52 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 49:57 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gopalganj | Gopalganj- Gallamari 132 kv Ckt-1 |  | 2021-10-01 16:55 |  | S/O | After maintenance work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV Ckt-2 | 2021-10-07 19:09 | 2021-10-07 20:40 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gallamari-Gopalganj 132 kV line-2 | 2021-10-09 08:54 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV Ckt-1 | 2021-10-11 09:18 | 2021-10-11 11:16 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV Ckt | 2021-10-16 09:59 | 2021-10-16 13:34 | 3:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bagerhat-Orion Rupsha 132 kV Ckt | 2021-10-16 13:46 | 2021-10-16 18:30 | 4:44 | S/O |  | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV Ckt |  | 2021-10-25 04:30 |  | S/O | After maintenance work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV Ckt-3 | 2021-10-25 06:20 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
| Gopalganj(N)-Faridpur 132 kV Ckt-1 | 2021-10-25 05:05 | 2021-10-25 20:48 | 15:43 | S/O | Due to D/W work | 0 | 0 | No interruption
| Gopalganj(N)-Faridpur 132 kV Ckt-2 | 2021-10-25 05:05 | 2021-10-25 20:37 | 15:32
| Gopalganj(N)-Gopalganj (O) 132 kV Ckt | 2021-10-25 04:54 | 2021-10-25 15:03 | 10:09 | S/O |  | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV Ckt-1 & 2 | 2021-10-25 05:58 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | Payra-Gopalganj (N) 400 kV Ckt-2 | 2021-10-25 03:09 | 2021-10-25 10:55 | 7:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | Gallamari-Gopalganj(O) 132 kV Ckt-1 | 2021-10-27 08:26 | 2021-10-27 15:25 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-2 | 2021-10-27 10:39 | 2021-10-27 21:12 | 10:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | Gallamari-Gopalganj(O) 132 kV Ckt-2 | 2021-10-27 15:31 | 2021-10-27 17:07 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt |  | 2021-10-28 00:07 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV Ckt | 2021-10-28 10:01 | 2021-10-28 13:57 | 3:56 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 84:02 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jhenaidah | Jhenaidah-Chuadanga 132 kV Ckt-2 | 2021-10-02 08:21 | 2021-10-02 10:44 | 2:23 | S/O | Due to D/W work | 50 | 119.1667 | Power interruption
HVDC | HVDC 400 kV 10CF15 filter | 2021-10-06 08:32 | 2021-10-06 08:32 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV Ckt-2 | 2021-10-07 09:35 | 2021-10-07 12:37 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV Ckt-1 | 2021-10-11 10:06 | 2021-10-11 14:50 | 4:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thaurgaon 132 kV Ckt-1 | 2021-10-12 07:15 |  |  | S/O
Shahjadpur | Shahjadpur-Baghabari 132 kV Ckt-2 | 2021-10-13 08:42 | 2021-10-13 17:06 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV Ckt-2 | 2021-10-16 10:05 | 2021-10-16 20:51 | 10:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Pabna 132 kV Ckt | 2021-10-17 08:50 | 2021-10-17 17:11 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara | Bharamara-Baharampur 400 kV Ckt-1 | 2021-10-18 11:34 | 2021-10-18 11:40 | 0:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Pabna 132 kV Ckt | 2021-10-18 08:39 | 2021-10-18 17:47 | 9:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara | Bharamara-Baharampur 400 kV Ckt-4 | 2021-10-19 11:58 | 2021-10-19 11:58 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bharamara HVDC | Bharamara HVDC-Jhenidah (new) 230 kV Ckt-1 | 2021-10-20 08:52 | 2021-10-20 17:06 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara HVDC-Jhenidah (new) 230 kV Ckt-1 | 2021-10-21 09:25 | 2021-10-21 15:31 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara HVDC-Rajshahi 230 kV Ckt-1 | 2021-10-23 08:46 | 2021-10-23 17:25 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara-Rajshahi 230 kV Ckt-1 | 2021-10-24 07:58 | 2021-10-24 17:25 | 9:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gollamari 132 kV Ckt-1 & 2 |  | 2021-10-24 23:51 |  | S/O | After maint.work | 0 | 0 | No interruption
Bharamara HVDC | HVDC Bheramara-Rajshahi 230 kV Ckt-2 | 2021-10-26 07:44 | 2021-10-26 17:12 | 9:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur-Baghabari 132 kV Ckt | 2021-10-26 09:22 | 2021-10-26 17:53 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara HVDC | HVDC Bheramara-Rajshahi 230 kV Ckt-2 | 2021-10-26 08:32 | 2021-10-26 17:20 | 8:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara-Rajshahi 230 kV Ckt-2 | 2021-10-28 07:47 | 2021-10-28 16:06 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara HVDC-Bharampur 400 kV Ckt-1 & 2 |  | 2021-10-30 09:54 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV Ckt | 2021-10-30 10:07 | 2021-10-30 13:40 | 3:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV Ckt | 2021-10-31 08:28 | 2021-10-31 15:56 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 125:27 |  | Unserved Energy: |  | 119.1667
Bogura Grid Circle :
Thakurgaon | Thakurgaon-Purbasadipur 132 Ckt-2 | 2021-10-02 07:20 | 2021-10-02 11:16 | 3:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura (O) | Bogura (O)-Bogura(N) 132 kV Ckt-1 | 2021-10-03 11:27 | 2021-10-03 15:18 | 3:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura (O)-Bogura(N) 132 kV Ckt-2 | 2021-10-03 15:23 | 2021-10-03 18:37 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mithapukur 132 kV Ckt | 2021-10-05 11:45 | 2021-10-05 15:07 | 3:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV Ckt-2 | 2021-10-12 06:15 | 2021-10-12 06:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV Ckt-1 | 2021-10-14 09:13 | 2021-10-14 15:01 | 5:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohastanghor | Mohastanghor-Palashbari 132 kV Ckt-1 | 2021-10-22 13:03 | 2021-10-22 13:37 | 0:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mohastanghor-Bogura 132 kV Ckt-1 | 2021-10-22 13:39 | 2021-10-22 14:38 | 0:59 | S/O |  | 0 | 0 | No interruption
Bogura | Bogura-Mohastanghor 132 kV Ckt-1 | 2021-10-24 09:53 | 2021-10-24 11:08 | 1:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Mohastanghor 132 kV Ckt-2 | 2021-10-24 11:09 | 2021-10-24 12:44 | 1:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Bheramara HVDC 230 kV Ckt-1 | 2021-10-25 08:33 | 2021-10-25 15:47 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV Ckt | 2021-10-25 08:25 | 2021-10-25 10:35 | 2:10 | S/O | Due to A/M work | 25 | 54.1667 | Power interruption
Thakurgaon | Thakurgaon-RPCL 132 kV Ckt-2 | 2021-10-26 09:25 | 2021-10-26 15:25 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bahabari 132 kV Ckt | 2021-10-27 09:40 | 2021-10-27 11:10 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Shahjadpur 132 kV Ckt | 2021-10-27 12:57 | 2021-10-27 13:57 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Sherpur 132 kV Ckt-1 | 2021-10-27 11:14 | 2021-10-27 12:03 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Sherpur 132 kV Ckt-2 | 2021-10-27 12:04 | 2021-10-27 12:44 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Sherpur 132 kV Ckt-1 | 2021-10-29 08:35 | 2021-10-29 17:25 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura(N)-Sherpur 132 kV Ckt-2 | 2021-10-31 08:47 | 2021-10-31 16:10 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 60:10 |  | Unserved Energy: |  | 54.1667
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-2 | 2021-10-08 09:12 | 2021-10-08 17:21 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 8:09 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1036:45 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October 2021
| Area | Previous Month (September' 2021) |  |  |  | Current Month (October '2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 30 | 15 | 124 | 169 | 16 | 2 | 115 | 133
2 | Dhaka (South) Grid Circle. | 9 | 0 | 16 | 25 | 14 | 6 | 26 | 46
3 | Chattogram Grid Circle. | 29 | 2 | 39 | 70 | 18 | 3 | 71 | 92
4 | Cumilla Grid Circle. | 30 | 11 | 31 | 72 | 26 | 8 | 26 | 60
5 | Khulna Grid Circle. | 22 | 8 | 49 | 79 | 16 | 7 | 61 | 84
6 | HVDC Grid Circle | 2 | 0 | 5 | 7 | 1 | 0 | 35 | 36
7 | Bogura Grid Circle. | 16 | 9 | 42 | 67 |  | 6 | 99 | 105
8 | Others | 0 | 0 | 0 | 0 | 1 |  | 1 | 2
9 | Total | 138 | 45 | 306 | 489 | 92 | 32 | 434 | 558
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October 2021
| Area | Previous Month (August' 2021) |  |  |  | Current Month (September '2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 785.56 | 468.2 | 289.17 | 1542.93 | 291 | 58.6667 | 495 | 844.6667
2 | Dhaka (South) Grid Circle. | 360.1 | 0 | 58 | 418.1 | 60.17 | 30.9 | 0 | 91.07
3 | Chattogram Grid Circle. | 96.97 | 139.43 | 2387.45 | 2623.85 | 72.64 | 0 | 103.05 | 175.69
4 | Cumilla Grid Circle. | 127.18 | 79 | 350.8 | 556.98 | 90.08 | 157.4 | 325.5 | 572.98
5 | Khulna Grid Circle. | 416.94 | 122.67 | 107.98 | 647.59 | 180.9 | 125.8 | 81.87 | 388.57
6 | HVDC Grid Circle | 0 | 0 | 0 | 0 | 0 | 0 | 140.72 | 140.72
7 | Bogura Grid Circle. | 84.67 | 733.97 | 1042.58 | 1861.22 | 162.33 | 253.27 | 209.22 | 624.82
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 1871.42 | 1543.27 | 4235.98 | 7650.67 | 857.12 | 626.0367 | 1355.36 | 2838.5167
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October 2021
A) Power Interruption | [10 empty] | 3
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 3 | 5 | 8 | 1 | 1 | 6 | 845.25
2 | Dhaka (South) | 5031.6 | 2 | - | 2 | 1 |  | 1 | 52.9
3 | Chattogram | 2042 | 2 | 1 | 3 |  | 2 | 1 | 85.3
4 | Khulna | 2434 | 11 | 4 | 15 | 4 | 2 | 9 | 384.07
5 | HVDC | 5954.3 | - | 1 | 1 | - | 1 | 1 | 21.55 |  |  | 58.03
6 | Bogura | 3145.6 | 6 | 6 | 12 | 3 | 2 | 7 | 330.18
7 | Cumilla | 2981 | 6 | 6 | 12 | 2 | 5 | 5 | 548.67
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 2267.92
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 100%
3 | Chattogram | 99.97%
4 | Khulna | 99.93%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.97% | [6 empty] | Information Management Division
7 | Cumilla | 99.92% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | - | - | - | - | - | -
2 | Dhaka (South) | 990.29 |  | 2 | - | 2 | 2 | - | - | 38.17
3 | Chattogram | 917 | - | 1 | 2 | 3 | 1 | - | 2 | 90.38
4 | Khulna | 1238.4 | - | 1 |  | 1 | 1 | - | - | 4.5 | -
5 | HVDC | 1325 | 501 | - | 1 | 1 |  |  | 1 | 119.17 | -
6 | Bogura | 1803.3 | - | 4 | 1 | 5 |  | 2 | 3 | 294.64
7 | Cumilla | 1648.16 | - | 2 |  | 2 | 1 |  | 1 | 24.32
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 571.18
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99% |  | 99.9924
2 | Dhaka (South) | 99.88%
3 | Chattogram | 99.96% |  | 99.884
4 | Khulna | 99.89%
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.93% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-10-18 | 18 | - | 5 | 05hr 42 min | 2 | 2hr50 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:October 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kabirpur | 1 | 0:40 | 88 | 58.6667 | Due to tripping of 132/33 kV Transformers-T1 & T2
Mymensingh | 1 | 0:17 | 175 | 49.5833
| 2 | 1:17 | 175 | 49.5833 | Due to tripping of 132/33 kV Transformers-T1 & T2
Kishoreganj | 1 | 8:04 | 30 | 242 | Due to tripping of 132/33 kV Transformer-T3
Bhaluka | 1 | 4:01 | 50 | 200.8333 | Due to S/D of 132/33 kV Transformer T1
Kabirpur | 1 | 5:02 | 10 | 50.3333 | Due to S/D of 132/33 kV Transformer T2
Mymensing | 1 | 1:28 | 45 | 66 | Due to S/D of 132/33 kV Transformer T1
Sherur | 1 | 5:02 | 35 | 176.1667 | Due to S/D of 132/33 kV Transformer T2
Bhaluka |  | 0:10 | 10 | 1.6667 | Due to S/D of 132/33 kV Transformer T1
Siddhirganj | 1 | 0:22 | 60 | 22 | Due to tripping of 132/33 kV Transformers-T1 & T2
Nawabganj | 1 | 1:43 | 18 | 30.9 | Due to red-hot maintenance of 132/33 kV Trasformer T1
Bashundhara | 1 | 0:14 | 85 | 19.8333 | Due to tripping of Bashundhara-Rampura 132 kV both Ckts
| 1 | 0:25 | 44 | 18.3333 | Due to tripping of Bashundhara-Banani 132 kV Ckt
Halishahar | 2 | 0:34 | 64 | 36.2667 | Due to 33 kV feeder fault
|  | 0:37 | 46 | 28.3667 | Due to tripping of bad weather
Dohazari | 1 | 0:16 | 30 | 8 | Due to S/D of Dohazari-Cox's Bazar 132 kV Ckt-2
Shahmirpur | 1 | 4:08 | 5 | 20.6667 | Due to S/D of 132/33 kV transformer T1
Dohazari | 1 | 1:23 | 30 | 41.5 | Due to S/D of Dohazari-Matarbari 132 kV Ckt
| 1 | 3:43 | 11 | 40.8833 | Due to S/D of Dohazari-Cox'sbazar 132 kV Ckt-1
Comilla(S) |  | 0:44 | 36 | 26.4 | Due to bursting of PT at 33 kV side
Shahjibazar |  | 0:46 | 30 | 23 | Due to tripping of 132/33 kV Transformer-T2
Biyanibazar |  | 0:30 | 50 | 25 | Due to tripping of 132/33 kV Transformers-T1 & T2
Dohazari |  | 0:41 | 26 | 17.7667
Cumilla(N) |  | 1:42 | 50 | 85 | Due to red-hot maint of 132/33 kV Transformer T3
Chowmuhani |  | 2:18 | 20 | 46
Chatak |  | 0:11 | 19 | 3.4833 | Due to S/D of Chatak-Sunamganj 132 kV Ckt
Sylhet |  | 2:05 | 10 | 20.8333 | Due to S/D Sylhet-Chatak 132 kV Ckt-1
Kulaura |  | 0:54 | 20 | 18 | Due to S/D of tripping of 132/33 kV Transformer-T1
Chowmuhani | 1 | 0:34 | 50 | 28.3333 | Due to S/D of 33 kV bus
Beanibazar |  | 0:05 | 35 | 2.9167 | Due to S/D of 132/33 kV Transformer-T2
Mohastanghor |  | 3:11 | 35 | 111.4167
B.Baria |  | 10:34 | 25 | 94.1667 | Due to S/D of 132/33 kV Transformer-T1
Daudkandi |  | 3:32 | 20 | 70.6667 | Due to S/D of 132/33 kV Transformer-T2 & T3
Jhenaidah |  | 1:13 | 10 | 12.1667 | Due to tripping of 230/132 kV Transformer-T2
Patuakhali |  | 0:12 | 46 | 9.2 | Due to S/D of 132/33 kV transformer T1
Goalpara |  | 0:22 | 26 | 9.5333 | Due to S/D of 132/33 kV transformer T6
Benapole |  | 0:27 | 50 | 22.5 | Due to tripping of 132/33 kV Transformers-T1 & T2
Shariatpur |  | 0:56 | 10 | 15.8333 | Due to red-hot maintenance of 33 kV Bus-2
Norail | 1 | 0:56 | 8 | 7.4667 | Due to red-hot maintenance of 132/33 kV Trasformer T1
Bagerhat |  | 4:04 | 20 | 123 | Due to tripping of 132/33 kV Transformers-T1 & T2 | #VALUE!
Norail | 1 | 2:10 | 12 | 26 | Due to red-hot maintenance of 132/33 kV Trasformer T2
Bagerhat | 1 | 1:18 | 45 | 58.5 | Due to red-hot maintenance of 132/33 kV Trasformer T3
Gollamari | 1 | 0:01 | 18 | 18 | Due to tripping of 132/33 kV Transformers-T1 & T2
Barisal |  | 0:06 | 45 | 4.5 | Due to tripping of Barisal-Patuakhali 132 kV line
Bagerhat | 1 | 0:43 | 14 | 10.0333 | Due to S/D of 132/33 kV Transformer T1
Shariatpur | 1 | 1:30 | 15 | 22.5 | Due to S/D of 132/33 kV Transformer T2
Madaripur | 1 | 2:08 | 20 | 42.6667 | Due to S/D of 132/33 kV Transformer-T1 & T3
Bhandaria | 1 | 1:20 | 5 | 6.6667 | Due to S/D of 132/33 kV Transformer T1
Pabna | 2 | 0:49 | 15 | 12.25 | Due to S/D of 132/33 kV Transformer T2
|  | 0:18 | 31 | 9.3 | Due to S/D of 132/33 kV Transformer T2
Jhenaidah | 1 | 2:23 | 50 | 119.1667 | Due to S/D of Jhenaidah-Chuadanga 132 kV Ckt-2
Purbasadipur | 2 | 1:06 | 45 | 75.75 | Due to fire occurred at capacitor bank
Palashbari |  | 1:15 | 24 | 30 | Due to red-hot maintenance of 132/33 kV Trasformer T2
Pabna |  | 0:10 | 5 | 0.83333 | Due to tripping of 132/33 kV Transformer-T1
Purbasadipur | 1 | 0:15 | 25 | 6.25 | Due to tripping of 132/33 kV Transformer-T3
| 1 | 1:13 | 27 | 32.85 | Due to red-hot maintenance of 132/33 kV Trasformer T1
Natore | 1 | 0:57 | 31 | 29.45 | Due to tripping of 132/33 kV Transformers-T1 & T2
Sherpur | 2 | 2:10 | 40 | 86.6667 | Due to S/D of 33 kV full Bus
|  | 0:40 | 42 | 28 | Due to PT burst
Thakurgaon | 1 | 0:42 | 59 | 41.3 | Due to tripping of Thakurgaon-Thakurgaon P.P &132 kV Ckts
Rangpur | 1 | 2:49 | 30 | 84.5 | Due to tripping of Rangpur-Lalmonirhat 132 kV Ckt
Barapukuria | 1 | 0:38 | 40 | 25.3333 | Due to S/D of 132/33 kV Transformer-T3 & T4
Niyamatpur | 1 | 0:29 | 8 | 3.8667 | Due to S/D of 132/33 kV Transformer T2
Bogura | 1 | 1:58 | 6 | 11.8
Natore | 1 | 1:19 | 47 | 61.8833 | Due to S/D of 132/33 kV Transformers-T1 & T2
Naogaon | 1 | 1:35 | 20 | 31.6667 | Due to S/D of 132/33 kV Transformer T3
Barapukuria | 1 | 1:22 | 15 | 20.5 | Due to S/D of 132/33 kV Transformer T4
Naogaon |  | 2:10 | 25 | 54.1667 | Due to S/D of Naogaon-Niyamatpur 132 kV Ckt
| Total Unserved energy : |  |  | 2839.08 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
#REF!
3242.7956
[5 empty] | Executive Engineer | 3226.32
[5 empty] | Information Management Division | 16.4756
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 12 | 2021-10-01 | 15:00
2 | Munsiganj | 110 | 12 | 2021-10-01 | 0:00
3 | Sonargaon | 85 | 10 | 2021-10-01 | 19:30
4 | Shyampur | 206 | 11 | 2021-10-01 | 10:00
5 | Bhulta | 219 | 7 | 2021-10-01 | 20:00
6 | Madanganj | 55 | 4 | 2021-10-01 | 13:00
7 | Shitalakhya | 120 | 10 | 2021-10-01 | 12:00
8 | Rahim steel | 28 | 30 | 2021-10-01 | 13:00
9 | Matuail | 66 | 2 | 2021-10-01 | 12:00
10 | Ghorasal | 95 | 7 | 2021-10-01 | 4:00
11 | Narsingdi | 193 | 12 | 2021-10-01 | 0:00
12 | Haripur (SBU) | 167 | 9 | 2021-10-01 | 20:00
13 | Sreenagar | 44 | 11 | 2021-10-01 | 22:00
14 | Ullon | 76 | 17 | 2021-10-01 | 16:00
15 | Hasnabad | 91 | 2 | 2021-10-01 | 23:00
16 | Magbazar | 111 | 11 | 2021-10-01 | 13:00
17 | Maniknagar | 80 | 10 | 2021-10-01 | 13:00
18 | Bangabhaban | 15 | 3 | 2021-10-01 | 11:00
19 | Narinda | 80 | 9 | 2021-10-01 | 18:00
20 | Dhanmondi | 228 | 3 | 2021-10-01 | 13:00
21 | Lalbag | 99 | 18 | 2021-10-01 | 13:00
22 | Madartek | 83 | 12 | 2021-10-01 | 0:00
23 | Dhaka University | 42 | 3 | 2021-10-01 | 13:00
24 | Aftabnagar | 17 | 10 | 2021-10-01 | 12:00
25 | Fatullah | 65 | 7 | 2021-10-01 | 15:00
26 | Nawabganj | 57 | 9 | 2021-10-01 | 18:00
27 | Mirpur | 146 | 12 | 2021-10-01 | 18:30
28 | Kalyanpur | 102 | 12 | 2021-10-01 | 18:00
29 | Gulshan | 140 | 12 | 2021-10-01 | 16:00
30 | Uttara | 104 | 11 | 2021-10-01 | 15:00
31 | Uttara(new) | 32 | 10 | 2021-10-01 | 13:00
32 | Kamrangirchar | 103 | 7 | 2021-10-01 | 18:30
33 | Savar | 192 | 17 | 2021-10-01 | 16:00
34 | Bhasantec | 150 | 13 | 2021-10-01 | 18:00
35 | Agargaon | 110 | 10 | 2021-10-01 | 13:00
36 | Satmosjid | 118 | 10 | 2021-10-01 | 18:00
37 | Tongi | 137 | 3 | 2021-10-01 | 15:00
38 | Kabirpur | 281 | 6 | 2021-10-01 | 13:00
39 | Basundhara | 222 | 12 | 2021-10-01 | 15:00
40 | Manikganj | 78 | 12 | 2021-10-01 | 21:00
41 | Joydevpur | 198 | 10 | 2021-10-01 | 18:00
42 | New Tongi | 94 | 2 | 2021-10-01 | 15:00
43 | Kodda | 312 | 4 | 2021-10-01 | 17:00
44 | Dhamrai | 124 | 12 | 2021-10-01 | 18:00
45 | Rajendrapur | 118 | 12 | 2021-10-01 | 18:30
46 | Valuka | 134 | 6 | 2021-10-01 | 18:00
47 | Tangail | 232 | 15 | 2021-10-01 | 22:00
48 | Mymensing | 231 | 16 | 2021-10-01 | 18:30
49 | Kishorganj | 160 | 16 | 2021-10-01 | 21:00
50 | Netrokona | 124 | 16 | 2021-10-01 | 2:00
51 | Jamalpur | 157 | 17 | 2021-10-01 | 20:00
52 | Sherpur | 142 | 17 | 2021-10-01 | 23:00
53 | Srimongal | 64 | 11 | 2021-10-01 | 22:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
54 | Shahjibazar | 125 | 11 | 2021-10-01 | 23:00
56 | Fenchuganj | 51 | 12 | 2021-10-01 | 18:00
57 | Kulawara | 56 | 15 | 2021-10-01 | 18:30
58 | Sylhet | 163 | 13 | 2021-10-01 | 18:00
59 | Chatak | 36 | 1 | 2021-10-01 | 21:00
60 | Sunamganj | 59 | 12 | 2021-10-01 | 21:00
61 | Bianibazar | 76 | 12 | 2021-10-01 | 19:30
62 | Cumilla (S) | 160 | 10 | 2021-10-01 | 18:00
63 | Cumilla(N) | 161 | 8 | 2021-10-01 | 22:00
64 | Chandpur | 83 | 11 | 2021-10-01 | 22:00
65 | Feni | 132 | 6 | 2021-10-01 | 18:00
66 | Chowmuhani | 226 | 14 | 2021-10-01 | 23:00
67 | Ashuganj | 50 | 12 | 2021-10-01 | 23:00
68 | Daudkandi | 164 | 7 | 2021-10-01 | 22:00
69 | B.Baria | 174 | 15 | 2021-10-01 | 21:00
70 | Ramganj | 100 | 7 | 2021-10-01 | 22:00
71 | Chaddagram | 59 | 11 | 2021-10-01 | 21:00
72 | PHP | 12 | 22 | 2021-10-01 | 18:30
73 | Kochua | 70 | 12 | 2021-10-01 | 19:00
74 | Madanhat | 66 | 2 | 2021-10-01 | 18:00
75 | Hathazari | 111 | 12 | 2021-10-01 | 18:00
76 | Khulshi | 213 | 2 | 2021-10-01 | 16:00
77 | Halishahar | 136 | 2 | 2021-10-01 | 14:00
78 | Baraulia | 163 | 26 | 2021-10-01 | 18:00
79 | Sikalbaha | 48 | 11 | 2021-10-01 | 16:00
80 | Dohazari | 116 | 6 | 2021-10-01 | 20:00
81 | Cox'sbazar | 122 | 11 | 2021-10-01 | 19:30
82 | Chandraghona | 58 | 18 | 2021-10-01 | 7:00
83 | Kaptai | 5 | 14 | 2021-10-01 | 18:00
84 | A. Khaer Stl. | 20 | 27 | 2021-10-01 | 23:00
85 | Bakulia | 129 | 12 | 2021-10-01 | 19:00
86 | Julda | 27 | 19 | 2021-10-01 | 12:00
87 | TK chemical | 34 | 13 | 2021-10-01 | 19:00
88 | Modern Steel | 11 | 4 | 2021-10-01 | 11:00
89 | Shahmirpur | 36 | 6 | 2021-10-01 | 18:00
90 | Khagrachhari | 30 | 6 | 2021-10-01 | 17:00
91 | Matarbari | 45 | 12 | 2021-10-01 | 21:00
92 | Baroiar Hat | 80 | 14 | 2021-10-01 | 18:00
93 | Rangamati | 16 | 11 | 2021-10-01 | 18:00
94 | Abul Khair 230 | 165 | 12 | 2021-10-01 | 1:00
95 | BSRM | 162 | 10 | 2021-10-01 | 10:00
96 | GPH Ispat | 98 | 30 | 2021-10-01 | 13:00
97 | Goalpara | 32 | 2 | 2021-10-01 | 13:00
98 | Central s/s | 108 | 11 | 2021-10-01 | 19:30
99 | Noapara | 50 | 2 | 2021-10-01 | 20:00
100 | Jashore | 128 | 9 | 2021-10-01 | 20:00
101 | Benapol | 68 | 1 | 2021-10-01 | 18:30
101 | Jhenidah | 121 | 13 | 2021-10-01 | 18:30
102 | Bottail | 132 | 9 | 2021-10-01 | 18:30
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
103 | G.K Project | 62 | 13 | 2021-10-01 | 20:00
104 | Faridpur | 159 | 10 | 2021-10-01 | 21:00
105 | Madaripur | 115 | 10 | 2021-10-01 | 21:00
106 | Sariatpur | 74 | 10 | 2021-10-01 | 21:00
107 | Gopalganj | 100 | 10 | 2021-10-01 | 21:00
108 | Bagerhat | 105 | 11 | 2021-10-01 | 20:00
109 | Mongla | 55 | 30 | 2021-10-01 | 15:00
110 | Satkhira | 112 | 9 | 2021-10-01 | 21:00
111 | Gallamari | 49 | 2 | 2021-10-01 | 18:00
112 | Magura | 60 | 10 | 2021-10-01 | 18:30
113 | Norail | 49 | 10 | 2021-10-01 | 19:30
114 | Chuadanga | 108 | 15 | 2021-10-01 | 22:00
115 | Barsal(N) | 50 | 10 | 2021-10-01 | 22:00
116 | Barsal(S) | 120 | 10 | 2021-10-01 | 22:00
117 | Patuakhali | 128 | 10 | 2021-10-01 | 22:00
118 | Bhandaria | 56 | 10 | 2021-10-01 | 21:00
119 | Borguna | 20 | 10 | 2021-10-01 | 20:00
120 | Borhan Uddin | 48 | 6 | 2021-10-01 | 18:00
121 | Ishurdi | 73 | 16 | 2021-10-01 | 18:30
122 | Ruppur Paromanobik | 4 | 1 | 2021-10-01 | 9:00
123 | Natore | 136 | 9 | 2021-10-01 | 21:00
124 | Bogura | 174 | 13 | 2021-10-01 | 20:00
125 | Naogaon | 125 | 13 | 2021-10-01 | 20:00
126 | Rajshahi | 158 | 2 | 2021-10-01 | 21:00
127 | Rajshahi New | 23 | 31 | 2021-10-01 | 18:30
128 | C.Nawabganj | 67 | 4 | 2021-10-01 | 20:00
129 | Amnura | 64 | 12 | 2021-10-01 | 21:00
130 | Pabna | 113 | 10 | 2021-10-01 | 18:00
131 | Shahjadpur | 106 | 9 | 2021-10-01 | 19:00
132 | Serajganj | 115 | 13 | 2021-10-01 | 20:00
133 | Niyamatpur | 89 | 9 | 2021-10-01 | 21:00
134 | Joypurhat | 61 | 2 | 2021-10-01 | 20:00
135 | Sherpur(Bogura) | 68 | 13 | 2021-10-01 | 20:00
136 | Mohastangar | 74 | 15 | 2021-10-01 | 21:00
137 | Bangura | 34 | 9 | 2021-10-01 | 21:00
138 | Rangpur | 138 | 2 | 2021-10-01 | 19:30
139 | Lalmonirhat | 50 | 26 | 2021-10-01 | 18:00
140 | Saidpur | 96 | 13 | 2021-10-01 | 18:30
141 | Purbasadipur | 100 | 11 | 2021-10-01 | 19:30
142 | Thakurgaon | 82 | 1 | 2021-10-01 | 19:30
143 | Palshbari | 120 | 10 | 2021-10-01 | 21:00
144 | Barapukuria | 51 | 6 | 2021-10-01 | 21:00
145 | Panchugar | 55 | 14 | 2021-10-01 | 18:30
146 | Joldhaka | 64 | 1 | 2021-10-01 | 19:00
147 | Kurigram | 61 | 1 | 2021-10-01 | 18:30
148 | Mitha Pukur | 33 | 21 | 2021-10-01 | 18:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:October 2021
Area | MW | Date | Hour | Remarks
Dhaka | 4944 | 17.10.21 | 16:00
Chattogram | 1510 | 07.10.21 | 18:00
Khulna | 1618 | 09.10.21 | 21:00
Rajshahi | 1451 | 13.10.21 | 20:00
Cumilla | 1283 | 11.10.21 | 21:00
Mymensingh | 1073 | 16.10.21 | 20:00
Sylhet | 595 | 12.10.21 | 22:00
Barisal | 615 | 30.10.21 | 22:00
Rangpur | 769 | 01.10.21 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 412 | 1 | 2021-10-01 | 18:30 | 399 | 10 | 2021-10-01 | 22:00
2 | Bheramara | 400 | 405 | 14 | 2021-10-01 | 7:00 | 393 | 21 | 2021-10-01 | 18:00
3 | Ashuganj(N) | 400 | 398 | 8 | 2021-10-01 | 6:00 | 379 | 23 | 2021-10-01 | 12:00
4 | Payra | 400 | 417 | 27 | 2021-10-01 | 8:00 | 396 | 12 | 2021-10-01 | 1:00
5 | Kaliakoir | 400 | 402 | 22 | 2021-10-01 | 9:00 | 383 | 27 | 2021-10-01 | 12:00
6 | Bhulta | 400 | 396 | 8 | 2021-10-01 | 17:00 | 371 | 23 | 2021-10-01 | 12:00
7 | Gopalganj | 400 | 420 | 27 | 2021-10-01 | 15:00 | 381 | 2 | 2021-10-01 | 22:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2021-10-01 | 20:00 | 227 | 2 | 2021-10-01 | 10:00
2 | Ishurdi | 230 | 235 | 1 | 2021-10-01 | 17:00 | 223 | 10 | 2021-10-01 | 24:00
3 | Ashuganj | 230 | 245 | 31 | 2021-10-01 | 18:00 | 230 | 23 | 2021-10-01 | 12:00
4 | Serajganj | 230 | 235 | 25 | 2021-10-01 | 18:00 | 224 | 2 | 2021-10-01 | 23:00
5 | Baghabari | 230 | 234 | 8 | 2021-10-01 | 17:00 | 224 | 2 | 2021-10-01 | 19:30
6 | Barapukuria | 230 | 239 | 4 | 2021-10-01 | 13:00 | 221 | 15 | 2021-10-01 | 22:00
7 | Bogura | 230 | 229 | 31 | 2021-10-01 | 15:00 | 212 | 2 | 2021-10-01 | 19:30
8 | Rajshahi | 230 | 232 | 2 | 2021-10-01 | 17:00 | 217 | 5 | 2021-10-01 | 1:00
9 | Khulna South | 230 | 235 | 8 | 2021-10-01 | 10:00 | 211 | 12 | 2021-10-01 | 9:00
10 | Rampura | 230 | 233 | 8 | 2021-10-01 | 13:00 | 221 | 3 | 2021-10-01 | 16:00
11 | Haripur | 230 | 234 | 8 | 2021-10-01 | 15:00 | 221 | 23 | 2021-10-01 | 12:00
12 | Hasnabad | 230 | 232 | 7 | 2021-10-01 | 7:00 | 219 | 3 | 2021-10-01 | 7:00
13 | Shyampur | 230 | 232 | 4 | 2021-10-01 | 21:00 | 219 | 3 | 2021-10-01 | 12:00
14 | Aminbazar | 230 | 234 | 22 | 2021-10-01 | 1:00 | 219 | 17 | 2021-10-01 | 2:00
15 | Tongi | 230 | 236 | 1 | 2021-10-01 | 5:00 | 215 | 3 | 2021-10-01 | 15:00
16 | Comilla (N) | 230 | 235 | 8 | 2021-10-01 | 18:00 | 210 | 6 | 2021-10-01 | 24:00
17 | Hathazari | 230 | 239 | 15 | 2021-10-01 | 20:00 | 215 | 23 | 2021-10-01 | 10:00
18 | Megnaghat | 230 | 236 | 1 | 2021-10-01 | 18:30 | 226 | 22 | 2021-10-01 | 11:00
19 | Fenchuganj | 230 | 247 | 20 | 2021-10-01 | 17:00 | 236 | 10 | 2021-10-01 | 18:00
20 | Siddhirganj | 230 | 235 | 8 | 2021-10-01 | 15:00 | 223 | 3 | 2021-10-01 | 16:00 |  | 7345
21 | Maniknagar | 230 | 234 | 8 | 2021-10-01 | 15:00 | 220 | 3 | 2021-10-01 | 6:00
22 | Old Airport | 230 | 232 | 8 | 2021-10-01 | 17:00 | 217 | 23 | 2021-10-01 | 12:00
23 | Barisal | 230 | 244 | 22 | 2021-10-01 | 21:00 | 221 | 15 | 2021-10-01 | 19:30
24 | Bhola 225 MW | 230 | 248 | 4 | 2021-10-01 | 15:00 | 235 | 17 | 2021-10-01 | 21:00
25 | AKSML | 230 | 238 | 15 | 2021-10-01 | 17:00 | 215 | 24 | 2021-10-01 | 4:00
26 | BSRM | 230 | 238 | 1 | 2021-10-01 | 18:30 | 216 | 21 | 2021-10-01 | 5:00
27 | Bibiyana | 230 | 245 | 20 | 2021-10-01 | 18:00 | 236 | 10 | 2021-10-01 | 22:00
28 | Bhulta | 230 | 239 | 8 | 2021-10-01 | 13:00 | 222 | 4 | 2021-10-01 | 15:00
29 | Ashuganj (S) | 230 | 232 | 0 | 2021-10-01 | 9:00 | 228 | 23 | 2021-10-01 | 12:00
30 | Kaliakoir | 230 | 234 | 22 | 2021-10-01 | 18:00 | 216 | 3 | 2021-10-01 | 17:00
31 | GPH | 230 | 238 | 20 | 2021-10-01 | 18:00 | 215 | 22 | 2021-10-01 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 8 | 2021-10-01 | 0.70833 | 129 | 3 | 2021-10-01 | 0.625
2 | Munsiganj | 132 | 139 | 8 | 2021-10-01 | 0.70833 | 129 | 3 | 2021-10-01 | 0.45833
3 | Sonargaon | 132 | 137 | 22 | 2021-10-01 | 0.75 | 129 | 3 | 2021-10-01 | 0.66667
4 | Shyampur | 132 | 139 | 8 | 2021-10-01 | 0.70833 | 130 | 3 | 2021-10-01 | 0.5
5 | Bhulta | 132 | 132 | 1 | 2021-10-01 | 0.70833 | 123 | 4 | 2021-10-01 | 0.625
6 | Madanganj | 132 | 139 | 8 | 2021-10-01 | 0.70833 | 128 | 3 | 2021-10-01 | 0.45833
7 | Shitalakhya | 132 | 139 | 8 | 2021-10-01 | 0.625 | 129 | 4 | 2021-10-01 | 0.66667
8 | Rahim Steal | 132 | 137 | 8 | 2021-10-01 | 0.625 | 129 | 4 | 2021-10-01 | 0.45833
9 | Matuail | 132 | 137 | 8 | 2021-10-01 | 0.70833 | 129 | 3 | 2021-10-01 | 0.625
10 | Ghorasal | 132 | 142 | 8 | 2021-10-01 | 0.54167 | 134 | 1 | 2021-10-01 | 0.54167
11 | Narsinghdi | 132 | 136 | 24 | 2021-10-01 | 0.33333 | 121 | 12 | 2021-10-01 | 0
12 | Haripur (SBU) | 132 | 138 | 25 | 2021-10-01 | 0.041667 | 129 | 4 | 2021-10-01 | 0.625
13 | Sreenagar | 132 | - |  | - | - | - | - | - | -
14 | Ullon | 132 | 136 | 6 | 2021-10-01 | 0.25 | 126 | 3 | 2021-10-01 | 0.66667
15 | Hasnabad | 132 | 138 | 5 | 2021-10-01 | 0.41667 | 128 | 4 | 2021-10-01 | 0.625
16 | Magbazar | 132 | 137 | 8 | 2021-10-01 | 0.25 | 125 | 12 | 2021-10-01 | 0.70833
17 | Maniknagar | 132 | 137 | 8 | 2021-10-01 | 0.70833 | 128 | 3 | 2021-10-01 | 0.45833
18 | Bangabhaban | 132 | 137 | 8 | 2021-10-01 | 0.70833 | 128 | 3 | 2021-10-01 | 0.45833
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
19 | Narinda | 132 | 137 | 8 | 2021-10-01 | 0.70833 | 128 | 3 | 2021-10-01 | 0.45833
20 | Dhanmondi | 132 | 136 | 7 | 2021-10-01 | 0.16667 | 127 | 4 | 2021-10-01 | 0.5
21 | Lalbag | 132 | 138 | 8 | 2021-10-01 | 0.77083 | 121 | 23 | 2021-10-01 | 0.5
22 | Madartek | 132 | 137 | 8 | 2021-10-01 | 0.25 | 126 | 4 | 2021-10-01 | 0.625
23 | Dhaka University | 132 | - | - | - | - | - | - | - | -
24 | Aftabnagar | 132 | 137 | 8 | 2021-10-01 | 0.20833 | 126 | 3 | 2021-10-01 | 0.5
25 | Fatullah | 132 | 140 | 22 | 2021-10-01 | 0.75 | 130 | 3 | 2021-10-01 | 0.5
26 | Nawabganj | 133 | 145 | 28 | 2021-10-01 | 0.20833 | 128 | 3 | 2021-10-01 | 0.5
27 | Mirpur | 132 | 134 | 2 | 2021-10-01 | 0.16667 | 123 | 23 | 2021-10-01 | 0.45833
28 | Kalyanpur | 132 | 134 | 2 | 2021-10-01 | 0.083333 | 123 | 23 | 2021-10-01 | 0.5
29 | Gulshan | 132 | 136 | 6 | 2021-10-01 | 0.25 | 124 | 6 | 2021-10-01 | 0.70833
30 | Uttara | 132 | 134 | 13 | 2021-10-01 | 0.29167 | 123 | 3 | 2021-10-01 | 0.5
31 | Uttara(New) | 132 | 137 | 5 | 2021-10-01 | 0.54167 | 122 | 23 | 2021-10-01 | 0.45833
32 | Kamrangirchar | 132 | 138 | 8 | 2021-10-01 | 0.75 | 127 | 30 | 2021-10-01 | 0.875
33 | Savar | 132 | 136 | 7 | 2021-10-01 | 0.16667 | 122 | 23 | 2021-10-01 | 0.45833
34 | Bhasantec | 132 | 138 | 29 | 2021-10-01 | 0.25 | 127 | 17 | 2021-10-01 | 0.5
35 | Agargaon | 132 | 139 | 13 | 2021-10-01 | 0.375 | 128 | 23 | 2021-10-01 | 0.5
36 | Satmosjid | 132 | 138 | 9 | 2021-10-01 | 0.16667 | 128 | 17 | 2021-10-01 | 0.625
37 | Tongi | 132 | 142 | 22 | 2021-10-01 | 0.75 | 128 | 3 | 2021-10-01 | 0.625
38 | Kabirpur | 132 | 139 | 20 | 2021-10-01 | 0.625 | 125 | 10 | 2021-10-01 | 0.75
39 | Basundhara | 132 | 141 | 24 | 2021-10-01 | 0.20833 | 124 | 3 | 2021-10-01 | 0.625
40 | Manikganj | 132 | 142 | 20 | 2021-10-01 | 16:00 | 127 | 24 | 2021-10-01 | 0.625
41 | Joydevpur | 132 | 141 | 13 | 2021-10-01 | 0.54167 | 129 | 3 | 2021-10-01 | 0.45833
42 | New Tongi | 132 | 142 | 22 | 2021-10-01 | 0.75 | 126 | 3 | 2021-10-01 | 0.625
43 | Kodda | 132 | 139 | 1 | 2021-10-01 | 0.75 | 120 | 3 | 2021-10-01 | 0.625
44 | Dhamrai | 132 | 140 | 1 | 2021-10-01 | 0.70833 | 129 | 23 | 2021-10-01 | 0.66667
45 | Rajendrapur | 132 | 139 | 8 | 2021-10-01 | 18:30 | 118 | 4 | 2021-10-01 | 12:00
46 | Valuka | 132 | 134 | 3 | 2021-10-01 | 0.70833 | 106 | 1 | 2021-10-01 | 0.83333
47 | Tangail | 132 | 142 | 29 | 2021-10-01 | 0.95833 | 120 | 10 | 2021-10-01 | 0.75
48 | Mymensing | 132 | 135 | 20 | 2021-10-01 | 0.70833 | 111 | 13 | 2021-10-01 | 0.20833
49 | Kishorganj | 132 | 135 | 20 | 2021-10-01 | 0.70833 | 116 | 8 | 2021-10-01 | 0.875
50 | Netrokona | 132 | 135 | 20 | 2021-10-01 | 0.70833 | 105 | 17 | 2021-10-01 | 0.875
51 | Jamalpur | 132 | 141 | 3 | 2021-10-01 | 0.54167 | 118 | 8 | 2021-10-01 | 0.875
52 | Sherpur | 132 | 140 | 3 | 2021-10-01 | 0.54167 | 115 | 8 | 2021-10-01 | 0.77083
53 | Srimongal | 132 | 140 | 3 | 2021-10-01 | 0.33333 | 129 | 9 | 2021-10-01 | 0.875
54 | Shahjibazar | 132 | 138 | 6 | 2021-10-01 | 0.33333 | 128 | 6 | 2021-10-01 | 0.91667
55 | Fenchuganj | 132 | 141 | 5 | 2021-10-01 | 1899-12-31 | 128 | 9 | 2021-10-01 | 0.91667
56 | Khulawara | 132 | 137 | 3 | 2021-10-01 | 0.375 | 127 | 10 | 2021-10-01 | 0.75
57 | Sylhet | 132 | 134 | 3 | 2021-10-01 | 0.375 | 121 | 11 | 2021-10-01 | 0.75
58 | Chattak | 132 | 135 | 24 | 2021-10-01 | 0.33333 | 118 | 10 | 2021-10-01 | 0.8125
59 | Sunamganj | 132 | 134 | 20 | 2021-10-01 | 0.75 | 114 | 10 | 2021-10-01 | 0.8125
60 | Biani Bazar | 132 | 135 | 4 | 2021-10-01 | 0.375 | 118 | 10 | 2021-10-01 | 0.8125
61 | Comilla(South) | 132 | 131 | 8 | 2021-10-01 | 0.33333 | 120 | 9 | 2021-10-01 | 0.75
62 | Comilla (North) | 132 | 143 | 19 | 2021-10-01 | 0.875 | 132 | 3 | 2021-10-01 | 0.625
63 | Chandpur | 132 | 143 | 13 | 2021-10-01 | 0.70833 | 131 | 23 | 2021-10-01 | 0.041667
64 | Feni | 132 | 139 | 12 | 2021-10-01 | 0.79167 | 126 | 23 | 2021-10-01 | 0.66667
65 | Chowmuhani | 132 | 137 | 13 | 2021-10-01 | 0.25 | 126 | 13 | 2021-10-01 | 0.125
66 | Ashuganj | 132 | 141 | 6 | 2021-10-01 | 0.33333 | 131 | 13 | 2021-10-01 | 0.875
67 | Daudkandi | 132 | 139 | 7 | 2021-10-01 | 0.83333 | 127 | 3 | 2021-10-01 | 0.625
68 | Brahminbaria | 132 | 135 | 1 | 2021-10-01 | 0.33333 | 124 | 13 | 2021-10-01 | 0.875
69 | Ramganj | 132 | 136 | 2 | 2021-10-01 | 0.70833 | 126 | 12 | 2021-10-01 | 0.95833
70 | Chaddagram | 132 | 138 | 1 | 2021-10-01 | 0.77083 | 129 | 21 | 2021-10-01 | 0.16667
71 | PHP | 132 | 137 | 2 | 2021-10-01 | 0.77083 | 125 | 21 | 2021-10-01 | 0.20833
72 | Kochua | 132 | 141 | 13 | 2021-10-01 | 0.25 | 130 | 23 | 2021-10-01 | 0.083333
73 | Madanhat | 132 | 141 | 16 | 2021-10-01 | 0.625 | 126 | 22 | 2021-10-01 | 0.375
74 | Hathazari | 132 | 139 | 2 | 2021-10-01 | 0.79167 | 128 | 23 | 2021-10-01 | 0.5
75 | Khulshi | 132 | 138 | 16 | 2021-10-01 | 0.66667 | 121 | 22 | 2021-10-01 | 0.5
76 | Halishahar | 132 | 139 | 12 | 2021-10-01 | 0.79167 | 123 | 22 | 2021-10-01 | 0.41667
77 | Baraulia | 132 | 140 | 15 | 2021-10-01 | 0.70833 | 123 | 22 | 2021-10-01 | 0.5
78 | Sikalbaha | 132 | 141 | 16 | 2021-10-01 | 0.66667 | 110 | 15 | 2021-10-01 | 0.83333
79 | Dohazari | 132 | 138 | 15 | 2021-10-01 | 0.77083 | 116 | 24 | 2021-10-01 | 0.25
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
80 | Cox'sbazar | 132 | 127 | 15 | 2021-10-01 | 0.70833 | 101 | 24 | 2021-10-01 | 0.25
81 | Chandraghona | 132 | 140 | 15 | 2021-10-01 | 0.70833 | 124 | 31 | 2021-10-01 | 0.16667
82 | Kaptai | 132 | 137 | 2 | 2021-10-01 | 0.75 | 125 | 31 | 2021-10-01 | 0.041667
83 | A. Khaer Stl. | 132 | 138 | 15 | 2021-10-01 | 0.70833 | 124 | 22 | 2021-10-01 | 0.5
84 | Bakulia | 132 | 139 | 12 | 2021-10-01 | 0.75 | 122 | 22 | 2021-10-01 | 0.5
85 | Julda | 132 | 140 | 8 | 2021-10-01 | 0.77083 | 123 | 22 | 2021-10-01 | 0.45833
86 | TK Chemical | 132 | 139 | 2 | 2021-10-01 | 0.79167 | 124 | 22 | 2021-10-01 | 0.45833
87 | Modern Steel | - | - | - | - | - | - | - | - | -
88 | Shahmirpur | 132 | 139 | 2 | 2021-10-01 | 0.79167 | 123 | 31 | 2021-10-01 | 0.20833
89 | Khagrachhari | 132 | 143 | 14 | 2021-10-01 | 0.54167 | 122 | 31 | 2021-10-01 | 0.16667
90 | Matarbari | 132 | 135 | 24 | 2021-10-01 | 0.54167 | 105 | 24 | 2021-10-01 | 0.25
91 | Baroiar Hat | 132 | 137 | 10 | 2021-10-01 | 0.5 | 126 | 22 | 2021-10-01 | 0.5
92 | Rangamati | 132 | 139 | 2 | 2021-10-01 | 0.79167 | 123 | 31 | 2021-10-01 | 0.16667
93 | Goalpara | 132 | 140 | 1 | 2021-10-01 | 0.70833 | 128 | 7 | 2021-10-01 | 0.95833
94 | Khulna Central | 132 | 140 | 15 | 2021-10-01 | 0.91667 | 127 | 7 | 2021-10-01 | 0.95833
95 | Noapara | 132 | 138 | 1 | 2021-10-01 | 0.70833 | 126 | 6 | 2021-10-01 | 0.47917
96 | Jessore | 132 | 138 | 17 | 2021-10-01 | 0.70833 | 123 | 6 | 2021-10-01 | 0.875
97 | Benapol | 132 | 137 | 8 | 2021-10-01 | 0.41667 | 123 | 6 | 2021-10-01 | 0.875
98 | Jhenida | 132 | 139 | 17 | 2021-10-01 | 0.70833 | 125 | 2 | 2021-10-01 | 0.91667
99 | Bottail | 132 | 138 | 22 | 2021-10-01 | 0.54167 | 128 | 2 | 2021-10-01 | 0.875
100 | G.K Project | 132 | 141 | 26 | 2021-10-01 | 0.25 | 129 | 20 | 2021-10-01 | 0.29167
101 | Faridpur | 132 | 139 | 26 | 2021-10-01 | 0.625 | 120 | 26 | 2021-10-01 | 0.41667
102 | Madaripur | 132 | 145 | 17 | 2021-10-01 | 0.70833 | 115 | 10 | 2021-10-01 | 0.91667
103 | Sariatpur | 132 | 144 | 17 | 2021-10-01 | 0.70833 | 128 | 11 | 2021-10-01 | 0.625
104 | Gopalganj | 132 | 145 | 17 | 2021-10-01 | 0.70833 | 128 | 10 | 2021-10-01 | 0.75
105 | Bagerhat | 132 | 140 | 15 | 2021-10-01 | 0.91667 | 120 | 16 | 2021-10-01 | 0.75
106 | Mongla | 132 | 138 | 15 | 2021-10-01 | 0.91667 | 121 | 16 | 2021-10-01 | 0.75
107 | Satkhira | 132 | 138 | 1 | 2021-10-01 | 0.70833 | 122 | 7 | 2021-10-01 | 0.95833
108 | Gallamari | 132 | 141 | 17 | 2021-10-01 | 0.70833 | 124 | 8 | 2021-10-01 | 0.79167
109 | Magura | 132 | 140 | 23 | 2021-10-01 | 0.33333 | 124 | 3 | 2021-10-01 | 0.041667
110 | Norail | 132 | 139 | 17 | 2021-10-01 | 0.70833 | 121 | 4 | 2021-10-01 | 0.91667
111 | Chuadanga | 132 | 137 | 31 | 2021-10-01 | 0.20833 | 117 | 2 | 2021-10-01 | 0.83333
112 | Barisal(N) | 132 | 144 | 17 | 2021-10-01 | 0.66667 | 127 | 28 | 2021-10-01 | 0.041667
113 | Barisal(S) | 132 | 143 | 17 | 2021-10-01 | 0.66667 | 127 | 15 | 2021-10-01 | 0.875
114 | Patuakhali | 132 | 142 | 17 | 2021-10-01 | 0.66667 | 124 | 11 | 2021-10-01 | 0.625
115 | Bhandaria | 132 | 145 | 17 | 2021-10-01 | 0.66667 | 122 | 9 | 2021-10-01 | 0.75
116 | Borguna | 132 | 144 | 17 | 2021-10-01 | 0.66667 | 125 | 11 | 2021-10-01 | 0.58333
117 | Ishurdi | 132 | 138 | 31 | 2021-10-01 | 0.25 | 130 | 28 | 2021-10-01 | 0.83333
118 | Ruppur paromanobik | 132 | 137 | 1 | 2021-10-01 | 0.75 | 130 | 28 | 2021-10-01 | 0.875
118 | Natore | 132 | 138 | 31 | 2021-10-01 | 0.75 | 128 | 3 | 2021-10-01 | 0.041667
119 | Bogra | 132 | 138 | 20 | 2021-10-01 | 0.58333 | 125 | 2 | 2021-10-01 | 0.83333
120 | Noagaon | 132 | 135 | 29 | 2021-10-01 | 0.625 | 118 | 1 | 2021-10-01 | 0.83333
121 | Rajshahi | 132 | 138 | 31 | 2021-10-01 | 0.75 | 127 | 13 | 2021-10-01 | 0.875
122 | Rajshahi New | 132 | 138 | 2 | 2021-10-01 | 0.75 | 126 | 13 | 2021-10-01 | 0.875
123 | C.Nawabganj | 132 | 139 | 18 | 2021-10-01 | 0.75 | 124 | 12 | 2021-10-01 | 0.54167
124 | Amnura | 132 | 139 | 18 | 2021-10-01 | 0.75 | 123 | 2 | 2021-10-01 | 0.083333
125 | Pabna | 132 | 136 | 1 | 2021-10-01 | 0.70833 | 120 | 16 | 2021-10-01 | 0.77083
126 | Shahjadpur | 132 | 141 | 27 | 2021-10-01 | 0.16667 | 132 | 9 | 2021-10-01 | 0.875
127 | Serajganj | 132 | 136 | 20 | 2021-10-01 | 0.625 | 125 | 1 | 2021-10-01 | 0.875
128 | Niyamatpur | 132 | 133 | 28 | 2021-10-01 | 0.79167 | 113 | 13 | 2021-10-01 | 0.83333
129 | Joypurhat | 132 | 136 | 30 | 2021-10-01 | 0.20833 | 116 | 13 | 2021-10-01 | 0.83333
130 | Sherpur(Bogura) | 132 | 137 | 31 | 2021-10-01 | 0.75 | 125 | 1 | 2021-10-01 | 0.83333
132 | Mohastangor | 132 | 138 | 20 | 2021-10-01 | 0.58333 | 122 | 1 | 2021-10-01 | 0.83333
133 | Bangura | 132 | 138 | 26 | 2021-10-01 | 0.25 | 129 | 13 | 2021-10-01 | 0.875
134 | Rangpur | 132 | 136 | 4 | 2021-10-01 | 0.54167 | 115 | 11 | 2021-10-01 | 0.95833
135 | Lalmonirhat | 132 | 135 | 3 | 2021-10-01 | 0.41667 | 115 | 2 | 2021-10-01 | 0.875
136 | Saidpur | 132 | 136 | 29 | 2021-10-01 | 0.625 | 112 | 2 | 2021-10-01 | 0.8125
137 | Purbasadipur | 132 | 136 | 3 | 2021-10-01 | 0.33333 | 109 | 14 | 2021-10-01 | 0.875
138 | Thakurgaon | 132 | 137 | 29 | 2021-10-01 | 0.25 | 108 | 6 | 2021-10-01 | 0.77083
139 | Palashbari | 132 | 136 | 29 | 2021-10-01 | 0.625 | 118 | 3 | 2021-10-01 | 0.041667
140 | Barapukuria | 132 | 139 | 4 | 2021-10-01 | 0.54167 | 122 | 15 | 2021-10-01 | 0.75
141 | Panchagar | 132 | 139 | 6 | 2021-10-01 | 0.25 | 109 | 14 | 2021-10-01 | 0.79167
142 | Joldhaka | 132 | 135 | 4 | 2021-10-01 | 0.54167 | 109 | 6 | 2021-10-01 | 0.77083
143 | Kurigram | 132 | 136 | 4 | 2021-10-01 | 0.25 | 113 | 2 | 2021-10-01 | 0.8125
144 | Mithapukur | 132 | 137 | 4 | 2021-10-01 | 0.54167 | 119 | 2 | 2021-10-01 | 0.8125
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:October 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 46 | 150 | 2021-09-10 | 10:00
Hasnabad | TR2 | 225 | 46 | 150
| TR3 | 225 | 0 | 0 | S/D
| TR1 | 225 | 185 | 540
Tongi | TR2 | 225 | 185 | 540 | 25/10/21 | 9:00
| TR3 | 225 | 185 | 540
Haripur | TR1 | 225 | 113 | 300
| TR2 | 225 | 113 | 300 | 16/10/21 | 10:00
| TR3 | 225 | 113 | 300
| TR1 | 225 | 197 | 540
Rampura | TR2 | 225 | 197 | 540 | 17/10/21 | 16:00
| TR3 | 225 | 197 | 540
Keraniganj | ATR1 | 300 | 104 | 288
| ATR2 | 300 | 104 | 288 | 2021-03-10 | 22:00
| ATR3 | 300 | 104 | 288
| TR1 | 225 | 132 | 360
Aminbazar | TR2 | 225 | 132 | 360 | 31/10/21 | 23:00
| TR3 | 225 | 137 | 371
Agargaon | TR1 | 300 | 182 | 517
| TR2 | 300 | 182 | 517 | 2021-11-10 | 18:00
Maniknagar | TR1 | 300 | 137 | 390 | 2021-10-10 | 13:00
| TR2 | 300 | 137 | 390
Cumilla (N) | TR1 | 225 | 170 | 470 | 24/10/21 | 16:00
| TR2 | 225 | 167 | 454
Fenchuganj | AT2 | 300 | 294 | 776 | 2021-07-10 | 18:00
| MT1 | 150 | 99 | 280
Hathazari | MT2 | 150 | 99 | 280 | 31/10/21 | 11:00
| MT3 | 150 | 99 | 280
| MT4 | 150 | 99 | 280
| TR1 | 225 | 88 | 217
Ishurdi | TR2 | 225 | 88 | 217 | 2021-07-10 | 21:00
| TR3 | 225 | 88 | 217
Khulna(S) | TR1 | 225 | 79 | 216
| TR2 | 225 | 79 | 216 | 2021-07-10 | 1:00
| TR3 | 300 | 101 | 375
Bogura | TR1 | 225 | 103 | 305
| TR2 | 225 | 103 | 305 | 13/10/21 | 20:00
| TR3 | 225 | 140 | 402
Baghabari | TR1 | 300 | 167 | 455 | 16/10/21 | 18:00
| TR2 | 225 | 118 | 320
Rajshahi | ATR-01 | 300 | 119 | 326 | 13/10/21 | 13:00
| ATR-02 | 300 | 119 | 326
Barapukuria | TR1 | 225 | 134 | 650 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 147 | 700 | 2021-04-10 | 13:00 | 132 kV current is being provided
| TR6 | 300 | 190 | 911
Bheramara | Transformer-1 | 225 | 85 | 220 | 27/10/21 | 3:00
| Transformer-2 | 225 | 85 | 220
Shyampur | ATR-01 | 300 | 125 | 386 | 2021-01-10 | 1:00
| ATR-02 | 300 | 125 | 386
Kaliakoir | TR1 | 300 | 127.9 | 340 | 2021-12-10 | 18:15
Sikalbaha | ATR-1 | 300 | 175 | 500 | 2021-05-10 | 16:00
| ATR-2 | 300 | 175 | 500
Jhenaidah | T1(230/132 kV) | 300 | 148 | 433 | 2021-05-10 | 19:00 | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:October 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 271.31 | 407 | 20/10/21 | 16:45
| TR2(400/230 kV) | 520 | 273.9 | 414
| TR1(400/132 kV) | 325 | 294.2 | 491 | 2021-09-10 | 18:15
| TR2(400/132 kV) | 325 | 294.7 | 490
Bibiyana | ICT1(400/230 kV) | 520 | 139 | 201 | 2021-02-10 | 2:00
| ICT2(400/230kV) | 520 | 135 | 195
Bhulta | ATR1(400/230 kV) | 520 | 209 | 386 | 2021-12-10 | 17:15
| ATR2(400/230kV) | 520 | 209 | 386
Ashuganj(N) | GSUT1 | 567 | 373 | 594.8 | 2021-01-10 | 7:33
Gopalganj | ATR1(400/138 kV) | 325 | 311 | 460 | 2021-12-10 | 19:00
| ATR2(400/138kV) | 325 | 311 | 460
Payra | GSUT1 | 270 | 210 | 933 | 2021-11-10 | 19:07
| GSUT2 | 270 | 210 | 907
| GSUT3 | 270 | 210 | 918
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:October 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:October 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-10-01 | 12308 | 12308 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-01 | 9693 | 9693 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-02 | 13178 | 13178 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-02 | 10805 | 10805 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-03 | 11569 | 11569 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-03 | 10430 | 10430 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-04 | 12425 | 12425 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-04 | 10354 | 10354 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-05 | 12406 | 12406 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-05 | 10505 | 10505 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-06 | 12829 | 12829 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-06 | 10784 | 10784 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-07 | 12972 | 12972 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-07 | 11291 | 11291 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-08 | 12349 | 12349 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-08 | 9556 | 9556 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-09 | 13243 | 13243 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-09 | 10263 | 10263 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-10 | 13390 | 13390 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-10 | 11533 | 11533 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-11 | 13482 | 13482 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-11 | 11837 | 11837 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-12 | 13420 | 13420 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-12 | 11973 | 11973 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-13 | 13445 | 13445 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-13 | 11513 | 11513 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-14 | 13102 | 13102 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-14 | 11987 | 11987 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-15 | 11744 | 11744 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-15 | 10398 | 10398 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-16 | 12829 | 12829 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-16 | 10815 | 10815 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-17 | 12100 | 12100 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-17 | 11277 | 11277 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-18 | 11556 | 11556 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-18 | 10248 | 10248 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-19 | 11009 | 11009 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-19 | 9437 | 9437 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-20 | 10550 | 10550 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-20 | 9154 | 9154 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-21 | 11874 | 11874 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-21 | 9930 | 9930 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-22 | 10215 | 10215 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-22 | 8300 | 8300 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-23 | 11457 | 11457 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-23 | 8710 | 8710 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-24 | 11618 | 11618 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-24 | 9809 | 9809 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-25 | 11615 | 11615 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-25 | 9650 | 9650 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-26 | 11827 | 11827 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-26 | 9962 | 9962 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-27 | 11784 | 11784 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-27 | 9839 | 9839 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-28 | 11926 | 11926 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-28 | 9973 | 9973 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-29 | 10780 | 10780 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-29 | 8438 | 8438 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-30 | 11641 | 11641 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-30 | 9475 | 9475 | - | - | - | - | - | - | - | - | - | - | - | -
2021-10-31 | 10779 | 10779 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-10-31 | 9445 | 9445 | - | - | - | - | - | - | - | - | - | - | - | -
Evening Peak | Max. L/S | 0 | - | -
| Min. L/S | 0 | - | -
| No. of Days | - | [12 empty] | 0 | 0 | 1
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | 0 | 0 | 29
[15 empty] | 0 | 0 | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:October 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13482 | 2021-10-11 | 21:00
2 | Maximum Day Peak Genaration | MW | 11987 | 2021-10-14 | 12:00
3 | Maximum Evening Peak Demand | MW | 13482 | 2021-10-11 | 21:00
4 | Minimum Generation | MW | 7486 | 2021-10-22 | 19:30
5 | Average of the daily evening peak Genaration | MW | 12110.3871
6 | Average of the daily day peak Genaration | MW | 10238.1935
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 7870.5646
12 | Total Generation by BPDB | MkWh | 1492.9513 | % of total Gen. | 18.97%
13 | Total Generation by IPP | MkWh | 3048.1141 | '' | 38.73%
14 | A) Total Generation by Generation Companies | MkWh | 2127.1934 | '' | 27.03%
| B) Total Generation by REB | MkWh | 147.564 | " | 1.875%
| C) Total Generation by RENTAL | MkWh | 437.4456 | " | 5.558%
| D) Total Imported from India (BIPTC) | MkWh | 529.1884 | " | 6.724%
| E) Total Imported from Tripura, India (A.C) | MkWh | 88.1078 | " | 1.119%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4548.5962 | % of total Gen. | 57.79%
| B) Oil | MkWh | 2181.4876 | '' | 27.72%
| C) Hydro | MkWh | 111.4727 | '' | 1.416%
| D) Solar | MkWh | 20.1353 | '' | 0.2558%
| E) Coal | MkWh | 391.5767 | '' | 4.975%
| F) BIPTC (Import from India) | MkWh | 529.1884 | '' | 6.724%
| G) A.C (Import from Tripura, India) | MkWh | 88.1078 | '' | 1.119%
16 | Maximun of the daily total Generation . | MkWh | 291.6333 | 2021-10-12
17 | Monthly Load factor | % | 78.4655
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 26655.7201
| A) Gas | M.Taka | 4816.0921
| B) Liquid fuel | M.Taka | 16775.5638
| C) Coal | M.Taka | 1813.8125
| D) BIPTC (Import from India) | M.Taka | 2610.3876
| E) Tripura(Import from India) | M.Taka | 639.864
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1124.7024 | 2021-10-12
| A) Gas | M.Taka | 163.726 | 2021-10-03
| B) Liquid fuel | M.Taka | 901.6907 | 2021-10-12
| C) Coal | M.Taka | 71.989 | 2021-10-12
| D) BIPTC (Import from India) | M.Taka | 88.421 | 2021-10-27
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.6211
| B) Excluding Hydro & Solar | Taka/kWhR | 3.6823
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.34 | 31/10/2021 | 06:00
b) | Actual | FT (MSL) | 108.9 | 31/10/2021 | 06:00
22 | Peak Genaration of October 2020 | MW | 12759 | 11/10/2021 | 19:00
23 | Peak Demand of October 2020 | MW | 12552 | 11/10/2021 | 19:00
24 | Maximum peak Generation recorded upto 31/10/2021 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 31/10/2021 | MW | 14097 | 27/04/21 | 20:00
26 | Maximum load shed recorded upto 31/10/2021 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.