## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-12-15 | Wednesday
|  | Date (day): | 2021-12-15 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11354.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13042 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-12-14 | 2021-12-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 100 | 90 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 82 | 101 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 271 | 398 | 0 | 0 | 412 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 342 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 15 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 24 | 25 | 25 |  | 75 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 82 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 51 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 25 | 25 | 25
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 52 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 130 | 285 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 118 | 90 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 6 | 70 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 132 | 144 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 56 | 57 | 0 | 0
| Dhaka area Total |  |  |  |  | 6178 | 5560 | 1942 | 2449 | 2407 | 3112 | 892 | 1499
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 16 | 25 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 50 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 72 | 73 | 73 | 73 |  | 157 | Low Water Level & Unit 2 & 4,5 U/M.
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 68 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 80 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 40 | 100 | 100
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 78 | 90 | 90 | 90 |  | 10 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 11 | 10 | 10
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 15 | 0 | 90 | 90 |  | 18 | Engine problem
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 300 | 16 | 300 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 38 | 110 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 90 | 100 | 100
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 66 | 105 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 725 | 795 | 1320 | 1324 | 0 | 1040
60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 90 | 100 | 100
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 166 | 160 | 225 | 225 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 245 | 250 | 270 | 270 |  | 90 | ST Under maint.
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 220 | 250 | 360 | 360 |  |  | FGMO
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 10 | 29 | 29 |  | 16 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55
66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 16
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 123 | 142 | 125 | 135 |  | 15 | Engine problem
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 34 | 200 | 200
72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 87 | 95 | 138 | 164
74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 52 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 13 | 114 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 59 | 109 | 113 | 113
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1120 | 1360 | 1982 | 2226 | 264 | 321
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 97 | 103 | 120 | 120 | 82 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 8 | 120 | 200 | 200
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 55 | 115 | 115 | 115
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 25 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 255 | 384 | 530.6 | 479 | 82 | 8
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 44 | 43 | 44 | 44 |  | 46 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 67 | 66 | 66
96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 77 | 80 | 80
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 70 | 70 |  | 30 | Engine prolem
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 220 | 220
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 24 | 24 | 24
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 392 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1003 | 1066 | 1199 | 1199 | 0 | 1175
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 660 | 708 | 675 | 723
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 6 | 0 | 0 | 40 |  | 69 | Engine problem
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 165 | 155 | 300 | 370 | 40 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 45 | 105 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 0 | 0 | 30 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 2248 | 2129 | 906 | 968 | 1130 | 1688 | 40 | 93
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 20 | 23 | 23 |  | 10 | Engine problem
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 64 | 72 | 72 |  | 122 | Machine problem.
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 76 | 11 | 11 | 84 |  | Gas shortage
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 270 | 590 | 620 | 620
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 160 | 0 | 200 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 0 | 150
| Barisal Area Total |  |  |  |  | 2046 | 2046 | 506 | 785 | 1036 | 1206 | 84 | 132
121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 50 | 50
123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 33 |  | 17 | Engine problem
127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 118 | 125 | 0 | 0 | 220 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 156 | 200 | 200 |  |  | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 337 | 335 | 400 | 400 |  |  | FGMO
131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35 |  | 15 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 52 | 52 | 52
136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 50 | 96 | 100
137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 91 | 113 | 113 | 113
139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 113 | 113 | 113
140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 818 | 1052 | 1368 | 1434 | 600 | 98
141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 82 | 80 | 81 | 81
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 169 | 169 | 180 | 180 | 94 |  | Coal shortage
143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 107 | 113 | 113 | 113
146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 363 | 362 | 382 | 374 | 94 | 125
| Total |  |  |  |  | 22031 | 20934 | 7638 | 9221 | 11354.6 | 13042 | 2056 | 4491
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7368.7938 | 8896 | 10954.3999 | 12582.3264
A. |  | 2021-12-14 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9221 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5814 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9221 | MW
3 | Day peak Generation : |  |  | 7638 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8896 | MW
4 | Evening peak Generation : |  |  | 9221 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 180.4701 | MKWHr | By Solar | 0.82611 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 102.6956 | MKWHr |  | By Oil: | 43.0465 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.0041 | MKWHr |  | By Hydro: | 1.6806 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2056 | MW | Dhaka | 3299 | 3299 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4491 | MW | Chittagong | 1014 | 1014 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 6547 | MW | Khulna | 1055 | 1055 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 780.67 | MMCFD |  |  | Rajshahi | 884 | 884 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 104326544.678 | ii) Oil : | Taka | 281894689.18 | Comilla | 745 | 745 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 77669529.54 | Total | Taka | 463890763.398 | Mymensingh | 706 | 706 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 336 | 336 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 206 | MW (E to W) at | 19:30 | hrs | Barisal | 260 | 260 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 126 | MW at | 1:00 | hrs | Rangpur | 597 | 597 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.7° C |  |  | Total | 8896 | 8896 |  | 0
B. |  | 2021-12-15 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 25.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13042 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
4 | Reserve(Generation end) |  |  |  | 3842 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 180.0591 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5793 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.2655 | MKWHr. | ii) HVDC Flow at Peak Time |  | 708 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9517 | MKWHr. | iii) Maximum HVDC Flow : |  | 708 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.41 |  | (b) Today: | 100.27 |  | (c) Rule Curve: |  | 104.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-12-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 400 | 349 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 25 | 28 | 20 | 33 | 0 | 0 | 31 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 21 | 38 | 0 | 0 | 80 | 190 | 220 | 132 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 30 | 9 | 72 | 103 | 0 | 22 | 0 | 42 | 44 | 53 | 0 | 130 | 0 | 65 | 81 | 0 | 190 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 100 | 0 | 35 | 0 | 0 | 0 | 260 | 54 | 0 | 0 | 112 | 0 | 400 | 53 | 0 | 162 | 0 | 0 | 17 | 0 | 0 | 56 |  | 445 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 169 | 0 | 0 | 0 | 0 | 120 | 0 | 11 | 0 | 157 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 218 | 0 | 0 | 0 | 0 |  | 4499 | 2120 | 6619 | 2938 | 445 | 1591 | 0 | 952 | 550 | 71 | 0 | 0 | 72 | 0 | 0 | 100.44
2:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 382 | 350 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 25 | 28 | 20 | 33 | 0 | 0 | 31 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 21 | 38 | 0 | 0 | 80 | 190 | 220 | 134 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 30 | 9 | 70 | 104 | 0 | 22 | 0 | 42 | 44 | 53 | 0 | 130 | 0 | 40 | 81 | 0 | 170 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 245 | 54 | 0 | 0 | 75 | 0 | 400 | 0 | 0 | 126 | 0 | 0 | 17 | 0 | 0 | 57 |  | 431 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 120 | 0 | 11 | 0 | 157 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 180 | 0 | 0 | 0 | 0 |  | 4157 | 2054 | 6211 | 2877 | 431 | 1552 | 0 | 671 | 539 | 71 | 0 | 0 | 70 | 0 | 0 | 100.43
3:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 379 | 322 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 25 | 28 | 20 | 33 | 0 | 0 | 31 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 21 | 38 | 0 | 0 | 80 | 190 | 220 | 132 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 30 | 9 | 70 | 102 | 0 | 22 | 0 | 42 | 44 | 53 | 0 | 110 | 0 | 40 | 81 | 0 | 165 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 210 | 54 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 108 | 0 | 0 | 17 | 0 | 0 | 56 |  | 431 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 170 | 0 | 0 | 0 | 0 | 120 | 0 | 11 | 0 | 157 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 181 | 0 | 0 | 0 | 0 |  | 3965 | 2065 | 6030 | 2874 | 431 | 1504 | 0 | 539 | 541 | 71 | 0 | 0 | 70 | 0 | 0 | 100.43
4:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 377 | 301 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 25 | 28 | 20 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 21 | 38 | 0 | 0 | 80 | 190 | 220 | 133 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 30 | 9 | 68 | 104 | 0 | 22 | 0 | 42 | 44 | 53 | 0 | 110 | 0 | 40 | 81 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 190 | 54 | 0 | 0 | 17 | 0 | 401 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 57 |  | 431 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 170 | 0 | 0 | 0 | 0 | 120 | 0 | 11 | 0 | 157 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 180 | 0 | 0 | 0 | 0 |  | 3852 | 2070 | 5922 | 2880 | 431 | 1482 | 0 | 447 | 542 | 72 | 0 | 0 | 68 | 0 | 0 | 100.42
5:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 381 | 301 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 25 | 24 | 20 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 21 | 40 | 0 | 0 | 80 | 190 | 220 | 133 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 30 | 9 | 67 | 104 | 0 | 22 | 0 | 42 | 44 | 53 | 0 | 110 | 0 | 40 | 10 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 155 | 54 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 56 |  | 431 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 170 | 0 | 0 | 0 | 0 | 120 | 0 | 11 | 0 | 160 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 180 | 0 | 0 | 0 | 0 |  | 3727 | 2087 | 5814 | 2887 | 431 | 1412 | 0 | 393 | 552 | 72 | 0 | 0 | 67 | 0 | 0 | 100.42
6:00 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 386 | 321 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 17 | 25 | 24 | 20 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 21 | 40 | 0 | 0 | 80 | 190 | 220 | 135 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 30 | 9 | 66 | 106 | 0 | 22 | 0 | 42 | 44 | 53 | 0 | 163 | 0 | 40 | 10 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 18 | 0 | 4 | 0 | 0 | 0 | 165 | 54 | 0 | 0 | 32 | 0 | 380 | 11 | 0 | 17 | 19 | 0 | 17 | 0 | 0 | 57 |  | 431 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 84 | 0 | 168 | 0 | 0 | 0 | 0 | 125 | 0 | 10 | 0 | 163 | 0 | 325 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 280 | 200 | 0 | 0 | 0 | 0 |  | 3808 | 2111 | 5919 | 2786 | 431 | 1506 | 0 | 526 | 532 | 72 | 0 | 0 | 66 | 0 | 0 | 100.41
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 303 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 17 | 25 | 24 | 20 | 33 | 0 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 32 | 21 | 31 | 0 | 0 | 80 | 190 | 220 | 138 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 6 | 21 | 8 | 30 | 9 | 65 | 105 | 0 | 22 | 0 | 42 | 44 | 53 | 0 | 130 | 0 | 71 | 81 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 76 | 0 | 36 | 0 | 24 | 0 | 0 | 0 | 235 | 54 | 5 | 0 | 57 | 10 | 400 | 71 | 0 | 92 | 72 | 0 | 17 | 2 | 0 | 57 |  | 431 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 168 | 0 | 0 | 0 | 0 | 125 | 0 | 10 | 0 | 166 | 0 | 327 | 5 | 0 | 56 | 0 | 35 | 0 | 0 | 35 | 270 | 220 | 0 | 0 | 0 | 2 |  | 4033 | 2250 | 6283 | 2585 | 431 | 1536 | 0 | 1066 | 521 | 73 | 0 | 0 | 65 | 6 | 0 | 100.41
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 321 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 14 | 25 | 24 | 20 | 33 | 0 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 0 | 0 | 80 | 190 | 220 | 164 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 12 | 21 | 8 | 33 | 9 | 66 | 105 | 0 | 20 | 1 | 42 | 44 | 53 | 0 | 130 | 0 | 71 | 81 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 14 | 0 | 0 | 2 | 0 | 23 | 0 | 76 | 0 | 83 | 0 | 65 | 0 | 0 | 1 | 280 | 54 | 35 | 0 | 58 | 10 | 350 | 104 | 12 | 128 | 87 | 0 | 17 | 10 | 0 | 57 |  | 431 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 22 | 0 | 11 | 82 | 0 | 168 | 0 | 0 | 0 | 0 | 125 | 0 | 10 | 0 | 168 | 0 | 326 | 36 | 0 | 96 | 0 | 90 | 0 | 1 | 100 | 300 | 205 | 0 | 0 | 0 | 4 |  | 4468 | 2466 | 6934 | 2638 | 431 | 1517 | 0 | 1630 | 550 | 73 | 0 | 0 | 66 | 29 | 0 | 100.4
9:00 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 379 | 347 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 25 | 24 | 20 | 33 | 22 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 38 | 21 | 6 | 0 | 0 | 80 | 250 | 220 | 145 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 16 | 21 | 8 | 33 | 9 | 79 | 106 | 0 | 20 | 1 | 43 | 44 | 53 | 0 | 130 | 0 | 70 | 75 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 82 | 0 | 0 | 24 | 0 | 42 | 0 | 40 | 0 | 108 | 0 | 86 | 0 | 0 | 2 | 260 | 54 | 17 | 0 | 58 | 10 | 400 | 104 | 27 | 108 | 68 | 0 | 17 | 18 | 0 | 57 |  | 465 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 22 | 0 | 11 | 81 | 0 | 168 | 0 | 0 | 0 | 0 | 125 | 0 | 10 | 0 | 168 | 0 | 326 | 35 | 0 | 110 | 0 | 109 | 0 | 3 | 70 | 300 | 190 | 0 | 0 | 0 | 11 |  | 4769 | 2500 | 7269 | 2749 | 465 | 1538 | 0 | 1754 | 549 | 73 | 0 | 0 | 79 | 62 | 0 | 100.4
10:00 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 323 | 320 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 17 | 25 | 28 | 28 | 33 | 47 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 10 | 0 | 38 | 21 | 6 | 0 | 0 | 80 | 240 | 220 | 160 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 16 | 21 | 8 | 33 | 9 | 81 | 103 | 0 | 22 | 2 | 42 | 44 | 53 | 0 | 163 | 0 | 70 | 75 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 110 | 0 | 0 | 35 | 0 | 58 | 0 | 40 | 0 | 123 | 0 | 75 | 0 | 0 | 3 | 260 | 54 | 17 | 0 | 59 | 20 | 400 | 104 | 39 | 108 | 51 | 0 | 17 | 25 | 0 | 57 |  | 666 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 0 | 11 | 84 | 0 | 168 | 0 | 0 | 0 | 0 | 125 | 0 | 10 | 0 | 162 | 0 | 326 | 35 | 0 | 50 | 0 | 90 | 0 | 4 | 50 | 280 | 160 | 0 | 0 | 0 | 21 |  | 4833 | 2502 | 7335 | 2675 | 666 | 1511 | 0 | 1703 | 532 | 73 | 0 | 0 | 81 | 94 | 0 | 100.39
11:00 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 324 | 320 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 17 | 25 | 24 | 28 | 33 | 51 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 38 | 21 | 6 | 0 | 0 | 80 | 240 | 220 | 153 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 16 | 21 | 8 | 33 | 9 | 84 | 100 | 0 | 22 | 2 | 43 | 44 | 53 | 0 | 130 | 0 | 65 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 110 | 0 | 0 | 24 | 0 | 98 | 18 | 40 | 0 | 127 | 0 | 75 | 0 | 0 | 4 | 300 | 54 | 17 | 0 | 58 | 20 | 400 | 104 | 45 | 108 | 51 | 0 | 17 | 25 | 0 | 56 |  | 667 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 84 | 0 | 169 | 0 | 0 | 0 | 0 | 120 | 0 | 11 | 0 | 158 | 0 | 328 | 35 | 0 | 50 | 0 | 90 | 0 | 5 | 50 | 270 | 160 | 0 | 0 | 0 | 28 |  | 4911 | 2509 | 7420 | 2644 | 667 | 1523 | 0 | 1777 | 523 | 72 | 0 | 3 | 84 | 127 | 0 | 100.39
12:00 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 271 | 343 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 16 | 12 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 24 | 28 | 33 | 51 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 10 | 15 | 38 | 21 | 0 | 0 | 0 | 80 | 245 | 220 | 166 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 24 | 21 | 8 | 0 | 9 | 87 | 97 | 0 | 22 | 2 | 43 | 44 | 53 | 0 | 163 | 0 | 65 | 40 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 130 | 0 | 0 | 8 | 0 | 118 | 19 | 78 | 0 | 123 | 0 | 55 | 6 | 0 | 4 | 300 | 54 | 38 | 0 | 59 | 10 | 370 | 104 | 46 | 132 | 66 | 0 | 17 | 30 | 0 | 56 |  | 660 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 82 | 0 | 169 | 0 | 0 | 0 | 0 | 118 | 0 | 11 | 0 | 150 | 0 | 337 | 45 | 0 | 91 | 0 | 107 | 0 | 5 | 60 | 270 | 160 | 0 | 0 | 5 | 30 |  | 5045 | 2593 | 7638 | 2525 | 660 | 1561 | 0 | 2049 | 521 | 72 | 0 | 22 | 87 | 141 | 0 | 100.38
13:00 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 260 | 343 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 48 | 16 | 24 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 24 | 28 | 33 | 51 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 24 | 38 | 21 | 12 | 0 | 0 | 80 | 250 | 220 | 155 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 37 | 21 | 8 | 0 | 9 | 89 | 96 | 0 | 22 | 2 | 43 | 44 | 50 | 0 | 130 | 0 | 66 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 15 | 11 | 0 | 182 | 0 | 0 | 8 | 0 | 119 | 18 | 50 | 0 | 125 | 0 | 75 | 17 | 0 | 4 | 300 | 54 | 78 | 0 | 57 | 35 | 400 | 90 | 42 | 162 | 82 | 0 | 17 | 26 | 0 | 57 |  | 660 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 20 | 0 | 11 | 85 | 0 | 169 | 0 | 0 | 0 | 0 | 118 | 0 | 11 | 0 | 139 | 0 | 344 | 80 | 0 | 113 | 0 | 90 | 0 | 5 | 95 | 290 | 160 | 0 | 0 | 4 | 32 |  | 5250 | 2695 | 7945 | 2521 | 660 | 1590 | 0 | 2320 | 544 | 72 | 0 | 16 | 89 | 133 | 0 | 100.38
14:00 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 301 | 300 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 24 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 24 | 25 | 33 | 51 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 38 | 21 | 10 | 0 | 0 | 80 | 30 | 220 | 202 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 7 | 9 | 91 | 96 | 0 | 22 | 2 | 43 | 44 | 53 | 0 | 130 | 0 | 65 | 76 | 0 | 165 | 18 | 0 | 10 | 0 | 15 | 11 | 0 | 130 | 0 | 0 | 32 | 0 | 76 | 15 | 50 | 0 | 135 | 0 | 55 | 17 | 0 | 3 | 300 | 54 | 68 | 0 | 58 | 50 | 398 | 70 | 33 | 162 | 86 | 0 | 17 | 24 | 0 | 57 |  | 661 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 11 | 82 | 0 | 169 | 0 | 0 | 0 | 0 | 105 | 0 | 8 | 0 | 134 | 0 | 322 | 90 | 0 | 113 | 0 | 50 | 0 | 4 | 113 | 350 | 0 | 0 | 0 | 3 | 28 |  | 4906 | 2488 | 7394 | 2325 | 661 | 1369 | 0 | 2163 | 601 | 72 | 0 | 0 | 91 | 112 | 0 | 100.37
15:00 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 303 | 340 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 24 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 24 | 25 | 17 | 34 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 6 | 0 | 0 | 80 | 45 | 250 | 201 | 8 | 0 | 5 | 5 | 0 | 35 | 0 | 0 | 34 | 21 | 11 | 33 | 9 | 90 | 93 | 0 | 20 | 1 | 43 | 43 | 53 | 0 | 163 | 0 | 64 | 75 | 0 | 165 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 130 | 0 | 0 | 32 | 0 | 53 | 10 | 20 | 0 | 137 | 0 | 55 | 0 | 0 | 2 | 300 | 54 | 51 | 0 | 81 | 20 | 395 | 100 | 23 | 144 | 87 | 0 | 17 | 18 | 0 | 57 |  | 661 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 11 | 83 | 0 | 169 | 0 | 0 | 0 | 0 | 108 | 0 | 60 | 0 | 133 | 0 | 301 | 70 | 0 | 70 | 0 | 96 | 0 | 3 | 70 | 420 | 0 | 0 | 3 | 2 | 18 |  | 4831 | 2488 | 7319 | 2365 | 661 | 1455 | 0 | 1927 | 672 | 72 | 0 | 0 | 90 | 77 | 0 | 100.37
16:00 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 252 | 300 |  | 0 | 270 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 48 | 0 | 24 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 24 | 25 | 33 | 34 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 12 | 0 | 21 | 6 | 0 | 0 | 110 | 260 | 250 | 184 | 8 | 0 | 10 | 5 | 0 | 35 | 0 | 0 | 34 | 21 | 8 | 33 | 9 | 87 | 97 | 0 | 20 | 0 | 43 | 43 | 53 | 0 | 110 | 0 | 40 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 158 | 0 | 0 | 32 | 0 | 48 | 5 | 10 | 14 | 140 | 0 | 55 | 0 | 11 | 1 | 300 | 54 | 65 | 0 | 105 | 10 | 350 | 104 | 11 | 144 | 87 | 0 | 17 | 7 | 0 | 56 |  | 661 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 108 | 0 | 44 | 0 | 138 | 0 | 302 | 53 | 0 | 70 | 0 | 75 | 0 | 2 | 50 | 400 | 0 | 0 | 17 | 0 | 11 |  | 4942 | 2400 | 7342 | 2500 | 661 | 1352 | 0 | 1984 | 649 | 72 | 0 | 0 | 87 | 37 | 0 | 100.36
17:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 315 | 338 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 48 | 48 | 24 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 24 | 25 | 33 | 34 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 2 | 8 | 18 | 0 | 21 | 7 | 0 | 0 | 110 | 260 | 250 | 196 | 8 | 0 | 10 | 5 | 0 | 43 | 0 | 0 | 34 | 21 | 11 | 33 | 9 | 88 | 100 | 0 | 22 | 0 | 43 | 43 | 53 | 0 | 163 | 0 | 55 | 75 | 0 | 165 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 192 | 0 | 0 | 32 | 0 | 35 | 0 | 50 | 17 | 142 | 0 | 67 | 0 | 17 | 0 | 300 | 54 | 71 | 0 | 100 | 10 | 350 | 104 | 1 | 144 | 87 | 0 | 17 | 1 | 0 | 57 |  | 660 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 22 | 0 | 11 | 82 | 0 | 169 | 0 | 0 | 0 | 0 | 125 | 0 | 30 | 0 | 153 | 0 | 300 | 53 | 0 | 70 | 0 | 82 | 0 | 0 | 50 | 410 | 0 | 0 | 17 | 0 | 3 |  | 5284 | 2499 | 7783 | 2695 | 660 | 1440 | 0 | 2105 | 661 | 72 | 0 | 57 | 88 | 5 | 0 | 100.36
18:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 290 | 347 |  | 0 | 270 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 82 | 82 | 24 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 14 | 25 | 33 | 52 | 0 | 32 | 40 | 0 | 0 | 6 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 30 | 18 | 33 | 21 | 4 | 0 | 0 | 90 | 210 | 250 | 191 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 48 | 21 | 11 | 33 | 9 | 93 | 100 | 0 | 22 | 0 | 43 | 43 | 53 | 0 | 163 | 0 | 68 | 75 | 0 | 165 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 275 | 0 | 0 | 46 | 0 | 66 | 0 | 90 | 17 | 138 | 0 | 115 | 16 | 28 | 0 | 300 | 54 | 106 | 17 | 108 | 40 | 400 | 104 | 0 | 144 | 105 | 0 | 17 | 0 | 0 | 57 |  | 708 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 0 | 34 | 0 | 45 | 35 | 22 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 125 | 0 | 68 | 0 | 155 | 0 | 334 | 100 | 0 | 102 | 0 | 113 | 0 | 0 | 113 | 460 | 0 | 0 | 35 | 0 | 0 |  | 5836 | 3024 | 8860 | 2657 | 708 | 1531 | 0 | 2847 | 709 | 72 | 0 | 243 | 93 | 0 | 0 | 100.35
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 363 | 342 |  | 0 | 270 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 102 | 82 | 24 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 26 | 25 | 33 | 52 | 0 | 33 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 40 | 18 | 50 | 21 | 13 | 0 | 0 | 90 | 250 | 250 | 164 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 96 | 99 | 0 | 22 | 0 | 43 | 44 | 53 | 0 | 163 | 0 | 66 | 75 | 0 | 165 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 295 | 0 | 0 | 100 | 0 | 130 | 0 | 90 | 19 | 130 | 0 | 115 | 35 | 35 | 0 | 0 | 54 | 110 | 17 | 109 | 70 | 400 | 104 | 0 | 144 | 105 | 0 | 17 | 0 | 0 | 57 |  | 708 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 0 | 50 | 0 | 52 | 0 | 21 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 125 | 0 | 76 | 0 | 156 | 0 | 334 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 35 | 0 | 0 |  | 5930 | 3126 | 9056 | 2754 | 708 | 1542 | 0 | 2876 | 799 | 73 | 0 | 208 | 96 | 0 | 0 | 100.34
19:30 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 398 | 342 |  | 0 | 270 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 24 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 26 | 25 | 33 | 52 | 0 | 33 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 40 | 0 | 50 | 21 | 11 | 0 | 0 | 90 | 250 | 250 | 160 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 95 | 103 | 0 | 22 | 0 | 43 | 43 | 53 | 0 | 163 | 0 | 67 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 285 | 0 | 0 | 120 | 0 | 90 | 0 | 90 | 34 | 142 | 0 | 115 | 70 | 68 | 0 | 16 | 54 | 110 | 13 | 109 | 90 | 392 | 104 | 0 | 144 | 105 | 0 | 17 | 0 | 0 | 57 |  | 708 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 0 | 50 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 125 | 0 | 76 | 0 | 156 | 0 | 335 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 0 | 0 | 35 | 0 | 0 |  | 6054 | 3167 | 9221 | 2780 | 708 | 1544 | 0 | 2974 | 839 | 73 | 0 | 208 | 95 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 397 | 342 |  | 0 | 270 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 48 | 24 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 25 | 33 | 52 | 0 | 33 | 40 | 0 | 0 | 23 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 16 | 0 | 0 | 90 | 230 | 250 | 164 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 97 | 102 | 0 | 22 | 0 | 42 | 43 | 53 | 0 | 163 | 0 | 67 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 285 | 0 | 0 | 100 | 0 | 113 | 0 | 60 | 0 | 140 | 0 | 115 | 70 | 51 | 0 | 110 | 54 | 68 | 0 | 108 | 70 | 400 | 104 | 0 | 144 | 105 | 0 | 17 | 0 | 0 | 56 |  | 708 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 52 | 0 | 20 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 126 | 0 | 74 | 0 | 158 | 0 | 335 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 0 | 0 | 35 | 0 | 0 |  | 5872 | 3149 | 9021 | 2781 | 708 | 1547 | 0 | 2878 | 839 | 73 | 0 | 98 | 97 | 0 | 0 | 100.34
21:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 390 | 336 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 32 | 24 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 25 | 33 | 52 | 0 | 33 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 21 | 25 | 0 | 0 | 80 | 220 | 250 | 182 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 94 | 103 | 0 | 22 | 0 | 42 | 43 | 53 | 0 | 130 | 0 | 71 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 293 | 0 | 0 | 100 | 0 | 85 | 0 | 60 | 0 | 143 | 0 | 115 | 35 | 0 | 0 | 286 | 54 | 34 | 0 | 108 | 0 | 400 | 104 | 0 | 161 | 105 | 0 | 17 | 0 | 0 | 55 |  | 707 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 25 | 0 | 52 | 0 | 21 | 0 | 11 | 80 | 0 | 168 | 0 | 0 | 0 | 0 | 125 | 0 | 76 | 0 | 164 | 0 | 380 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 0 | 0 | 35 | 0 | 0 |  | 5728 | 3170 | 8898 | 2777 | 707 | 1565 | 0 | 2762 | 838 | 73 | 0 | 82 | 94 | 0 | 0 | 100.34
22:00 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 380 | 314 |  | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 26 | 25 | 33 | 34 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 38 | 21 | 25 | 0 | 0 | 80 | 220 | 250 | 195 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 86 | 102 | 0 | 22 | 0 | 42 | 43 | 53 | 0 | 130 | 0 | 71 | 78 | 0 | 165 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 0 | 0 | 65 | 0 | 83 | 0 | 10 | 0 | 142 | 0 | 115 | 0 | 0 | 0 | 277 | 54 | 17 | 0 | 118 | 0 | 400 | 104 | 0 | 162 | 17 | 0 | 17 | 0 | 0 | 56 |  | 708 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 125 | 0 | 82 | 0 | 169 | 0 | 380 | 105 | 0 | 113 | 0 | 90 | 0 | 0 | 90 | 550 | 10 | 0 | 17 | 0 | 0 |  | 5343 | 3020 | 8363 | 2794 | 708 | 1553 | 0 | 2350 | 799 | 73 | 0 | 0 | 86 | 0 | 0 | 100.33
23:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 251 | 311 |  | 0 | 270 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 26 | 25 | 33 | 8 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 38 | 21 | 27 | 0 | 0 | 80 | 220 | 250 | 207 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 81 | 104 | 0 | 22 | 0 | 42 | 43 | 53 | 0 | 130 | 0 | 71 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 215 | 0 | 0 | 65 | 0 | 66 | 0 | 0 | 0 | 142 | 0 | 115 | 0 | 0 | 0 | 280 | 54 | 17 | 0 | 118 | 0 | 400 | 104 | 0 | 162 | 17 | 0 | 17 | 0 | 0 | 57 |  | 708 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 125 | 0 | 82 | 0 | 170 | 0 | 380 | 17 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 450 | 28 | 0 | 0 | 0 | 0 |  | 5074 | 2746 | 7820 | 2685 | 708 | 1572 | 0 | 2003 | 699 | 72 | 0 | 0 | 81 | 0 | 0 | 100.33
24:00 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 49 | 312 |  | 0 | 270 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 24 | 0 | 25 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 31 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 38 | 21 | 12 | 0 | 0 | 80 | 220 | 250 | 214 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 76 | 104 | 0 | 22 | 0 | 42 | 43 | 53 | 0 | 130 | 0 | 71 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 145 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 143 | 0 | 115 | 0 | 0 | 0 | 280 | 54 | 17 | 0 | 117 | 0 | 400 | 104 | 0 | 162 | 17 | 0 | 17 | 0 | 0 | 56 |  | 627 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 115 | 0 | 82 | 0 | 169 | 0 | 380 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 420 | 29 | 0 | 0 | 0 | 0 |  | 4819 | 2485 | 7304 | 2612 | 627 | 1561 | 0 | 1688 | 669 | 71 | 0 | 0 | 76 | 0 | 0 | 100.32
KWH | 0 | 0 | 0 | 0 | 1544745 | 1290090 | 0 | 7929860 | 7898000 |  | 0 | 6650000 | 0 | 0 | 0 | 270279 | 95345 | 0 | 0 | 0 | 891072 | 318240 | 313825 | 0 | 0 | 0 | 876960 | 536764 | 1027342 | 421668 | 600000 | 572040 | 698600 | 825800 | 659520 | 0 | 700620 | 980000 | 0 | 0 | 70630 | 0 | 0 | 0 | 0 |  | 415680 | 0 | 126763 | 129600 | 118080 | 811200 | 491760 | 487200 | 0 | 0 | 2033654 | 5131800 | 5661000 | 3977000 | 217454 | 0 | 204624 | 143520 | 0 | 1119722 | 0 | 0 | 668947 | 502092 | 228240 | 719800 | 243070 | 1951680 | 2403840 | 0 | 496908 | 11850 | 1008000 | 1026120 | 1269000 | 0 | 3609327 | 0 | 1477056 | 1665600 | 0 | 4065350 | 420000 | 0 | 253620 | 0 | 525648 | 248976 | 0 | 3239235 | 0 | 0 | 799200 | 0 | 1297440 | 88290 | 1018560 | 94560 | 2540872 | 0 | 1600800 | 229200 | 171454 | 23641 | 6144764 | 1369742 | 945923 | 41040 | 1909320 | 397440 | 9401600 | 2020800 | 274450 | 3150720 | 1392545 | 0 | 444960 | 186481 | 0 | 1231200 |  | 14265454 | 0 | 4282560 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 0 | 1337000 | 404600 | 0 | 0 | 0 | 0 | 68768 | 0 | 217440 | 0 | 159368 | 0 | 591840 | 46828 | 477360 | 0 | 239184 | 1937018 | 0 | 4111400 | 0 | 0 | 0 | 0 | 3112355 | 0 | 780519 | 0 | 3990827 | 0 | 8006509 | 1193280 | 0 | 169776 | 0 | 1581523 | 0 | 31645 | 1490976 | 9955700 | 2506582 | 0 | 242400 | 17220 | 192536 |  | 119049818 | 61420268 | 180470086 | 65916522 | 14265454 | 36779103 | 0 | 42258837 | 16004118 | 1680620 | 0 | 787639 | 1951680 | 826113 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 1714666.95 | 1702918.8 | 0 | 8009158.6 | 8134940 |  | 0 | 7248500 | 0 | 0 | 0 | 2286560.34 | 99158.8 | 0 | 0 | 0 | 8126576.64 | 3131481.6 | 2893466.5 | 0 | 0 | 0 | 6401808 | 4149185.72 | 10129592.12 | 316251 | 450000 | 0 | 0 | 0 | 6377558.4 | 0 | 189167.4 | 264600 | 0 | 0 | 656152.7 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1229601.1 | 1237680 | 1027296 | 6424704 | 619617.6 | 1446984 | 0 | 0 | 2989471.38 | 3797532 | 5661000 | 3658840 | 280515.66 | 0 | 231225.12 | 200928 | 0 | 1914724.62 | 0 | 0 | 6388443.85 | 637656.84 | 171180 | 1259650 | 182302.5 | 14637600 | 2548070.4 | 0 | 631073.16 | 188889 | 1653120 | 1641792 | 2258820 | 0 | 4114632.78 | 0 | 2909800.32 | 3181296 | 0 | 7033055.5 | 919800 | 0 | 517384.8 | 0 | 394236 | 189221.76 | 0 | 24488616.6 | 0 | 0 | 4155840 | 0 | 12766809.6 | 1032110.1 | 8301264 | 1025976 | 17913147.6 | 0 | 14599296 | 2165940 | 1493364.34 | 0 | 46454415.84 | 11930452.82 | 8314663.17 | 409579.2 | 16362872.4 | 2646950.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 82169015.04 | 0 | 4496688 | 0 | 0 | 0 | 0 | 0 | 0 | 100608 | 0 | 1510810 | 627130 | 0 | 0 | 0 | 0 | 676677.12 | 0 | 1924344 | 0 | 2154655.36 | 0 | 5734929.6 | 454231.6 | 916531.2 | 0 | 181062.288 | 11680218.54 | 0 | 22283788 | 0 | 0 | 0 | 0 | 4108308.6 | 0 | 1170778.5 | 0 | 4669267.59 | 0 | 7926443.91 | 12457843.2 | 0 | 1611174.24 | 0 | 12272618.48 | 0 | 349677.25 | 11018312.64 | 43705523 | 0 | 0 | 0 | 0 | 0 |  | 328521186.03 | 234200636.158 | 562721822.188 | 62684016.408 | 82169015.04 | 41642528.27 | 0 | 274377745.76 | 77669529.54 | 453767.4 | 0 | 7516943.42 | 14637600 | 1570676.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 271 | 343 |  | 0 | 270 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 16 | 12 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 24 | 28 | 33 | 51 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 10 | 15 | 38 | 21 | 0 | 0 | 0 | 80 | 245 | 220 | 166 | 8 | 0 | 5 | 5 | 0 | 43 | 0 | 0 | 24 | 21 | 8 | 0 | 9 | 87 | 97 | 0 | 22 | 2 | 43 | 44 | 53 | 0 | 163 | 0 | 65 | 40 | 0 | 165 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 130 | 0 | 0 | 8 | 0 | 118 | 19 | 78 | 0 | 123 | 0 | 55 | 6 | 0 | 4 | 300 | 54 | 38 | 0 | 59 | 10 | 370 | 104 | 46 | 132 | 66 | 0 | 17 | 30 | 0 | 56 |  | 660 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 82 | 0 | 169 | 0 | 0 | 0 | 0 | 118 | 0 | 11 | 0 | 150 | 0 | 337 | 45 | 0 | 91 | 0 | 107 | 0 | 5 | 60 | 270 | 160 | 0 | 0 | 5 | 30 |  | 7638 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 398 | 342 | 0 | 0 | 270 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 24 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 26 | 25 | 33 | 52 | 0 | 33 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 40 | 0 | 50 | 21 | 11 | 0 | 0 | 90 | 250 | 250 | 160 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 95 | 103 | 0 | 22 | 0 | 43 | 43 | 53 | 0 | 163 | 0 | 67 | 77 | 0 | 165 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 285 | 0 | 0 | 120 | 0 | 90 | 0 | 90 | 34 | 142 | 0 | 115 | 70 | 68 | 0 | 16 | 54 | 110 | 13 | 109 | 90 | 392 | 104 | 0 | 144 | 105 | 0 | 17 | 0 | 0 | 57 |  | 708 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 0 | 50 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 169 | 0 | 0 | 0 | 0 | 125 | 0 | 76 | 0 | 156 | 0 | 335 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 0 | 0 | 35 | 0 | 0 |  | 9221 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 0 | 360 | 0 | 0 | 270 | 300 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 51 | 0 | 33 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 80 | 100 | 90 | 50 | 21 | 10 | 0 | 0 | 100 | 270 | 360 | 225 | 16 | 0 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 120 | 0 | 22 | 0 | 42 | 44 | 51 | 0 | 163 | 0 | 66 | 80 | 0 | 220 | 18 | 0 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 135 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 70 | 17 |  |  |  |  | 723 | 0 | 370 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 72 | 23 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 25 | 50 | 33 | 52 | 35 | 22 | 0 | 11 | 81 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 360 | 0 | 0 | 270 | 15 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 51 | 0 | 33 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 21 | 10 | 0 | 0 | 100 | 270 | 360 | 225 | 8 | 0 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 120 | 0 | 22 | 1.6 | 42 | 44 | 51 | 0 | 163 | 0 | 66 | 80 | 0 | 220 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 0 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 125 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 70 | 17 | 30 |  |  |  | 675 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 23 | 110 | 0 | 0 | 0 | 50 | 30 | 96 | 25 | 50 | 0 | 52 | 0 | 22 | 0 | 11 | 81 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 351 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 40 | 0 | 25 | 0 | 0 | 0 | 35 | 52 | 35 | 22 | 25 | 6 | 25 | 33 | 0 | 0 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 38 | 21 | 13 | 0 | 0 | 90 | 190 | 305 | 197 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 11 | 33 | 9 | 72 | 105 | 0 | 22 | 1 | 42 | 43 | 50 | 0 | 130 | 0 | 20 | 73 | 0 | 164 | 18 | 0 | 10 | 0 | 20 | 11 | 0 | 54 | 0 | 0 | 9 | 0 | 30 | 8 | 50 | 0 | 125 | 0 | 115 | 0 | 0 | 1 | 255 | 54 | 17 | 0 | 57 | 0 | 350 | 104 | 12 | 162 | 66 | 0 | 17 | 8 | 0 | 57 | 0 | 426 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 22 | 0 | 11 | 80 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 170 | 0 | 339 | 36 | 0 | 89 | 0 | 100 | 0 | 1 | 35 | 380 | 95 | 0 | 0 | 0 | 5 | 0
199
| Minimum Generation |  | 5814 | 5:00
| Highest Generation |  | 9221 | 19:30
| Day Peak Generation |  | 7638 | 12:00
| Evening Peak Generation |  | 9221 | 19:30
| HVDC Max Flow |  | 708 | 18:00
| HVDC EvPeak Flow |  | 708 | 19:30
| Load factor L.F |  | 81.55%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-12-15
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-12-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7638 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5793 | MW
Evening Peak Generation : |  | 9221 | MW Hour : | 19:30 | Available Max Generation : |  | 13042 | MW
E.P. Demand (at gen end) : |  | 9221 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 9221 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3842 | MW
Total Gen. (MKWH) : |  | 180.4701 | System Load Factor : | 81.55% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 126 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-12-15
Actual : | 100.27 | Ft.(MSL) , | Rule curve : | 104.7 | Ft.( MSL )
Gas Consumed : | Total = | 780.67 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104326544.678
: |  | Coal : | 77669529.54 | Oil : | 281894689.18 | Total : | 463890763.398
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3312.3342 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1121.7688 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1004.2465 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 907.1299 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 819.9209 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 661.6356 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 375.8841 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 170.5103 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 510.2578 |  |  | 0 | 0%
Total | 0 |  | 8883.6881 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Summit Bibiyana-2
|  |  |  | 2) Ghorasal-3,4,5 |  | 11) Haripur 412 MW EGCB
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit-1 & 2
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-3
9) Chandpur-163 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barapukuria 132 kV Bus-A was under shut down from 08:07 to 15:20 for A/M.
b) Bhulta 400/230 kV ATR-01 transformer was under shut down from 08:58 to 15:45 for A/M.
c) Bogura(New)-Bogura(Old) 132 kV Ckt-2 was under shut down from 08:20 to 10:02 for A/M.
d) Sherpur 132/33 kV T-1 transformer was under shut down from 09:30 to 10:47 for A/M.
e) Chapainawabganj-Amnura 132 kV Ckt-2 was under shut down from 08:25 to 14:45 for A/M.
f) Fenchuganj S/S-Fenchuganj P.P. 132 kV Ckt-1 was under shut down from 09:33 to 16:29 for A/M.
g) Gollamari-Khulna(S) 132 kV Ckt-1&2 were closed at 08:44.
h) Cumilla(N)-Kachua 132 kV Ckt-2 is under shut down since 13:09 for A/M.
i) Ghorashal-Bhulta 230 kV Ckt-1 was under shut down from 08:36 to 13:21 for C/M.
j) Gopalganj(Old)-Gopalganj(New) 132 kV Ckt-1 was closed at 08:22.
k) Gopalganj-Faridpur 132 kV Ckt-1 was under shut down from 08:47 to 16:18 for A/M.
l) Halishahar-Khulshi 132 kV Ckt-2 was under shut down from 08:33 to 16:20 for A/M.
m) Haripur-Meghnaghat 230 kV Ckt-2 was under shut down from 10:40 to 20:05 for A/M.
n) Hasnabad 230/132 kV T-02 transformer was under shut down from 08:31 to 17:03 for A/M.
o) HVDC-Bheramara 230 kV Ckt-2 was under shut down from 08:53 to 16:04 for A/M.
p) Ishwardi 230/132 kV T-01 transformer was under shut down from 08:53 to 16:58 for A/M.
q) Barisal(N) 230/132 kV T-02 transformer was under shut down from 09:20 to 15:15 for A/M.
r) Kishoreganj 132/33 kV T-3 transformer was under shut down from 09:10 to 15:34 for A/M.
s) Kodda 132/33 kV T-2 transformer was under shut down from 09:08 to 17:01 for A/M.
t) Natore-Rajshahi 132 kV Ckt-2 was under shut down from 08:20 to 15:45 for A/M.
u) Rangpur-Barapukuria 132 kV Ckt-1 was under shut down from 08:15 to 12:09 for A/M.
v) Savar 132 kV Transfer Bus was under shut down from 09:20 to 16:20 for A/M.
w) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 09:30 to 10:15 for C/M.
x) Tongi-Kabirpur 132 kV Ckt-2 was under shut down from 10:17 to 10:58 for C/M.
y) Barisal(N) 230/132 kV T-01 transformer tripped at 13:03 showing winding temperature high and was switched
on at 13:35.
z) Rangpur-Barapukuria 132 kV Ckt-2 was under shut down from 12:12 to 15:30 for C/M.
aa) Chowmuhoni 132/33 kV T-2 transformer was under shut down from 08:23 to 16:02 for A/M.
ab) Mymensingh 132/33 kV T-3 transformer was under shut down from 09:45 to 17:06 for A/M.
ac) Rampura 132 kV Bus-2 was under shut down from 08:25 to 16:16 for A/M.
ad) Madanganj 132 kV reserve Bus was under shut down from 10:58 to 19:55 for A/M.
ae) Barisal(N) 230/132 kV T-01 transformer was under shut down from 15:26 to 17:15 for C/M.
af) Bhola 225 MW GT-2 was synchronized at 16:05.
ag) Cumilla(S)-Tripura 132 kV Ckt-1 was charged at 20:26 from Tripura end.
ah) Cumilla(S) 132 kV both Buses were charged at 20:26.
ai) Cumilla(S) 132/33 kV T-3 transformer was charged at 20:37.
aj) Anwara 300 MW tripped at 18:43 due to high voltage and was synchronized at 19:22.
ak) Bhola Natun Biddut GT-2 & ST were synchronized at 21:19 & 00:29(15/12/2021) respectively.
al) Siddhirganj 335 MW GT was synchronized at 22:43.
am) Haripur 412 MW EGCB was shutdown at 23:27 due to gas shortage.
an) Sirajganj unit-2 was shutdown at 00:55(15/12/2021) due to gas shortage.
ao) Ashuganj Unit-5 tripped at 04:28(15/12/2021) due to shaft vibration and was synchronized at 05:36(15/12/2021).
ap) Khulna-Satkhira 132 kV Ckt-1 tripped at 04:01(15/12/2021) from both ends showing Dist. A at Khulna end &
Dist. At Satkhira end.
aq) Kallyanpur-Lalbag 132 kV Ckt-2 was shut down at 06:50(15-12-2021) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-12-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 1544745 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 1290090 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 398 | 7929860 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 342 | 7898000 | Engine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6650000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 270279
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 24 | 313825 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 421668
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 95345 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 891072
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 876960 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 318240 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 536764
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1027342
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1172040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 698600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 825800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 52 | 659520
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 285 | 3239235 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 90 | 1297440 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 229200 | High Voltage.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2020800
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3150720 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 186481
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 57 | 1231200 | On test
| Dhaka area Total |  |  |  | 5560 | 2449 | 44775226
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 70630 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 88290
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 811200
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 73 | 1680620 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 68 | 171454 | High Voltage.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 126763 | Low demand.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 129600 | High Voltage.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1018560 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 491760
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 11 | 487200
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 118080 | High Voltage.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23641
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 6144764 | High Voltage.
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1369742
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 945923
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 397440 | High Voltage.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 105 | 1392545 | High Voltage.
| Chattogram area Total |  |  |  | 2382 | 795 | 15468212
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 90 | 2033654 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 160 | 3977000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 250 | 5131800 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 5661000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 204624 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 143520 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1119722
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 2540872 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 34 | 94560 | High Voltage.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 502092 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 95 | 1951680
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 719800
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 668947
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 243070 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 13 | 41040 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 109 | 1909320
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444960 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3034 | 1360 | 27833355
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 2403840 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 496908
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11850
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 120 | 799200 | High Voltage.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1600800
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 274450
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 415680
| Mymensingh Area Total |  |  |  | 622 | 384 | 6002728
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1008000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1026120 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3609327
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Engine problem
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1269000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 248976
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1477056
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1665600 | Engine problem
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | On test
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 4065350 | Gas shortage
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000 | Engine problem
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 525648
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 253620
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 392 | 9401600
| Sylhet Area Total |  |  |  | 2377 | 1066 | 24970297
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 708 | 14265454
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 9600 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 155 | 4282560 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1193280
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 0 | 0 | 192536 | On test
| Khulna Area Total |  |  |  | 2129 | 968 | 19943430
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 404600 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 64 | 1337000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 780519 | Engine problem
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 9955700 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 2506582 | TRIP
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 242400 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 785 | 15226801
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 68768 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 159368
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under SD
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 125 | 3112355 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 156 | 3990827 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 335 | 8006509 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 46828 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 477360
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239184
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 591840
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 217440 | Low demand.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 169776
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1490976
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17220
| Rajshahi Area Total |  |  |  | 2179 | 1052 | 18588451
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1937018
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 169 | 4111400 | Machine problem
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1581523
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31645
| Rangpur Area Total |  |  |  | 605 | 362 | 7661586
| Total |  |  |  | 20934 | 9221 | 180470086
| Eastern Grid Total |  |  |  | 13975 | 6054 | 119049818
| Western Grid Total |  |  |  | 6959 | 3167 | 61420268
| National Grid Total |  |  |  | 20934 | 9221 | 180470086
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-12-14
(a) ENTIRE EASTERN GRID : |  | 6100 | MW | (b) ENTIRE WESTERN GRID : |  | 2796 | MW
i) Dhaka area |  | 3299 | MW | i) Khulna area |  | 1055 | MW
ii) Chittagong area |  | 1014 | MW | ii) Rajshahi area |  | 884 | MW
iii) Comilla area |  | 745 | MW | iii) Barisal area |  | 260 | MW
iv) Mymensingh area |  | 706 | MW | iv) Rangpur area |  | 597 | MW
v) Sylhet area |  | 336 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8896 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 95 | 15:00 | Tangail | 138 | 18:30 | Noapara | 40 | 20:00
Munsiganj | 65 | 13:00 | Mymensing | 158 | 18:00 | Jessore | 76 | 18:30
Sonargaon | 57 | 21:00 | Kishoreganj | 94 | 21:00 | Benapol | 38 | 19:00
Shyampur | 160 | 12:00 | Netrokona | 82 | 18:30 | Jhenida(Old) | 76 | 19:00
Bhulta | 165 | 11:00 | Jamalpur | 96 | 18:00 | Bottail | 89 | 19:00
Madanganj | 42 | 0:00 | Sherpur | 90 | 19:00 | G.K Project | 36 | 18:30
Shitalakhya | 92 | 16:00 | Srimongal | 25 | 19:30 | Faridpur | 110 | 19:00
Rahim steel | 12 | 1:00 | Shahjibazar | 83 | 18:30 | Rajbari | 30 | 18:30
Matuail | 54 | 10:00 | Fenchuganj | 34 | 18:30 | Madaripur | 62 | 19:00
Ghorasal | 60 | 18:00 | Kulawara | 30 | 19:30 | Sariatpur | 42 | 19:30
Narsingdi | 120 | 20:00 | Sylhet | 90 | 18:30 | Gopalganj | 67 | 18:00
Haripur (SBU) | 98 | 19:30 | Chatak | 17 | 18:00 | Bagerhat | 78 | 18:30
Sreenagar | 25 | 19:30 | Sunamganj | 30 | 18:00 | Mongla | 36 | 10:00
Ullon | 46 | 19:00 | Biani Bazar | 39 | 18:00 | Satkhira | 68 | 18:30
Hasnabad | 60 | 18:30 | Comilla (S) | 97 | 20:00 | Gallamari | 34 | 12:00
Magbazar | 54 | 16:00 | Comilla(N) | 79 | 20:00 | Magura | 40 | 18:00
Maniknagar | 50 | 13:00 | Chandpur | 42 | 19:00 | Norail | 32 | 18:00
Bangabhaban | 6 | 10:00 | Feni | 82 | 18:00 | Chuadanga | 62 | 13:00
Motijheel | 18 | 13:00 | Chowmuhani | 124 | 21:00 | Barisal(N) | 28 | 18:00
Narinda | 42 | 13:00 | Ashuganj | 21 | 18:00 | Barisal (S) | 88 | 13:00
Kazla | 71 | 13:00 | Daudkandi | 92 | 19:30 | Patuakhali | 75 | 20:00
Dhanmondi | 125 | 13:00 | B.Baria | 100 | 19:30 | Bhandaria | 38 | 456:00
Lalbag | 73 | 13:00 | Ramganj | 52 | 19:30 | Borguna | 12 | 20:00
Madartek | 43 | 18:30 | Chaddagram | 25 | 1:00 | Borhan Uddin | 29 | 20:00
Dhaka University | 22 | 12:00 | PHP | 10 | 10:00 | Ishurdi | 51 | 18:00
Aftabnagar | 11 | 12:00 | Kochua | 38 | 18:00 | Ruppur Paromanobik | 3 | 9:00
Fatullah | 47 | 12:00 | Madunaghat | 43 | 18:00 | Natore | 87 | 19:30
Nawabganj | 136 | 2:00 | Hathazari | 66 | 18:30 | Bogra | 108 | 18:00
Keraniganj | 50 | 19:30 | Khulshi | 149 | 12:00 | Noagaon | 80 | 19:30
Banani | 40 | 13:00 | Halishahar | 67 | 17:00 | Rajshahi | 98 | 18:00
Mirpur | 81 | 18:00 | Baraulia | 126 | 7:00 | Rajshahi New | 13 | 18:00
Kalyanpur | 66 | 18:00 | Sikalbaha | 20 | 18:30 | C.Nawabganj | 45 | 13:00
Gulshan | 76 | 0:00 | Dohazari | 58 | 18:30 | Amnura | 34 | 18:00
Uttara | 54 | 13:00 | Cox'sbazar | 82 | 18:00 | Pabna | 68 | 19:00
Uttara New | 11 | 18:30 | Chandraghona | 20 | 18:00 | Shahjadpur | 70 | 18:30
Kamrangirchar | 78 | 18:30 | Kaptai | 3.4 | 18:00 | Serajganj | 64 | 18:30
Savar | 130 | 17:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 40 | 18:00
Bhasantec | 84 | 13:00 | Bakulia | 83 | 18:30 | Joypurhat | 48 | 18:00
Agargaon | 52 | 13:00 | Julda | 24 | 9:00 | Sherpur(Bogura) | 46 | 18:00
Satmosjid | 67 | 13:00 | TK chemical | 23 | 18:00 | Mohastangor | 44 | 18:00
Tongi | 97 | 17:00 | Modern Steel | 0 | 1:00 | Bhangura | 20 | 18:00
Kabirpur | 166 | 18:30 | Shahmirpur | 31 | 18:30 | Rangpur | 95 | 18:30
Basundhara | 135 | 18:30 | Khagrachhari | 20 | 8:00 | Lalmonirhat | 41 | 18:00
Purbachal | 55 | 19:30 | Matarbari | 23 | 17:00 | Saidpur | 81 | 18:30
Manikganj | 142 | 19:00 | Baroiar Hat | 32 | 18:00 | Purbasadipur | 88 | 20:00
Joydevpur | 66 | 12:00 | Rangamati | 10 | 18:00 | Thakurgaon | 67 | 18:30
New Tongi | 212 | 24:00 | Abul Khair 230 | 5 | 5:00 | Palashbari | 87 | 18:00
Kodda | 80 | 18:30 | BSRM | 155 | 11:00 | Barapukuria | 42 | 18:00
Dhamrai | 82 | 18:30 | GPH Ispat | 91 | 23:00 | Panchagar | 46 | 18:00
Rajendrapur | 11 | 18:00 | Agrabad | 60 | 18:00 | Joldhaka | 27 | 18:00
Tongi Millgate | 38 | 10:00 | Goalpara | 23 | 13:00 | Kurigram | 50 | 18:00
Valuka | 84 | 18:00 | Central S/S | 60 | 18:30 | Mithapukur | 24 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-12-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 9:00 | 402 | 15:00 | Kaliakoir | 409 | 0.41667 | 401 | 0.041667
| Bheramara | 405 | 22:00 | 393 | 18:00 | Bhulta | 401 | 0.375 | 380 | 0.58333
| Ashuganj(N) | 402 | 9:00 | 382 | 15:00 | Gopalganj | 417 | 0.625 | 393 | 0.875
| Payra | 417 | 20:00 | 406 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 22:00 | 235 | 15:00 | Hathazari | 243 | 18:00 | 232 | 10:00
| Ishurdi | 244 | 23:00 | 238 | 7:00 | Megnaghat | 245 | 22:00 | 238 | 1:00
| Ashuganj | 248 | 23:00 | 241 | 11:00 | Fenchuganj | 248 | 18:30 | 241 | 15:00
| Serajganj | 240 | 9:00 | 237 | 6:00 | Siddhirganj | 238 | 8:00 | 232 | 11:00
| Baghabari | 240 | 8:00 | 231 | 13:00 | Maniknagar | 237 | 8:00 | 229 | 15:00
| Barapukuria | 238 | 16:00 | 230 | 11:00 | Agargaon | 238 | 24:00 | 229 | 15:00
| Bogra | 237 | 14:00 | 232 | 7:00 | Barisal | 247 | 21:00 | 240 | 14:00
| Rajshahi | 240 | 19:30 | 232 | 9:00 | Bhola 225 MW | 250 | 23:00 | 240 | 14:00
| Khulna South | 244 | 4:00 | 236 | 18:30 | AKSML | 241 | 21:00 | 231 | 11:00
| Rampura | 236 | 22:00 | 230 | 15:00 | BSRM | 241 | 19:30 | 232 | 4:00
| Haripur | 238 | 23:00 | 230 | 11:00 | Bibiyana | 245 | 1:00 | 239 | 10:00
| Hasnabad | 237 | 8:00 | 232 | 10:00 | Bhulta | 240 | 22:00 | 230 | 14:00
| Shyampur | 237 | 20:00 | 228 | 15:00 | Ashuganj (S) | 243 | 19:30 | 236 | 15:00
| Aminbazar | 239 | 1:00 | 229 | 2:00 | Kaliakoir | 237 | 21:00 | 226 | 1:00
| Tongi | 237 | 19:30 | 226 | 7:00 | GPH | 241 | 18:00 | 231 | 4:00
| Comilla (N) | 239 | 21:00 | 232 | 11:00 | Jhenaidah | 243 | 22:00 | 232 | 18:30
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 19:30 | 135 | 12:00 | Kachua | 142 | 0.29167 | 137 | 0.45833
| Munsiganj | 142 | 19:30 | 135 | 11:00 | Madanhat | 143 | 0.66667 | 138 | 0.16667
| Sonargaon | 141 | 0:00 | 136 | 10:00 | Hathazari | 142 | 0.75 | 135 | 0.41667
| Shyampur | 140 | 8:00 | 135 | 11:00 | Khulshi | 139 | 0.33333 | 132 | 0.16667
| Bhulta | 136 | 0:00 | 132 | 11:00 | Halishahar | 140 | 0.58333 | 133 | 0.625
| Madanganj | 141 | 19:30 | 136 | 11:00 | Baraulia | 142 | 0.54167 | 134 | 0.45833
| Shitalakhya | 142 | 19:30 | 104 | 0:00 | Sikalbaha | 143 | 0.77083 | 134 | 0.20833
| Rahim steal | 139 | 3:00 | 135 | 11:00 | Dohazari | 137 | 0.75 | 132 | 0.45833
| Matuail | 139 | 19:30 | 135 | 12:00 | Cox'sbazar | 127 | 0.41667 | 116 | 0.75
| Ghorasal | 142 | 18:00 | 138 | 15:00 | Chandraghona | 142 | 0.33333 | 136 | 0.20833
| Narsinghdi | 136 | 9:00 | 132 | 15:00 | Kaptai | 140 | 0.54167 | 136 | 0.75
| Haripur (SBU) | 140 | 20:00 | 136 | 11:00 | A. Khaer Stl. | 140 | 0.75 | 127 | 0.41667
| Sreenagar | 138 | 20:00 | 133 | 9:00 | Bakulia | 140 | 0.33333 | 134 | 0.5
| Ullon | 138 | 0:00 | 133 | 11:00 | Julda | 142 | 0.77083 | 135 | 0.5
| Hasnabad | 140 | 6:00 | 138 | 1:00 | TK Chemical | 142 | 0.77083 | 135 | 0.45833
| Magbazar | 139 | 23:00 | 132 | 15:00 | Modern Steel | 139 | 0.77083 | 135 | 0.625
| Maniknagar | 139 | 6:00 | 134 | 11:00 | Shahmirpur | 140 | 0.29167 | 134 | 0.20833
| Bangabhaban | 139 | 6:00 | 134 | 11:00 | Khagrachhari | 141 | 0.33333 | 135 | 0.45833
| Motijheel | 139 | 6:00 | 134 | 11:00 | Matarbari | 128 | 0.41667 | 115 | 0.83333
| Narinda | 139 | 6:00 | 134 | 11:00 | Baroiar Hat | 142 | 19:30 | 136 | 11:00
| Kazla | 139 | 6:00 | 134 | 11:00 | Rangamati | 141 | 23:00 | 136 | 5:00
| Dhanmondi | 140 | 23:00 | 135 | 11:00 | Agrabad | 140 | 17:00 | 134 | 0.45833
| Lalbag | 137 | 21:00 | 129 | 11:00 | Goalpara S/S | 140 | 9:00 | 135 | 0.29167
| Madartek | 138 | 21:00 | 131 | 15:00 | Khulna Central S/S | 139 | 22:00 | 135 | 0.33333
| Dhaka University | 138 | 22:00 | 133 | 10:00 | Noapara | 139 | 2:00 | 134 | 0.77083
| Aftabnagar | 139 | 0:00 | 133 | 14:00 | Jessore | 138 | 0.41667 | 134 | 0.75
| Fatullah | 141 | 19:30 | 135 | 11:00 | Benapol | 139 | 3:00 | 133 | 0.58333
| Nawabganj | 139 | 22:00 | 118 | 4:00 | Jhenida(Old) | 141 | 0.083333 | 136 | 0.29167
| Keraniganj | 138 | 8:00 | 133 | 11:00 | Bottail | 141 | 0.95833 | 138 | 0.041667
| Banani | 139 | 0:00 | 133 | 11:00 | G.K Project | 144 | 0.95833 | 139 | 0.33333
| Mirpur | 137 | 20:00 | 131 | 10:00 | Faridpur | 140 | 0.25 | 134 | 0.77083
| Kalyanpur | 137 | 21:00 | 132 | 10:00 | Rajbari | 141 | 0.375 | 134 | 0.79167
| Gulshan | 138 | 0:00 | 132 | 12:00 | Madaripur | 144 | 4:00 | 137 | 0.8125
| Uttara | 137 | 20:00 | 130 | 14:00 | Shariyatpur S/S | 143 | 0.083333 | 138 | 0.83333
| Uttara New | 138 | 23:00 | 130 | 14:00 | Gopalganj | 143 | 23:00 | 138 | 0.29167
| Kamrangirchar | 138 | 20:00 | 133 | 10:00 | Bagerhat | 138 | 16:00 | 130 | 0.77083
| Savar | 138 | 1:00 | 131 | 14:00 | Mongla | 137 | 10:00 | 134 | 8:00
| Bhasantec | 139 | 8:00 | 133 | 14:00 | Satkhira | 137 | 0.16667 | 132 | 18:30
| Agargaon | 140 | 8:00 | 134 | 15:00 | Gallamari | 140 | 4:00 | 136 | 0.79167
| Satmosjid | 140 | 8:00 | 134 | 14:00 | Magura | 142 | 0.95833 | 136 | 0.33333
| Tongi | 142 | 23:00 | 137 | 15:00 | Narail | 140 | 4:00 | 137 | 0.54167
| Kabirpur | 139 | 24:00 | 135 | 15:00 | Chuadanga | 139 | 22:00 | 133 | 0.54167
| Basundhara | 141 | 22:00 | 133 | 15:00 | Barisal(N) | 144 | 4:00 | 138 | 14:00
| Purbachal | 141 | 21:00 | 136 | 18:00 | Barisal (S) | 143 | 0.041667 | 128 | 0.54167
| Manikganj | 141 | 24:00 | 95 | 19:00 | Patuakhali(S) | 142 | 0.25 | 126 | 0.54167
| Joydevpur | 142 | 22:00 | 135 | 15:00 | Bhandaria | 142 | 0.20833 | 136 | 0.625
| New Tongi | 140 | 24:00 | 130 | 15:00 | Borguna | 142 | 1:00 | 138 | 14:00
| Kodda | 138 | 21:00 | 132 | 15:00 | Jhenaidah(New) | 141 | 23:00 | 136 | 18:30
| Dhamrai | 139 | 19:30 | 129 | 17:00 | Ishurdi | 141 | 1:00 | 138 | 6:00
| Rajendrapur | 140 | 22:00 | 132 | 11:00 | Ruppur Paromanobik | 140 | 13:00 | 138 | 4:00
| Tongi Millgate | 141 | 19:30 | 133 | 15:00 | Natore | 141 | 20:00 | 137 | 7:00
| Valuka | 133 | 22:00 | 125 | 7:00 | Bogra | 140 | 20:00 | 136 | 9:00
| Tangail | 139 | 21:00 | 133 | 7:00 | Noagaon | 135 | 6:00 | 131 | 11:00
| Mymensing | 135 | 9:00 | 127 | 7:00 | Rajshahi | 141 | 19:00 | 135 | 9:00
| Kishorganj | 136 | 9:00 | 130 | 18:00 | Rajshahi New | 141 | 18:00 | 135 | 9:00
| Netrokona | 133 | 10:00 | 128 | 7:00 | C.Nawabganj | 140 | 19:00 | 132 | 12:00
| Jamalpur | 140 | 10:00 | 126 | 7:00 | Amnura | 142 | 20:00 | 132 | 8:00
| Sherpur | 140 | 10:00 | 125 | 7:00 | Pabna | 140 | 1:00 | 137 | 7:00
| Srimongal | 140 | 9:00 | 138 | 1:00 | Shahjadpur | 143 | 1:00 | 140 | 7:00
| Shahjibazar | 138 | 10:00 | 135 | 1:00 | Serajganj | 140 | 14:00 | 136 | 7:00
| Fenchuganj | 139 | 8:00 | 136 | 13:00 | Niyamatpur | 135 | 14:00 | 129 | 11:00
| Khulawara | 137 | 1:00 | 136 | 11:00 | Joypurhat | 136 | 14:00 | 131 | 11:00
| Sylhet | 136 | 7:00 | 134 | 13:00 | Sherpur(Bogura) | 140 | 14:00 | 136 | 6:00
| Chatak | 137 | 24:00 | 135 | 9:00 | Mohastangor | 139 | 17:00 | 135 | 11:00
| Sunamganj | 134 | 1:00 | 133 | 13:00 | Bangura | 142 | 1:00 | 138 | 11:00
| Biani Bazar | 136 | 4:00 | 134 | 11:00 | Rangpur | 137 | 17:00 | 127 | 13:00
| Comilla(s) | 129 | 1:00 | 125 | 13:00 | Lalmonirhat | 134 | 17:00 | 126 | 11:00
| Comilla(n) | 145 | 3:00 | 140 | 11:00 | Saidpur | 134 | 16:00 | 126 | 11:00
| Chandpur | 142 | 0:00 | 137 | 11:00 | Purbasadipur | 134 | 4:00 | 124 | 11:00
| Feni | 142 | 8:00 | 137 | 5:00 | Thakurgaon | 132 | 16:00 | 120 | 9:00
| Chowmuhani | 140 | 2:00 | 135 | 12:00 | Palashbari | 136 | 16:00 | 130 | 9:00
| Ashuganj | 140 | 1:00 | 139 | 12:00 | Barapukuria | 138 | 0.66667 | 130 | 0.45833
| Daudkandi | 142 | 0:00 | 137 | 11:00 | Panchagar | 134 | 0.16667 | 123 | 0.5
| B.Baria | 136 | 10:20 | 134 | 12:00 | Joldhaka | 134 | 0.66667 | 124 | 0.54167
| Ramganj | 140 | 1:00 | 136 | 13:00 | Kurigram | 134 | 0.70833 | 126 | 0.33333
| Chaddagram | 144 | 7:00 | 138 | 12:00 | Mithapukur | 137 | 17:00 | 131 | 11:00
| PHP | 141 | 1:00 | 137 | 5:00

## L-Curve
Date | 2021-12-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 229 | 4819 | 2485 | 7304 |  |  |  | QF-LDC-11
0:30 | 177.5 | 4659 | 2302.5 | 6961.5 | Date: | 2021-12-14
1:00 | 126 | 4499 | 2120 | 6619
1:30 | 164 | 4328 | 2087 | 6415
2:00 | 202 | 4157 | 2054 | 6211
2:30 | 257 | 4061 | 2059.5 | 6120.5 | [5 empty] | Gen. at Eve. Peak | 9221 | 9221 MW (19:30 )
3:00 | 312 | 3965 | 2065 | 6030 | [6 empty] | 19:30
3:30 | 333 | 3908.5 | 2067.5 | 5976 | [5 empty] | Gen. at Day Peak | 7638 | 7638 MW (12:00 )
4:00 | 354 | 3852 | 2070 | 5922 | [6 empty] | 12:00
4:30 | 379 | 3789.5 | 2078.5 | 5868 | [5 empty] | Highest Generation | 9221
5:00 | 404 | 3727 | 2087 | 5814 | [6 empty] | 19:30
5:30 | 389 | 3767.5 | 2099 | 5866.5
6:00 | 374 | 3808 | 2111 | 5919
6:30 | 285 | 3920.5 | 2180.5 | 6101
7:00 | 196 | 4033 | 2250 | 6283
7:30 | 172 | 4250.5 | 2358 | 6608.5
8:00 | 148 | 4468 | 2466 | 6934
8:30 | 211 | 4618.5 | 2483 | 7101.5
9:00 | 274 | 4769 | 2500 | 7269
9:30 | 355 | 4801 | 2501 | 7302
10:00 | 436 | 4833 | 2502 | 7335
10:30 | 454 | 4872 | 2505.5 | 7377.5
11:00 | 472 | 4911 | 2509 | 7420
11:30 | 462 | 4978 | 2551 | 7529
12:00 | 452 | 5045 | 2593 | 7638
12:30 | 421 | 5147.5 | 2644 | 7791.5
13:00 | 390 | 5250 | 2695 | 7945
13:30 | 452 | 5078 | 2591.5 | 7669.5
14:00 | 514 | 4906 | 2488 | 7394
14:30 | 551 | 4868.5 | 2488 | 7356.5
15:00 | 588 | 4831 | 2488 | 7319
15:30 | 513 | 4886.5 | 2444 | 7330.5
16:00 | 438 | 4942 | 2400 | 7342
16:30 | 443 | 5113 | 2449.5 | 7562.5
17:00 | 448 | 5284 | 2499 | 7783
17:30 | 380 | 5560 | 2761.5 | 8321.5
18:00 | 312 | 5836 | 3024 | 8860
18:30 | 301 | 5883 | 3075 | 8958
19:00 | 290 | 5930 | 3126 | 9056
19:30 | 206 | 6054 | 3167 | 9221
20:00 | 250 | 5872 | 3149 | 9021 |  |  |  | Executive Engineer
20:30 | 271 | 5800 | 3159.5 | 8959.5 |  |  |  | Network Operation Division
21:00 | 292 | 5728 | 3170 | 8898
21:30 | 330.5 | 5535.5 | 3095 | 8630.5
22:00 | 369 | 5343 | 3020 | 8363 |  |  |  |  | Page 6 of 7
22:30 | 346.5 | 5208.5 | 2883 | 8091.5
23:00 | 324 | 5074 | 2746 | 7820
23:30 | 276.5 | 4946.5 | 2615.5 | 7562
24:00 | 229 | 4819 | 2485 | 7304
9221 MW (19:30 )
7638 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-12-14 |  | Energy |  | 180470086
[13 empty] | 2021-12-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2612 | 627 | 1561 | 0 | 1688 | 669 | 71 | 0 | 0 | 76 | 0 | 0
0:30 | 2775 | 536 | 1576 | 0 | 1320 | 609.5 | 71 | 0 | 0 | 74 | 0 | 0 | Date: | 2021-12-14
1:00 | 2938 | 445 | 1591 | 0 | 952 | 550 | 71 | 0 | 0 | 72 | 0 | 0
1:30 | 2907.5 | 438 | 1571.5 | 0 | 811.5 | 544.5 | 71 | 0 | 0 | 71 | 0 | 0 | [8 empty] | Total Energy | 180.4701 | Total Energy Gen 180.470 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.470 MKWHr
2:00 | 2877 | 431 | 1552 | 0 | 671 | 539 | 71 | 0 | 0 | 70 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2875.5 | 431 | 1528 | 0 | 605 | 540 | 71 | 0 | 0 | 70 | 0 | 0 | [8 empty] | Energy Requirement | 180.4701
3:00 | 2874 | 431 | 1504 | 0 | 539 | 541 | 71 | 0 | 0 | 70 | 0 | 0
3:30 | 2877 | 431 | 1493 | 0 | 493 | 541.5 | 71.5 | 0 | 0 | 69 | 0 | 0 | [6 empty] | Shortage
4:00 | 2880 | 431 | 1482 | 0 | 447 | 542 | 72 | 0 | 0 | 68 | 0 | 0
4:30 | 2883.5 | 431 | 1447 | 0 | 420 | 547 | 72 | 0 | 0 | 67.5 | 0 | 0
5:00 | 2887 | 431 | 1412 | 0 | 393 | 552 | 72 | 0 | 0 | 67 | 0 | 0
5:30 | 2836.5 | 431 | 1459 | 0 | 459.5 | 542 | 72 | 0 | 0 | 66.5 | 0 | 0
6:00 | 2786 | 431 | 1506 | 0 | 526 | 532 | 72 | 0 | 0 | 66 | 0 | 0
6:30 | 2685.5 | 431 | 1521 | 0 | 796 | 526.5 | 72.5 | 0 | 0 | 65.5 | 3 | 0 |  |  |  |  | Coal
7:00 | 2585 | 431 | 1536 | 0 | 1066 | 521 | 73 | 0 | 0 | 65 | 6 | 0
7:30 | 2611.5 | 431 | 1526.5 | 0 | 1348 | 535.5 | 73 | 0 | 0 | 65.5 | 17.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2638 | 431 | 1517 | 0 | 1630 | 550 | 73 | 0 | 0 | 66 | 29 | 0
8:30 | 2693.5 | 448 | 1527.5 | 0 | 1692 | 549.5 | 73 | 0 | 0 | 72.5 | 45.5 | 0
9:00 | 2749 | 465 | 1538 | 0 | 1754 | 549 | 73 | 0 | 0 | 79 | 62 | 0
9:30 | 2712 | 565.5 | 1524.5 | 0 | 1728.5 | 540.5 | 73 | 0 | 0 | 80 | 78 | 0
10:00 | 2675 | 666 | 1511 | 0 | 1703 | 532 | 73 | 0 | 0 | 81 | 94 | 0
10:30 | 2659.5 | 666.5 | 1517 | 0 | 1740 | 527.5 | 72.5 | 0 | 1.5 | 82.5 | 110.5 | 0
11:00 | 2644 | 667 | 1523 | 0 | 1777 | 523 | 72 | 0 | 3 | 84 | 127 | 0
11:30 | 2584.5 | 663.5 | 1542 | 0 | 1913 | 522 | 72 | 0 | 12.5 | 85.5 | 134 | 0
12:00 | 2525 | 660 | 1561 | 0 | 2049 | 521 | 72 | 0 | 22 | 87 | 141 | 0
12:30 | 2523 | 660 | 1575.5 | 0 | 2184.5 | 532.5 | 72 | 0 | 19 | 88 | 137 | 0
13:00 | 2521 | 660 | 1590 | 0 | 2320 | 544 | 72 | 0 | 16 | 89 | 133 | 0
13:30 | 2521 | 660 | 1590 | 0 | 2320 | 544 | 72 | 0 | 16 | 89 | 133 | 0
14:00 | 2521 | 660 | 1590 | 0 | 2320 | 544 | 72 | 0 | 16 | 89 | 133 | 0
14:30 | 2443 | 660.5 | 1522.5 | 0 | 2123.5 | 608 | 72 | 0 | 8 | 89.5 | 105 | 0
15:00 | 2365 | 661 | 1455 | 0 | 1927 | 672 | 72 | 0 | 0 | 90 | 77 | 0
15:30 | 2432.5 | 661 | 1403.5 | 0 | 1955.5 | 660.5 | 72 | 0 | 0 | 88.5 | 57 | 0
16:00 | 2500 | 661 | 1352 | 0 | 1984 | 649 | 72 | 0 | 0 | 87 | 37 | 0
16:30 | 2597.5 | 660.5 | 1396 | 0 | 2044.5 | 655 | 72 | 0 | 28.5 | 87.5 | 21 | 0
17:00 | 2695 | 660 | 1440 | 0 | 2105 | 661 | 72 | 0 | 57 | 88 | 5 | 0
17:30 | 2676 | 684 | 1485.5 | 0 | 2476 | 685 | 72 | 0 | 150 | 90.5 | 2.5 | 0
18:00 | 2657 | 708 | 1531 | 0 | 2847 | 709 | 72 | 0 | 243 | 93 | 0 | 0
18:30 | 2705.5 | 708 | 1536.5 | 0 | 2861.5 | 754 | 72.5 | 0 | 225.5 | 94.5 | 0 | 0
19:00 | 2754 | 708 | 1542 | 0 | 2876 | 799 | 73 | 0 | 208 | 96 | 0 | 0
19:30 | 2780 | 708 | 1544 | 0 | 2974 | 839 | 73 | 0 | 208 | 95 | 0 | 0
20:00 | 2781 | 708 | 1547 | 0 | 2878 | 839 | 73 | 0 | 98 | 97 | 0 | 0
20:30 | 2779 | 707.5 | 1556 | 0 | 2820 | 838.5 | 73 | 0 | 90 | 95.5 | 0 | 0
21:00 | 2777 | 707 | 1565 | 0 | 2762 | 838 | 73 | 0 | 82 | 94 | 0 | 0
21:30 | 2785.5 | 707.5 | 1559 | 0 | 2556 | 818.5 | 73 | 0 | 41 | 90 | 0 | 0
22:00 | 2794 | 708 | 1553 | 0 | 2350 | 799 | 73 | 0 | 0 | 86 | 0 | 0
22:30 | 2739.5 | 708 | 1562.5 | 0 | 2176.5 | 749 | 72.5 | 0 | 0 | 83.5 | 0 | 0
23:00 | 2685 | 708 | 1572 | 0 | 2003 | 699 | 72 | 0 | 0 | 81 | 0 | 0
23:30 | 2648.5 | 667.5 | 1566.5 | 0 | 1845.5 | 684 | 71.5 | 0 | 0 | 78.5 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 26.7° C
24:00 | 2612 | 627 | 1561 | 0 | 1688 | 669 | 71 | 0 | 0 | 76 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.470 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.470 MKWHr
Note on W13: Author:

## Generation
g | 2021-12-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 31 | 31 | 31 | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 33 | 33 | 33 | 33 | 33 | 32 | 31 | 700620
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 980000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 6 |  | 8 | 16 | 23 | 25 |  |  | 0 | 70630
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 |  |  |  | 18 | 19 | 18 | 15 | 10 | 5 | 0 | [9 empty] | 88290
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 2 | 51 |  | 51 | 51 |  |  |  |  | 0 | 126763
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [15 empty] | 11 | 17 | 28 |  | 35 | 68 | 51 |  |  |  | 0 | 171454
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [24 empty] | 11 | 147 | 95345
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 14 | 82 | 110 | 110 | 130 | 182 | 130 | 130 | 158 | 192 | 275 |  | 295 | 285 | 285 | 293 | 300 | 215 | 145 | 3239235
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 147 | [19 empty] | 0 | 1544745
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 110 | 110 | 90 |  | 90 | 90 | 90 | 80 | 80 | 80 | 80 | 2033654
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 204624
33 | Ashuganj 225 MW CCPP | 132 | 134 | 132 | 133 | 133 | 135 | 138 | 164 | 145 | 160 | 153 | 166 | 155 | 202 | 201 | 184 | 196 | 191 |  | 164 | 160 | 164 | 182 | 195 | 207 | 214 | 3977000
34 | Ashuganj 450 MW CCPP(South) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5661000
| Ashuganj 450 MW CCPP(North) | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 250 | 240 | 240 | 245 | 250 | 30 | 45 | 260 | 260 | 210 |  | 250 | 250 | 230 | 220 | 220 | 220 | 220 | 5131800
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143520
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 400 | 382 | 379 | 377 | 381 | 386 | 285 | 359 | 379 | 323 | 324 | 271 | 260 | 301 | 303 | 252 | 315 | 290 |  | 363 | 398 | 397 | 390 | 380 | 251 | 49 | 7929860
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6650000
41 | Haripur 360MW CCPP(HPL) | 349 | 350 | 322 | 301 | 301 | 321 | 303 | 321 | 347 | 320 | 320 | 343 | 343 | 300 | 340 | 300 | 338 | 347 |  | 342 | 342 | 342 | 336 | 314 | 311 | 312 | 7898000
42 | RPCL 210MW CCPP | 103 | 104 | 102 | 104 | 104 | 106 | 105 | 105 | 106 | 103 | 100 | 97 | 96 | 96 | 93 | 97 | 100 | 100 |  | 99 | 103 | 102 | 103 | 102 | 104 | 104 | 2403840
43 | Sutiakhali 50 MW Solar PP | [7 empty] | 12 | 27 | 39 | 45 | 46 | 42 | 33 | 23 | 11 | 1 | [9 empty] | 274450
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 1008000
45 | Fenchugonj CCPP Phase-2 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1026120
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 40 | 40 | 40 | 40 | 40 | 71 | 71 | 70 | 70 | 65 | 65 | 66 | 65 | 64 | 40 | 55 | 68 |  | 66 | 67 | 67 | 71 | 71 | 71 | 71 | 1477056
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 10 | 10 | 81 | 81 | 75 | 75 | 77 | 40 | 77 | 76 | 75 | 77 | 75 | 75 |  | 75 | 77 | 77 | 77 | 78 | 77 | 77 | 1665600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 170 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 |  | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 4065350
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 420000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253620
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 248976
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1269000
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 22 | 22 | 22 | 24 |  | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 525648
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 400 | 401 | 400 | 380 | 400 | 350 | 400 | 400 | 400 | 370 | 400 | 398 | 395 | 350 | 350 | 400 |  | 400 | 392 | 400 | 400 | 400 | 400 | 400 | 9401600
58 | Nababganj 55 MW PP (Southern power ) | [5 empty] | 25 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1027342
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 1 | 18 | 24 | 25 | 24 | 25 | 24 | 24 | 24 | 22 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 415680
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 491760
61 | Narshingdi 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 421668
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496908
63 | Impoprt (Tripura) | 72 | 70 | 70 | 68 | 67 | 66 | 65 | 66 | 79 | 81 | 84 | 87 | 89 | 91 | 90 | 87 | 88 | 93 |  | 96 | 95 | 97 | 94 | 86 | 81 | 76 | 1951680
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 40 | 40 | 31 | 11 | 6 | 6 | 6 | 0 | 12 | 10 | 6 | 6 | 7 | 4 |  | 13 | 11 | 16 | 25 | 25 | 27 | 12 | 487200
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 502092
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 228240
67 | Jangalia 33MW PP (Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 |  |  | 7 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 719800
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 243070
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 14 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 572040
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 698600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 825800
73 | Ghorashal 108MW PP (Regent) | [8 empty] | 22 | 40 | 65 | 82 | 91 | 97 | 94 | 98 | 101 | 101 |  | 101 | 101 | 101 | 101 | 98 | 101 | 101 | 1290090
| Feni Lanka Power | [17 empty] | 17 |  | 17 | 13 |  |  |  |  | 0 | 41040
| Chowmuhani 113 MW | 112 | 75 | 17 | 17 | 17 | 32 | 57 | 58 | 58 | 59 | 58 | 59 | 57 | 58 | 81 | 105 | 100 | 108 |  | 109 | 109 | 108 | 108 | 118 | 118 | 117 | 1909320
| Manikgonj 162MW PP(MPGL) | 162 | 126 | 108 | 35 | 17 | 17 | 92 | 128 | 108 | 108 | 108 | 132 | 162 | 162 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 161 | 162 | 162 | 162 | 3150720
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 22 | 47 | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 52 |  | 52 | 52 | 52 | 52 | 34 | 8 | 0 | 659520
79 | Kodda 150MW PP | [11 empty] | 16 | 16 |  |  |  | 48 | 82 |  | 82 | 82 | 48 | 32 |  |  | 0 | 318240
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | [6 empty] | 6 | 12 | 16 | 16 | 16 | 24 | 37 | 43 | 34 | 34 | 34 | 48 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 668947
| Gazipur 100 MW PP | [11 empty] | 6 | 17 | 17 |  |  |  | 16 |  | 35 | 70 | 70 | 35 |  |  | 0 | 229200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 23641
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1369742
| Karnaphuli Power Ltd. | [6 empty] | 5 | 35 | 17 | 17 | 17 | 38 | 78 | 68 | 51 | 65 | 71 | 106 |  | 110 | 110 | 68 | 34 | 17 | 17 | 17 | 945923
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 12 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 25 | 24 | 25 | 313825
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 53 |  |  |  |  | 11 | 71 | 104 | 104 | 104 | 104 | 104 | 90 | 70 | 100 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2020800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 10 | 10 | 10 | 10 |  |  |  | 8 | 30 |  | 40 | 40 |  |  |  |  | 0 | 129600
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1119722
94 | Gagnagar 102 MW PP (Digital Power) | 16 | [6 empty] | 16 | 32 | 24 | 24 | 32 | 48 | 32 | 32 | 48 | 48 | 82 |  | 102 | 102 | 102 | 64 | 48 | 24 | 24 | 891072
95 | Patenga 50MW PP (Baraka) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 34 | 38 | 38 | 38 | 38 | 38 | 38 |  |  |  | 33 |  | 50 | 50 | 50 | 50 | 38 | 38 | 38 | 811200
96 | Chattogram 108 MW PP (ECPV) | [11 empty] | 15 | 24 |  |  | 12 | 18 | 18 |  | 18 | [5 empty] | 0 | 118080
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 15 | 15 | 15 | 15 | 15 |  |  | 3 | 15 | 20 |  | 44 | 55 | 55 | 15 |  |  | 0 | 270279
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 35 | 35 | 17 | 17 | 55 | 35 | 35 | 17 | 17 | 17 | 35 |  | 55 | 55 | 55 | 55 | 35 | 35 | 0 | 536764
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 110 | 110 | 110 | 163 | 130 | 130 | 130 | 163 | 130 | 163 | 130 | 130 | 163 | 110 | 163 | 163 |  | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 3609327
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 11850
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 876960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 2 | 24 | 35 | 24 | 8 | 8 | 32 | 32 | 32 | 32 | 46 |  | 100 | 120 | 100 | 100 | 65 | 65 | 16 | 799200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 23 | 42 | 58 | 98 | 118 | 119 | 76 | 53 | 48 | 35 | 66 |  | 130 | 90 | 113 | 85 | 83 | 66 | 52 | 1297440
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | 10 |  |  |  | 30 | 76 | 76 | 40 | 40 | 40 | 78 | 50 | 50 | 20 | 10 | 50 | 90 |  | 90 | 90 | 60 | 60 | 10 |  |  | 1018560
116 | Chandpur 200MW (Desh energy) | [15 empty] | 14 | 17 | 17 |  | 19 | 34 |  |  |  |  | 0 | 94560
117 | Ashuganj 150MW PP (Midland) | 100 | 20 | 10 | 10 | 10 | 18 | 36 | 83 | 108 | 123 | 127 | 123 | 125 | 135 | 137 | 140 | 142 | 138 |  | 130 | 142 | 140 | 143 | 142 | 142 | 143 | 2540872
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 35 |  |  |  |  | 4 | 24 | 65 | 86 | 75 | 75 | 55 | 75 | 55 | 55 | 55 | 67 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1600800
| Anwara 300 MW PP (United) | 260 | 245 | 210 | 190 | 155 | 165 | 235 | 280 | 260 | 260 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 0 | 16 | 110 | 286 | 277 | 280 | 280 | 6144764
| Juldah unit-2 (Acorn) | [6 empty] | 10 | 10 | 10 | 20 | 20 | 10 | 35 | 50 | 20 | 10 | 10 | 40 |  | 70 | 90 | 70 |  |  |  | 0 | 397440
| Anlima Energy Ltd. | [5 empty] | 19 | 72 | 87 | 68 | 51 | 51 | 66 | 82 | 86 | 87 | 87 | 87 | 105 |  | 105 | 105 | 105 | 105 | 17 | 17 | 17 | 1392545
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444960
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 10 | 18 | 25 | 25 | 30 | 26 | 24 | 18 | 7 | 1 | [9 empty] | 186481
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | 56 | 57 | 56 | 57 | 56 | 57 | 57 | 57 | 57 | 57 | 56 | 56 | 57 | 57 | 57 | 56 | 57 | 57 |  | 57 | 57 | 56 | 55 | 56 | 57 | 56 | 1231200
120 | Eastern Zone Total | 4499 | 4157 | 3965 | 3852 | 3727 | 3808 | 4033 | 4468 | 4769 | 4833 | 4911 | 5045 | 5250 | 4906 | 4831 | 4942 | 5284 | 5836 |  | 5930 | 6054 | 5872 | 5728 | 5343 | 5074 | 4819 | 119049818
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 5 | 36 | 35 | 35 | 35 | 45 | 80 | 90 | 70 | 53 | 53 | 100 |  | 105 | 105 | 105 | 105 | 105 | 17 | 0 | 1193280
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 4 | 11 | 21 | 28 | 30 | 32 | 28 | 18 | 11 | 3 | [9 empty] | 192536
131
132 | United Payra Power Ltd. | [14 empty] | 3 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 17 |  | 0 | 242400
133 | Bhola Nutan Biddut BD LTD (GAS) | 218 | 180 | 181 | 180 | 180 | 200 | 220 | 205 | 190 | 160 | 160 | 160 | 160 | [10 empty] | 10 | 28 | 29 | 2506582
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 8 | 60 | 44 | 30 | 68 |  | 76 | 76 | 74 | 76 | 82 | 82 | 82 | 780519
| Bhola 225 MW CCPP | 69 | 68 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 50 | 50 | 50 | 50 |  |  |  | 65 | 65 |  | 65 | 64 | 65 | 60 | 65 | 65 | 65 | 1337000
140 | Bhola 33 MW PP (Venture) | 20 | 17 | 17 | 17 | 16 | 18 | 15 | 14 | 13 | 12 | 16 | 15 | 16 | 17 | 15 | 12 | 15 | 20 |  | 20 | 20 | 22 | 22 | 21 | 20 | 19 | 404600
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [10 empty] | 3 | 6 | [14 empty] | 9600
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 445 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 465 | 666 | 667 | 660 | 660 | 661 | 661 | 661 | 660 | 708 |  | 708 | 708 | 708 | 707 | 708 | 708 | 627 | 14265454
147 | Bheramara 410 MW CCPP | 175 | 175 | 180 | 185 | 190 | 195 | 200 | 195 | 190 | 180 | 175 | 165 | 165 | 165 | 150 | 150 | 150 | 155 |  | 155 | 155 | 160 | 160 | 165 | 160 | 160 | 4282560
148 | Payra 1320 MW | 300 | 290 | 290 | 290 | 300 | 280 | 270 | 300 | 300 | 280 | 270 | 270 | 290 | 350 | 420 | 400 | 410 | 460 |  | 550 | 590 | 590 | 590 | 550 | 450 | 420 | 9955700
149
150 | Barapukuria TPP Unit-1 | 81 | 80 | 81 | 82 | 82 | 84 | 83 | 82 | 81 | 84 | 84 | 82 | 85 | 82 | 83 | 80 | 82 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1937018
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 169 | 169 | 170 | 170 | 170 | 168 | 168 | 168 | 168 | 168 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 |  | 169 | 169 | 169 | 168 | 169 | 169 | 169 | 4111400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 25 |  | 25 | 25 | [5 empty] | 68768
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 17220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 120 | 120 | 120 | 120 | 120 | 125 | 125 | 125 | 125 | 125 | 120 | 118 | 118 | 105 | 108 | 108 | 125 | 125 |  | 125 | 125 | 126 | 125 | 125 | 125 | 115 | 3112355
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 157 | 157 | 157 | 157 | 160 | 163 | 166 | 168 | 168 | 162 | 158 | 150 | 139 | 134 | 133 | 138 | 153 | 155 |  | 156 | 156 | 158 | 164 | 169 | 170 | 169 | 3990827
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 325 | 326 | 325 | 325 | 325 | 325 | 327 | 326 | 326 | 326 | 328 | 337 | 344 | 322 | 301 | 302 | 300 | 334 |  | 334 | 335 | 335 | 380 | 380 | 380 | 380 | 8006509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 21 | 21 | 20 | 20 | 20 | 22 | 22 | 22 |  | 21 | 22 | 20 | 21 | 18 | 19 | 22 | 477360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 239184
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 34 |  | 50 | 50 | 50 | 25 |  |  | 0 | 159368
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [16 empty] | 7 | 35 |  | 0 | [6 empty] | 46828
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 10 | 23 | 8 | 8 | 25 | 38 | 43 | 25 | 25 | 25 | 45 |  | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 591840
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 |  |  |  | 217440
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [5 empty] | 10 | 56 | 96 | 110 | 50 | 50 | 91 | 113 | 113 | 70 | 70 | 70 | 102 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 169776
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 35 | 100 | 70 | 50 | 50 | 60 | 95 | 113 | 70 | 50 | 50 | 113 |  | 113 | 113 | 113 | 113 | 90 | 70 | 35 | 1490976
173 | Rangpur 20 MW GTPP | [5 empty] | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 35 | 90 | 109 | 90 | 90 | 107 | 90 | 50 | 96 | 75 | 82 | 113 |  | 113 | 113 | 113 | 113 | 90 | 70 | 70 | 1581523
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 31645
178
178