## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-12-23 | Thursday
|  | Date (day): | 2021-12-23 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11074.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12470 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-12-22 | 2021-12-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 150 | 120 | 120 | 120 | 245 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 357 | 285 | 300 | 300 | 60 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 260 | 260 | 260 | 190 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 240 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 11 | 11 | 11 |  | 89 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 82 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 28 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 22 | 22 | 22 |  | 11 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 25 | 25 |  | 8 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 62 | 265 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 58 | 132 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 48 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 95 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 23 | 0 | 30 | 0
| Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 0 | 0 | 57 | 0
| Dhaka area Total |  |  |  |  | 6178 | 5560 | 1915 | 2236 | 2584 | 2847 | 1460 | 1217
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 28 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 84 | 84 | 84 |  | 146 | Low Water Level & Unit 4 & 5 U/M.
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 17 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 70 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 30 | 100 | 100
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 19 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 18 | 10 | 20
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 23 | 37 | 90 | 90 |  | 18 | Engine problem
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 282 | 300 | 300 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 53 | 110 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 30 | 30 | 100 | 100
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 98 | 105 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 803 | 972 | 1329 | 1334 | 0 | 1039
60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 100 | 34 |  | Gas shortage
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 171 | 206 | 225 | 225 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 280 | 360 | 360 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 |  | 16 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5
66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 81 | 78 | 36 | 36 | 159 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 137 | 137 | 135 | 137 |  | 13 | Engine problem
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 16 | 50 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 139 | 139 | 138 | 140 |  | 23 | Machine problem.
71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 83 | 87 | 138 | 164
74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 15 | 25 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 85 | 113 | 113
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1238 | 1306 | 1838 | 2068 | 457 | 449
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 96 | 97 | 100 | 110 | 92 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 17 | 17 | 17 |  | 5 | Engine problem
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 130 | 200 | 200
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 23 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 25 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 318 | 384 | 505.6 | 464 | 92 | 13
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 42 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 20 | 40 | 60
96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 77 | 75 | 77
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 75 | 75 | 75 | 75 |  | 20 | Engine prolem
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 196 | 196 | 200 | 200 |  | 31 | Machine problem
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 415 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1131 | 1100 | 1152 | 1175 | 0 | 1196
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 482 | 721 | 491 | 732
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 355 | 350 | 360 | 50 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 87 | 105 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 0 | 0 | 60 | 0 | 10 | 0
| Khulna Area Total |  |  |  |  | 2248 | 2129 | 929 | 1181 | 1006 | 1687 | 50 | 93
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 20 | 20 | 20 |  | 13 | Engine problem
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 67 | 70 | 70 | 104 |  | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 250 | 370 | 620 | 620
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 130 | 220 | 200 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
| Barisal Area Total |  |  |  |  | 2046 | 2046 | 456 | 688 | 1031 | 1201 | 188 | 13
121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 13 | 30 | 30 |  | 41 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 16 | 50 | 50
126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 33 |  | 17 | Engine problem
127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 146 | 180 | 200 | 200 |  |  | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 382 | 309 | 400 | 400 |  |  | FGMO
131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30 |  | 20 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 10 | 11
135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 52 | 52 | 52
136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 67 | 90 | 100
137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 93 | 90 | 95 |  | 18 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 674 | 987 | 1338 | 1411 | 600 | 121
141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 76 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 300 | 270 | 170 | 170 | 104 |  | Coal shortage
143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 112 | 113 | 113
146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 495 | 458 | 291 | 283 | 104 | 210
| Total |  |  |  |  | 22031 | 20934 | 7959 | 9312 | 11074.6 | 12470 | 2951 | 4351
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7597.4604 | 8889 | 10571.5334 | 11903.547
A. |  | 2021-12-22 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9312 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5832 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9312 | MW
3 | Day peak Generation : |  |  | 7959 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8889 | MW
4 | Evening peak Generation : |  |  | 9312 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 183.8444 | MKWHr | By Solar | 0.81752 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 109.243 | MKWHr |  | By Oil: | 42.2825 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 15.5637 | MKWHr |  | By Hydro: | 2.0228 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2951 | MW | Dhaka | 3258 | 3258 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4351 | MW | Chittagong | 1030 | 1030 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 7302 | MW | Khulna | 1077 | 1077 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 835.41 | MMCFD |  |  | Rajshahi | 880 | 880 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 109343172.846 | ii) Oil : | Taka | 287928841.92 | Comilla | 720 | 720 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 77028969.62 | Total | Taka | 474300984.386 | Mymensingh | 726 | 726 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.382 | MKWHr. | Sylhet | 329 | 329 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 280 | MW (E to W) at | 19:00 | hrs | Barisal | 247 | 247 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 152 | MW at | 7:00 | hrs | Rangpur | 622 | 622 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 24.2° C |  |  | Total | 8889 | 8889 |  | 0
B. |  | 2021-12-23 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 24.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12470 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7900 | MW
4 | Reserve(Generation end) |  |  |  | 3070 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 185.5818 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5853 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.2705 | MKWHr. | ii) HVDC Flow at Peak Time |  | 721 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.6445 | MKWHr. | iii) Maximum HVDC Flow : |  | 722 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.64 |  | (b) Today: | 99.52 |  | (c) Rule Curve: |  | 103.9
.

## YesterdayGen
2021-12-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 100 | 0 | 0 | 103 | 0 | 0 | 300 |  | 0 | 280 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 31 | 0 | 0 | 80 | 300 | 0 | 187 | 73 | 138 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 58 | 108 | 0 | 22 | 0 | 42 | 43 | 53 | 0 | 163 | 0 | 69 | 80 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 35 | 0 | 0 | 0 | 300 | 54 | 17 | 0 | 0 | 0 | 410 | 36 | 0 | 162 | 51 | 75 | 17 | 0 | 0 | 0 |  | 346 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 147 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4431 | 2182 | 6613 | 2632 | 346 | 2097 | 0 | 814 | 580 | 86 | 0 | 0 | 58 | 0 | 0 | 99.66
2:00 | 0 | 0 | 98 | 0 | 0 | 103 | 0 | 0 | 300 |  | 0 | 280 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 31 | 0 | 0 | 80 | 300 | 0 | 184 | 73 | 140 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 58 | 104 | 0 | 22 | 0 | 42 | 43 | 50 | 0 | 163 | 0 | 69 | 80 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 300 | 54 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 108 | 17 | 75 | 17 | 0 | 0 | 0 |  | 344 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 145 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4175 | 2125 | 6300 | 2619 | 344 | 2042 | 0 | 571 | 580 | 86 | 0 | 0 | 58 | 0 | 0 | 99.66
3:00 | 0 | 0 | 100 | 0 | 0 | 103 | 0 | 0 | 300 |  | 0 | 280 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 31 | 0 | 0 | 80 | 300 | 0 | 184 | 73 | 140 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 56 | 109 | 0 | 22 | 0 | 42 | 43 | 50 | 0 | 130 | 0 | 69 | 80 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 245 | 54 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 0 | 75 | 17 | 0 | 0 | 0 |  | 344 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 142 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 180 | 0 | 0 | 0 | 0 | 0 |  | 3961 | 2098 | 6059 | 2620 | 344 | 2013 | 0 | 368 | 572 | 86 | 0 | 0 | 56 | 0 | 0 | 99.65
4:00 | 0 | 0 | 90 | 0 | 0 | 103 | 0 | 0 | 300 |  | 0 | 280 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 31 | 0 | 0 | 80 | 300 | 0 | 196 | 73 | 141 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 56 | 109 | 0 | 22 | 0 | 42 | 43 | 50 | 0 | 130 | 0 | 69 | 80 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 54 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 75 | 17 | 0 | 0 | 0 |  | 344 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 147 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 0 | 0 | 0 | 0 | 0 |  | 3863 | 2000 | 5863 | 2594 | 344 | 1925 | 0 | 286 | 572 | 86 | 0 | 0 | 56 | 0 | 0 | 99.65
5:00 | 0 | 0 | 99 | 0 | 0 | 103 | 0 | 0 | 300 |  | 0 | 280 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 31 | 0 | 0 | 80 | 300 | 0 | 193 | 73 | 141 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 56 | 110 | 0 | 22 | 0 | 42 | 43 | 50 | 0 | 130 | 0 | 69 | 80 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 190 | 54 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 75 | 17 | 0 | 0 | 0 |  | 344 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 150 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 130 | 0 | 0 | 0 | 0 | 0 |  | 3890 | 1942 | 5832 | 2576 | 344 | 1921 | 0 | 287 | 562 | 86 | 0 | 0 | 56 | 0 | 0 | 99.64
6:00 | 0 | 0 | 101 | 0 | 0 | 103 | 0 | 0 | 360 |  | 0 | 280 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 31 | 0 | 0 | 80 | 300 | 0 | 188 | 73 | 141 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 56 | 109 | 0 | 22 | 0 | 42 | 43 | 50 | 0 | 130 | 0 | 69 | 80 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 16 | 0 | 0 | 0 | 190 | 54 | 0 | 0 | 0 | 0 | 410 | 20 | 0 | 54 | 21 | 75 | 17 | 0 | 0 | 0 |  | 343 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 145 | 0 | 355 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 130 | 0 | 0 | 0 | 0 | 0 |  | 4071 | 1970 | 6041 | 2567 | 343 | 1983 | 0 | 445 | 561 | 86 | 0 | 0 | 56 | 0 | 0 | 99.64
7:00 | 0 | 0 | 101 | 0 | 0 | 103 | 0 | 0 | 360 |  | 0 | 280 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 29 | 0 | 0 | 80 | 300 | 0 | 188 | 73 | 140 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 53 | 110 | 0 | 22 | 0 | 43 | 43 | 50 | 0 | 130 | 0 | 34 | 80 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 32 | 0 | 0 | 0 | 200 | 54 | 6 | 0 | 3 | 0 | 410 | 53 | 1 | 108 | 37 | 75 | 17 | 1 | 0 | 0 |  | 419 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 145 | 0 | 347 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 300 | 130 | 0 | 0 | 0 | 0 | 0 |  | 4229 | 2183 | 6412 | 2563 | 419 | 1971 | 0 | 736 | 582 | 86 | 0 | 0 | 53 | 2 | 0 | 99.63
8:00 | 0 | 0 | 126 | 0 | 0 | 53 | 0 | 0 | 360 |  | 0 | 280 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 25 | 19 | 11 | 0 | 0 | 80 | 300 | 0 | 187 | 73 | 141 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 65 | 110 | 0 | 22 | 1 | 42 | 43 | 50 | 0 | 163 | 0 | 34 | 77 | 0 | 197 | 18 | 0 | 10 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 40 | 0 | 103 | 0 | 64 | 0 | 0 | 1 | 260 | 54 | 17 | 0 | 16 | 0 | 410 | 84 | 5 | 151 | 51 | 75 | 17 | 6 | 0 | 0 |  | 484 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 162 | 0 | 425 | 11 | 0 | 60 | 0 | 42 | 0 | 1 | 70 | 300 | 136 | 0 | 0 | 0 | 7 | 0 |  | 4612 | 2480 | 7092 | 2646 | 484 | 2061 | 0 | 1142 | 582 | 86 | 0 | 0 | 65 | 26 | 0 | 99.63
9:00 | 0 | 0 | 100 | 0 | 0 | 53 | 0 | 0 | 326 |  | 0 | 280 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 0 | 28 | 33 | 2 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 6 | 22 | 19 | 3 | 0 | 0 | 80 | 300 | 0 | 182 | 73 | 141 | 23 | 5 | 0 | 51 | 0 | 0 | 2 | 21 | 5 | 33 | 9 | 75 | 110 | 0 | 22 | 1 | 43 | 43 | 50 | 0 | 163 | 0 | 34 | 77 | 0 | 197 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 5 | 0 | 0 | 10 | 0 | 17 | 11 | 70 | 0 | 137 | 0 | 115 | 0 | 5 | 2 | 282 | 54 | 30 | 0 | 69 | 10 | 410 | 95 | 7 | 162 | 69 | 75 | 17 | 12 | 0 | 0 |  | 484 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 82 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 183 | 0 | 378 | 48 | 0 | 90 | 0 | 91 | 0 | 2 | 70 | 250 | 130 | 0 | 0 | 1 | 22 | 0 |  | 4841 | 2560 | 7401 | 2597 | 484 | 1906 | 0 | 1614 | 571 | 86 | 0 | 10 | 75 | 58 | 0 | 99.62
10:00 | 0 | 0 | 114 | 0 | 100 | 0 | 0 | 0 | 293 |  | 0 | 280 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 0 | 28 | 20 | 41 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 15 | 25 | 19 | 4 | 0 | 0 | 80 | 265 | 0 | 171 | 73 | 141 | 23 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 5 | 30 | 9 | 80 | 100 | 0 | 20 | 1 | 43 | 43 | 50 | 0 | 110 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 30 | 0 | 0 | 40 | 0 | 17 | 15 | 70 | 0 | 137 | 0 | 115 | 0 | 17 | 3 | 282 | 54 | 34 | 0 | 106 | 10 | 324 | 94 | 19 | 162 | 87 | 75 | 17 | 18 | 0 | 0 |  | 484 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 81 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 156 | 0 | 394 | 70 | 0 | 94 | 0 | 112 | 0 | 3 | 70 | 250 | 130 | 0 | 0 | 2 | 39 | 0 |  | 4904 | 2678 | 7582 | 2493 | 484 | 1817 | 0 | 1859 | 631 | 86 | 0 | 32 | 80 | 100 | 0 | 99.62
11:00 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 292 |  | 0 | 280 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 0 | 25 | 17 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 18 | 25 | 18 | 4 | 0 | 0 | 80 | 295 | 0 | 177 | 73 | 141 | 23 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 25 | 9 | 85 | 100 | 0 | 20 | 1 | 43 | 43 | 52 | 0 | 110 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 30 | 0 | 0 | 40 | 0 | 17 | 18 | 90 | 0 | 135 | 0 | 115 | 0 | 17 | 4 | 282 | 54 | 34 | 0 | 103 | 10 | 320 | 95 | 29 | 162 | 90 | 75 | 17 | 22 | 0 | 0 |  | 482 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 83 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 157 | 0 | 355 | 70 | 0 | 94 | 0 | 112 | 0 | 4 | 70 | 250 | 130 | 0 | 0 | 3 | 52 | 0 |  | 5033 | 2592 | 7625 | 2506 | 482 | 1776 | 0 | 1892 | 633 | 86 | 0 | 32 | 85 | 133 | 0 | 99.61
12:00 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 357 |  | 0 | 280 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 25 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 23 | 25 | 18 | 4 | 0 | 0 | 80 | 265 | 0 | 171 | 81 | 139 | 29 | 5 | 0 | 51 | 0 | 0 | 15 | 21 | 5 | 25 | 9 | 83 | 96 | 0 | 20 | 2 | 43 | 43 | 50 | 0 | 163 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 62 | 0 | 0 | 40 | 0 | 58 | 19 | 90 | 0 | 137 | 0 | 115 | 0 | 17 | 4 | 282 | 54 | 53 | 0 | 105 | 30 | 415 | 95 | 23 | 162 | 98 | 75 | 17 | 23 | 0 | 0 |  | 482 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 78 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 146 | 0 | 382 | 87 | 0 | 0 | 0 | 112 | 0 | 5 | 70 | 250 | 130 | 0 | 0 | 3 | 60 | 0 |  | 5405 | 2554 | 7959 | 2565 | 482 | 1908 | 0 | 2036 | 628 | 86 | 0 | 32 | 83 | 139 | 0 | 99.61
13:00 | 0 | 0 | 101 | 0 | 150 | 0 | 0 | 0 | 330 |  | 0 | 280 | 260 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 25 | 30 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 32 | 25 | 18 | 10 | 0 | 0 | 80 | 275 | 0 | 166 | 81 | 142 | 29 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 5 | 25 | 9 | 83 | 96 | 0 | 20 | 1 | 43 | 43 | 50 | 0 | 163 | 0 | 20 | 77 | 0 | 197 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 85 | 0 | 0 | 55 | 0 | 111 | 9 | 90 | 0 | 138 | 0 | 115 | 0 | 17 | 3 | 282 | 54 | 71 | 0 | 105 | 30 | 415 | 104 | 11 | 162 | 116 | 75 | 17 | 13 | 0 | 0 |  | 482 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 83 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 154 | 0 | 366 | 105 | 0 | 0 | 0 | 112 | 0 | 5 | 70 | 250 | 130 | 0 | 0 | 3 | 59 | 0 |  | 5577 | 2624 | 8201 | 2640 | 482 | 1862 | 0 | 2263 | 633 | 86 | 0 | 48 | 83 | 104 | 0 | 99.6
14:00 | 0 | 0 | 116 | 0 | 150 | 0 | 0 | 0 | 289 |  | 0 | 280 | 320 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 48 | 48 | 9 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 0 | 25 | 28 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 35 | 0 | 18 | 0 | 0 | 0 | 80 | 285 | 0 | 160 | 78 | 141 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 25 | 9 | 83 | 82 | 0 | 17 | 1 | 43 | 43 | 53 | 0 | 110 | 0 | 20 | 77 | 0 | 197 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 95 | 0 | 0 | 25 | 0 | 124 | 14 | 70 | 0 | 142 | 0 | 100 | 0 | 17 | 3 | 282 | 45 | 80 | 0 | 105 | 10 | 335 | 104 | 11 | 162 | 116 | 75 | 17 | 15 | 0 | 0 |  | 482 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 81 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 164 | 0 | 324 | 35 | 0 | 0 | 0 | 112 | 0 | 4 | 35 | 250 | 130 | 0 | 0 | 2 | 55 | 0 |  | 5301 | 2511 | 7812 | 2597 | 482 | 1775 | 0 | 2006 | 630 | 86 | 0 | 48 | 83 | 105 | 0 | 99.6
15:00 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 357 |  | 0 | 280 | 255 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 32 | 11 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 0 | 25 | 25 | 51 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 38 | 0 | 18 | 0 | 0 | 0 | 80 | 270 | 0 | 161 | 78 | 139 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 25 | 9 | 82 | 84 | 0 | 17 | 1 | 43 | 43 | 53 | 0 | 110 | 0 | 20 | 76 | 0 | 197 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 95 | 0 | 0 | 16 | 0 | 90 | 11 | 30 | 0 | 138 | 0 | 70 | 0 | 17 | 2 | 282 | 54 | 87 | 0 | 65 | 10 | 360 | 60 | 11 | 162 | 87 | 75 | 17 | 9 | 0 | 0 |  | 484 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 86 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 417 | 17 | 0 | 0 | 0 | 93 | 0 | 3 | 35 | 250 | 130 | 0 | 0 | 1 | 36 | 0 |  | 5023 | 2507 | 7530 | 2571 | 484 | 1868 | 0 | 1709 | 636 | 74 | 0 | 32 | 82 | 74 | 0 | 99.59
16:00 | 0 | 0 | 103 | 0 | 120 | 0 | 0 | 0 | 302 |  | 0 | 280 | 255 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 64 | 11 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 25 | 0 | 25 | 25 | 45 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 4 | 36 | 0 | 18 | 5 | 0 | 0 | 80 | 315 | 0 | 158 | 78 | 140 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 79 | 95 | 0 | 14 | 0 | 43 | 43 | 53 | 0 | 163 | 0 | 20 | 76 | 0 | 197 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 95 | 0 | 0 | 16 | 0 | 60 | 3 | 50 | 0 | 128 | 0 | 84 | 2 | 17 | 0 | 282 | 54 | 74 | 0 | 65 | 10 | 380 | 35 | 6 | 162 | 101 | 75 | 17 | 4 | 0 | 0 |  | 484 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 85 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 423 | 17 | 0 | 0 | 0 | 70 | 0 | 2 | 35 | 250 | 130 | 0 | 0 | 0 | 25 | 0 |  | 5050 | 2519 | 7569 | 2649 | 484 | 1878 | 0 | 1654 | 635 | 86 | 0 | 64 | 79 | 40 | 0 | 99.59
17:00 | 0 | 0 | 98 | 0 | 120 | 0 | 0 | 0 | 274 |  | 0 | 260 | 230 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 48 | 98 | 12 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 25 | 0 | 25 | 25 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 15 | 30 | 36 | 0 | 18 | 8 | 0 | 0 | 80 | 280 | 0 | 181 | 78 | 140 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 9 | 86 | 96 | 0 | 14 | 0 | 43 | 43 | 53 | 0 | 110 | 0 | 20 | 30 | 0 | 151 | 18 | 0 | 10 | 0 | 21 | 11 | 0 | 185 | 0 | 0 | 48 | 0 | 80 | 0 | 60 | 0 | 127 | 0 | 115 | 19 | 51 | 0 | 282 | 54 | 79 | 0 | 65 | 30 | 330 | 35 | 1 | 162 | 105 | 75 | 17 | 1 | 0 | 0 |  | 578 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 25 | 8 | 19 | 0 | 11 | 76 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 207 | 0 | 316 | 40 | 0 | 20 | 0 | 104 | 0 | 0 | 50 | 260 | 130 | 0 | 0 | 0 | 7 | 0 |  | 5094 | 2597 | 7691 | 2542 | 578 | 1600 | 0 | 2023 | 636 | 86 | 0 | 131 | 86 | 9 | 0 | 99.58
18:00 | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 282 |  | 0 | 260 | 250 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 85 | 115 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 0 | 22 | 25 | 22 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 30 | 36 | 24 | 18 | 11 | 0 | 0 | 80 | 280 | 0 | 199 | 78 | 140 | 29 | 5 | 0 | 51 | 0 | 16 | 8 | 21 | 8 | 33 | 9 | 92 | 96 | 0 | 14 | 0 | 43 | 43 | 53 | 0 | 163 | 0 | 20 | 77 | 0 | 197 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 255 | 0 | 0 | 105 | 0 | 112 | 0 | 90 | 0 | 127 | 0 | 115 | 52 | 51 | 0 | 300 | 54 | 110 | 0 | 65 | 30 | 400 | 99 | 0 | 162 | 105 | 75 | 17 | 0 | 0 | 0 |  | 627 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20 | 0 | 0 | 0 | 0 | 34 | 6 | 101 | 0 | 34 | 32 | 40 | 29 | 22 | 0 | 11 | 75 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 174 | 0 | 395 | 103 | 0 | 70 | 0 | 112 | 0 | 0 | 113 | 330 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5920 | 3251 | 9171 | 2657 | 627 | 1908 | 0 | 2742 | 675 | 86 | 0 | 384 | 92 | 0 | 0 | 99.58
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 285 |  | 0 | 260 | 240 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 3 | 22 | 25 | 51 | 0 | 44 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 51 | 30 | 37 | 28 | 18 | 18 | 0 | 0 | 80 | 280 | 0 | 206 | 78 | 139 | 29 | 5 | 0 | 51 | 0 | 16 | 25 | 21 | 8 | 33 | 9 | 87 | 97 | 0 | 17 | 0 | 43 | 43 | 53 | 0 | 130 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 265 | 0 | 0 | 130 | 0 | 132 | 0 | 90 | 0 | 137 | 0 | 115 | 48 | 17 | 0 | 300 | 54 | 110 | 0 | 85 | 30 | 400 | 104 | 0 | 162 | 105 | 75 | 17 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20 | 0 | 0 | 0 | 0 | 50 | 13 | 67 | 0 | 16 | 32 | 52 | 29 | 22 | 0 | 11 | 76 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 309 | 105 | 0 | 93 | 0 | 112 | 0 | 0 | 113 | 370 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5998 | 3314 | 9312 | 2694 | 721 | 1789 | 0 | 2881 | 716 | 84 | 0 | 340 | 87 | 0 | 0 | 99.56
19:30 | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 285 |  | 0 | 260 | 275 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 12 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 3 | 22 | 25 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 30 | 30 | 48 | 18 | 18 | 0 | 0 | 80 | 280 | 0 | 214 | 78 | 141 | 29 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 33 | 9 | 88 | 96 | 0 | 17 | 0 | 43 | 43 | 53 | 0 | 130 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 270 | 0 | 0 | 100 | 0 | 132 | 0 | 90 | 0 | 142 | 0 | 115 | 52 | 17 | 0 | 300 | 54 | 68 | 0 | 85 | 30 | 400 | 94 | 0 | 162 | 68 | 75 | 17 | 0 | 0 | 0 |  | 722 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 50 | 17 | 60 | 0 | 8 | 33 | 52 | 29 | 22 | 0 | 11 | 80 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 361 | 105 | 0 | 93 | 0 | 112 | 0 | 0 | 113 | 380 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5883 | 3312 | 9195 | 2691 | 722 | 1877 | 0 | 2761 | 682 | 86 | 0 | 288 | 88 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 285 |  | 0 | 260 | 270 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 64 | 11 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 3 | 22 | 25 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 10 | 23 | 25 | 18 | 22 | 0 | 0 | 80 | 280 | 0 | 219 | 78 | 140 | 29 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 33 | 9 | 88 | 99 | 0 | 17 | 0 | 43 | 43 | 53 | 0 | 130 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 270 | 0 | 0 | 100 | 0 | 132 | 0 | 90 | 0 | 142 | 0 | 115 | 52 | 17 | 0 | 300 | 54 | 68 | 0 | 85 | 10 | 400 | 104 | 0 | 162 | 68 | 75 | 17 | 0 | 0 | 0 |  | 721 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 67 | 0 | 8 | 12 | 52 | 29 | 22 | 0 | 11 | 84 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 164 | 0 | 337 | 105 | 0 | 93 | 0 | 112 | 0 | 0 | 113 | 380 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5810 | 3222 | 9032 | 2701 | 721 | 1852 | 0 | 2700 | 645 | 86 | 0 | 239 | 88 | 0 | 0 | 99.57
21:00 | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 285 |  | 0 | 260 | 235 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 40 | 11 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 3 | 22 | 25 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 30 | 0 | 0 | 80 | 320 | 0 | 0 | 78 | 140 | 29 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 9 | 84 | 100 | 0 | 17 | 0 | 42 | 43 | 53 | 0 | 163 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 270 | 0 | 0 | 80 | 0 | 132 | 0 | 90 | 0 | 142 | 0 | 115 | 17 | 0 | 0 | 300 | 54 | 68 | 0 | 85 | 0 | 400 | 104 | 0 | 162 | 68 | 75 | 17 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 52 | 29 | 21 | 0 | 11 | 66 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 168 | 0 | 362 | 105 | 0 | 93 | 0 | 112 | 0 | 0 | 113 | 410 | 214 | 0 | 0 | 0 | 0 | 0 |  | 5480 | 3162 | 8642 | 2516 | 721 | 1876 | 0 | 2577 | 646 | 86 | 0 | 136 | 84 | 0 | 0 | 99.56
22:00 | 0 | 0 | 91 | 0 | 120 | 0 | 0 | 0 | 264 |  | 0 | 260 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 40 | 48 | 11 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 3 | 22 | 25 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 18 | 37 | 0 | 0 | 114 | 325 | 0 | 0 | 78 | 140 | 29 | 51 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 9 | 80 | 101 | 0 | 17 | 0 | 42 | 43 | 53 | 0 | 163 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 276 | 0 | 0 | 80 | 0 | 132 | 0 | 90 | 0 | 100 | 0 | 115 | 17 | 0 | 0 | 300 | 54 | 68 | 0 | 85 | 0 | 400 | 104 | 0 | 162 | 68 | 75 | 17 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 24 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 186 | 0 | 391 | 53 | 0 | 93 | 0 | 112 | 0 | 0 | 70 | 400 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5303 | 2962 | 8265 | 2572 | 721 | 1858 | 0 | 2297 | 570 | 86 | 0 | 81 | 80 | 0 | 0 | 99.56
23:00 | 0 | 0 | 80 | 0 | 120 | 0 | 0 | 0 | 264 |  | 0 | 260 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 0 | 43 | 0 | 35 | 19 | 25 | 3 | 22 | 25 | 25 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 39 | 0 | 0 | 130 | 350 | 0 | 24 | 78 | 140 | 29 | 54 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 74 | 101 | 0 | 17 | 0 | 42 | 43 | 53 | 0 | 163 | 0 | 20 | 78 | 0 | 177 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 276 | 0 | 0 | 40 | 0 | 118 | 0 | 0 | 0 | 100 | 0 | 115 | 0 | 0 | 0 | 230 | 54 | 0 | 0 | 35 | 0 | 400 | 104 | 0 | 162 | 34 | 75 | 17 | 0 | 0 | 0 |  | 721 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 183 | 0 | 415 | 35 | 0 | 50 | 0 | 112 | 0 | 0 | 35 | 390 | 223 | 0 | 0 | 0 | 0 | 0 |  | 4839 | 2886 | 7725 | 2610 | 721 | 1891 | 0 | 1750 | 559 | 86 | 0 | 34 | 74 | 0 | 0 | 99.55
24:00 | 0 | 0 | 90 | 0 | 120 | 0 | 0 | 0 | 264 |  | 0 | 260 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 0 | 45 | 0 | 35 | 19 | 25 | 3 | 22 | 25 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 39 | 0 | 0 | 130 | 320 | 0 | 33 | 78 | 140 | 29 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 69 | 108 | 0 | 17 | 0 | 42 | 43 | 53 | 0 | 163 | 0 | 20 | 77 | 0 | 177 | 18 | 0 | 10 | 0 | 22 | 11 | 0 | 245 | 0 | 0 | 16 | 0 | 96 | 0 | 0 | 0 | 100 | 0 | 115 | 0 | 0 | 0 | 230 | 54 | 0 | 0 | 35 | 0 | 400 | 104 | 0 | 162 | 34 | 75 | 17 | 0 | 0 | 0 |  | 543 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 382 | 0 | 0 | 35 | 0 | 112 | 0 | 0 | 0 | 360 | 221 | 0 | 0 | 0 | 0 | 0 |  | 4715 | 2494 | 7209 | 2601 | 543 | 1855 | 0 | 1526 | 529 | 86 | 0 | 0 | 69 | 0 | 0 | 99.55
KWH | 0 | 0 | 2387000 | 0 | 1878600 | 890727 | 0 | 0 | 7356000 |  | 0 | 6693050 | 6265367 | 0 | 0 | 430357 | 0 | 0 | 0 | 0 | 849168 | 730080 | 126913 | 0 | 0 | 0 | 596880 | 446566 | 670348 | 414036 | 600000 | 86940 | 707600 | 684100 | 676320 | 0 | 1054800 | 968000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 394080 | 0 | 125240 | 114000 | 345600 | 527040 | 428352 | 454560 | 0 | 0 | 2033654 | 7323700 | 0 | 3878000 | 1856727 | 3354960 | 645264 | 291360 | 0 | 1254896 | 0 | 30824 | 225946 | 467640 | 195660 | 764400 | 229870 | 1644480 | 2408640 | 0 | 438012 | 8200 | 1012000 | 1000680 | 1252200 | 0 | 3667663 | 0 | 842208 | 1814400 | 0 | 4634280 | 418000 | 0 | 253080 | 0 | 517056 | 201312 | 0 | 2616981 | 0 | 0 | 902400 | 0 | 1468224 | 103275 | 1605120 | 0 | 2539200 | 0 | 1941600 | 246000 | 331199 | 19922 | 6506072 | 1359233 | 1098140 | 0 | 1424640 | 253440 | 9317800 | 1717440 | 138530 | 3339360 | 1649727 | 1817000 | 445320 | 124747 | 0 | 0 |  | 12270545 | 0 | 8601408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1411000 | 399700 | 0 | 0 | 0 | 0 | 112224 | 24620 | 363152 | 0 | 71786 | 80950 | 596640 | 114547 | 508320 | 0 | 223668 | 1726254 | 0 | 5702400 | 0 | 0 | 0 | 0 | 0 | 0 | 269995 | 0 | 4161055 | 0 | 8886364 | 1141440 | 0 | 1058304 | 0 | 1732636 | 0 | 26307 | 1252704 | 8135000 | 4044655 | 0 | 0 | 19980 | 376560 | 0 |  | 120532206 | 63312214 | 183844420 | 63083895 | 12270545 | 46159064 | 0 | 40700824 | 15563654 | 2022800 | 0 | 1581637 | 1644480 | 817521 | 0
Fuel Cost | 0 | 0 | 3485020 | 0 | 2085246 | 1175759.64 | 0 | 0 | 7576680 |  | 0 | 7295424.5 | 6954557.37 | 0 | 0 | 3640820.22 | 0 | 0 | 0 | 0 | 7744412.16 | 7183987.2 | 1170137.86 | 0 | 0 | 0 | 4357224 | 3451955.18 | 6609631.28 | 310527 | 450000 | 0 | 0 | 0 | 6540014.4 | 0 | 284796 | 261360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1214828 | 1088700 | 3006720 | 4174156.8 | 539723.52 | 1350043.2 | 0 | 0 | 2989471.38 | 5419538 | 0 | 3567760 | 2395177.83 | 3858204 | 729148.32 | 407904 | 0 | 2145872.16 | 0 | 311322.4 | 2157784.3 | 593902.8 | 146745 | 1337700 | 172402.5 | 12333600 | 2553158.4 | 0 | 556275.24 | 130708 | 1659680 | 1601088 | 2228916 | 0 | 4181135.82 | 0 | 1659149.76 | 3465504 | 0 | 8017304.4 | 915420 | 0 | 516283.2 | 0 | 387792 | 152997.12 | 0 | 19784376.36 | 0 | 0 | 4692480 | 0 | 14447324.16 | 1207284.75 | 13081728 | 0 | 17901360 | 0 | 17707392 | 2324700 | 2884743.29 | 0 | 49185904.32 | 11838919.43 | 9652650.6 | 0 | 12209164.8 | 1687910.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 70678339.2 | 0 | 9031478.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1594430 | 619535 | 0 | 0 | 0 | 0 | 1104284.16 | 250139.2 | 3213895.2 | 0 | 970546.72 | 784405.5 | 5781441.6 | 1111105.9 | 975974.4 | 0 | 169316.676 | 10409311.62 | 0 | 30907008 | 0 | 0 | 0 | 0 | 0 | 0 | 404992.5 | 0 | 4868434.35 | 0 | 8797500.36 | 11916633.6 | 0 | 10043304.96 | 0 | 13445255.36 | 0 | 290692.35 | 9257482.56 | 35712650 | 0 | 0 | 0 | 0 | 0 | 0 |  | 327149607.07 | 232338157.616 | 559487764.686 | 58851912.866 | 70678339.2 | 50491259.98 | 0 | 272754874.36 | 77028969.62 | 546156 | 0 | 15173967.56 | 12333600 | 1628685.1 | 0
Yesterday Day Peak | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 357 |  | 0 | 280 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 0 | 25 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 23 | 25 | 18 | 4 | 0 | 0 | 80 | 265 | 0 | 171 | 81 | 139 | 29 | 5 | 0 | 51 | 0 | 0 | 15 | 21 | 5 | 25 | 9 | 83 | 96 | 0 | 20 | 2 | 43 | 43 | 50 | 0 | 163 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 62 | 0 | 0 | 40 | 0 | 58 | 19 | 90 | 0 | 137 | 0 | 115 | 0 | 17 | 4 | 282 | 54 | 53 | 0 | 105 | 30 | 415 | 95 | 23 | 162 | 98 | 75 | 17 | 23 | 0 | 0 |  | 482 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 78 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 146 | 0 | 382 | 87 | 0 | 0 | 0 | 112 | 0 | 5 | 70 | 250 | 130 | 0 | 0 | 3 | 60 | 0 |  | 7959 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 285 | 0 | 0 | 260 | 240 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 3 | 22 | 25 | 51 | 0 | 44 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 30 | 37 | 28 | 18 | 18 | 0 | 0 | 80 | 280 | 0 | 206 | 78 | 139 | 29 | 5 | 0 | 51 | 0 | 16 | 25 | 21 | 8 | 33 | 9 | 87 | 97 | 0 | 17 | 0 | 43 | 43 | 53 | 0 | 130 | 0 | 20 | 77 | 0 | 196 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 265 | 0 | 0 | 130 | 0 | 132 | 0 | 90 | 0 | 137 | 0 | 115 | 48 | 17 | 0 | 300 | 54 | 110 | 0 | 85 | 30 | 400 | 104 | 0 | 162 | 105 | 75 | 17 | 0 | 0 | 0 |  | 721 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20 | 0 | 0 | 0 | 0 | 50 | 13 | 67 | 0 | 16 | 32 | 52 | 29 | 22 | 0 | 11 | 76 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 309 | 105 | 0 | 93 | 0 | 112 | 0 | 0 | 113 | 370 | 220 | 0 | 0 | 0 | 0 | 0 |  | 9312 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 260 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 10 | 22 | 25 | 51 | 0 | 44 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 70 | 100 | 90 | 50 | 20 | 20 | 0 | 0 | 100 | 360 | 0 | 225 | 36 | 140 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 110 | 0 | 17 | 0 | 43 | 43 | 51 | 0 | 163 | 0 | 60 | 77 | 0 | 200 | 18 | 0 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 137 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 75 | 17 |  |  |  |  | 732 | 0 | 360 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 70 | 20 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 25 | 50 | 33 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 95 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 100 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 260 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 10 | 22 | 25 | 51 | 0 | 44 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 19 | 10 | 0 | 0 | 100 | 360 | 0 | 225 | 36 | 138 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 100 | 0 | 17 | 1.6 | 42 | 43 | 51 | 0 | 163 | 0 | 40 | 75 | 0 | 200 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 0 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 135 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 75 | 17 | 30 |  | 57 |  | 491 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 20 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 25 | 50 | 0 | 52 | 0 | 22 | 0 | 10 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 90 | 0 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6 | 10
Generation at 08:00(Today) | 0 | 0 | 91 | 0 | 120 | 0 | 0 | 0 | 265 | 0 | 0 | 260 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 5 | 0 | 0 | 0 | 35 | 17 | 35 | 16 | 25 | 3 | 25 | 28 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 18 | 11 | 0 | 0 | 100 | 325 | 0 | 193 | 73 | 142 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 61 | 84 | 0 | 17 | 0 | 42 | 43 | 53 | 0 | 163 | 0 | 20 | 74 | 0 | 177 | 18 | 0 | 10 | 0 | 18 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 23 | 5 | 10 | 0 | 81 | 0 | 71 | 0 | 0 | 1 | 255 | 54 | 0 | 0 | 36 | 0 | 400 | 48 | 9 | 124 | 0 | 75 | 17 | 2 | 0 | 0 | 0 | 675 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 177 | 0 | 414 | 36 | 0 | 0 | 0 | 111 | 0 | 1 | 90 | 280 | 220 | 0 | 0 | 0 | 6 | 0 | 0
199
| Minimum Generation |  | 5832 | 5:00
| Highest Generation |  | 9312 | 19:00
| Day Peak Generation |  | 7959 | 12:00
| Evening Peak Generation |  | 9312 | 19:00
| HVDC Max Flow |  | 722 | 19:30
| HVDC EvPeak Flow |  | 721 | 19:00
| Load factor L.F |  | 82.26%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-12-23
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-12-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7959 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5853 | MW
Evening Peak Generation : |  | 9312 | MW Hour : | 19:00 | Available Max Generation : |  | 12470 | MW
E.P. Demand (at gen end) : |  | 9312 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9400 | MW
Maximum Generation : |  | 9312 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3070 | MW
Total Gen. (MKWH) : |  | 183.8444 | System Load Factor : | 82.26% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 152 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-12-23
Actual : | 99.52 | Ft.(MSL) , | Rule curve : | 103.9 | Ft.( MSL )
Gas Consumed : | Total = | 835.41 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 109343172.846
: |  | Coal : | 77028969.62 | Oil : | 287928841.92 | Total : | 474300984.386
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3349.0035 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1134.5042 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1015.7044 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 917.4999 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 829.2829 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 669.191 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 379.7666 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 172.4466 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 516.0866 |  |  | 0 | 0%
Total | 0 |  | 8983.4855 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,5
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit-1 & 2
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-2,3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Kallyanpur 132 kV Ckt-2 was under shut down from 08:32 to 16:51 for A/M.
b) Ashuganj-Kishorganj 132 kV Ckt-1 was under shut down from 08:56 to 16:53 for A/M.
c) B.Baria-Shahjibazar 132 kV Ckt-1 was under shut down from 08:36 to 16:16 for A/M.
d) Barapukuria 132/33 kV T-3 transformer was under shut down from 10:06 to 12:23 for C/M.
e) Barishal(O) 132/33 kV T-2 transformer was under shut down from 07:52 to 16:43 for A/M.
f) Chandpur 132/33 kV T-2 transformer was under shut down from 08:36 to 19:05 for A/M.
g) Faridpur-Gopalganj(N) 132 kV Ckt-2 was under shut down from 08:46 to 15:56 for A/M.
h) Ghorasal-Ishurdi 132 kV Ckt-2 was under shut down from 08:24 to 17:08 for A/M.
i) Ghorasal-Joydevpur 132 kV Ckt-1 was under shut down from 09:15 to 17:14 for A/M.
j) Gulshan 132/33 kV T-1 transformer was under shut down from 09:56 to 10:43 for A/M.
k) GPH-BSRM 230 kV Ckt-2 was under shut down from 09:02 to 15:20 for A/M.
l) Halishahar-Khulsi 132 kV Ckt-3 was under shut down from 08:49 to 19:40 for A/M.
m) Haripur-Siddirganj 230 kV Ckt-2 was under shut down from 09:55 to 17:36 for A/M.
n) Hasnabad 230 kV Bus-1 was under shut down from 09:11 to 13:32 for A/M.
o) Jashore-Noapara 132 kV Ckt-2 was under shut down from 08:31 to 14:42 for A/M.
p) Kabirpur-Kaliakoir 132 kV Ckt-1 was under shut down from 10:01 to 15:39 for A/M.
q) Khulna(S)-Gollamari 132 kV Ckt-2 was under shut down from 09:38 to 14:58 for A/M.
r) Kodda 132/33 kV T-3 transformer was under shut down from 09:05 to 17:05 for A/M.
s) Madunaghat-Chandraghona 132 kV Ckt-2 was shut down at 09:56 for D/W.
t) Mongla-Bagerhat 132 kV Ckt-2 was under shut down from 07:12 to 08:30 for breaker replacement.
u) Rampura-Gulshan 132 kV Ckt-1 was under shut down from 10:12 to 10:31 for A/M.
v) Sherpur 132/33 kV T-1 transformer was under shut down from 08:55 to 13:56 for C/M.
w) Siddirganj S/S-Siddirganj peaking 132 kV Ckt tripped at 08:13 showing line overload and was switched on at 08:36.
y) Siddirganj-Matuail 132 kV Ckt tripped at 08:13 showing O/C relay and was switched on at 08:32.
z) Tongi-Tongi Milgate 132 kV Ckt-2 was under shut down from 11:50 to 19:28 for D/W.
aa) Rajshahi 230/132 kV T-1 transformer was under shut down from 11:23 to 13:01 for C/M.
ab) Mohastanghor 132/33 kV T-1 transformer was under shut down from 08:26 to 11:02 for C/M.
ac) Saidpur-Purbasadipur 132 kV Ckt-2 was under shut down from 08:20 to 16:08 for A/M.
ad) Bogura(N)-Bogura(O) 132 kV Ckt-2 was shut down at 10:44 for C/M.
ae) Shahjadpur 132/33 kV T-2 transformer was under shut down from 08:30 to 16:18 for A/M.
af) Bogura(N)-Confidence-2 132 kV Ckt was under shut down from 11:18 to 15:44 for D/W.
ag) Bogura(N)-Sherpur 132 kV Ckt-2 was under shut down from 10:42 to 14:04 for D/W.
ah) Bogura(N)-Sherpur 132 kV Ckt-1 was under shut down from 10:41 to 14:03 for D/W.
ai) Bogura(N) 132 kV main bus was shut down at 10:44 for D/W.
aj) Madunaghat 132/33 kV T-2 transformer was shut down at 12:27 for D/W.
ak) Tongi-Tongi(N) 132 kV Ckt-1 was under shut down from 12:35 to 15:09 for protection test.
al) Satmosjid 132 kV Bus-2 was under shut down from 09:29 to 12:31 for C/M.
am) Savar 33 kV Capacitor bank was under shut down from 09:15 to 16:05 for A/M.
an) Ghorasal #7 was synchronized at 09:11.
ao) Saidpur 132/33 kV T-4 transformer was under shut down from 11:45 to 16:12 for C/M.
ap) Saidpur 132 kV Bus-B was under shut down from 11:40 to 15:50 for C/M.
aq) Tongi(N) 132/33 kV T-1 transformer was under shut down from 13:54 to 15:09 for protection test.
ar) Natore-Bogura(O) 132 kV Ckt-1 was under shut down from 13:05 to 14:25 for C/M.
as) Julda-Shahmirpur 132 kV Ckt-1 was under shut down from 13:24 to 15:00 for C/M.
at) Halishahar 132/33 kV T-1 & T-2 transformers were under shut down from 13:26 to 15:04 for C/M. | [5 empty] | About 25 MW power interruption occurred under
au) Tongi(N)-Tongi 132 kV Ckt-2 was under shut down from 15:27 to 16:18 for protection work. | [5 empty] | Halishahar S/S area from 13:26 to 15:04.
ad) Julda-Shahmirpur 132 kV Ckt-2 was under shut down from 15:01 to 16:16 for C/M.
aw) New Tongi 132/33 kV T-1 transformer was under shut down from 15:25 to 16:28 for A/M.
ay) Ashuganj-225 MW tripped at 20:40 due to flame monitoring system failure and GT & ST were synchronized at
22:36 & 02:11(23/12/21) respectively.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-12-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2387000 | Machine problem
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 1878600 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 890727
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Engine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 285 | 7356000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 260 | 6693050 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 6265367 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 430357
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 11 | 126913 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 414036
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 849168
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 596880 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 730080 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 446566
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 670348
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 28 | 686940 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 707600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 684100
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 676320
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 265 | 2616981 | High Voltage.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 1468224 | High Voltage.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 48 | 246000 | High Voltage.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1717440
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3339360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 124747
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 5560 | 2236 | 42002804
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 103275
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 28 | 527040 | High Voltage.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 84 | 2022800 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 331199 | High Voltage.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 125240 | High Voltage.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 114000 | High Voltage.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1605120
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 428352
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 454560
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 345600 | High Voltage.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19922
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 6506072
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1359233
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1098140
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 30 | 253440 | High Voltage.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 105 | 1649727 | High Voltage.
| Chattogram area Total |  |  |  | 2382 | 972 | 16943720
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2033654 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 3878000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7323700 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 645264 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 291360 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 78 | 1856727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1254896
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 2539200 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 30824 | High Voltage.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 139 | 3354960 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 467640
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 195660 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 87 | 1644480
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 764400
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 225946 | High Voltage.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 229870 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 85 | 1424640 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 445320 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3034 | 1306 | 28606541
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 97 | 2408640 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 438012
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8200
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 130 | 902400 | High Voltage.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1941600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 138530
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 394080
| Mymensingh Area Total |  |  |  | 622 | 384 | 6231462
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1012000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1000680 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3667663 | frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1252200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 201312
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 842208 | GT-8 under maint.
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1814400 | Engine problem
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 75 | 1817000 | On test
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 196 | 4634280
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 418000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 517056
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 253080
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9317800
| Sylhet Area Total |  |  |  | 2377 | 1100 | 26747679
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 721 | 12270545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 8601408 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1141440
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 0 | 0 | 376560 | On test
| Khulna Area Total |  |  |  | 2129 | 1181 | 22389953
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 399700 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1411000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 269995 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 370 | 8135000 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4044655
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | High Voltage.
| Barisal Area Total |  |  |  | 2046 | 688 | 14260350
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 112224
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 13 | 24620 | High Voltage.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 16 | 71786 | High Voltage.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 80950 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4161055 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 309 | 8886364 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 114547 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 508320
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 223668
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 596640
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 67 | 363152 | High Voltage.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 93 | 1058304 | High Voltage.
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1252704
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19980
| Rajshahi Area Total |  |  |  | 2179 | 987 | 17474314
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1726254
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 270 | 5702400
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 1732636
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26307
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 0 | On test
| Rangpur Area Total |  |  |  | 605 | 458 | 9187597
| Total |  |  |  | 20934 | 9312 | 183844420
| Eastern Grid Total |  |  |  | 13975 | 5998 | 120532206
| Western Grid Total |  |  |  | 6959 | 3314 | 63312214
| National Grid Total |  |  |  | 20934 | 9312 | 183844420
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-12-22
(a) ENTIRE EASTERN GRID : |  | 6063 | MW | (b) ENTIRE WESTERN GRID : |  | 2826 | MW
i) Dhaka area |  | 3258 | MW | i) Khulna area |  | 1077 | MW
ii) Chittagong area |  | 1030 | MW | ii) Rajshahi area |  | 880 | MW
iii) Comilla area |  | 720 | MW | iii) Barisal area |  | 247 | MW
iv) Mymensingh area |  | 726 | MW | iv) Rangpur area |  | 622 | MW
v) Sylhet area |  | 329 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8889 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 95 | 16:00 | Tangail | 132 | 18:30 | Noapara | 39 | 18:00
Munsiganj | 64 | 21:00 | Mymensing | 153 | 18:00 | Jessore | 76 | 18:30
Sonargaon | 60 | 12:00 | Kishoreganj | 92 | 19:30 | Benapol | 38 | 18:30
Shyampur | 154 | 11:00 | Netrokona | 79 | 18:00 | Jhenida(Old) | 80 | 18:00
Bhulta | 150 | 19:00 | Jamalpur | 103 | 18:30 | Bottail | 92 | 18:30
Madanganj | 42 | 19:00 | Sherpur | 100 | 18:00 | G.K Project | 38 | 18:30
Shitalakhya | 96 | 12:00 | Srimongal | 35 | 18:00 | Faridpur | 101 | 18:30
Rahim steel | 17 | 23:00 | Shahjibazar | 76 | 18:30 | Rajbari | 38 | 18:00
Matuail | 56 | 9:00 | Fenchuganj | 28 | 17:00 | Madaripur | 63 | 20:00
Ghorasal | 56 | 18:30 | Kulawara | 26 | 18:00 | Sariatpur | 42 | 21:00
Narsingdi | 114 | 19:00 | Sylhet | 96 | 18:00 | Gopalganj | 67 | 18:30
Haripur (SBU) | 104 | 11:00 | Chatak | 11 | 18:00 | Bagerhat | 77 | 18:00
Sreenagar | 26 | 20:00 | Sunamganj | 29 | 19:00 | Mongla | 38 | 9:00
Ullon | 43 | 13:00 | Biani Bazar | 40 | 18:00 | Satkhira | 73 | 18:30
Hasnabad | 61 | 13:00 | Comilla (S) | 92 | 18:00 | Gallamari | 30 | 13:00
Magbazar | 61 | 13:00 | Comilla(N) | 81 | 19:00 | Magura | 40 | 18:00
Maniknagar | 44 | 13:00 | Chandpur | 43 | 19:30 | Norail | 37 | 18:00
Bangabhaban | 7 | 12:00 | Feni | 74 | 18:30 | Chuadanga | 64 | 18:00
Motijheel | 17 | 12:00 | Chowmuhani | 128 | 19:00 | Barisal(N) | 29 | 20:00
Narinda | 40 | 17:00 | Ashuganj | 31 | 18:00 | Barisal (S) | 78 | 18:30
Kazla | 72 | 12:00 | Daudkandi | 94 | 19:30 | Patuakhali | 73 | 20:00
Dhanmondi | 126 | 13:00 | B.Baria | 86 | 19:30 | Bhandaria | 38 | 20:00
Lalbag | 73 | 13:00 | Ramganj | 52 | 19:30 | Borguna | 12 | 19:30
Madartek | 43 | 13:00 | Chaddagram | 34 | 20:00 | Borhan Uddin | 28 | 22:00
Dhaka University | 20 | 12:00 | PHP | 6 | 14:00 | Ishurdi | 51 | 18:30
Aftabnagar | 10 | 12:00 | Kochua | 38 | 19:00 | Ruppur Paromanobik | 3 | 20:00
Fatullah | 47 | 12:00 | Madunaghat | 40 | 18:00 | Natore | 87 | 18:00
Nawabganj | 32 | 21:00 | Hathazari | 69 | 18:00 | Bogra | 101 | 20:00
Keraniganj | 48 | 18:30 | Khulshi | 147 | 14:00 | Noagaon | 80 | 20:00
Banani | 38 | 18:00 | Halishahar | 66 | 17:00 | Rajshahi | 97 | 18:00
Mirpur | 80 | 18:30 | Baraulia | 138 | 11:00 | Rajshahi New | 14 | 19:00
Kalyanpur | 66 | 12:00 | Sikalbaha | 22 | 18:00 | C.Nawabganj | 45 | 11:00
Gulshan | 68 | 5:00 | Dohazari | 66 | 19:00 | Amnura | 32 | 20:00
Uttara | 49 | 18:00 | Cox'sbazar | 76 | 18:00 | Pabna | 68 | 18:30
Uttara New | 11 | 13:00 | Chandraghona | 34 | 13:00 | Shahjadpur | 74 | 18:30
Kamrangirchar | 77 | 13:00 | Kaptai | 3.5 | 18:00 | Serajganj | 64 | 18:30
Savar | 142 | 11:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 42 | 18:00
Bhasantec | 82 | 18:00 | Bakulia | 78 | 12:00 | Joypurhat | 43 | 18:00
Agargaon | 53 | 13:00 | Julda | 23 | 16:00 | Sherpur(Bogura) | 44 | 18:00
Satmosjid | 472 | 11:00 | TK chemical | 21 | 18:00 | Mohastangor | 42 | 18:00
Old Tongi | 90 | 14:00 | Modern Steel | 0 | 1:00 | Bhangura | 19 | 18:30
Kabirpur | 181 | 18:00 | Shahmirpur | 35 | 18:30 | Rangpur | 104 | 18:00
Bashundara | 128 | 13:00 | Khagrachhari | 18 | 7:00 | Lalmonirhat | 40 | 18:30
Manikgong | 56 | 19:00 | Matarbari | 24 | 17:00 | Saidpur | 85 | 18:00
Joydevpur | 114 | 18:30 | Baroiar Hat | 32 | 18:00 | Purbasadipur | 97 | 18:30
New Tongi | 64 | 12:00 | Rangamati | 10 | 18:00 | Thakurgaon | 61 | 18:00
Kodda | 221 | 12:00 | Abul Khair 230 | 169 | 13:00 | Palashbari | 86 | 18:00
Dhamrai | 64 | 18:30 | BSRM | 161 | 2:00 | Barapukuria | 42 | 20:00
Rajendrapur | 86 | 18:30 | GPH Ispat | 95 | 6:00 | Panchagar | 44 | 19:00
Purbachal | 11 | 18:00 | Agrabad | 54 | 18:30 | Joldhaka | 23 | 18:00
Tongi Millgate | 36 | 12:00 | Goalpara | 16 | 13:00 | Kurigram | 53 | 18:00
Valuka | 82 | 12:00 | Central S/S | 78 | 18:30 | Mithapukur | 25 | 18:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-12-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 9:00 | 407 | 11:00 | Kaliakoir | 410 | 0.20833 | 403 | 0.41667
| Bheramara | 408 | 21:00 | 397 | 18:00 | Bhulta | 404 | 0.375 | 392 | 0.66667
| Ashuganj(N) | 407 | 13:00 | 400 | 3:00 | Gopalganj | 420 | 0.625 | 405 | 0.875
| Payra | 420 | 6:00 | 412 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 248 | 1:00 | 245 | 11:00 | Hathazari | 241 | 17:00 | 234 | 6:00
| Ishurdi | 245 | 4:00 | 240 | 8:00 | Megnaghat | 246 | 7:00 | 244 | 6:00
| Ashuganj | 250 | 14:00 | 245 | 10:00 | Fenchuganj | 247 | 20:00 | 243 | 8:00
| Serajganj | 240 | 2:00 | 237 | 16:00 | Siddhirganj | 242 | 6:00 | 236 | 10:00
| Baghabari | 242 | 3:00 | 237 | 11:00 | Maniknagar | 241 | 6:00 | 234 | 11:00
| Barapukuria | 237 | 24:00 | 233 | 13:00 | Agargaon | 242 | 5:00 | 235 | 11:00
| Bogra | 240 | 9:00 | 233 | 13:00 | Barisal | 247 | 9:00 | 241 | 18:30
| Rajshahi | 245 | 18:30 | 234 | 8:00 | Bhola 225 MW | 249 | 3:00 | 245 | 18:00
| Khulna South | 249 | 4:00 | 236 | 18:00 | AKSML | 243 | 9:00 | 232 | 23:00
| Rampura | 240 | 7:00 | 233 | 10:00 | BSRM | 242 | 9:00 | 231 | 23:00
| Haripur | 240 | 1:00 | 234 | 16:00 | Bibiyana | 247 | 13:00 | 242 | 11:00
| Hasnabad | 241 | 21:00 | 234 | 16:00 | Bhulta | 243 | 6:00 | 235 | 15:00
| Shyampur | 241 | 6:00 | 234 | 11:00 | Ashuganj (S) | 246 | 19:30 | 241 | 11:00
| Aminbazar | 243 | 1:00 | 237 | 2:00 | Kaliakoir | 241 | 19:00 | 234 | 11:00
| Tongi | 240 | 17:00 | 233 | 9:00 | GPH | 242 | 19:00 | 231 | 23:00
| Comilla (N) | 243 | 19:00 | 236 | 16:00 | Jhenaidah | 243 | 2:00 | 234 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 141 | 6:00 | 136 | 11:00 | Kachua | 142 | 0.041667 | 140 | 0.66667
| Munsiganj | 142 | 18:30 | 135 | 16:00 | Madanhat | 142 | 0.20833 | 138 | 0.375
| Sonargaon | 139 | 1:00 | 138 | 2:00 | Hathazari | 141 | 0.70833 | 137 | 0.25
| Shyampur | 139 | 19:00 | 134 | 11:00 | Khulshi | 139 | 0.29167 | 134 | 0.33333
| Bhulta | 135 | 1:00 | 132 | 10:00 | Halishahar | 142 | 0.77083 | 135 | 0.33333
| Madanganj | 142 | 21:00 | 135 | 16:00 | Baraulia | 142 | 0.70833 | 135 | 0.45833
| Shitalakhya | 143 | 21:00 | 136 | 10:00 | Sikalbaha | 142 | 0.79167 | 136 | 0.45833
| Rahim steal | 140 | 2:00 | 136 | 16:00 | Dohazari | 139 | 0.77083 | 135 | 0.041667
| Matuail | 141 | 6:00 | 136 | 11:00 | Cox'sbazar | 126 | 0.5 | 121 | 0.79167
| Ghorasal | 144 | 1:00 | 141 | 7:00 | Chandraghona | 142 | 0.33333 | 136 | 0.29167
| Narsinghdi | 139 | 0:00 | 134 | 8:00 | Kaptai | 140 | 0.041667 | 138 | 0.33333
| Haripur (SBU) | 141 | 5:00 | 140 | 1:00 | A. Khaer Stl. | 141 | 0.75 | 136 | 0.625
| Sreenagar | 139 | 1:00 | 134 | 10:00 | Bakulia | 141 | 0.77083 | 135 | 0.45833
| Ullon | 137 | 5:00 | 132 | 11:00 | Julda | 141 | 0.58333 | 136 | 0.125
| Hasnabad | 142 | 13:00 | 139 | 16:00 | TK Chemical | 142 | 0.79167 | 137 | 0.041667
| Magbazar | 139 | 5:00 | 133 | 12:00 | Modern Steel | 140 | 0.33333 | 137 | 0.125
| Maniknagar | 142 | 5:00 | 137 | 10:00 | Shahmirpur | 141 | 0.79167 | 134 | 0.45833
| Bangabhaban | 142 | 5:00 | 137 | 10:00 | Khagrachhari | 140 | 0.29167 | 136 | 0.66667
| Motijheel | 142 | 5:00 | 137 | 10:00 | Matarbari | 125 | 0.41667 | 118 | 0.8125
| Narinda | 142 | 5:00 | 137 | 10:00 | Baroiar Hat | 142 | 18:30 | 138 | 8:00
| Kazla | 142 | 5:00 | 137 | 10:00 | Rangamati | 142 | 19:00 | 136 | 16:00
| Dhanmondi | 141 | 4:00 | 135 | 16:00 | Agrabad | 140 | 19:00 | 135 | 0.45833
| Lalbag | 139 | 2:00 | 133 | 11:00 | Goalpara S/S | 142 | 5:00 | 134 | 0.8125
| Madartek | 137 | 5:00 | 131 | 16:00 | Khulna Central S/S | 140 | 5:00 | 135 | 0.75
| Dhaka University | 138 | 7:00 | 133 | 10:00 | Noapara | 141 | 3:00 | 135 | 0.5
| Aftabnagar | 139 | 0:00 | 132 | 10:00 | Jessore | 139 | 0.125 | 133 | 0.5
| Fatullah | 139 | 1:00 | 135 | 16:00 | Benapol | 140 | 2:00 | 132 | 0.75
| Nawabganj | 138 | 6:00 | 133 | 11:00 | Jhenida(Old) | 141 | 0.20833 | 135 | 0.33333
| Keraniganj | 138 | 2:00 | 133 | 11:00 | Bottail | 141 | 0.083333 | 137 | 0.33333
| Banani | 138 | 7:00 | 132 | 16:00 | G.K Project | 143 | 0.041667 | 141 | 0.45833
| Mirpur | 140 | 18:30 | 135 | 10:00 | Faridpur | 141 | 0.16667 | 137 | 0.75
| Kalyanpur | 140 | 21:00 | 136 | 9:00 | Rajbari | 141 | 0.16667 | 138 | 0.75
| Gulshan | 137 | 5:00 | 132 | 11:00 | Madaripur | 146 | 5:00 | 140 | 0.875
| Uttara | 141 | 13:00 | 133 | 16:00 | Shariyatpur S/S | 145 | 0.16667 | 140 | 0.83333
| Uttara New | 140 | 21:00 | 135 | 14:00 | Gopalganj | 144 | 5:00 | 140 | 0.75
| Kamrangirchar | 139 | 4:00 | 133 | 15:00 | Bagerhat | 140 | 4:00 | 133 | 0.66667
| Savar | 141 | 21:00 | 135 | 10:00 | Mongla | 138 | 3:00 | 130 | 8:00
| Bhasantec | 139 | 2:00 | 134 | 10:00 | Satkhira | 139 | 0.16667 | 132 | 8:00
| Agargaon | 139 | 1:00 | 135 | 11:00 | Gallamari | 142 | 5:00 | 138 | 0.45833
| Satmosjid | 139 | 2:00 | 134 | 15:00 | Magura | 142 | 0.20833 | 135 | 0.75
| Tongi | 143 | 13:00 | 138 | 9:00 | Narail | 141 | 4:00 | 134 | 0.33333
| Kabirpur | 139 | 22:00 | 135 | 15:00 | Chuadanga | 140 | 4:00 | 132 | 0.70833
| Basundhara | 141 | 5:00 | 134 | 11:00 | Barisal(N) | 145 | 5:00 | 141 | 12:00
| Purbachal | 138 | 24:00 | 133 | 16:00 | Barisal (S) | 144 | 0.125 | 139 | 0.8125
| Manikganj | 143 | 21:00 | 136 | 15:00 | Patuakhali(S) | 142 | 0.083333 | 137 | 0.83333
| Joydevpur | 141 | 17:00 | 135 | 14:00 | Bhandaria | 143 | 0.29167 | 136 | 0.83333
| New Tongi | 140 | 23:00 | 130 | 10:00 | Borguna | 143 | 2:00 | 139 | 18:00
| Kodda | 141 | 19:00 | 135 | 11:00 | Jhenaidah(New) | 140 | 2:00 | 135 | 8:00
| Dhamrai | 138 | 18:00 | 129 | 11:00 | Ishurdi | 142 | 4:00 | 138 | 8:00
| Rajendrapur | 139 | 8:00 | 133 | 10:00 | Ruppur Paromanobik | 140 | 1:00 | 139 | 7:00
| Tongi Millgate | 141 | 13:00 | 134 | 16:00 | Natore | 140 | 18:30 | 136 | 13:00
| Valuka | 133 | 0:00 | 128 | 15:00 | Bogra | 140 | 19:00 | 137 | 12:00
| Tangail | 137 | 4:00 | 134 | 8:00 | Noagaon | 137 | 19:00 | 131 | 13:00
| Mymensing | 135 | 10:00 | 126 | 8:00 | Rajshahi | 139 | 18:30 | 134 | 8:00
| Kishorganj | 136 | 0:00 | 132 | 15:00 | Rajshahi New | 141 | 18:30 | 133 | 8:00
| Netrokona | 134 | 0:00 | 126 | 8:00 | C.Nawabganj | 139 | 18:30 | 132 | 12:00
| Jamalpur | 140 | 10:00 | 128 | 6:00 | Amnura | 140 | 18:30 | 131 | 12:00
| Sherpur | 139 | 12:00 | 124 | 8:00 | Pabna | 141 | 2:00 | 136 | 16:00
| Srimongal | 141 | 1:00 | 138 | 9:00 | Shahjadpur | 144 | 1:00 | 141 | 13:00
| Shahjibazar | 139 | 6:00 | 137 | 8:00 | Serajganj | 140 | 1:00 | 136 | 13:00
| Fenchuganj | 139 | 24:00 | 136 | 2:00 | Niyamatpur | 135 | 4:00 | 128 | 8:00
| Khulawara | 138 | 5:00 | 136 | 11:00 | Joypurhat | 138 | 19:00 | 132 | 8:00
| Sylhet | 135 | 1:00 | 134 | 15:00 | Sherpur(Bogura) | 140 | 19:00 | 135 | 11:00
| Chatak | 136 | 1:00 | 135 | 10:00 | Mohastangor | 138 | 18:30 | 135 | 8:00
| Sunamganj | 135 | 2:00 | 133 | 10:00 | Bangura | 142 | 1:00 | 139 | 15:00
| Biani Bazar | 136 | 3:00 | 134 | 11:00 | Rangpur | 135 | 15:00 | 131 | 18:00
| Comilla(s) | 130 | 1:00 | 126 | 9:00 | Lalmonirhat | 133 | 4:00 | 129 | 18:30
| Comilla(n) | 146 | 18:00 | 142 | 11:00 | Saidpur | 133 | 3:00 | 127 | 18:00
| Chandpur | 142 | 1:00 | 140 | 21:00 | Purbasadipur | 132 | 1:00 | 123 | 13:00
| Feni | 143 | 9:00 | 140 | 1:00 | Thakurgaon | 131 | 5:00 | 119 | 13:00
| Chowmuhani | 142 | 13:00 | 138 | 1:00 | Palashbari | 135 | 4:00 | 132 | 15:00
| Ashuganj | 142 | 13:00 | 140 | 8:00 | Barapukuria | 136 | 0.16667 | 133 | 0.75
| Daudkandi | 142 | 5:00 | 138 | 15:00 | Panchagar | 132 | 0.16667 | 123 | 0.54167
| B.Baria | 138 | 13:00 | 135 | 21:00 | Joldhaka | 133 | 0.20833 | 127 | 0.75
| Ramganj | 141 | 1:00 | 138 | 21:00 | Kurigram | 134 | 0.625 | 128 | 0.75
| Chaddagram | 144 | 18:00 | 140 | 23:00 | Mithapukur | 139 | 7:00 | 132 | 8:00
| PHP | 142 | 19:00 | 138 | 8:00

## L-Curve
Date | 2021-12-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 356 | 4715 | 2494 | 7209 |  |  |  | QF-LDC-11
0:30 | 291 | 4573 | 2338 | 6911 | Date: | 2021-12-22
1:00 | 226 | 4431 | 2182 | 6613
1:30 | 254 | 4303 | 2153.5 | 6456.5
2:00 | 282 | 4175 | 2125 | 6300
2:30 | 292 | 4068 | 2111.5 | 6179.5 | [5 empty] | Gen. at Eve. Peak | 9312 | 9312 MW (19:00 )
3:00 | 302 | 3961 | 2098 | 6059 | [6 empty] | 19:00
3:30 | 291 | 3912 | 2049 | 5961 | [5 empty] | Gen. at Day Peak | 7959 | 7959 MW (12:00 )
4:00 | 280 | 3863 | 2000 | 5863 | [6 empty] | 12:00
4:30 | 248 | 3876.5 | 1971 | 5847.5 | [5 empty] | Highest Generation | 9312
5:00 | 216 | 3890 | 1942 | 5832 | [6 empty] | 19:00
5:30 | 193 | 3980.5 | 1956 | 5936.5
6:00 | 170 | 4071 | 1970 | 6041
6:30 | 161 | 4150 | 2076.5 | 6226.5
7:00 | 152 | 4229 | 2183 | 6412
7:30 | 173 | 4420.5 | 2331.5 | 6752
8:00 | 194 | 4612 | 2480 | 7092
8:30 | 259 | 4726.5 | 2520 | 7246.5
9:00 | 324 | 4841 | 2560 | 7401
9:30 | 427 | 4872.5 | 2619 | 7491.5
10:00 | 530 | 4904 | 2678 | 7582
10:30 | 510.5 | 4968.5 | 2635 | 7603.5
11:00 | 491 | 5033 | 2592 | 7625
11:30 | 395.5 | 5219 | 2573 | 7792
12:00 | 300 | 5405 | 2554 | 7959
12:30 | 251.5 | 5491 | 2589 | 8080
13:00 | 203 | 5577 | 2624 | 8201
13:30 | 292.5 | 5439 | 2567.5 | 8006.5
14:00 | 382 | 5301 | 2511 | 7812
14:30 | 437.5 | 5162 | 2509 | 7671
15:00 | 493 | 5023 | 2507 | 7530
15:30 | 533.5 | 5036.5 | 2513 | 7549.5
16:00 | 574 | 5050 | 2519 | 7569
16:30 | 572 | 5072 | 2558 | 7630
17:00 | 570 | 5094 | 2597 | 7691
17:30 | 451 | 5507 | 2924 | 8431
18:00 | 332 | 5920 | 3251 | 9171
18:30 | 306 | 5959 | 3282.5 | 9241.5
19:00 | 280 | 5998 | 3314 | 9312
19:30 | 352 | 5883 | 3312 | 9195
20:00 | 286 | 5810 | 3222 | 9032 |  |  |  | Executive Engineer
20:30 | 332 | 5645 | 3192 | 8837 |  |  |  | Network Operation Division
21:00 | 378 | 5480 | 3162 | 8642
21:30 | 394 | 5391.5 | 3062 | 8453.5
22:00 | 410 | 5303 | 2962 | 8265 |  |  |  |  | Page 6 of 7
22:30 | 502 | 5071 | 2924 | 7995
23:00 | 594 | 4839 | 2886 | 7725
23:30 | 475 | 4777 | 2690 | 7467
24:00 | 356 | 4715 | 2494 | 7209
9312 MW (19:00 )
7959 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-12-22 |  | Energy |  | 183844420
[13 empty] | 2021-12-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2601 | 543 | 1855 | 0 | 1526 | 529 | 86 | 0 | 0 | 69 | 0 | 0
0:30 | 2616.5 | 444.5 | 1976 | 0 | 1170 | 554.5 | 86 | 0 | 0 | 63.5 | 0 | 0 | Date: | 2021-12-22
1:00 | 2632 | 346 | 2097 | 0 | 814 | 580 | 86 | 0 | 0 | 58 | 0 | 0
1:30 | 2625.5 | 345 | 2069.5 | 0 | 692.5 | 580 | 86 | 0 | 0 | 58 | 0 | 0 | [8 empty] | Total Energy | 183.8444 | Total Energy Gen 183.844 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 183.844 MKWHr
2:00 | 2619 | 344 | 2042 | 0 | 571 | 580 | 86 | 0 | 0 | 58 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2619.5 | 344 | 2027.5 | 0 | 469.5 | 576 | 86 | 0 | 0 | 57 | 0 | 0 | [8 empty] | Energy Requirement | 183.8444
3:00 | 2620 | 344 | 2013 | 0 | 368 | 572 | 86 | 0 | 0 | 56 | 0 | 0
3:30 | 2607 | 344 | 1969 | 0 | 327 | 572 | 86 | 0 | 0 | 56 | 0 | 0 | [6 empty] | Shortage
4:00 | 2594 | 344 | 1925 | 0 | 286 | 572 | 86 | 0 | 0 | 56 | 0 | 0
4:30 | 2585 | 344 | 1923 | 0 | 286.5 | 567 | 86 | 0 | 0 | 56 | 0 | 0
5:00 | 2576 | 344 | 1921 | 0 | 287 | 562 | 86 | 0 | 0 | 56 | 0 | 0
5:30 | 2571.5 | 343.5 | 1952 | 0 | 366 | 561.5 | 86 | 0 | 0 | 56 | 0 | 0
6:00 | 2567 | 343 | 1983 | 0 | 445 | 561 | 86 | 0 | 0 | 56 | 0 | 0
6:30 | 2565 | 381 | 1977 | 0 | 590.5 | 571.5 | 86 | 0 | 0 | 54.5 | 1 | 0 |  |  |  |  | Coal
7:00 | 2563 | 419 | 1971 | 0 | 736 | 582 | 86 | 0 | 0 | 53 | 2 | 0
7:30 | 2604.5 | 451.5 | 2016 | 0 | 939 | 582 | 86 | 0 | 0 | 59 | 14 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2646 | 484 | 2061 | 0 | 1142 | 582 | 86 | 0 | 0 | 65 | 26 | 0
8:30 | 2621.5 | 484 | 1983.5 | 0 | 1378 | 576.5 | 86 | 0 | 5 | 70 | 42 | 0
9:00 | 2597 | 484 | 1906 | 0 | 1614 | 571 | 86 | 0 | 10 | 75 | 58 | 0
9:30 | 2545 | 484 | 1861.5 | 0 | 1736.5 | 601 | 86 | 0 | 21 | 77.5 | 79 | 0
10:00 | 2493 | 484 | 1817 | 0 | 1859 | 631 | 86 | 0 | 32 | 80 | 100 | 0
10:30 | 2499.5 | 483 | 1796.5 | 0 | 1875.5 | 632 | 86 | 0 | 32 | 82.5 | 116.5 | 0
11:00 | 2506 | 482 | 1776 | 0 | 1892 | 633 | 86 | 0 | 32 | 85 | 133 | 0
11:30 | 2535.5 | 482 | 1842 | 0 | 1964 | 630.5 | 86 | 0 | 32 | 84 | 136 | 0
12:00 | 2565 | 482 | 1908 | 0 | 2036 | 628 | 86 | 0 | 32 | 83 | 139 | 0
12:30 | 2602.5 | 482 | 1885 | 0 | 2149.5 | 630.5 | 86 | 0 | 40 | 83 | 121.5 | 0
13:00 | 2640 | 482 | 1862 | 0 | 2263 | 633 | 86 | 0 | 48 | 83 | 104 | 0
13:30 | 2640 | 482 | 1862 | 0 | 2263 | 633 | 86 | 0 | 48 | 83 | 104 | 0
14:00 | 2640 | 482 | 1862 | 0 | 2263 | 633 | 86 | 0 | 48 | 83 | 104 | 0
14:30 | 2605.5 | 483 | 1865 | 0 | 1986 | 634.5 | 80 | 0 | 40 | 82.5 | 89 | 0
15:00 | 2571 | 484 | 1868 | 0 | 1709 | 636 | 74 | 0 | 32 | 82 | 74 | 0
15:30 | 2610 | 484 | 1873 | 0 | 1681.5 | 635.5 | 80 | 0 | 48 | 80.5 | 57 | 0
16:00 | 2649 | 484 | 1878 | 0 | 1654 | 635 | 86 | 0 | 64 | 79 | 40 | 0
16:30 | 2595.5 | 531 | 1739 | 0 | 1838.5 | 635.5 | 86 | 0 | 97.5 | 82.5 | 24.5 | 0
17:00 | 2542 | 578 | 1600 | 0 | 2023 | 636 | 86 | 0 | 131 | 86 | 9 | 0
17:30 | 2599.5 | 602.5 | 1754 | 0 | 2382.5 | 655.5 | 86 | 0 | 257.5 | 89 | 4.5 | 0
18:00 | 2657 | 627 | 1908 | 0 | 2742 | 675 | 86 | 0 | 384 | 92 | 0 | 0
18:30 | 2675.5 | 674 | 1848.5 | 0 | 2811.5 | 695.5 | 85 | 0 | 362 | 89.5 | 0 | 0
19:00 | 2694 | 721 | 1789 | 0 | 2881 | 716 | 84 | 0 | 340 | 87 | 0 | 0
19:30 | 2691 | 722 | 1877 | 0 | 2761 | 682 | 86 | 0 | 288 | 88 | 0 | 0
20:00 | 2701 | 721 | 1852 | 0 | 2700 | 645 | 86 | 0 | 239 | 88 | 0 | 0
20:30 | 2608.5 | 721 | 1864 | 0 | 2638.5 | 645.5 | 86 | 0 | 187.5 | 86 | 0 | 0
21:00 | 2516 | 721 | 1876 | 0 | 2577 | 646 | 86 | 0 | 136 | 84 | 0 | 0
21:30 | 2544 | 721 | 1867 | 0 | 2437 | 608 | 86 | 0 | 108.5 | 82 | 0 | 0
22:00 | 2572 | 721 | 1858 | 0 | 2297 | 570 | 86 | 0 | 81 | 80 | 0 | 0
22:30 | 2591 | 721 | 1874.5 | 0 | 2023.5 | 564.5 | 86 | 0 | 57.5 | 77 | 0 | 0
23:00 | 2610 | 721 | 1891 | 0 | 1750 | 559 | 86 | 0 | 34 | 74 | 0 | 0
23:30 | 2605.5 | 632 | 1873 | 0 | 1638 | 544 | 86 | 0 | 17 | 71.5 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 24.2° C
24:00 | 2601 | 543 | 1855 | 0 | 1526 | 529 | 86 | 0 | 0 | 69 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 183.844 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 183.844 MKWHr
Note on W13: Author:

## Generation
g | 2021-12-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 34 | 46 | 46 | 46 |  | 44 | 46 | 46 | 46 | 46 | 46 | 46 | 1054800
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 5 | 11 | 15 | 18 | 19 | 9 | 14 | 11 | 3 | 0 | [9 empty] | 103275
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 15 | 51 |  | 51 | 17 | 17 |  |  |  |  | 125240
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 51 |  | 17 | 17 | 17 |  |  |  |  | 331199
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 16 |  | 16 | [6 empty] | 30824
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 5 | 30 | 30 | 62 | 85 | 95 | 95 | 95 | 185 | 255 |  | 265 | 270 | 270 | 270 | 276 | 276 | 245 | 2616981
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 81 | 81 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1856727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 98 | 100 | 90 | 99 | 101 | 101 | 126 | 100 | 114 | 100 | 100 | 101 | 116 | 100 | 103 | 98 | 100 |  | 100 | 100 | 100 | 100 | 91 | 80 | 90 | 2387000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | [9 empty] | 100 | 150 | 150 | 150 | 150 | 150 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 1878600
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 114 | 130 | 130 | 2033654
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 23 | 23 | 23 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 645264
33 | Ashuganj 225 MW CCPP | 187 | 184 | 184 | 196 | 193 | 188 | 188 | 187 | 182 | 171 | 177 | 171 | 166 | 160 | 161 | 158 | 181 | 199 |  | 206 | 214 | 219 |  |  | 24 | 33 | 3878000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 265 | 295 | 265 | 275 | 285 | 270 | 315 | 280 | 280 |  | 280 | 280 | 280 | 320 | 325 | 350 | 320 | 7323700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 51 | 54 | 55 | 291360
36 | Chandpur 150 MW CCPP | 138 | 140 | 140 | 141 | 141 | 141 | 140 | 141 | 141 | 141 | 141 | 139 | 142 | 141 | 139 | 140 | 140 | 140 |  | 139 | 141 | 140 | 140 | 140 | 140 | 140 | 3354960
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6693050
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 300 | 360 | 360 | 360 | 326 | 293 | 292 | 357 | 330 | 289 | 357 | 302 | 274 | 282 |  | 285 | 285 | 285 | 285 | 264 | 264 | 264 | 7356000
42 | RPCL 210MW CCPP | 108 | 104 | 109 | 109 | 110 | 109 | 110 | 110 | 110 | 100 | 100 | 96 | 96 | 82 | 84 | 95 | 96 | 96 |  | 97 | 96 | 99 | 100 | 101 | 101 | 108 | 2408640
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 5 | 7 | 19 | 29 | 23 | 11 | 11 | 11 | 6 | 1 | [9 empty] | 138530
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 1012000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1000680
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 69 | 69 | 69 | 69 | 69 | 34 | 34 | 34 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 842208
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 76 | 76 | 30 | 77 |  | 77 | 77 | 77 | 77 | 77 | 78 | 77 | 1814400
| Shahjibazar 100 MW GTPP | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1817000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 196 | 196 | 196 | 197 | 197 | 197 | 197 | 151 | 197 |  | 196 | 196 | 196 | 196 | 196 | 177 | 177 | 4634280
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253080
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 5 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201312
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 50 | 50 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1252200
56 | Shahjahanulla 25 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 16 | 21 | 21 | 21 | 21 | 21 | 24 |  | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 517056
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 324 | 320 | 415 | 415 | 335 | 360 | 380 | 330 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9317800
58 | Nababganj 55 MW PP (Southern power ) | 17 |  |  |  |  | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 670348
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 4 | 17 | 24 | 25 | 22 | 23 | 25 | 25 | 25 | 24 | 24 |  | 25 | 24 | 24 | 24 | 25 | 24 | 24 | 394080
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 428352
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 414036
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 17 | 17 | 14 | 14 | 14 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438012
63 | Impoprt (Tripura) | 58 | 58 | 56 | 56 | 56 | 56 | 53 | 65 | 75 | 80 | 85 | 83 | 83 | 83 | 82 | 79 | 86 | 92 |  | 87 | 88 | 88 | 84 | 80 | 74 | 69 | 1644480
64 | Malancha, Ctg. EPZ (United) | 31 | 31 | 31 | 31 | 31 | 31 | 29 | 11 | 3 | 4 | 4 | 4 | 10 | 0 | 0 | 5 | 8 | 11 |  | 18 | 18 | 22 | 30 | 37 | 39 | 39 | 454560
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 467640
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 11 | 8 | 8 |  | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 195660
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 764400
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 229870
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 86940
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 707600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 20 | 17 | 33 | 30 | 28 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 684100
73 | Ghorashal 108MW PP (Regent) | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 53 | 53 | [17 empty] | 890727
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [6 empty] | 3 | 16 | 69 | 106 | 103 | 105 | 105 | 105 | 65 | 65 | 65 | 65 |  | 85 | 85 | 85 | 85 | 85 | 35 | 35 | 1424640
| Manikgonj 162MW PP(MPGL) | 162 | 108 | 17 |  |  | 54 | 108 | 151 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3339360
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 2 | 41 | 51 | 51 | 51 | 51 | 51 | 45 |  | 22 |  | 51 | 51 | 51 | 51 | 51 | 25 |  | 676320
79 | Kodda 150MW PP | [8 empty] | 10 | 32 | 32 | 32 | 48 | 48 | 32 | 64 | 98 | 115 |  | 82 | 82 | 64 | 40 | 48 |  |  | 730080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [8 empty] | 2 | 8 | 8 | 15 | 25 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 |  |  | 225946
| Gazipur 100 MW PP | [15 empty] | 2 | 19 | 52 |  | 48 | 52 | 52 | 17 | 17 |  |  | 246000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 3 | 2 | 0 | [10 empty] | 19922
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 45 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1359233
| Karnaphuli Power Ltd. | 17 | [5 empty] | 6 | 17 | 30 | 34 | 34 | 53 | 71 | 80 | 87 | 74 | 79 | 110 |  | 110 | 68 | 68 | 68 | 68 |  |  | 1098140
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [13 empty] | 9 | 11 | 11 | 12 | 12 |  | 11 | 12 | 11 | 11 | 11 | 11 | 11 | 126913
86 | Meghnaghat CCPP ( Summit) | 280 | 280 | 300 | 275 | 300 | 275 | 275 | 320 | 260 | 295 | 290 | 270 | 260 | 320 | 255 | 255 | 230 | 250 |  | 240 | 275 | 270 | 235 | 150 | 150 | 150 | 6265367
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 36 |  |  |  |  | 20 | 53 | 84 | 95 | 94 | 95 | 95 | 104 | 104 | 60 | 35 | 35 | 99 |  | 104 | 94 | 104 | 104 | 104 | 104 | 104 | 1717440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [15 empty] | 4 | 30 | 30 |  | 30 | 30 | 10 |  |  |  |  | 114000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1254896
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 7 | 16 | 16 | 48 | 70 | 48 | 24 | 24 | 48 | 85 |  | 102 | 102 | 102 | 102 | 40 | 16 | 16 | 849168
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 25 | 25 | 25 | 25 |  |  |  |  | 24 |  | 28 | 48 | 25 | 25 | 25 | 25 | 25 | 527040
96 | Chattogram 108 MW PP (ECPV) | [8 empty] | 6 | 15 | 18 | 23 | 32 | 35 | 38 | 36 | 36 | 36 |  | 37 | 30 | 23 |  |  |  |  | 345600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 30 | 15 | 15 | 15 | 25 | 55 |  | 55 | 55 | 55 | 55 | 30 | 30 | 15 | 430357
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 17 | 17 | 17 | 55 | 55 | 17 | 17 | 17 | 17 | 55 |  | 55 | 35 | 35 | 35 |  |  |  | 446566
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 110 | 110 | 163 | 163 | 110 | 110 | 163 | 110 | 163 |  | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 3667663
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 8200
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 43 | 45 | 596880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 10 | 40 | 40 | 40 | 55 | 25 | 16 | 16 | 48 | 105 |  | 130 | 100 | 100 | 80 | 80 | 40 | 16 | 902400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 4 | 17 | 17 | 17 | 58 | 111 | 124 | 90 | 60 | 80 | 112 |  | 132 | 132 | 132 | 132 | 132 | 118 | 96 | 1468224
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 40 | 70 | 70 | 90 | 90 | 90 | 70 | 30 | 50 | 60 | 90 |  | 90 | 90 | 90 | 90 | 90 |  |  | 1605120
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | 100 | 50 | 10 |  | 1 | 23 | 80 | 103 | 137 | 137 | 135 | 137 | 138 | 142 | 138 | 128 | 127 | 127 |  | 137 | 142 | 142 | 142 | 100 | 100 | 100 | 2539200
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 35 |  |  |  |  | 16 | 32 | 64 | 115 | 115 | 115 | 115 | 115 | 100 | 70 | 84 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1941600
| Anwara 300 MW PP (United) | 300 | 300 | 245 | 190 | 190 | 190 | 200 | 260 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 300 |  | 300 | 300 | 300 | 300 | 300 | 230 | 230 | 6506072
| Juldah unit-2 (Acorn) | [8 empty] | 10 | 10 | 10 | 30 | 30 | 10 | 10 | 10 | 30 | 30 |  | 30 | 30 | 10 |  |  |  |  | 253440
| Anlima Energy Ltd. | 51 | 17 |  |  |  | 21 | 37 | 51 | 69 | 87 | 90 | 98 | 116 | 116 | 87 | 101 | 105 | 105 |  | 105 | 68 | 68 | 68 | 68 | 34 | 34 | 1649727
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445320
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 12 | 18 | 22 | 23 | 13 | 15 | 9 | 4 | 1 | [9 empty] | 124747
Chandpur 115(Doreen)
| Kanchan Purbachal Power Generation Ltd. | [26 empty] | 0
120 | Eastern Zone Total | 4431 | 4175 | 3961 | 3863 | 3890 | 4071 | 4229 | 4612 | 4841 | 4904 | 5033 | 5405 | 5577 | 5301 | 5023 | 5050 | 5094 | 5920 |  | 5998 | 5883 | 5810 | 5480 | 5303 | 4839 | 4715 | 120532206
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 11 | 48 | 70 | 70 | 87 | 105 | 35 | 17 | 17 | 40 | 103 |  | 105 | 105 | 105 | 105 | 53 | 35 |  | 1141440
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 7 | 22 | 39 | 52 | 60 | 59 | 55 | 36 | 25 | 7 | [9 empty] | 376560
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 200 | 180 | 130 | 130 | 130 | 130 | 136 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 220 |  | 220 | 220 | 220 | 214 | 220 | 223 | 221 | 4044655
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 269995
| Bhola 225 MW CCPP | 73 | 72 | 72 | 72 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 67 |  | 67 | 67 | 69 | 61 | 70 | 71 | 70 | 1411000
140 | Bhola 33 MW PP (Venture) | 19 | 16 | 16 | 16 | 16 | 17 | 15 | 14 | 14 | 12 | 14 | 15 | 16 | 15 | 14 | 14 | 15 | 20 |  | 20 | 21 | 21 | 21 | 21 | 20 | 19 | 399700
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 346 | 344 | 344 | 344 | 344 | 343 | 419 | 484 | 484 | 484 | 482 | 482 | 482 | 482 | 484 | 484 | 578 | 627 |  | 721 | 722 | 721 | 721 | 721 | 721 | 543 | 12270545
147 | Bheramara 410 MW CCPP | 360 | 360 | 360 | 320 | 320 | 320 | 350 | 395 | 360 | 365 | 300 | 300 | 355 | 380 | 360 | 400 | 360 | 355 |  | 355 | 360 | 360 | 355 | 355 | 360 | 360 | 8601408
148 | Payra 1320 MW | 300 | 300 | 290 | 290 | 280 | 280 | 300 | 300 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 260 | 330 |  | 370 | 380 | 380 | 410 | 400 | 390 | 360 | 8135000
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 82 | 82 | 82 | 81 | 82 | 82 | 82 | 81 | 83 | 78 | 83 | 81 | 86 | 85 | 76 | 75 |  | 76 | 80 | 84 | 66 |  |  |  | 1726254
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 239 | 300 | 300 | 300 | 300 | 299 | 300 | 300 | 300 | 270 |  | 270 | 222 | 181 | 170 | 170 | 169 | 169 | 5702400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 34 |  | 50 | 50 | 50 |  |  |  |  | 112224
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 2 | 3 | 3 | 3 | 2 | 1 | 0 | 0 | [9 empty] | 19980
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 147 | 145 | 142 | 147 | 150 | 145 | 145 | 162 | 183 | 156 | 157 | 146 | 154 | 164 | 163 | 165 | 207 | 174 |  | 180 | 163 | 164 | 168 | 186 | 183 | 182 | 4161055
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 396 | 367 | 371 | 358 | 329 | 355 | 347 | 425 | 378 | 394 | 355 | 382 | 366 | 324 | 417 | 423 | 316 | 395 |  | 309 | 361 | 337 | 362 | 391 | 415 | 382 | 8886364
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 6 |  | 13 | 17 | [5 empty] | 24620
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 19 | 22 |  | 22 | 22 | 22 | 21 | 21 | 22 | 22 | 508320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 223668
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 34 |  | 16 | 8 | 8 |  |  |  |  | 71786
167 | Katakhali 50 MW Peaking PP | [16 empty] | 5 | 32 |  | 32 | 33 | 12 |  |  |  |  | 80950
168 | Santahar 50 MW Peaking PP | [16 empty] | 8 | 29 |  | 29 | 29 | 29 | 29 |  |  |  | 114547
169 | Natore 52 MW PP (Rajlanka) | [8 empty] | 25 | 25 | 25 | 43 | 43 | 52 | 25 | 25 | 25 | 40 |  | 52 | 52 | 52 | 52 | 24 | 24 |  | 596640
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 5 | 101 |  | 67 | 60 | 67 | 67 | 33 | 34 |  | 363152
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [5 empty] | 8 | 35 | 60 | 90 | 94 | 94 | 0 |  |  |  |  | 20 | 70 |  | 93 | 93 | 93 | 93 | 93 | 50 | 35 | 1058304
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 35 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 50 | 113 |  | 113 | 113 | 113 | 113 | 70 | 35 |  | 1252704
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 34 | 42 | 91 | 112 | 112 | 112 | 112 | 112 | 93 | 70 | 104 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 1732636
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 26307
178 | Energypac Power Venture Thakurgaon Ltd.
178