## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-12-26 | Sunday
|  | Date (day): | 2021-12-26 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11777.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13215 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-12-25 | 2021-12-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 230 | 230 | 230 | 230 | 135 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 244 | 245 | 300 | 300 | 60 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 24 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 11 | 12 | 11 | 11 |  | 89 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 9 | 20 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 31 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 20 | 20 |  | 13 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 30 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 277 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 28 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 48 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 26 | 0 | 30 | 0
| Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 0 | 45 | 55 | 55
| Dhaka area Total |  |  |  |  | 6178 | 5560 | 1612 | 2238 | 2724 | 3047 | 1340 | 1192
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 150 | 150 | 150 | 30
41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 0 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 84 | 86 |  | 144 | Low Water Level & Unit 4 & 5 U/M.
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 70 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 100 | 100
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 40 | 76 | 90 | 90 |  | 10 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 4 | 10 | 10
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 282 | 282 | 300 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 93 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 70 | 100 | 100
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 51 | 55 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 732 | 960 | 1479 | 1476 | 30 | 857
60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 115 | 116 | 18 |  | Gas shortage
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 189 | 179 | 225 | 225 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 360 | 360 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 170 | 220 | 200 | 360 |  | 0
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 17 | 17 |  | 28 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 10 | 10 | 45 |  | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 78 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 135 | 133 | 135 | 137 |  | 13 | Engine problem
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 141 | 138 | 140 |  | 23 | Machine problem.
71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 22 | 22
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 89 | 86 | 138 | 164
74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 46 | 108 | 113 | 113
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1346 | 1459 | 2018 | 2409 | 514 | 101
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 148 | 112 | 140 | 150 | 52 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | under maint.
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 32 | 70 | 200 | 200
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 379 | 338 | 545.6 | 504 | 52 | 13
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 42 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 43 | 43 |  | 47 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 51 | 51 | 51
| Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 72 | 72 | 72
96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 74 | 80 | 80 | 80
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 75 | 75 |  | 25
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 137 | 137 | 200 | 200 |  | 31
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 18 | 24 | 24
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 330 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2422 | 2377 | 919 | 1010 | 1189 | 1190 | 0 | 1201
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 610 | 709 | 623 | 723
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 8 | 0 | 40 |  | 69 | Engine problem
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 235 | 210 | 270 | 300 | 110 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 73 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 0 | 0 | 65 | 0 | 10 | 0
| Khulna Area Total |  |  |  |  | 2248 | 2129 | 945 | 1000 | 1058 | 1618 | 110 | 93
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 20 | 20 | 22 |  | 11 | Engine problem
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 90 | 90 | 90 | 104 |  | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 290 | 380 | 620 | 620
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 181 | 215 | 200 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
| Barisal Area Total |  |  |  |  | 2046 | 2046 | 586 | 716 | 1051 | 1223 | 188 | 11
121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 50 | 50
123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 50 | 50 | 50
126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 33 | 30 | 33 |  | 17 | Engine problem
127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 155 | 200 | 200 |  |  | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 360 | 311 | 400 | 400 |  |  | FGMO
131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36 |  | 14 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 66 | 59 | 90 | 100
137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 873 | 980 | 1392 | 1435 | 600 | 97
141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 112 | 113 | 113
146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 239 | 312 | 321 | 313 | 74 | 210
| Total |  |  |  |  | 22031 | 20934 | 7631 | 9013 | 11777.6 | 13215 | 2908 | 3775
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7284.7136 | 8604 | 11243.1455 | 12615.3179
A. |  | 2021-12-25 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 9013 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5452 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9013 | MW
3 | Day peak Generation : |  |  | 7631 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8604 | MW
4 | Evening peak Generation : |  |  | 9013 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 175.7817 | MKWHr | By Solar | 1.012 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 109.6095 | MKWHr |  | By Oil: | 35.541 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 13.3523 | MKWHr |  | By Hydro: | 2.0745 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2908 | MW | Dhaka | 3143 | 3143 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3775 | MW | Chittagong | 953 | 953 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 6683 | MW | Khulna | 1045 | 1045 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 876.36 | MMCFD |  |  | Rajshahi | 876 | 876 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 112870836.586 | ii) Oil : | Taka | 244313439.48 | Comilla | 705 | 705 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 63618380 | Total | Taka | 420802656.066 | Mymensingh | 699 | 699 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.012 | MKWHr. | Sylhet | 331 | 331 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 64 | MW (E to W) at | 19:00 | hrs | Barisal | 241 | 241 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 6 | MW at | 1:00 | hrs | Rangpur | 611 | 611 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.0° C |  |  | Total | 8604 | 8604 |  | 0
B. |  | 2021-12-26 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 25.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13215 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7800 | MW
4 | Reserve(Generation end) |  |  |  | 3715 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 185.2797 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5837 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.4596 | MKWHr. | ii) HVDC Flow at Peak Time |  | 709 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7328 | MKWHr. | iii) Maximum HVDC Flow : |  | 709 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.28 |  | (b) Today: | 99.16 |  | (c) Rule Curve: |  | 103.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-12-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 45 | 19 | 40 | 0 | 0 | 80 | 285 | 170 | 204 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 59 | 170 | 0 | 17 | 0 | 42 | 42 | 53 | 0 | 130 | 0 | 73 | 81 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 75 | 0 | 0 | 0 | 190 | 54 | 0 | 0 | 26 | 0 | 400 | 0 | 0 | 108 | 0 | 0 | 17 | 0 | 0 | 0 |  | 326 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 145 | 0 | 353 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 290 | 222 | 0 | 0 | 0 | 0 | 0 |  | 4330 | 1903 | 6233 | 2848 | 326 | 1663 | 0 | 761 | 490 | 86 | 0 | 0 | 59 | 0 | 0 | 99.3
2:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 40 | 19 | 40 | 0 | 0 | 80 | 285 | 170 | 203 | 8 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 55 | 170 | 0 | 17 | 0 | 42 | 42 | 53 | 0 | 110 | 0 | 73 | 81 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 45 | 0 | 0 | 0 | 155 | 54 | 0 | 0 | 26 | 0 | 350 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 0 |  | 326 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 151 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4028 | 1812 | 5840 | 2816 | 326 | 1571 | 0 | 497 | 489 | 86 | 0 | 0 | 55 | 0 | 0 | 99.3
3:00 | 0 | 0 | 92 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 80 | 285 | 170 | 186 | 8 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 51 | 167 | 0 | 17 | 0 | 42 | 42 | 53 | 0 | 110 | 0 | 72 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 24 | 0 | 0 | 0 | 115 | 54 | 0 | 0 | 8 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 |  | 326 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 159 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 151 | 0 | 0 | 0 | 0 | 0 |  | 3775 | 1806 | 5581 | 2810 | 326 | 1550 | 0 | 268 | 490 | 86 | 0 | 0 | 51 | 0 | 0 | 99.29
4:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 80 | 285 | 170 | 186 | 8 | 139 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 49 | 169 | 0 | 17 | 0 | 42 | 42 | 53 | 0 | 110 | 0 | 73 | 40 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 115 | 54 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 |  | 326 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 0 | 0 | 0 | 0 | 0 |  | 3683 | 1769 | 5452 | 2830 | 326 | 1453 | 0 | 219 | 489 | 86 | 0 | 0 | 49 | 0 | 0 | 99.29
5:00 | 0 | 0 | 83 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 80 | 290 | 170 | 188 | 8 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 13 | 9 | 47 | 169 | 0 | 17 | 0 | 42 | 42 | 23 | 0 | 110 | 0 | 73 | 40 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 80 | 54 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 |  | 326 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 183 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 130 | 0 | 0 | 0 | 0 | 0 |  | 3597 | 1856 | 5453 | 2839 | 326 | 1472 | 0 | 184 | 499 | 86 | 0 | 0 | 47 | 0 | 0 | 99.28
6:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 80 | 285 | 170 | 185 | 8 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 24 | 9 | 49 | 170 | 0 | 17 | 0 | 42 | 42 | 23 | 0 | 130 | 0 | 73 | 40 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 15 | 0 | 8 | 0 | 0 | 0 | 135 | 54 | 0 | 0 | 26 | 0 | 350 | 4 | 0 | 22 | 17 | 0 | 17 | 0 | 0 | 0 |  | 326 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 188 | 0 | 319 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 300 | 131 | 0 | 0 | 0 | 0 | 0 |  | 3794 | 1851 | 5645 | 2870 | 326 | 1466 | 0 | 349 | 499 | 86 | 0 | 0 | 49 | 0 | 0 | 99.28
7:00 | 0 | 0 | 87 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 40 | 0 | 0 | 80 | 315 | 170 | 205 | 8 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 53 | 170 | 0 | 17 | 0 | 42 | 42 | 23 | 0 | 130 | 0 | 73 | 73 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 60 | 0 | 8 | 0 | 0 | 0 | 140 | 54 | 15 | 0 | 46 | 0 | 351 | 27 | 1 | 54 | 34 | 0 | 17 | 2 | 0 | 0 |  | 326 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 355 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 10 | 300 | 130 | 0 | 0 | 0 | 0 | 0 |  | 4068 | 1931 | 5999 | 2934 | 326 | 1533 | 0 | 564 | 499 | 86 | 0 | 0 | 53 | 4 | 0 | 99.27
8:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 30 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 15 | 0 | 0 | 80 | 280 | 180 | 230 | 8 | 142 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 65 | 168 | 0 | 17 | 0 | 42 | 42 | 53 | 0 | 130 | 0 | 72 | 74 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 60 | 0 | 65 | 0 | 16 | 0 | 0 | 1 | 190 | 54 | 17 | 0 | 46 | 0 | 400 | 53 | 8 | 70 | 34 | 0 | 17 | 7 | 0 | 0 |  | 420 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 16 | 30 | 26 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 350 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 300 | 182 | 0 | 0 | 0 | 6 | 0 |  | 4325 | 2275 | 6600 | 2995 | 420 | 1585 | 0 | 840 | 499 | 86 | 0 | 81 | 65 | 29 | 0 | 99.27
9:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 243 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 5 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 25 | 19 | 5 | 0 | 0 | 80 | 275 | 180 | 183 | 8 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 9 | 74 | 168 | 0 | 17 | 1 | 42 | 42 | 53 | 0 | 163 | 0 | 64 | 74 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 11 | 60 | 0 | 113 | 0 | 93 | 0 | 0 | 2 | 230 | 54 | 17 | 0 | 46 | 0 | 400 | 53 | 22 | 100 | 34 | 0 | 17 | 17 | 0 | 0 |  | 420 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 50 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 186 | 0 | 410 | 14 | 0 | 90 | 0 | 70 | 0 | 2 | 50 | 300 | 202 | 0 | 0 | 2 | 25 | 0 |  | 4544 | 2580 | 7124 | 2904 | 420 | 1690 | 0 | 1268 | 500 | 86 | 0 | 100 | 74 | 82 | 0 | 99.26
10:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 240 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 25 | 19 | 4 | 0 | 0 | 80 | 285 | 180 | 179 | 73 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 29 | 9 | 77 | 164 | 0 | 17 | 2 | 42 | 42 | 53 | 0 | 163 | 0 | 64 | 74 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 20 | 0 | 123 | 0 | 115 | 0 | 0 | 3 | 230 | 54 | 17 | 0 | 46 | 0 | 400 | 53 | 34 | 126 | 34 | 0 | 17 | 22 | 0 | 0 |  | 421 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 8 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 189 | 0 | 414 | 17 | 0 | 70 | 0 | 34 | 0 | 5 | 70 | 300 | 182 | 0 | 0 | 4 | 43 | 0 |  | 4661 | 2504 | 7165 | 2897 | 421 | 1735 | 0 | 1222 | 500 | 86 | 0 | 98 | 77 | 129 | 0 | 99.26
11:00 | 0 | 0 | 86 | 0 | 230 | 0 | 0 | 0 | 244 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 6 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 110 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 26 | 19 | 2 | 0 | 0 | 80 | 280 | 170 | 178 | 73 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 9 | 85 | 150 | 0 | 17 | 2 | 42 | 42 | 53 | 0 | 130 | 0 | 64 | 77 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 8 | 0 | 5 | 0 | 0 | 22 | 0 | 5 | 18 | 40 | 0 | 127 | 0 | 115 | 0 | 0 | 4 | 282 | 54 | 17 | 0 | 46 | 0 | 360 | 64 | 41 | 142 | 41 | 0 | 17 | 27 | 0 | 0 |  | 459 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 8 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 178 | 0 | 313 | 35 | 0 | 70 | 0 | 34 | 0 | 5 | 70 | 300 | 182 | 0 | 0 | 4 | 57 | 0 |  | 4804 | 2447 | 7251 | 2831 | 459 | 1606 | 0 | 1428 | 500 | 86 | 0 | 98 | 85 | 158 | 0 | 99.25
12:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 244 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 11 | 0 | 0 | 9 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 0 | 0 | 46 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 37 | 19 | 4 | 0 | 0 | 80 | 280 | 170 | 189 | 73 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 11 | 25 | 9 | 89 | 148 | 0 | 17 | 2 | 42 | 42 | 53 | 0 | 130 | 0 | 62 | 74 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 45 | 0 | 0 | 32 | 0 | 28 | 18 | 40 | 0 | 135 | 0 | 115 | 0 | 0 | 4 | 282 | 54 | 17 | 0 | 46 | 0 | 330 | 104 | 43 | 162 | 51 | 0 | 17 | 26 | 0 | 0 |  | 610 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 8 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 177 | 0 | 360 | 35 | 0 | 70 | 0 | 34 | 0 | 5 | 70 | 290 | 181 | 0 | 0 | 5 | 65 | 0 |  | 4988 | 2643 | 7631 | 2825 | 610 | 1652 | 0 | 1613 | 490 | 86 | 0 | 98 | 89 | 168 | 0 | 99.25
13:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 243 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 11 | 0 | 0 | 19 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 7 | 0 | 46 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 19 | 8 | 0 | 0 | 80 | 280 | 170 | 202 | 73 | 142 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 9 | 89 | 121 | 0 | 17 | 1 | 42 | 42 | 53 | 0 | 163 | 0 | 63 | 75 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 45 | 0 | 0 | 50 | 0 | 43 | 16 | 70 | 0 | 135 | 0 | 115 | 0 | 0 | 4 | 282 | 54 | 39 | 0 | 57 | 25 | 368 | 104 | 37 | 162 | 51 | 0 | 17 | 28 | 0 | 0 |  | 611 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 357 | 17 | 0 | 100 | 0 | 34 | 0 | 5 | 90 | 300 | 181 | 0 | 0 | 4 | 65 | 0 |  | 5205 | 2652 | 7857 | 2797 | 611 | 1687 | 0 | 1829 | 500 | 86 | 0 | 98 | 89 | 160 | 0 | 99.24
14:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 243 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 11 | 0 | 0 | 20 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 170 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 7 | 0 | 0 | 80 | 280 | 170 | 162 | 73 | 142 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 23 | 9 | 92 | 110 | 0 | 17 | 1 | 43 | 42 | 53 | 0 | 110 | 0 | 63 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 15 | 0 | 0 | 35 | 0 | 70 | 15 | 40 | 0 | 137 | 0 | 115 | 0 | 0 | 3 | 282 | 54 | 17 | 0 | 78 | 25 | 340 | 73 | 32 | 162 | 51 | 0 | 17 | 24 | 0 | 0 |  | 611 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 298 | 17 | 0 | 70 | 0 | 34 | 0 | 4 | 50 | 290 | 160 | 0 | 0 | 3 | 55 | 0 |  | 5081 | 2439 | 7520 | 2760 | 611 | 1557 | 0 | 1722 | 490 | 86 | 0 | 65 | 92 | 137 | 0 | 99.24
15:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 238 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 11 | 0 | 0 | 20 | 35 | 35 | 0 | 22 | 25 | 6 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 150 | 1 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 3 | 0 | 0 | 80 | 280 | 195 | 163 | 73 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 9 | 88 | 111 | 0 | 17 | 1 | 43 | 43 | 53 | 0 | 110 | 0 | 67 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 15 | 0 | 0 | 8 | 0 | 70 | 11 | 20 | 0 | 135 | 0 | 65 | 0 | 0 | 2 | 282 | 54 | 17 | 0 | 78 | 25 | 340 | 70 | 14 | 162 | 51 | 0 | 17 | 17 | 0 | 0 |  | 611 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 32 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 394 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 290 | 160 | 0 | 0 | 2 | 42 | 0 |  | 4886 | 2423 | 7309 | 2772 | 611 | 1643 | 0 | 1463 | 490 | 86 | 0 | 65 | 88 | 91 | 0 | 99.23
16:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 244 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 12 | 0 | 0 | 20 | 35 | 35 | 17 | 22 | 25 | 6 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 150 | 8 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 50 | 19 | 3 | 0 | 0 | 80 | 280 | 260 | 163 | 73 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 2 | 33 | 9 | 88 | 106 | 0 | 17 | 0 | 43 | 42 | 23 | 0 | 110 | 0 | 69 | 50 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 15 | 0 | 0 | 8 | 0 | 70 | 5 | 20 | 0 | 127 | 0 | 65 | 0 | 0 | 1 | 282 | 54 | 17 | 0 | 75 | 25 | 300 | 34 | 6 | 158 | 51 | 0 | 12 | 7 | 0 | 0 |  | 611 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 32 | 8 | 0 | 22 | 0 | 9 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 359 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 290 | 140 | 0 | 0 | 0 | 18 | 0 |  | 4830 | 2340 | 7170 | 2827 | 611 | 1535 | 0 | 1431 | 490 | 86 | 0 | 64 | 88 | 38 | 0 | 99.23
17:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 234 |  | 0 | 270 | 150 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 102 | 32 | 12 | 0 | 0 | 19 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 150 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 0 | 0 | 80 | 270 | 230 | 162 | 78 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 2 | 20 | 2 | 33 | 9 | 81 | 112 | 0 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 0 | 71 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 28 | 0 | 0 | 8 | 0 | 86 | 0 | 45 | 0 | 128 | 0 | 85 | 6 | 0 | 0 | 282 | 54 | 21 | 0 | 75 | 25 | 400 | 46 | 1 | 162 | 51 | 0 | 17 | 1 | 0 | 1 |  | 613 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 0 | 0 | 7 | 0 | 49 | 0 | 8 | 32 | 10 | 12 | 22 | 0 | 9 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 157 | 0 | 277 | 40 | 0 | 42 | 0 | 70 | 0 | 0 | 90 | 290 | 133 | 0 | 0 | 0 | 5 | 0 |  | 5097 | 2393 | 7490 | 2878 | 613 | 1527 | 0 | 1676 | 490 | 86 | 0 | 132 | 81 | 7 | 0 | 99.22
18:00 | 0 | 0 | 80 | 0 | 230 | 0 | 0 | 0 | 242 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 102 | 40 | 11 | 0 | 0 | 19 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 46 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 4 | 0 | 0 | 19 | 4 | 0 | 0 | 80 | 280 | 260 | 188 | 78 | 139 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 2 | 33 | 9 | 91 | 111 | 0 | 17 | 0 | 43 | 43 | 53 | 0 | 163 | 0 | 71 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 228 | 0 | 0 | 24 | 0 | 129 | 0 | 90 | 0 | 130 | 0 | 115 | 17 | 0 | 0 | 282 | 54 | 51 | 0 | 78 | 50 | 400 | 80 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 43 |  | 708 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 59 | 0 | 25 | 32 | 25 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 144 | 0 | 383 | 65 | 0 | 109 | 0 | 112 | 0 | 0 | 113 | 330 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5778 | 2949 | 8727 | 2929 | 708 | 1762 | 0 | 2384 | 530 | 86 | 0 | 237 | 91 | 0 | 0 | 99.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 245 |  | 0 | 270 | 150 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 102 | 48 | 12 | 0 | 0 | 20 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 0 | 0 | 19 | 4 | 0 | 0 | 80 | 280 | 220 | 179 | 78 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 33 | 9 | 86 | 112 | 0 | 17 | 0 | 42 | 42 | 51 | 0 | 130 | 0 | 72 | 80 | 0 | 137 | 18 | 0 | 9 | 0 | 18 | 11 | 0 | 277 | 0 | 0 | 70 | 0 | 149 | 0 | 76 | 0 | 133 | 0 | 115 | 48 | 0 | 0 | 282 | 54 | 93 | 0 | 108 | 70 | 400 | 104 | 0 | 162 | 55 | 0 | 17 | 0 | 0 | 45 |  | 709 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 59 | 0 | 50 | 33 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 311 | 73 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 380 | 215 | 0 | 0 | 0 | 0 | 0 |  | 6005 | 3008 | 9013 | 2903 | 709 | 1652 | 0 | 2737 | 580 | 86 | 0 | 260 | 86 | 0 | 0 | 99.2
19:30 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 242 |  | 0 | 270 | 150 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 48 | 12 | 0 | 0 | 0 | 45 | 3 | 35 | 22 | 25 | 6 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 0 | 0 | 19 | 10 | 0 | 0 | 80 | 280 | 220 | 182 | 78 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 33 | 9 | 90 | 111 | 0 | 17 | 0 | 43 | 42 | 51 | 0 | 130 | 0 | 71 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 18 | 11 | 0 | 277 | 0 | 0 | 55 | 0 | 149 | 0 | 76 | 0 | 135 | 0 | 115 | 17 | 0 | 0 | 283 | 54 | 110 | 0 | 116 | 30 | 400 | 104 | 0 | 162 | 55 | 0 | 17 | 0 | 0 | 55 |  | 709 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 8 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 388 | 73 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 400 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5931 | 2983 | 8914 | 2911 | 709 | 1739 | 0 | 2611 | 600 | 86 | 0 | 168 | 90 | 0 | 0 | 0
20:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 242 |  | 0 | 270 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 84 | 32 | 11 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 20 | 0 | 1 | 19 | 14 | 0 | 0 | 80 | 280 | 220 | 188 | 78 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 33 | 9 | 86 | 123 | 0 | 17 | 0 | 43 | 42 | 51 | 0 | 130 | 0 | 71 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 18 | 11 | 0 | 277 | 0 | 0 | 45 | 0 | 149 | 0 | 76 | 0 | 135 | 0 | 115 | 17 | 0 | 0 | 282 | 54 | 110 | 0 | 116 | 30 | 400 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 53 |  | 709 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 363 | 73 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 400 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5887 | 2957 | 8844 | 2933 | 709 | 1720 | 0 | 2575 | 600 | 86 | 0 | 135 | 86 | 0 | 0 | 99.21
21:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 243 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 11 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 8 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 38 | 19 | 22 | 0 | 0 | 80 | 280 | 220 | 188 | 78 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 33 | 9 | 84 | 126 | 0 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 0 | 71 | 80 | 0 | 136 | 18 | 0 | 10 | 0 | 20 | 11 | 0 | 225 | 0 | 0 | 45 | 0 | 128 | 0 | 30 | 0 | 137 | 0 | 115 | 0 | 0 | 0 | 282 | 54 | 68 | 0 | 115 | 10 | 400 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 37 |  | 709 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 157 | 0 | 397 | 73 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 400 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5622 | 2957 | 8579 | 2942 | 709 | 1765 | 0 | 2344 | 600 | 86 | 0 | 49 | 84 | 0 | 0 | 99.2
22:00 | 0 | 0 | 87 | 0 | 230 | 0 | 0 | 0 | 239 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 12 | 0 | 0 | 0 | 35 | 17 | 35 | 22 | 25 | 8 | 20 | 33 | 34 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 0 | 50 | 19 | 36 | 0 | 0 | 80 | 280 | 220 | 183 | 78 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 33 | 9 | 80 | 124 | 0 | 17 | 0 | 43 | 43 | 53 | 0 | 130 | 0 | 73 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 20 | 11 | 0 | 195 | 0 | 0 | 8 | 0 | 98 | 0 | 10 | 0 | 135 | 0 | 115 | 0 | 0 | 0 | 282 | 54 | 17 | 0 | 107 | 0 | 400 | 87 | 0 | 162 | 34 | 0 | 17 | 0 | 0 | 35 |  | 709 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 341 | 70 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 390 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5376 | 2821 | 8197 | 2932 | 709 | 1716 | 0 | 2068 | 590 | 86 | 0 | 16 | 80 | 0 | 0 | 99.2
23:00 | 0 | 0 | 89 | 0 | 230 | 0 | 0 | 0 | 243 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 11 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 8 | 20 | 33 | 16 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 37 | 0 | 0 | 80 | 280 | 220 | 179 | 78 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 9 | 78 | 124 | 0 | 17 | 0 | 43 | 42 | 51 | 0 | 130 | 0 | 73 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 20 | 11 | 0 | 145 | 0 | 0 | 8 | 0 | 55 | 0 | 10 | 0 | 137 | 0 | 95 | 0 | 0 | 0 | 282 | 54 | 17 | 0 | 75 | 0 | 400 | 50 | 0 | 126 | 34 | 0 | 17 | 0 | 0 | 55 |  | 674 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 345 | 35 | 0 | 113 | 0 | 70 | 0 | 0 | 70 | 370 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5073 | 2625 | 7698 | 2927 | 674 | 1723 | 0 | 1625 | 569 | 86 | 0 | 16 | 78 | 0 | 0 | 99.19
24:00 | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 243 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 8 | 20 | 33 | 0 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 50 | 19 | 38 | 0 | 0 | 80 | 280 | 220 | 178 | 78 | 140 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 2 | 33 | 9 | 71 | 127 | 0 | 17 | 0 | 42 | 42 | 51 | 0 | 130 | 0 | 73 | 80 | 0 | 137 | 18 | 0 | 10 | 0 | 20 | 11 | 0 | 95 | 0 | 0 | 8 | 0 | 52 | 0 | 10 | 0 | 137 | 0 | 55 | 0 | 0 | 0 | 246 | 54 | 17 | 0 | 35 | 0 | 400 | 35 | 0 | 126 | 17 | 0 | 17 | 0 | 0 | 0 |  | 486 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 345 | 35 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 350 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4745 | 2325 | 7070 | 2935 | 486 | 1703 | 0 | 1240 | 549 | 86 | 0 | 0 | 71 | 0 | 0 | 99.19
KWH | 0 | 0 | 2152000 | 0 | 5489845 | 0 | 0 | 0 | 5804000 |  | 0 | 6419350 | 3629149 | 0 | 0 | 93374 | 0 | 0 | 0 | 0 | 894816 | 215520 | 145844 | 0 | 0 | 151680 | 598680 | 390369 | 603897 | 522900 | 600000 | 142920 | 658200 | 835300 | 382080 | 0 | 1102500 | 972000 | 0 | 3100000 | 22237 | 0 | 0 | 0 | 0 |  | 395760 | 0 | 150116 | 39600 | 0 | 770400 | 446544 | 534720 | 0 | 0 | 1933474 | 7127600 | 4816000 | 4541000 | 1221090 | 3338880 | 150984 | 145920 | 0 | 1237512 | 0 | 0 | 46123 | 399816 | 154440 | 728900 | 240290 | 1732800 | 3352320 | 0 | 386460 | 10050 | 1010000 | 1002600 | 1120200 | 0 | 3372218 | 0 | 1669440 | 1733760 | 0 | 3216150 | 421000 | 0 | 252360 | 0 | 397228 | 204288 | 0 | 1914436 | 0 | 0 | 482400 | 0 | 1124210 | 115290 | 755520 | 0 | 2562618 | 0 | 1912800 | 111600 | 0 | 23641 | 5582727 | 1369447 | 669926 | 0 | 1466640 | 276480 | 9018400 | 1307520 | 241340 | 2855520 | 843055 | 0 | 438120 | 173556 | 0 | 289800 |  | 12459636 | 0 | 5423040 | 0 | 0 | 0 | 0 | 0 | 0 | 13312 | 0 | 2184504 | 387800 | 0 | 0 | 0 | 0 | 50918 | 0 | 712240 | 0 | 180087 | 347684 | 636960 | 60215 | 515280 | 0 | 230328 | 0 | 0 | 4856100 | 0 | 0 | 0 | 0 | 0 | 0 | 272495 | 0 | 4245245 | 0 | 8516690 | 627360 | 0 | 1572960 | 0 | 1137878 | 0 | 23968 | 1338048 | 8496200 | 4306855 | 0 | 0 | 28860 | 395280 | 0 |  | 116761750 | 59019943 | 175781693 | 70140096 | 12459636 | 39469399 | 0 | 33990972 | 13352300 | 2074500 | 0 | 1550005 | 1732800 | 1011985 | 0
Fuel Cost | 0 | 0 | 3141920 | 0 | 6093727.95 | 0 | 0 | 0 | 5978120 |  | 0 | 6997091.5 | 4028355.39 | 0 | 0 | 789944.04 | 0 | 0 | 0 | 0 | 8160721.92 | 2120716.8 | 1344681.68 | 0 | 0 | 1378771.2 | 4370364 | 3017552.37 | 5954424.42 | 392175 | 450000 | 0 | 0 | 0 | 3694713.6 | 0 | 297675 | 262440 | 0 | 5611000 | 206581.73 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1456125.2 | 378180 | 0 | 6101568 | 562645.44 | 1588118.4 | 0 | 0 | 2842206.78 | 5274424 | 4816000 | 4177720 | 1575206.1 | 3839712 | 170611.92 | 204288 | 0 | 2116145.52 | 0 | 0 | 440474.65 | 507766.32 | 115830 | 1275575 | 180217.5 | 12996000 | 3553459.2 | 0 | 490804.2 | 160197 | 1656400 | 1604160 | 1993956 | 0 | 3844328.52 | 0 | 3288796.8 | 3311481.6 | 0 | 5563939.5 | 921990 | 0 | 514814.4 | 0 | 297921 | 155258.88 | 0 | 14473136.16 | 0 | 0 | 2508480 | 0 | 11062226.4 | 1347740.1 | 6157488 | 0 | 18066456.9 | 0 | 17444736 | 1054620 | 0 | 0 | 42205416.12 | 11927883.37 | 5888649.54 | 0 | 12569104.8 | 1841356.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 71767503.36 | 0 | 5694192 | 0 | 0 | 0 | 0 | 0 | 0 | 139509.76 | 0 | 2468489.52 | 601090 | 0 | 0 | 0 | 0 | 501033.12 | 0 | 6303324 | 0 | 2434776.24 | 3369057.96 | 6172142.4 | 584085.5 | 989337.6 | 0 | 174358.296 | 0 | 0 | 26320062 | 0 | 0 | 0 | 0 | 0 | 0 | 408742.5 | 0 | 4966936.65 | 0 | 8431523.1 | 6549638.4 | 0 | 14927390.4 | 0 | 8829933.28 | 0 | 264846.4 | 9888174.72 | 37298318 | 0 | 0 | 0 | 0 | 0 | 0 |  | 288814592.72 | 219084465.206 | 507899057.926 | 70288237.956 | 71767503.36 | 42582598.63 | 0 | 229839587.14 | 63618380 | 560115 | 0 | 14473852.34 | 12996000 | 1772783.5 | 0
Yesterday Day Peak | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 244 |  | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 11 | 0 | 0 | 9 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 0 | 0 | 46 | 40 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 37 | 19 | 4 | 0 | 0 | 80 | 280 | 170 | 189 | 73 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 11 | 25 | 9 | 89 | 148 | 0 | 17 | 2 | 42 | 42 | 53 | 0 | 130 | 0 | 62 | 74 | 0 | 137 | 18 | 0 | 10 | 0 | 16 | 5 | 0 | 45 | 0 | 0 | 32 | 0 | 28 | 18 | 40 | 0 | 135 | 0 | 115 | 0 | 0 | 4 | 282 | 54 | 17 | 0 | 46 | 0 | 330 | 104 | 43 | 162 | 51 | 0 | 17 | 26 | 0 | 0 |  | 610 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 8 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 177 | 0 | 360 | 35 | 0 | 70 | 0 | 34 | 0 | 5 | 70 | 290 | 181 | 0 | 0 | 5 | 65 | 0 |  | 7631 | DayPeak
Yesterday Evening Peak | 0 | 0 | 90 | 0 | 230 | 0 | 0 | 0 | 245 | 0 | 0 | 270 | 150 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 102 | 48 | 12 | 0 | 0 | 20 | 35 | 35 | 35 | 22 | 25 | 6 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 20 | 0 | 0 | 19 | 4 | 0 | 0 | 80 | 280 | 220 | 179 | 78 | 141 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 33 | 9 | 86 | 112 | 0 | 17 | 0 | 42 | 42 | 51 | 0 | 130 | 0 | 72 | 80 | 0 | 137 | 18 | 0 | 9 | 0 | 18 | 11 | 0 | 277 | 0 | 0 | 70 | 0 | 149 | 0 | 76 | 0 | 133 | 0 | 115 | 48 | 0 | 0 | 282 | 54 | 93 | 0 | 108 | 70 | 400 | 104 | 0 | 162 | 55 | 0 | 17 | 0 | 0 | 45 |  | 709 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 59 | 0 | 50 | 33 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 311 | 73 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 380 | 215 | 0 | 0 | 0 | 0 | 0 |  | 9013 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 300 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 10 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 150 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 70 | 100 | 90 | 50 | 20 | 10 | 0 | 0 | 116 | 360 | 360 | 225 | 8 | 140 | 17 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 150 | 0 | 17 | 0 | 43 | 43 | 51 | 0 | 163 | 0 | 72 | 80 | 0 | 200 | 18 | 0 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 137 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 75 | 17 |  |  | 55 |  | 723 | 0 | 300 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 90 | 22 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 25 | 50 | 33 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 300 | 0 | 0 | 270 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 10 | 20 | 30 | 51 | 0 | 44 | 40 | 0 | 150 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 19 | 10 | 0 | 0 | 115 | 360 | 200 | 225 | 8 | 138 | 17 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 140 | 0 | 17 | 1.6 | 42 | 43 | 51 | 0 | 163 | 0 | 72 | 80 | 0 | 200 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 0 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 135 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 75 | 17 | 30 |  | 55 |  | 623 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 25 | 50 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6 | 10
Generation at 08:00(Today) | 0 | 0 | 80 | 0 | 230 | 0 | 0 | 0 | 238 | 0 | 0 | 270 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 28 | 22 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 10 | 0 | 42 | 19 | 8 | 0 | 0 | 116 | 320 | 65 | 184 | 108 | 139 | 17 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 2 | 33 | 9 | 67 | 115 | 0 | 17 | 0 | 42 | 42 | 51 | 0 | 163 | 0 | 40 | 78 | 0 | 137 | 18 | 0 | 10 | 0 | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 50 | 0 | 105 | 0 | 17 | 0 | 6 | 0 | 220 | 36 | 51 | 0 | 0 | 10 | 373 | 63 | 10 | 108 | 51 | 75 | 12 | 6 | 0 | 0 | 0 | 437 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 290 | 5 | 0 | 67 | 0 | 47 | 0 | 1 | 70 | 290 | 150 | 0 | 0 | 0 | 7 | 0 | 0
199
| Minimum Generation |  | 5452 | 4:00
| Highest Generation |  | 9013 | 19:00
| Day Peak Generation |  | 7631 | 12:00
| Evening Peak Generation |  | 9013 | 19:00
| HVDC Max Flow |  | 709 | 19:00
| HVDC EvPeak Flow |  | 709 | 19:00
| Load factor L.F |  | 81.26%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-12-26
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-12-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7631 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5837 | MW
Evening Peak Generation : |  | 9013 | MW Hour : | 19:00 | Available Max Generation : |  | 13215 | MW
E.P. Demand (at gen end) : |  | 9013 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9013 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3715 | MW
Total Gen. (MKWH) : |  | 175.7817 | System Load Factor : | 81.26% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 6 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-12-26
Actual : | 99.16 | Ft.(MSL) , | Rule curve : | 103.6 | Ft.( MSL )
Gas Consumed : | Total = | 876.36 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 112870836.586
: |  | Coal : | 63618380 | Oil : | 244313439.48 | Total : | 420802656.066
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3384.2321 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1146.7393 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1026.7121 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 927.4625 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 838.277 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 676.4496 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 383.4965 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.3068 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 521.6863 |  |  | 0 | 0%
Total | 0 |  | 9079.3622 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,5
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit-1
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-2,3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barisal (S)-Barisal Summit 132 kV Ckt was shut down from 08:30 to 15:42 for A/M.
b) Sreemangal-Fenchuganj 132 kV Ckt-2 was under shut down from 08:56 to 15:13 for C/M.
c) Feni 132/33 kV T1 transformer was under shut down from 08:34 to 18:04 for A/M.
d) Tangail-Kaliakoir 132 kV Ckt-2 was under shut down from 08:10 to 18:07 for A/M.
e) Lalbag-Kallyanpur 132 kV Ckt-1 tripped at 08:55 showing dist C phase relay and was switched on at 09:16.
f) Madunaghat GIS-TK Chemical 132 kV Ckt was under shut down from 09:22 to 12:46 for D/W.
g) Madunaghat old -TK Chemical 132 kV Ckt was under shut down since at 08:30 for D/W.
h) Madaripur-Gopalganj 132 kV Ckt-1,2 were under shut down from 09:23 to 20:38 for D/W.
i) Madunaghat- Noapara 33 kV PBS feeder was under shut down since 09:05 for OPGW stringing work by PBS.
j) Rajshahi-HVDC Bheramara 230 kV Ckt-1,2 were under shut down from 08:11 to 15:03 for A/M.
k) BSRM-BR power GEN 230 kV Ckt was under shut down from 12:52 to 21:03 for D/W.
l) Tongi-Bashundhara 132 kV Ckt-1 tripped at 13:29 showing no signal.
m) Sreemangal-Fenchuganj 132 kV Ckt-1 was under shut down from 15:14 to 17:35 for C/M.
n) Keraniganj 132/33 kV T-1,2 transformer tripped at 00:03 showing dist R-phase E/F relay due to 33 kV feeder fault | [5 empty] | About 32 MW power interruption occurred under
and was switched on at 00:26(26-12-21). | [5 empty] | Keraniganj S/S area from 00:03 to 00:26.
o) Madunaghat GIS-Kulshi 132 kV Ckt-1 was switched on at 16:17.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-12-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 90 | 2152000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 230 | 5489845 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 245 | 5804000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6419350 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3629149 | Gas shortage GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 24 | 93374 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 12 | 145844 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 522900
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 894816
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 20 | 151680
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 598680 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 215520 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 390369 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 603897 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 742920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 658200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 835300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 382080
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 277 | 1914436
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1124210
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 48 | 111600 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1307520
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2855520
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 173556
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 45 | 289800
| Dhaka area Total |  |  |  | 5560 | 2238 | 37506566
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3100000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 22237 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 115290
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 770400 | 33 kV bus S/D
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2074500 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | High Voltage.
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 150116 | High Voltage.
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 39600 | High Voltage.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 76 | 755520 | High Voltage.
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 446544
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 4 | 534720
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23641
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 282 | 5582727
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1369447
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 93 | 669926 | Engine problem
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 70 | 276480 | High Voltage.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 55 | 843055 | High Voltage.
| Chattogram area Total |  |  |  | 2382 | 960 | 16774203
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1933474 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4541000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7127600 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 220 | 4816000 | ST preparation
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 150984 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 145920 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 78 | 1221090 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1237512
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 2562618 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 141 | 3338880 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | High Voltage.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 399816
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 154440 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 86 | 1732800
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 728900
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 46123 | High Voltage.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 240290 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 108 | 1466640
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 438120 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3034 | 1459 | 32282207
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 112 | 3352320 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 386460 | Engine problem
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10050
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 70 | 482400 | High Voltage.
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1912800
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 241340
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 395760
| Mymensingh Area Total |  |  |  | 622 | 338 | 6781130
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1010000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1002600 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3372218
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 1120200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 204288
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 72 | 1669440
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1733760
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | On test
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 137 | 3216150 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 18 | 397228
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 252360
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9018400
| Sylhet Area Total |  |  |  | 2377 | 1010 | 23417644
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 709 | 12459636
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 8 | 13312 | High Voltage.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 210 | 5423040 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 73 | 627360 | High Voltage.
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 0 | 0 | 395280 | On test
| Khulna Area Total |  |  |  | 2129 | 1000 | 18918628
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 387800 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 2184504 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 272495 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 380 | 8496200 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 215 | 4306855
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | High Voltage.
| Barisal Area Total |  |  |  | 2046 | 716 | 15647854
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 50918
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 180087
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 347684 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 155 | 4245245 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 311 | 8516690 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 60215 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 515280
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 230328
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 636960
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 59 | 712240 | High Voltage.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1572960
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1338048
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28860
| Rajshahi Area Total |  |  |  | 2179 | 980 | 18435515
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4856100
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 1137878
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23968
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 0 | On test
| Rangpur Area Total |  |  |  | 605 | 312 | 6017946
| Total |  |  |  | 20934 | 9013 | 175781693
| Eastern Grid Total |  |  |  | 13975 | 6005 | 116761750
| Western Grid Total |  |  |  | 6959 | 3008 | 59019943
| National Grid Total |  |  |  | 20934 | 9013 | 175781693
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-12-25
(a) ENTIRE EASTERN GRID : |  | 5831 | MW | (b) ENTIRE WESTERN GRID : |  | 2773 | MW
i) Dhaka area |  | 3143 | MW | i) Khulna area |  | 1045 | MW
ii) Chittagong area |  | 953 | MW | ii) Rajshahi area |  | 876 | MW
iii) Comilla area |  | 705 | MW | iii) Barisal area |  | 241 | MW
iv) Mymensingh area |  | 699 | MW | iv) Rangpur area |  | 611 | MW
v) Sylhet area |  | 331 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8604 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 84 | 11:00 | Tangail | 122 | 18:30 | Noapara | 40 | 18:30
Munsiganj | 62 | 21:00 | Mymensing | 156 | 18:00 | Jessore | 74 | 18:30
Sonargaon | 58 | 0:00 | Kishoreganj | 94 | 20:00 | Benapol | 38 | 18:00
Shyampur | 148 | 12:00 | Netrokona | 81 | 18:00 | Jhenida(Old) | 80 | 18:00
Bhulta | 159 | 13:00 | Jamalpur | 92 | 20:00 | Bottail | 98 | 18:00
Madanganj | 39 | 20:00 | Sherpur | 98 | 18:00 | G.K Project | 37 | 18:00
Shitalakhya | 97 | 12:00 | Srimongal | 34 | 18:00 | Faridpur | 98 | 19:30
Rahim steel | 16 | 12:00 | Shahjibazar | 73 | 19:30 | Rajbari | 40 | 18:00
Matuail | 51 | 11:00 | Fenchuganj | 28 | 17:00 | Madaripur | 63 | 20:00
Ghorasal | 61 | 18:30 | Kulawara | 28 | 18:00 | Sariatpur | 42 | 20:00
Narsingdi | 124 | 18:30 | Sylhet | 91 | 18:30 | Gopalganj | 65 | 18:00
Haripur (SBU) | 94 | 10:00 | Chatak | 14 | 18:00 | Bagerhat | 76 | 19:30
Sreenagar | 25 | 19:30 | Sunamganj | 30 | 18:30 | Mongla | 24 | 13:00
Ullon | 42 | 13:00 | Biani Bazar | 39 | 18:00 | Satkhira | 73 | 18:30
Hasnabad | 65 | 11:00 | Comilla (S) | 92 | 14:00 | Gallamari | 26 | 18:00
Magbazar | 55 | 18:00 | Comilla(N) | 79 | 20:00 | Magura | 40 | 18:00
Maniknagar | 38 | 13:00 | Chandpur | 43 | 19:30 | Norail | 36 | 18:00
Bangabhaban | 4 | 11:00 | Feni | 75 | 14:00 | Chuadanga | 62 | 18:30
Motijheel | 13 | 13:00 | Chowmuhani | 124 | 19:30 | Barisal(N) | 27 | 19:30
Narinda | 36 | 14:00 | Ashuganj | 22 | 21:00 | Barisal (S) | 72 | 20:00
Kazla | 68 | 19:00 | Daudkandi | 92 | 19:00 | Patuakhali | 76 | 20:00
Dhanmondi | 116 | 13:00 | B.Baria | 94 | 19:30 | Bhandaria | 38 | 20:00
Lalbag | 67 | 13:00 | Ramganj | 52 | 20:00 | Borguna | 12 | 20:00
Madartek | 46 | 13:00 | Chaddagram | 34 | 20:00 | Borhan Uddin | 29 | 20:00
Dhaka University | 18 | 13:00 | PHP | 3 | 1:00 | Ishurdi | 47 | 18:00
Aftabnagar | 10 | 13:00 | Kochua | 38 | 19:00 | Ruppur Paromanobik | 3 | 17:00
Fatullah | 50 | 23:00 | Madunaghat | 41 | 18:30 | Natore | 89 | 18:30
Nawabganj | 31 | 20:00 | Hathazari | 65 | 18:00 | Bogra | 105 | 18:30
Keraniganj | 46 | 18:00 | Khulshi | 120 | 23:00 | Noagaon | 82 | 19:00
Banani | 35 | 18:00 | Halishahar | 56 | 23:00 | Rajshahi | 94 | 18:30
Mirpur | 78 | 18:30 | Baraulia | 128 | 18:00 | Rajshahi New | 14 | 18:30
Kalyanpur | 60 | 18:00 | Sikalbaha | 17 | 11:00 | C.Nawabganj | 42 | 18:00
Gulshan | 60 | 1:00 | Dohazari | 56 | 18:00 | Amnura | 34 | 18:30
Uttara | 38 | 18:00 | Cox'sbazar | 81 | 18:00 | Pabna | 65 | 18:30
Uttara New | 20 | 13:00 | Chandraghona | 26 | 12:00 | Shahjadpur | 69 | 18:30
Kamrangirchar | 60 | 13:00 | Kaptai | 3.3 | 19:00 | Serajganj | 57 | 18:30
Savar | 117 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 42 | 18:00
Bhasantec | 79 | 18:00 | Bakulia | 75 | 18:30 | Joypurhat | 44 | 18:00
Agargaon | 43 | 18:00 | Julda | 19 | 11:00 | Sherpur(Bogura) | 46 | 18:30
Satmosjid | 69 | 13:00 | TK chemical | 22 | 18:00 | Mohastangor | 42 | 18:00
Old Tongi | 89 | 18:30 | Modern Steel | 0 | 1:00 | Bhangura | 20 | 18:30
Kabirpur | 166 | 16:00 | Shahmirpur | 34 | 17:00 | Rangpur | 93 | 18:00
Bashundara | 124 | 18:30 | Khagrachhari | 24 | 1:00 | Lalmonirhat | 24 | 18:00
Manikgong | 55 | 21:00 | Matarbari | 25 | 18:00 | Saidpur | 77 | 18:00
Joydevpur | 101 | 18:30 | Baroiar Hat | 50 | 18:00 | Purbasadipur | 90 | 18:00
New Tongi | 60 | 18:00 | Rangamati | 10 | 18:00 | Thakurgaon | 63 | 18:30
Kodda | 204 | 18:00 | Abul Khair 230 | 127 | 2:00 | Palashbari | 79 | 18:30
Dhamrai | 70 | 18:00 | BSRM | 155 | 5:00 | Barapukuria | 43 | 19:00
Rajendrapur | 78 | 18:30 | GPH Ispat | 92 | 11:00 | Panchagar | 45 | 18:00
Purbachal | 12 | 19:00 | Agrabad | 50 | 18:00 | Joldhaka | 42 | 18:0
Tongi Millgate | 36 | 11:00 | Goalpara | 20 | 13:00 | Kurigram | 47 | 18:00
Valuka | 80 | 18:00 | Central S/S | 66 | 13:00 | Mithapukur | 27 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-12-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 417 | 17:00 | 407 | 15:00 | Kaliakoir | 415 | 0.25 | 402 | 0.58333
| Bheramara | 408 | 19:00 | 395 | 12:00 | Bhulta | 403 | 0.70833 | 388 | 0.41667
| Ashuganj(N) | 407 | 22:00 | 392 | 12:00 | Gopalganj | 420 | 0.625 | 411 | 0.77083
| Payra | 421 | 1:00 | 414 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 245 | 1:00 | 245 | 1:00 | Hathazari | 241 | 19:00 | 233 | 10:00
| Ishurdi | 246 | 4:00 | 237 | 12:00 | Megnaghat | 249 | 1:00 | 242 | 15:00
| Ashuganj | 252 | 23:00 | 246 | 10:00 | Fenchuganj | 247 | 6:00 | 242 | 10:00
| Serajganj | 243 | 1:00 | 237 | 12:00 | Siddhirganj | 245 | 1:00 | 240 | 8:00
| Baghabari | 243 | 6:00 | 235 | 13:00 | Maniknagar | 242 | 1:00 | 233 | 12:00
| Barapukuria | 238 | 17:00 | 232 | 12:00 | Agargaon | 243 | 3:00 | 234 | 12:00
| Bogra | 239 | 3:00 | 234 | 8:00 | Barisal | 247 | 18:00 | 241 | 19:30
| Rajshahi | 246 | 24:00 | 230 | 9:00 | Bhola 225 MW | 249 | 6:00 | 244 | 18:00
| Khulna South | 250 | 4:00 | 235 | 15:00 | AKSML | 243 | 18:00 | 232 | 4:00
| Rampura | 240 | 22:00 | 232 | 12:00 | BSRM | 243 | 20:00 | 233 | 5:00
| Haripur | 242 | 1:00 | 234 | 11:00 | Bibiyana | 248 | 20:00 | 241 | 10:00
| Hasnabad | 240 | 3:00 | 234 | 12:00 | Bhulta | 245 | 1:00 | 236 | 10:00
| Shyampur | 242 | 1:00 | 234 | 12:00 | Ashuganj (S) | 248 | 19:00 | 241 | 12:00
| Aminbazar | 244 | 1:00 | 235 | 2:00 | Kaliakoir | 240 | 1:00 | 224 | 14:00
| Tongi | 240 | 1:00 | 232 | 12:00 | GPH | 243 | 20:00 | 230 | 5:00
| Comilla (N) | 242 | 6:00 | 236 | 16:00 | Jhenaidah | 242 | 6:00 | 231 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 1:00 | 135 | 12:00 | Kachua | 143 | 0.125 | 139 | 0.45833
| Munsiganj | 143 | 19:00 | 136 | 10:00 | Madanhat | 143 | 0.66667 | 137 | 0.125
| Sonargaon | 140 | 5:00 | 136 | 10:00 | Hathazari | 142 | 0.79167 | 137 | 0.29167
| Shyampur | 139 | 1:00 | 134 | 12:00 | Khulshi | 139 | 0.25 | 133 | 0.20833
| Bhulta | 136 | 22:00 | 130 | 10:00 | Halishahar | 141 | 0.95833 | 135 | 0.20833
| Madanganj | 141 | 18:30 | 134 | 11:00 | Baraulia | 142 | 0.083333 | 136 | 0.29167
| Shitalakhya | 143 | 18:00 | 136 | 10:00 | Sikalbaha | 141 | 0.25 | 135 | 0.20833
| Rahim steal | 141 | 1:00 | 136 | 11:00 | Dohazari | 139 | 0.79167 | 132 | 0.5
| Matuail | 140 | 1:00 | 135 | 12:00 | Cox'sbazar | 126 | 0.625 | 120 | 0.8125
| Ghorasal | 144 | 19:30 | 143 | 1:00 | Chandraghona | 142 | 0.79167 | 137 | 0.41667
| Narsinghdi | 139 | 17:00 | 135 | 7:00 | Kaptai | 140 | 0.041667 | 138 | 0.54167
| Haripur (SBU) | 141 | 6:00 | 140 | 1:00 | A. Khaer Stl. | 140 | 0.375 | 135 | 0.5
| Sreenagar | 139 | 5:00 | 133 | 12:00 | Bakulia | 139 | 0.70833 | 135 | 0.41667
| Ullon | 138 | 1:00 | 132 | 12:00 | Julda | 140 | 0.041667 | 135 | 0.5
| Hasnabad | 143 | 0:00 | 139 | 9:00 | TK Chemical | 141 | 0.16667 | 134 | 0.41667
| Magbazar | 139 | 5:00 | 133 | 12:00 | Modern Steel | 140 | 0.20833 | 137 | 0.45833
| Maniknagar | 143 | 6:00 | 137 | 12:00 | Shahmirpur | 140 | 0.77083 | 133 | 0.41667
| Bangabhaban | 143 | 6:00 | 137 | 12:00 | Khagrachhari | 140 | 0.041667 | 137 | 0.20833
| Motijheel | 143 | 6:00 | 137 | 12:00 | Matarbari | 130 | 0.083333 | 125 | 0.875
| Narinda | 143 | 6:00 | 137 | 12:00 | Baroiar Hat | 141 | 1:00 | 136 | 10:00
| Kazla | 143 | 7:00 | 137 | 12:00 | Rangamati | 141 | 18:00 | 136 | 10:00
| Dhanmondi | 142 | 1:00 | 136 | 11:00 | Agrabad | 140 | 13:00 | 136 | 0.041667
| Lalbag | 139 | 1:00 | 133 | 10:00 | Goalpara S/S | 142 | 3:00 | 134 | 0.5
| Madartek | 138 | 6:00 | 132 | 12:00 | Khulna Central S/S | 140 | 3:00 | 134 | 0.54167
| Dhaka University | 138 | 1:00 | 132 | 12:00 | Noapara | 141 | 5:00 | 133 | 0.5
| Aftabnagar | 138 | 1:00 | 132 | 12:00 | Jessore | 140 | 0.083333 | 130 | 0.54167
| Fatullah | 141 | 1:00 | 134 | 12:00 | Benapol | 141 | 2:00 | 131 | 0.54167
| Nawabganj | 140 | 6:00 | 134 | 10:00 | Jhenida(Old) | 141 | 0.083333 | 134 | 0.5
| Keraniganj | 139 | 1:00 | 133 | 10:00 | Bottail | 141 | 0.16667 | 135 | 0.5
| Banani | 139 | 1:00 | 132 | 12:00 | G.K Project | 143 | 0.041667 | 138 | 0.5
| Mirpur | 141 | 1:00 | 136 | 9:00 | Faridpur | 141 | 0.25 | 136 | 0.5
| Kalyanpur | 141 | 22:00 | 136 | 9:00 | Rajbari | 141 | 0.16667 | 136 | 0.5
| Gulshan | 137 | 1:00 | 131 | 12:00 | Madaripur | 145 | 5:00 | 140 | 0.75
| Uttara | 140 | 1:00 | 133 | 10:00 | Shariyatpur S/S | 145 | 0.125 | 141 | 0.5
| Uttara New | 140 | 1:00 | 136 | 10:00 | Gopalganj | 145 | 17:00 | 139 | 0.5
| Kamrangirchar | 139 | 1:00 | 133 | 11:00 | Bagerhat | 141 | 4:00 | 132 | 0.5
| Savar | 141 | 1:00 | 136 | 11:00 | Mongla | 139 | 4:00 | 130 | 18:30
| Bhasantec | 139 | 2:00 | 134 | 11:00 | Satkhira | 140 | 0.041667 | 131 | 13:00
| Agargaon | 140 | 1:00 | 134 | 12:00 | Gallamari | 143 | 17:00 | 136 | 0.58333
| Satmosjid | 140 | 1:00 | 134 | 11:00 | Magura | 142 | 0.16667 | 134 | 0.54167
| Old Tongi | 142 | 18:30 | 135 | 16:00 | Narail | 140 | 1:00 | 132 | 0.5
| Kabirpur | 139 | 1:00 | 134 | 10:00 | Chuadanga | 140 | 2:00 | 128 | 0.54167
| Bashundara | 141 | 1:00 | 133 | 12:00 | Barisal(N) | 145 | 3:00 | 141 | 13:00
| Manikgong | 136 | 8:00 | 132 | 16:00 | Barisal (S) | 144 | 0.083333 | 139 | 0.8125
| Joydevpur | 143 | 1:00 | 134 | 12:00 | Patuakhali(S) | 143 | 0.125 | 136 | 0.75
| New Tongi | 141 | 2:00 | 134 | 10:00 | Bhandaria | 144 | 0.125 | 136 | 0.83333
| Kodda | 140 | 18:00 | 128 | 10:00 | Borguna | 144 | 1:00 | 139 | 18:00
| Dhamrai | 142 | 1:00 | 135 | 18:30 | Jhenaidah(New) | 140 | 5:00 | 133 | 13:00
| Rajendrapur | 139 | 18:30 | 128 | 11:00 | Ishurdi | 142 | 2:00 | 137 | 12:00
| Purbachal | 138 | 1:00 | 132 | 12:00 | Ruppur Paromanobik | 141 | 1:00 | 138 | 8:00
| Tongi Millgate | 141 | 18:00 | 134 | 10:00 | Natore | 141 | 18:00 | 136 | 12:00
| Valuka | 133 | 2:00 | 127 | 18:00 | Bogra | 142 | 17:00 | 137 | 15:00
| Tangail | 137 | 24:00 | 131 | 18:00 | Noagaon | 137 | 3:00 | 130 | 12:00
| Mymensing | 135 | 1:00 | 130 | 8:00 | Rajshahi | 140 | 17:00 | 132 | 15:00
| Kishorganj | 136 | 1:00 | 132 | 18:00 | Rajshahi New | 141 | 17:00 | 132 | 15:00
| Netrokona | 134 | 1:00 | 129 | 16:00 | C.Nawabganj | 139 | 18:30 | 130 | 13:00
| Jamalpur | 141 | 14:00 | 129 | 16:00 | Amnura | 140 | 19:00 | 129 | 13:00
| Sherpur | 138 | 11:00 | 130 | 4:00 | Pabna | 141 | 1:00 | 136 | 12:00
| Srimongal | 140 | 1:00 | 138 | 11:00 | Shahjadpur | 146 | 2:00 | 139 | 12:00
| Shahjibazar | 138 | 1:00 | 136 | 15:00 | Serajganj | 141 | 5:00 | 136 | 12:00
| Fenchuganj | 139 | 22:00 | 136 | 9:00 | Niyamatpur | 136 | 3:00 | 128 | 12:00
| Khulawara | 138 | 23:00 | 136 | 11:00 | Joypurhat | 139 | 17:00 | 131 | 12:00
| Sylhet | 136 | 24:00 | 134 | 9:00 | Sherpur(Bogura) | 141 | 17:00 | 136 | 12:00
| Chatak | 137 | 1:00 | 134 | 14:00 | Mohastangor | 141 | 17:00 | 135 | 12:00
| Sunamganj | 135 | 2:00 | 133 | 12;00 | Bangura | 143 | 1:00 | 138 | 12:00
| Biani Bazar | 136 | 1:00 | 133 | 12:00 | Rangpur | 136 | 4:00 | 131 | 8:00
| Comilla(s) | 131 | 22:00 | 126 | 8:00 | Lalmonirhat | 137 | 6:00 | 130 | 12:00
| Comilla(n) | 146 | 6:00 | 141 | 10:00 | Saidpur | 136 | 6:00 | 127 | 12:00
| Chandpur | 142 | 6:00 | 140 | 9:00 | Purbasadipur | 132 | 1:00 | 124 | 12:00
| Feni | 143 | 5:00 | 138 | 12:00 | Thakurgaon | 132 | 3:00 | 123 | 12:00
| Chowmuhani | 141 | 6:00 | 137 | 12:00 | Palashbari | 138 | 17:00 | 133 | 12:00
| Ashuganj | 142 | 1:00 | 140 | 11:00 | Barapukuria | 138 | 0.70833 | 132 | 0.5
| Daudkandi | 142 | 1:00 | 138 | 10:00 | Panchagar | 134 | 0.16667 | 125 | 0.5
| B.Baria | 138 | 5:00 | 135 | 12:00 | Joldhaka | 134 | 0.16667 | 126 | 0.5
| Ramganj | 142 | 22:00 | 138 | 9:00 | Kurigram | 134 | 0.041667 | 129 | 0.54167
| Chaddagram | 144 | 18:30 | 138 | 10:00 | Mithapukur | 138 | 17:00 | 132 | 12:00
| PHP | 141 | 2:00 | 136 | 13:00

## L-Curve
Date | 2021-12-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 180 | 4745 | 2325 | 7070 |  |  |  | QF-LDC-11
0:30 | 93 | 4537.5 | 2114 | 6651.5 | Date: | 2021-12-25
1:00 | 6 | 4330 | 1903 | 6233
1:30 | 40 | 4179 | 1857.5 | 6036.5
2:00 | 74 | 4028 | 1812 | 5840
2:30 | 111 | 3901.5 | 1809 | 5710.5 | [5 empty] | Gen. at Eve. Peak | 9013 | 9013 MW (19:00 )
3:00 | 148 | 3775 | 1806 | 5581 | [6 empty] | 19:00
3:30 | 164 | 3729 | 1787.5 | 5516.5 | [5 empty] | Gen. at Day Peak | 7631 | 7631 MW (12:00 )
4:00 | 180 | 3683 | 1769 | 5452 | [6 empty] | 12:00
4:30 | 195 | 3640 | 1812.5 | 5452.5 | [5 empty] | Highest Generation | 9013
5:00 | 210 | 3597 | 1856 | 5453 | [6 empty] | 19:00
5:30 | 171 | 3695.5 | 1853.5 | 5549
6:00 | 132 | 3794 | 1851 | 5645
6:30 | 197 | 3931 | 1891 | 5822
7:00 | 262 | 4068 | 1931 | 5999
7:30 | 240 | 4196.5 | 2103 | 6299.5
8:00 | 218 | 4325 | 2275 | 6600
8:30 | 270 | 4434.5 | 2427.5 | 6862
9:00 | 322 | 4544 | 2580 | 7124
9:30 | 356 | 4602.5 | 2542 | 7144.5
10:00 | 390 | 4661 | 2504 | 7165
10:30 | 356 | 4732.5 | 2475.5 | 7208
11:00 | 322 | 4804 | 2447 | 7251
11:30 | 382 | 4896 | 2545 | 7441
12:00 | 442 | 4988 | 2643 | 7631
12:30 | 331 | 5096.5 | 2647.5 | 7744
13:00 | 220 | 5205 | 2652 | 7857
13:30 | 263 | 5143 | 2545.5 | 7688.5
14:00 | 306 | 5081 | 2439 | 7520
14:30 | 398 | 4983.5 | 2431 | 7414.5
15:00 | 490 | 4886 | 2423 | 7309
15:30 | 463 | 4858 | 2381.5 | 7239.5
16:00 | 436 | 4830 | 2340 | 7170
16:30 | 383 | 4963.5 | 2366.5 | 7330
17:00 | 330 | 5097 | 2393 | 7490
17:30 | 239 | 5437.5 | 2671 | 8108.5
18:00 | 148 | 5778 | 2949 | 8727
18:30 | 106 | 5891.5 | 2978.5 | 8870
19:00 | 64 | 6005 | 3008 | 9013
19:30 | 82 | 5931 | 2983 | 8914
20:00 | 78 | 5887 | 2957 | 8844 |  |  |  | Executive Engineer
20:30 | 146 | 5754.5 | 2957 | 8711.5 |  |  |  | Network Operation Division
21:00 | 214 | 5622 | 2957 | 8579
21:30 | 245 | 5499 | 2889 | 8388
22:00 | 276 | 5376 | 2821 | 8197 |  |  |  |  | Page 6 of 7
22:30 | 274 | 5224.5 | 2723 | 7947.5
23:00 | 272 | 5073 | 2625 | 7698
23:30 | 226 | 4909 | 2475 | 7384
24:00 | 180 | 4745 | 2325 | 7070
9013 MW (19:00 )
7631 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-12-25 |  | Energy |  | 175781693
[13 empty] | 2021-12-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2935 | 486 | 1703 | 0 | 1240 | 549 | 86 | 0 | 0 | 71 | 0 | 0
0:30 | 2891.5 | 406 | 1683 | 0 | 1000.5 | 519.5 | 86 | 0 | 0 | 65 | 0 | 0 | Date: | 2021-12-25
1:00 | 2848 | 326 | 1663 | 0 | 761 | 490 | 86 | 0 | 0 | 59 | 0 | 0
1:30 | 2832 | 326 | 1617 | 0 | 629 | 489.5 | 86 | 0 | 0 | 57 | 0 | 0 | [8 empty] | Total Energy | 175.7817 | Total Energy Gen 175.782 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 175.782 MKWHr
2:00 | 2816 | 326 | 1571 | 0 | 497 | 489 | 86 | 0 | 0 | 55 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2813 | 326 | 1560.5 | 0 | 382.5 | 489.5 | 86 | 0 | 0 | 53 | 0 | 0 | [8 empty] | Energy Requirement | 175.7817
3:00 | 2810 | 326 | 1550 | 0 | 268 | 490 | 86 | 0 | 0 | 51 | 0 | 0
3:30 | 2820 | 326 | 1501.5 | 0 | 243.5 | 489.5 | 86 | 0 | 0 | 50 | 0 | 0 | [6 empty] | Shortage
4:00 | 2830 | 326 | 1453 | 0 | 219 | 489 | 86 | 0 | 0 | 49 | 0 | 0
4:30 | 2834.5 | 326 | 1462.5 | 0 | 201.5 | 494 | 86 | 0 | 0 | 48 | 0 | 0
5:00 | 2839 | 326 | 1472 | 0 | 184 | 499 | 86 | 0 | 0 | 47 | 0 | 0
5:30 | 2854.5 | 326 | 1469 | 0 | 266.5 | 499 | 86 | 0 | 0 | 48 | 0 | 0
6:00 | 2870 | 326 | 1466 | 0 | 349 | 499 | 86 | 0 | 0 | 49 | 0 | 0
6:30 | 2902 | 326 | 1499.5 | 0 | 456.5 | 499 | 86 | 0 | 0 | 51 | 2 | 0 |  |  |  |  | Coal
7:00 | 2934 | 326 | 1533 | 0 | 564 | 499 | 86 | 0 | 0 | 53 | 4 | 0
7:30 | 2964.5 | 373 | 1559 | 0 | 702 | 499 | 86 | 0 | 40.5 | 59 | 16.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2995 | 420 | 1585 | 0 | 840 | 499 | 86 | 0 | 81 | 65 | 29 | 0
8:30 | 2949.5 | 420 | 1637.5 | 0 | 1054 | 499.5 | 86 | 0 | 90.5 | 69.5 | 55.5 | 0
9:00 | 2904 | 420 | 1690 | 0 | 1268 | 500 | 86 | 0 | 100 | 74 | 82 | 0
9:30 | 2900.5 | 420.5 | 1712.5 | 0 | 1245 | 500 | 86 | 0 | 99 | 75.5 | 105.5 | 0
10:00 | 2897 | 421 | 1735 | 0 | 1222 | 500 | 86 | 0 | 98 | 77 | 129 | 0
10:30 | 2864 | 440 | 1670.5 | 0 | 1325 | 500 | 86 | 0 | 98 | 81 | 143.5 | 0
11:00 | 2831 | 459 | 1606 | 0 | 1428 | 500 | 86 | 0 | 98 | 85 | 158 | 0
11:30 | 2828 | 534.5 | 1629 | 0 | 1520.5 | 495 | 86 | 0 | 98 | 87 | 163 | 0
12:00 | 2825 | 610 | 1652 | 0 | 1613 | 490 | 86 | 0 | 98 | 89 | 168 | 0
12:30 | 2811 | 610.5 | 1669.5 | 0 | 1721 | 495 | 86 | 0 | 98 | 89 | 164 | 0
13:00 | 2797 | 611 | 1687 | 0 | 1829 | 500 | 86 | 0 | 98 | 89 | 160 | 0
13:30 | 2797 | 611 | 1687 | 0 | 1829 | 500 | 86 | 0 | 98 | 89 | 160 | 0
14:00 | 2797 | 611 | 1687 | 0 | 1829 | 500 | 86 | 0 | 98 | 89 | 160 | 0
14:30 | 2784.5 | 611 | 1665 | 0 | 1646 | 495 | 86 | 0 | 81.5 | 88.5 | 125.5 | 0
15:00 | 2772 | 611 | 1643 | 0 | 1463 | 490 | 86 | 0 | 65 | 88 | 91 | 0
15:30 | 2799.5 | 611 | 1589 | 0 | 1447 | 490 | 86 | 0 | 64.5 | 88 | 64.5 | 0
16:00 | 2827 | 611 | 1535 | 0 | 1431 | 490 | 86 | 0 | 64 | 88 | 38 | 0
16:30 | 2852.5 | 612 | 1531 | 0 | 1553.5 | 490 | 86 | 0 | 98 | 84.5 | 22.5 | 0
17:00 | 2878 | 613 | 1527 | 0 | 1676 | 490 | 86 | 0 | 132 | 81 | 7 | 0
17:30 | 2903.5 | 660.5 | 1644.5 | 0 | 2030 | 510 | 86 | 0 | 184.5 | 86 | 3.5 | 0
18:00 | 2929 | 708 | 1762 | 0 | 2384 | 530 | 86 | 0 | 237 | 91 | 0 | 0
18:30 | 2916 | 708.5 | 1707 | 0 | 2560.5 | 555 | 86 | 0 | 248.5 | 88.5 | 0 | 0
19:00 | 2903 | 709 | 1652 | 0 | 2737 | 580 | 86 | 0 | 260 | 86 | 0 | 0
19:30 | 2911 | 709 | 1739 | 0 | 2611 | 600 | 86 | 0 | 168 | 90 | 0 | 0
20:00 | 2933 | 709 | 1720 | 0 | 2575 | 600 | 86 | 0 | 135 | 86 | 0 | 0
20:30 | 2937.5 | 709 | 1742.5 | 0 | 2459.5 | 600 | 86 | 0 | 92 | 85 | 0 | 0
21:00 | 2942 | 709 | 1765 | 0 | 2344 | 600 | 86 | 0 | 49 | 84 | 0 | 0
21:30 | 2937 | 709 | 1740.5 | 0 | 2206 | 595 | 86 | 0 | 32.5 | 82 | 0 | 0
22:00 | 2932 | 709 | 1716 | 0 | 2068 | 590 | 86 | 0 | 16 | 80 | 0 | 0
22:30 | 2929.5 | 691.5 | 1719.5 | 0 | 1846.5 | 579.5 | 86 | 0 | 16 | 79 | 0 | 0
23:00 | 2927 | 674 | 1723 | 0 | 1625 | 569 | 86 | 0 | 16 | 78 | 0 | 0
23:30 | 2931 | 580 | 1713 | 0 | 1432.5 | 559 | 86 | 0 | 8 | 74.5 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 27.0° C
24:00 | 2935 | 486 | 1703 | 0 | 1240 | 549 | 86 | 0 | 0 | 71 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 175.782 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 175.782 MKWHr
Note on W13: Author:

## Generation
g | 2021-12-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1102500
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 120 | 120 | 170 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3100000
5 | Raozan 25 MW PP | [14 empty] | 1 | 8 | 8 | [9 empty] | 22237
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 11 | 16 | 18 | 18 | 16 | 15 | 11 | 5 | 0 | [9 empty] | 115290
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 34 |  |  |  |  | 150116
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 75 | 45 | 15 | 0 | [6 empty] | 5 | 45 | 45 | 15 | 15 | 15 | 28 | 228 |  | 277 | 277 | 277 | 225 | 195 | 145 | 95 | 1914436
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1221090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 90 | 90 | 92 | 90 | 83 | 90 | 87 | 90 | 90 | 90 | 86 | 90 | 90 | 90 | 90 | 90 | 90 | 80 |  | 90 | 90 | 90 | 90 | 87 | 89 | 90 | 2152000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5489845
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1933474
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 150984
33 | Ashuganj 225 MW CCPP | 204 | 203 | 186 | 186 | 188 | 185 | 205 | 230 | 183 | 179 | 178 | 189 | 202 | 162 | 163 | 163 | 162 | 188 |  | 179 | 182 | 188 | 188 | 183 | 179 | 178 | 4541000
34 | Ashuganj 450 MW CCPP(South) | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 | 170 | 170 | 170 | 170 | 195 | 260 | 230 | 260 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4816000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 290 | 285 | 315 | 280 | 275 | 285 | 280 | 280 | 280 | 280 | 280 | 280 | 270 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7127600
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 145920
36 | Chandpur 150 MW CCPP | 138 | 141 | 141 | 139 | 140 | 140 | 140 | 142 | 140 | 141 | 140 | 141 | 142 | 142 | 141 | 141 | 140 | 139 |  | 141 | 141 | 140 | 141 | 140 | 138 | 140 | 3338880
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6419350
41 | Haripur 360MW CCPP(HPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 243 | 240 | 244 | 244 | 243 | 243 | 238 | 244 | 234 | 242 |  | 245 | 242 | 242 | 243 | 239 | 243 | 243 | 5804000
42 | RPCL 210MW CCPP | 170 | 170 | 167 | 169 | 169 | 170 | 170 | 168 | 168 | 164 | 150 | 148 | 121 | 110 | 111 | 106 | 112 | 111 |  | 112 | 111 | 123 | 126 | 124 | 124 | 127 | 3352320
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 22 | 34 | 41 | 43 | 37 | 32 | 14 | 6 | 1 | [9 empty] | 241340
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 |  | 42 | 43 | 43 | 43 | 43 | 43 | 42 | 1010000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 42 | 43 |  | 42 | 42 | 42 | 42 | 43 | 42 | 42 | 1002600
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 73 | 73 | 72 | 73 | 73 | 73 | 73 | 72 | 64 | 64 | 64 | 62 | 63 | 63 | 67 | 69 | 71 | 71 |  | 72 | 71 | 71 | 71 | 73 | 73 | 73 | 1669440
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 80 | 40 | 40 | 40 | 73 | 74 | 74 | 74 | 77 | 74 | 75 | 80 | 80 | 50 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1733760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 |  | 137 | 137 | 137 | 136 | 137 | 137 | 137 | 3216150
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 252360
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 204288
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 23 | 23 | 23 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 23 | 53 | 53 |  | 51 | 51 | 51 | 53 | 53 | 51 | 51 | 1120200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 397228
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 350 | 350 | 350 | 350 | 350 | 351 | 400 | 400 | 400 | 360 | 330 | 368 | 340 | 340 | 300 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9018400
58 | Nababganj 55 MW PP (Southern power ) |  |  |  |  | 0 | 15 | 17 | 30 | 35 | 35 | 35 | 35 | 35 | 35 |  | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 603897
59 | Tangail Palli Power Gen 22 MW | [8 empty] | 20 | 25 | 24 | 22 | 23 | 24 | 24 | 23 | 22 | 24 |  | 24 | 24 | 24 | 24 | 25 | 24 | 24 | 395760
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 446544
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 522900
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 386460
63 | Impoprt (Tripura) | 59 | 55 | 51 | 49 | 47 | 49 | 53 | 65 | 74 | 77 | 85 | 89 | 89 | 92 | 88 | 88 | 81 | 91 |  | 86 | 90 | 86 | 84 | 80 | 78 | 71 | 1732800
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 5 | 4 | 2 | 4 | 8 | 7 | 3 | 3 | 6 | 4 |  | 4 | 10 | 14 | 22 | 36 | 37 | 38 | 534720
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 18 | 20 |  |  |  | 19 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 399816
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 11 |  |  |  | 2 | 2 | 2 |  | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 154440
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 13 | 24 | 33 | 33 | 33 | 29 | 25 | 25 | 25 | 23 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 728900
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 240290
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 142920
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 658200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 835300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 26 | 26 | 8 | 0 | 0 | 26 | 46 | 46 | 46 | 46 | 46 | 46 | 57 | 78 | 78 | 75 | 75 | 78 |  | 108 | 116 | 116 | 115 | 107 | 75 | 35 | 1466640
| Manikgonj 162MW PP(MPGL) | 108 | 35 | 0 | 0 | 0 | 22 | 54 | 70 | 100 | 126 | 142 | 162 | 162 | 162 | 162 | 158 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 126 | 126 | 2855520
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [12 empty] | 7 | 25 | 25 | 25 | 25 | 46 |  | 51 | 51 | 51 | 51 | 34 | 16 |  | 382080
79 | Kodda 150MW PP | [16 empty] | 32 | 40 |  | 48 | 48 | 32 | 16 | 16 | 16 |  | 215520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 2 | 8 |  | 8 | 8 | 8 | 8 | 8 |  |  | 46123
| Gazipur 100 MW PP | [16 empty] | 6 | 17 |  | 48 | 17 | 17 |  |  |  |  | 111600
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 23641
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1369447
| Karnaphuli Power Ltd. | [6 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 39 | 17 | 17 | 17 | 21 | 51 |  | 93 | 110 | 110 | 68 | 17 | 17 | 17 | 669926
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 3 | 11 | 11 | 11 | 11 | 12 | 12 | 11 |  | 12 | 12 | 11 | 11 | 12 | 11 |  | 145844
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3629149
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) |  |  |  |  | 0 | 4 | 27 | 53 | 53 | 53 | 64 | 104 | 104 | 73 | 70 | 34 | 46 | 80 |  | 104 | 104 | 104 | 104 | 87 | 50 | 35 | 1307520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 4 |  | 20 | 20 | 20 |  |  |  |  | 39600
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1237512
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 24 | 32 | 72 | 93 | 64 | 64 | 102 | 102 |  | 102 | 102 | 84 | 64 | 64 | 24 |  | 894816
95 | Patenga 50MW PP (Baraka) | 45 | 40 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 37 | 50 | 50 | 50 | 50 | [5 empty] | 1 | 38 | 50 | 50 | 50 | 770400
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [15 empty] | 0
97 | katpotti 52 MW | [11 empty] | 9 | 19 | 20 | 20 | 20 | 19 | 19 |  | 20 | [6 empty] | 151680
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 1 | 15 |  | 24 | 30 | 15 |  |  |  |  | 93374
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 3 | 35 | 35 | 17 |  |  | 390369
101 | Kushiara 163 MW CCPP (KP) | 130 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 163 | 110 | 110 | 110 | 130 | 163 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3372218
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 10050
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 0 |  |  |  |  | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 45 | 35 | 35 | 35 | 17 | 17 | 598680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 10 | 16 | 22 | 32 | 50 | 35 | 8 | 8 | 8 | 24 |  | 70 | 55 | 45 | 45 | 8 | 8 | 8 | 482400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 5 | 28 | 43 | 70 | 70 | 70 | 86 | 129 |  | 149 | 149 | 149 | 128 | 98 | 55 | 52 | 1124210
115 | Juldah 100 MW PP Unit-3 (Acorn) |  |  |  |  | 0 | 10 | 10 | 60 | 60 | 20 | 40 | 40 | 70 | 40 | 20 | 20 | 45 | 90 |  | 76 | 76 | 76 | 30 | 10 | 10 | 10 | 755520
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | 120 | 80 | 10 | 0 | 0 | 15 | 60 | 65 | 113 | 123 | 127 | 135 | 135 | 137 | 135 | 127 | 128 | 130 |  | 133 | 135 | 135 | 137 | 135 | 137 | 137 | 2562618
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 75 | 45 | 24 | 8 | 8 | 8 | 8 | 16 | 93 | 115 | 115 | 115 | 115 | 115 | 65 | 65 | 85 | 115 |  | 115 | 115 | 115 | 115 | 115 | 95 | 55 | 1912800
| Anwara 300 MW PP (United) | 190 | 155 | 115 | 115 | 80 | 135 | 140 | 190 | 230 | 230 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 |  | 282 | 283 | 282 | 282 | 282 | 282 | 246 | 5582727
| Juldah unit-2 (Acorn) | [12 empty] | 25 | 25 | 25 | 25 | 25 | 50 |  | 70 | 30 | 30 | 10 |  |  |  | 276480
| Anlima Energy Ltd. |  |  |  |  | 0 | 17 | 34 | 34 | 34 | 34 | 41 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 55 | 55 | 51 | 51 | 34 | 34 | 17 | 843055
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 12 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438120
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 7 | 17 | 22 | 27 | 26 | 28 | 24 | 17 | 7 | 1 | [9 empty] | 173556
Chandpur 115(Doreen)
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 1 | 43 |  | 45 | 55 | 53 | 37 | 35 | 55 |  | 289800
120 | Eastern Zone Total | 4330 | 4028 | 3775 | 3683 | 3597 | 3794 | 4068 | 4325 | 4544 | 4661 | 4804 | 4988 | 5205 | 5081 | 4886 | 4830 | 5097 | 5778 |  | 6005 | 5931 | 5887 | 5622 | 5376 | 5073 | 4745 | 116761750
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 14 | 17 | 35 | 35 | 17 | 17 | 17 | 17 | 40 | 65 |  | 73 | 73 | 73 | 73 | 70 | 35 | 35 | 627360
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 6 | 25 | 43 | 57 | 65 | 65 | 55 | 42 | 18 | 5 | [9 empty] | 395280
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 180 | 151 | 130 | 130 | 131 | 130 | 182 | 202 | 182 | 182 | 181 | 181 | 160 | 160 | 140 | 133 | 220 |  | 215 | 221 | 221 | 221 | 220 | 220 | 200 | 4306855
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 272495
| Bhola 225 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 88 | 89 | 89 | 90 |  | 90 | 91 | 91 | 91 | 90 | 90 | 90 | 2184504
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 15 | 15 | 16 | 15 | 14 | 13 | 13 | 13 | 14 | 15 | 14 | 13 | 14 | 17 | 20 |  | 20 | 20 | 22 | 22 | 22 | 21 | 20 | 387800
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 8 | 10 | 10 |  |  |  |  | 13312
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 326 | 326 | 326 | 326 | 326 | 326 | 326 | 420 | 420 | 421 | 459 | 610 | 611 | 611 | 611 | 611 | 613 | 708 |  | 709 | 709 | 709 | 709 | 709 | 674 | 486 | 12459636
147 | Bheramara 410 MW CCPP | 185 | 195 | 200 | 215 | 225 | 240 | 250 | 260 | 260 | 250 | 235 | 235 | 220 | 220 | 220 | 220 | 210 | 215 |  | 210 | 215 | 220 | 220 | 215 | 215 | 225 | 5423040
148 | Payra 1320 MW | 290 | 290 | 290 | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 290 | 300 | 290 | 290 | 290 | 290 | 330 |  | 380 | 400 | 400 | 400 | 390 | 370 | 350 | 8496200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 199 | 200 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 4856100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 7 | 25 |  | 25 | [6 empty] | 50918
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 4 | 4 | 5 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 28860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 145 | 151 | 159 | 165 | 183 | 188 | 185 | 185 | 186 | 189 | 178 | 177 | 169 | 163 | 163 | 163 | 157 | 144 |  | 155 | 155 | 155 | 157 | 160 | 160 | 160 | 4245245
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 353 | 324 | 334 | 298 | 347 | 319 | 355 | 350 | 410 | 414 | 313 | 360 | 357 | 298 | 394 | 359 | 277 | 383 |  | 311 | 388 | 363 | 397 | 341 | 345 | 345 | 8516690
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 20 | 21 | 21 | 515280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 230328
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 16 | 50 | 8 | 8 | 8 |  |  |  |  | 8 | 25 |  | 50 | 8 | [5 empty] | 180087
167 | Katakhali 50 MW Peaking PP | [7 empty] | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 33 | [6 empty] | 347684
168 | Santahar 50 MW Peaking PP | [16 empty] | 12 | 30 |  | 36 | [6 empty] | 60215
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 26 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 10 | 25 |  | 52 | 52 | 52 | 52 | 24 |  |  | 636960
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 51 | 68 | 66 | 66 | 66 | 66 | 33 | 33 | 32 | 49 | 59 |  | 59 | 59 | 59 | 33 |  |  |  | 712240
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 |  |  |  |  | 0 | 1 | 30 | 35 | 90 | 70 | 70 | 70 | 100 | 70 | 35 | 35 | 42 | 109 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 1572960
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 10 | 35 | 50 | 70 | 70 | 70 | 90 | 50 | 35 | 35 | 90 | 113 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 1338048
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 | [5 empty] | 34 | 70 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 70 | 112 |  | 112 | 112 | 112 | 112 | 112 | 70 | 70 | 1137878
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 5 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 23968
178 | Energypac Power Venture Thakurgaon Ltd.
178