## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-12-30 | Thursday
|  | Date (day): | 2021-12-30 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10917.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12076 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-12-29 | 2021-12-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 109 | 101 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 230 | 230 | 230 | 230 | 135 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 193 | 175 | 250 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 270 | 270 | 180 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 28 | 30 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 11 | 11 | 11 | 11 |  | 89 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 11 | 51 | 0 | 20 |  |  | On test
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 150 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 25 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 18 | 25 | 16 | 16 |  | 17 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 26 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 42 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 273 | 280 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 110 | 209 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 30 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 26 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 96 | 131 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 12 | 0 | 30 | 0
| Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 45 | 55 | 55 | 55
| Dhaka area Total |  |  |  |  | 6178 | 5560 | 2139 | 2446 | 2804 | 2844 | 1540 | 1196
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 100 | 100 |  | 80 | Machine problem.
41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 47 | 50 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 84 | 86 |  | 144 | Low Water Level & Unit 4 & 5 U/M.
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 70 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 30 | 100 | 100 | 100
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 77 | 77 |  | 23 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 7 | 5 | 5
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 75 | 88 | 90 | 90 |  | 18 | Engine problem
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 80 | 225 | 300 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 54 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 93 | 110 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 51 | 51 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 826 | 1118 | 1411 | 1407 | 0 | 950
60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 90 | 90 | 44 |  | Gas shortage
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 218 | 200 | 220 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 140 | 140 | 140 | 140 |  |  | FGMO,ST S/D due to gas shortage.
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 350 | 350 |  | 10 | FGMO
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 30 | 30 |  | 15 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 10 | 10 | 45 |  | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 86 | 113 | 135 | 137 |  | 13 | Engine problem
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 42 | 42 | 50 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 139 | 131 | 141 | 141 |  | 22 | Machine problem.
71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 19 | 22 | 22
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 90 | 138 | 164
74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 0 | 200
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 62 | 117 | 113 | 113
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1293 | 1428 | 1914 | 2162 | 540 | 97
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 51 | 51 | 120 | 120 | 82 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 17 | 17 |  | 5 | Engine problem
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 195 | 185 | 200 | 200
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 40 | 115 | 115 | 115
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 12 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 340 | 395 | 525.6 | 474 | 82 | 13
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 42 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 43 | 43 |  | 47 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
| Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 69 | 72 | 72
96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 80 | 80
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Machine problem
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 24 | 24 | 24
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 401 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2422 | 2377 | 850 | 903 | 914 | 915 | 0 | 1476
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 436 | 423 | 420 | 708
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 10 | 95 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 0 | 0 | 56 | 0 | 10 | 0
| Khulna Area Total |  |  |  |  | 2248 | 2129 | 607 | 623 | 585 | 1303 | 410 | 93
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 23 | 20 | 22 |  | 11 | Engine problem
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 90 | 90 | 104 |  | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 540 | 620 | 620
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 190 | 220 | 200 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
| Barisal Area Total |  |  |  |  | 2046 | 2046 | 602 | 859 | 1051 | 1223 | 188 | 11
121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 30 | 30 |  | 41 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 50 | 50
126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 32 | 30 | 33 |  | 17 | Engine problem
127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 178 | 185 | 200 | 200 |  |  | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 418 | 415 | 400 | 400 |  |  | FGMO
131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 29 | 29 | 0 | 36 |  | 14 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 90 | 100
137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 50 | 100 | 200 | 200
138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 110 | 113 | 113
139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1077 | 1290 | 1392 | 1435 | 600 | 97
141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 | 74 |  | Coal shortage
143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 0 |  | 20
144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 0 |  | 20
145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 111 | 113 | 113
146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
| Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 312 | 336 | 321 | 313 | 74 | 210
| Total |  |  |  |  | 22031 | 20934 | 8046 | 9398 | 10917.6 | 12076 | 3434 | 4143
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7746.3511 | 9048 | 10511.0071 | 11626.266
A. |  | 2021-12-29 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9398 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5943 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9398 | MW
3 | Day peak Generation : |  |  | 8046 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9048 | MW
4 | Evening peak Generation : |  |  | 9398 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 185.8814 | MKWHr | By Solar | 0.68024 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 90.891 | MKWHr |  | By Oil: | 65.6798 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.7209 | MKWHr |  | By Hydro: | 2.0397 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3434 | MW | Dhaka | 3294 | 3294 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4143 | MW | Chittagong | 1116 | 1116 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 7577 | MW | Khulna | 1083 | 1083 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 700.57 | MMCFD |  |  | Rajshahi | 883 | 883 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 88888200.996 | ii) Oil : | Taka | 506188874.94 | Comilla | 753 | 753 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 69622620 | Total | Taka | 664699695.936 | Mymensingh | 716 | 716 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.001 | MKWHr. | Sylhet | 333 | 333 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 58 | MW (E to W) at | 19:00 | hrs | Barisal | 256 | 256 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 12 | MW at | 8:00 | hrs | Rangpur | 614 | 614 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 25.1° C |  |  | Total | 9048 | 9048 |  | 0
B. |  | 2021-12-30 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 25.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12076 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8100 | MW
4 | Reserve(Generation end) |  |  |  | 2576 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 187.8988 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5947 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.1149 | MKWHr. | ii) HVDC Flow at Peak Time |  | 423 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7549 | MKWHr. | iii) Maximum HVDC Flow : |  | 437 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.75 |  | (b) Today: | 98.63 |  | (c) Rule Curve: |  | 103.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-12-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 99 | 0 | 230 | 0 | 0 | 0 | 191 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 81 | 50 | 19 | 30 | 0 | 0 | 80 | 140 | 265 | 180 | 8 | 136 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 64 | 53 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 163 | 0 | 71 | 81 | 0 | 88 | 18 | 0 | 9 | 0 | 20 | 11 | 0 | 245 | 0 | 0 | 180 | 0 | 0 | 0 | 90 | 0 | 137 | 0 | 16 | 70 | 34 | 0 | 0 | 36 | 110 | 0 | 45 | 60 | 410 | 72 | 0 | 0 | 51 | 0 | 17 | 0 | 0 | 55 |  | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 137 | 0 | 349 | 17 | 0 | 35 | 0 | 112 | 0 | 0 | 70 | 320 | 221 | 0 | 0 | 0 | 0 | 0 |  | 4645 | 2086 | 6731 | 2351 | 390 | 1460 | 0 | 1832 | 520 | 80 | 0 | 34 | 64 | 0 | 0 | 98.77
2:00 | 0 | 0 | 93 | 0 | 230 | 0 | 0 | 0 | 204 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 81 | 50 | 19 | 35 | 0 | 0 | 80 | 140 | 310 | 185 | 8 | 138 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 64 | 52 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 130 | 0 | 71 | 81 | 0 | 79 | 18 | 0 | 9 | 0 | 20 | 11 | 0 | 195 | 0 | 0 | 135 | 0 | 0 | 0 | 90 | 0 | 132 | 0 | 0 | 17 | 0 | 0 | 0 | 36 | 110 | 0 | 45 | 60 | 410 | 44 | 0 | 0 | 51 | 0 | 17 | 0 | 0 | 55 |  | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 152 | 0 | 410 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 70 | 290 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4378 | 2043 | 6421 | 2402 | 389 | 1504 | 0 | 1492 | 490 | 80 | 0 | 0 | 64 | 0 | 0 | 98.77
3:00 | 0 | 0 | 101 | 0 | 230 | 0 | 0 | 0 | 213 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 81 | 50 | 19 | 32 | 0 | 0 | 80 | 140 | 265 | 180 | 8 | 138 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 62 | 53 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 130 | 0 | 72 | 81 | 0 | 79 | 18 | 0 | 9 | 0 | 20 | 11 | 0 | 95 | 0 | 0 | 115 | 0 | 0 | 0 | 90 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 68 | 0 | 45 | 60 | 410 | 35 | 0 | 0 | 51 | 0 | 17 | 0 | 0 | 55 |  | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 410 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 35 | 280 | 221 | 0 | 0 | 0 | 0 | 0 |  | 4137 | 2009 | 6146 | 2373 | 388 | 1511 | 0 | 1252 | 480 | 80 | 0 | 0 | 62 | 0 | 0 | 98.76
4:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 211 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 81 | 50 | 19 | 25 | 0 | 0 | 80 | 140 | 270 | 181 | 8 | 138 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 61 | 53 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 130 | 0 | 72 | 81 | 0 | 79 | 18 | 0 | 9 | 0 | 20 | 8 | 0 | 45 | 0 | 0 | 115 | 0 | 0 | 0 | 90 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 34 | 0 | 17 | 60 | 410 | 34 | 0 | 0 | 51 | 0 | 17 | 0 | 0 | 0 |  | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 411 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 35 | 270 | 220 | 0 | 0 | 0 | 0 | 0 |  | 3935 | 2008 | 5943 | 2385 | 388 | 1501 | 0 | 1058 | 470 | 80 | 0 | 0 | 61 | 0 | 0 | 98.76
5:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 222 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 8 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 81 | 50 | 19 | 25 | 0 | 0 | 80 | 140 | 270 | 190 | 8 | 138 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 58 | 53 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 130 | 0 | 73 | 81 | 0 | 79 | 18 | 0 | 9 | 0 | 20 | 8 | 0 | 45 | 0 | 0 | 115 | 0 | 0 | 0 | 90 | 0 | 125 | 0 | 0 | 18 | 9 | 0 | 15 | 36 | 34 | 0 | 17 | 60 | 411 | 17 | 0 | 20 | 51 | 0 | 17 | 0 | 0 | 0 |  | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 179 | 0 | 373 | 14 | 0 | 0 | 0 | 112 | 0 | 0 | 35 | 270 | 217 | 0 | 0 | 0 | 0 | 0 |  | 3995 | 1988 | 5983 | 2401 | 389 | 1471 | 0 | 1114 | 470 | 80 | 0 | 0 | 58 | 0 | 0 | 98.75
6:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 223 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 81 | 50 | 19 | 30 | 0 | 0 | 80 | 140 | 275 | 178 | 8 | 138 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 58 | 53 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 130 | 0 | 73 | 81 | 0 | 79 | 18 | 0 | 9 | 0 | 20 | 8 | 0 | 45 | 0 | 0 | 120 | 0 | 0 | 0 | 90 | 0 | 122 | 0 | 0 | 39 | 17 | 0 | 15 | 36 | 35 | 0 | 17 | 80 | 412 | 17 | 0 | 38 | 51 | 0 | 17 | 0 | 0 | 0 |  | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 414 | 35 | 0 | 1 | 0 | 112 | 0 | 0 | 60 | 270 | 221 | 0 | 0 | 0 | 0 | 0 |  | 4066 | 2094 | 6160 | 2402 | 388 | 1523 | 0 | 1239 | 470 | 80 | 0 | 0 | 58 | 0 | 0 | 98.75
7:00 | 0 | 0 | 113 | 0 | 230 | 0 | 0 | 0 | 219 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 81 | 50 | 19 | 28 | 0 | 0 | 80 | 140 | 300 | 161 | 8 | 138 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 54 | 53 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 130 | 0 | 72 | 75 | 0 | 79 | 18 | 0 | 9 | 0 | 20 | 8 | 0 | 128 | 0 | 0 | 163 | 0 | 10 | 1 | 90 | 0 | 120 | 0 | 0 | 88 | 17 | 0 | 45 | 36 | 95 | 0 | 77 | 100 | 350 | 17 | 2 | 69 | 51 | 0 | 17 | 0 | 0 | 0 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 184 | 0 | 295 | 70 | 0 | 18 | 0 | 112 | 0 | 0 | 113 | 270 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4444 | 2122 | 6566 | 2334 | 436 | 1370 | 0 | 1809 | 470 | 80 | 0 | 10 | 54 | 3 | 0 | 98.74
8:00 | 0 | 0 | 110 | 0 | 230 | 0 | 0 | 0 | 219 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 48 | 6 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 18 | 33 | 25 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 75 | 50 | 19 | 4 | 0 | 0 | 80 | 140 | 320 | 193 | 8 | 139 | 29 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 43 | 53 | 0 | 17 | 0 | 42 | 30 | 51 | 0 | 163 | 0 | 70 | 75 | 0 | 40 | 18 | 0 | 9 | 0 | 20 | 8 | 0 | 165 | 0 | 0 | 184 | 0 | 32 | 7 | 90 | 0 | 117 | 0 | 20 | 105 | 33 | 1 | 45 | 36 | 107 | 0 | 75 | 80 | 350 | 17 | 6 | 94 | 51 | 0 | 17 | 6 | 0 | 7 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 414 | 70 | 0 | 31 | 0 | 112 | 0 | 1 | 113 | 290 | 220 | 0 | 0 | 0 | 10 | 0 |  | 4715 | 2297 | 7012 | 2337 | 436 | 1516 | 0 | 2031 | 490 | 80 | 0 | 48 | 43 | 31 | 0 | 98.74
9:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 222 |  | 0 | 250 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 64 | 115 | 11 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 0 | 18 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 10 | 76 | 50 | 19 | 2 | 0 | 0 | 80 | 140 | 280 | 165 | 8 | 139 | 26 | 5 | 0 | 51 | 0 | 0 | 13 | 21 | 11 | 33 | 9 | 45 | 52 | 0 | 17 | 0 | 42 | 30 | 48 | 0 | 130 | 0 | 72 | 75 | 0 | 0 | 18 | 0 | 9 | 0 | 20 | 8 | 0 | 213 | 70 | 0 | 194 | 0 | 63 | 12 | 90 | 0 | 123 | 0 | 24 | 105 | 85 | 2 | 80 | 36 | 85 | 0 | 35 | 100 | 400 | 33 | 8 | 150 | 51 | 0 | 17 | 5 | 0 | 28 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 23 | 177 | 0 | 353 | 94 | 20 | 52 | 0 | 112 | 0 | 1 | 113 | 310 | 220 | 0 | 0 | 1 | 22 | 0 |  | 5051 | 2353 | 7404 | 2245 | 436 | 1422 | 113 | 2382 | 509 | 86 | 0 | 115 | 45 | 51 | 0 | 98.73
10:00 | 0 | 0 | 97 | 0 | 230 | 0 | 0 | 0 | 224 |  | 0 | 250 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 84 | 115 | 12 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 0 | 18 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 10 | 82 | 50 | 19 | 3 | 0 | 0 | 80 | 140 | 275 | 170 | 8 | 139 | 23 | 10 | 0 | 51 | 0 | 0 | 42 | 21 | 11 | 25 | 9 | 51 | 52 | 0 | 17 | 1 | 43 | 30 | 48 | 0 | 163 | 0 | 64 | 75 | 0 | 0 | 18 | 0 | 9 | 0 | 22 | 8 | 0 | 275 | 130 | 0 | 196 | 0 | 72 | 16 | 90 | 0 | 115 | 0 | 24 | 105 | 105 | 3 | 80 | 36 | 85 | 0 | 35 | 70 | 390 | 53 | 19 | 162 | 51 | 0 | 17 | 12 | 0 | 27 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 50 | 5 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 27 | 178 | 0 | 414 | 105 | 20 | 86 | 0 | 112 | 0 | 1 | 113 | 300 | 220 | 0 | 0 | 1 | 36 | 5 |  | 5311 | 2499 | 7810 | 2224 | 436 | 1524 | 177 | 2590 | 499 | 86 | 0 | 134 | 51 | 89 | 0 | 98.73
11:00 | 0 | 0 | 98 | 0 | 230 | 0 | 0 | 0 | 201 |  | 0 | 250 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 102 | 132 | 11 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 0 | 18 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 82 | 47 | 19 | 3 | 0 | 0 | 80 | 140 | 270 | 175 | 8 | 137 | 10 | 5 | 0 | 51 | 0 | 0 | 46 | 21 | 11 | 25 | 9 | 70 | 53 | 0 | 17 | 1 | 43 | 30 | 45 | 0 | 163 | 0 | 64 | 75 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 281 | 110 | 0 | 195 | 0 | 94 | 18 | 76 | 0 | 46 | 0 | 30 | 105 | 105 | 4 | 80 | 36 | 85 | 0 | 41 | 70 | 370 | 53 | 30 | 162 | 51 | 0 | 17 | 6 | 0 | 16 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 43 | 16 | 52 | 6 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 20 | 177 | 0 | 417 | 105 | 39 | 94 | 0 | 112 | 0 | 1 | 113 | 320 | 215 | 0 | 0 | 0 | 44 | 9 |  | 5234 | 2586 | 7820 | 2163 | 436 | 1492 | 169 | 2577 | 519 | 86 | 0 | 204 | 70 | 104 | 0 | 98.73
12:00 | 0 | 0 | 109 | 0 | 230 | 0 | 0 | 0 | 193 |  | 0 | 250 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 102 | 132 | 11 | 0 | 0 | 11 | 35 | 55 | 17 | 0 | 25 | 0 | 18 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 75 | 47 | 16 | 5 | 0 | 0 | 80 | 140 | 270 | 181 | 8 | 139 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 21 | 11 | 25 | 9 | 84 | 51 | 0 | 17 | 1 | 43 | 30 | 48 | 0 | 130 | 0 | 64 | 78 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 273 | 110 | 0 | 195 | 0 | 96 | 18 | 90 | 0 | 86 | 0 | 40 | 105 | 105 | 4 | 80 | 36 | 93 | 0 | 62 | 90 | 400 | 53 | 12 | 162 | 51 | 0 | 17 | 12 | 0 | 45 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 43 | 16 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 178 | 0 | 418 | 105 | 50 | 94 | 0 | 112 | 0 | 1 | 113 | 320 | 190 | 0 | 0 | 1 | 56 | 0 |  | 5448 | 2598 | 8046 | 2215 | 436 | 1435 | 170 | 2727 | 519 | 86 | 0 | 269 | 84 | 105 | 0 | 98.72
13:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 194 |  | 0 | 250 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 132 | 12 | 0 | 0 | 20 | 35 | 55 | 17 | 0 | 25 | 0 | 18 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 75 | 50 | 16 | 9 | 0 | 0 | 80 | 140 | 270 | 165 | 8 | 139 | 10 | 5 | 0 | 51 | 0 | 45 | 52 | 21 | 11 | 25 | 9 | 83 | 51 | 0 | 17 | 1 | 43 | 30 | 45 | 0 | 163 | 0 | 63 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 275 | 100 | 0 | 188 | 0 | 110 | 17 | 90 | 0 | 95 | 0 | 40 | 105 | 105 | 4 | 80 | 36 | 110 | 0 | 84 | 90 | 400 | 70 | 16 | 162 | 51 | 0 | 17 | 8 | 0 | 55 |  | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 50 | 0 | 48 | 0 | 43 | 16 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 17 | 178 | 0 | 418 | 105 | 50 | 94 | 0 | 112 | 0 | 1 | 113 | 340 | 190 | 0 | 0 | 1 | 54 | 0 |  | 5550 | 2672 | 8222 | 2189 | 435 | 1475 | 167 | 2826 | 539 | 86 | 0 | 320 | 83 | 102 | 0 | 98.71
14:00 | 0 | 0 | 97 | 0 | 230 | 0 | 0 | 0 | 194 |  | 0 | 250 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 82 | 11 | 0 | 0 | 20 | 35 | 55 | 17 | 19 | 25 | 0 | 18 | 24 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 82 | 50 | 16 | 7 | 0 | 0 | 80 | 140 | 270 | 174 | 8 | 137 | 10 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 25 | 9 | 86 | 51 | 0 | 17 | 1 | 43 | 30 | 53 | 0 | 110 | 0 | 64 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 278 | 11 | 0 | 185 | 0 | 90 | 15 | 90 | 0 | 115 | 0 | 40 | 105 | 105 | 3 | 80 | 36 | 106 | 0 | 88 | 90 | 317 | 70 | 9 | 162 | 51 | 0 | 17 | 15 | 0 | 55 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 17 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 43 | 20 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 169 | 0 | 352 | 105 | 10 | 94 | 0 | 112 | 0 | 1 | 113 | 340 | 190 | 0 | 0 | 1 | 46 | 0 |  | 5315 | 2544 | 7859 | 2116 | 436 | 1361 | 31 | 2832 | 539 | 86 | 0 | 281 | 86 | 91 | 0 | 0
15:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 195 |  | 0 | 250 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 64 | 12 | 0 | 0 | 20 | 35 | 55 | 17 | 0 | 25 | 0 | 18 | 24 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 88 | 50 | 16 | 4 | 0 | 0 | 80 | 140 | 270 | 189 | 8 | 137 | 10 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 25 | 9 | 87 | 51 | 0 | 17 | 0 | 43 | 30 | 53 | 0 | 130 | 0 | 69 | 78 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 275 | 0 | 0 | 191 | 0 | 68 | 11 | 90 | 0 | 110 | 0 | 30 | 105 | 105 | 2 | 80 | 36 | 110 | 0 | 55 | 90 | 341 | 70 | 5 | 162 | 51 | 0 | 17 | 5 | 0 | 55 |  | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 25 | 24 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 150 | 0 | 354 | 70 | 0 | 94 | 0 | 75 | 0 | 1 | 70 | 340 | 190 | 0 | 0 | 1 | 38 | 9 |  | 5227 | 2382 | 7609 | 2124 | 437 | 1376 | 0 | 2630 | 539 | 86 | 0 | 267 | 87 | 63 | 0 | 0
16:00 | 0 | 0 | 101 | 0 | 230 | 0 | 0 | 0 | 180 |  | 0 | 250 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 64 | 11 | 0 | 0 | 19 | 35 | 55 | 17 | 0 | 25 | 0 | 18 | 26 | 25 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 88 | 50 | 16 | 5 | 0 | 0 | 80 | 140 | 270 | 190 | 8 | 132 | 10 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 11 | 30 | 9 | 79 | 51 | 0 | 17 | 0 | 43 | 30 | 53 | 0 | 130 | 0 | 68 | 78 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 275 | 0 | 0 | 186 | 0 | 52 | 6 | 90 | 0 | 102 | 0 | 30 | 105 | 105 | 1 | 80 | 36 | 110 | 0 | 55 | 96 | 341 | 60 | 3 | 162 | 51 | 0 | 17 | 4 | 0 | 55 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 25 | 24 | 25 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 159 | 0 | 356 | 70 | 0 | 94 | 0 | 70 | 0 | 1 | 70 | 350 | 190 | 0 | 0 | 0 | 21 | 0 |  | 5152 | 2342 | 7494 | 2139 | 436 | 1363 | 0 | 2539 | 549 | 86 | 0 | 267 | 79 | 36 | 0 | 0
17:00 | 0 | 0 | 86 | 0 | 230 | 0 | 0 | 0 | 181 |  | 0 | 250 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 133 | 12 | 0 | 0 | 28 | 35 | 55 | 17 | 19 | 25 | 0 | 25 | 26 | 25 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 45 | 88 | 50 | 19 | 7 | 0 | 0 | 80 | 140 | 270 | 194 | 8 | 130 | 10 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 11 | 30 | 9 | 83 | 51 | 0 | 17 | 0 | 43 | 30 | 53 | 0 | 163 | 0 | 69 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 10 | 278 | 0 | 0 | 192 | 0 | 52 | 0 | 90 | 0 | 107 | 0 | 55 | 105 | 105 | 0 | 120 | 36 | 110 | 0 | 73 | 100 | 338 | 59 | 1 | 162 | 51 | 0 | 17 | 1 | 0 | 55 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 50 | 18 | 99 | 0 | 25 | 24 | 25 | 28 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 186 | 0 | 414 | 70 | 10 | 94 | 0 | 111 | 0 | 0 | 100 | 340 | 190 | 0 | 0 | 0 | 7 | 0 |  | 5421 | 2551 | 7972 | 2180 | 436 | 1462 | 20 | 2755 | 539 | 86 | 0 | 402 | 83 | 9 | 0 | 0
18:00 | 0 | 0 | 106 | 0 | 230 | 0 | 0 | 0 | 178 |  | 0 | 250 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 11 | 0 | 0 | 51 | 35 | 55 | 17 | 19 | 25 | 0 | 25 | 26 | 32 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 100 | 88 | 50 | 0 | 9 | 0 | 0 | 80 | 140 | 270 | 203 | 8 | 131 | 10 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 11 | 25 | 9 | 95 | 51 | 0 | 17 | 0 | 43 | 30 | 53 | 0 | 163 | 0 | 71 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 60 | 280 | 308 | 50 | 185 | 76 | 60 | 0 | 90 | 0 | 108 | 0 | 81 | 105 | 105 | 0 | 155 | 36 | 110 | 0 | 104 | 100 | 411 | 81 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 50 | 18 | 100 | 0 | 43 | 28 | 34 | 29 | 22 | 0 | 11 | 0 | 0 | 198 | 17 | 10 | 0 | 0 | 0 | 0 | 11 | 35 | 185 | 0 | 414 | 93 | 80 | 94 | 0 | 111 | 0 | 0 | 113 | 440 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6281 | 2866 | 9147 | 2266 | 423 | 1497 | 609 | 3030 | 638 | 86 | 27 | 476 | 95 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 101 | 0 | 230 | 0 | 0 | 0 | 175 |  | 0 | 250 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 150 | 11 | 0 | 0 | 51 | 35 | 55 | 17 | 19 | 25 | 0 | 25 | 26 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 100 | 88 | 50 | 19 | 7 | 0 | 0 | 80 | 140 | 270 | 218 | 8 | 131 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 19 | 11 | 25 | 9 | 90 | 51 | 0 | 20 | 0 | 43 | 30 | 53 | 0 | 163 | 0 | 69 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 20 | 280 | 209 | 30 | 185 | 26 | 131 | 0 | 90 | 0 | 113 | 0 | 115 | 105 | 105 | 0 | 225 | 36 | 110 | 0 | 117 | 100 | 401 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 50 | 28 | 100 | 0 | 43 | 32 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 17 | 8 | 0 | 0 | 0 | 0 | 11 | 95 | 185 | 0 | 415 | 105 | 100 | 110 | 0 | 111 | 0 | 0 | 113 | 540 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6290 | 3108 | 9398 | 2286 | 423 | 1494 | 480 | 3292 | 740 | 86 | 25 | 482 | 90 | 0 | 0 | 0
19:30 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 175 |  | 0 | 250 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 102 | 150 | 11 | 0 | 0 | 51 | 35 | 55 | 17 | 19 | 25 | 6 | 25 | 26 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 100 | 88 | 50 | 19 | 10 | 0 | 0 | 80 | 140 | 270 | 210 | 8 | 133 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 19 | 11 | 25 | 9 | 91 | 53 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 71 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 20 | 280 | 250 | 30 | 185 | 25 | 131 | 0 | 90 | 0 | 116 | 0 | 115 | 105 | 105 | 0 | 225 | 36 | 110 | 0 | 118 | 100 | 401 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 28 | 100 | 0 | 43 | 32 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 17 | 0 | 0 | 0 | 0 | 0 | 11 | 98 | 185 | 0 | 416 | 105 | 70 | 113 | 0 | 111 | 0 | 0 | 113 | 480 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6345 | 3017 | 9362 | 2288 | 423 | 1499 | 493 | 3304 | 679 | 86 | 17 | 482 | 91 | 0 | 0 | 0
20:00 | 0 | 0 | 98 | 0 | 230 | 0 | 0 | 0 | 175 |  | 0 | 240 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 102 | 150 | 11 | 0 | 0 | 51 | 35 | 55 | 17 | 19 | 25 | 9 | 25 | 24 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 100 | 88 | 50 | 19 | 18 | 0 | 0 | 80 | 140 | 270 | 208 | 8 | 129 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 19 | 11 | 26 | 9 | 91 | 53 | 0 | 20 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 71 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 278 | 152 | 30 | 185 | 25 | 145 | 0 | 90 | 0 | 117 | 0 | 115 | 105 | 105 | 0 | 150 | 36 | 110 | 0 | 118 | 100 | 400 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 28 | 100 | 0 | 43 | 32 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 200 | 17 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 185 | 0 | 414 | 105 | 50 | 113 | 0 | 111 | 0 | 0 | 113 | 510 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6156 | 2983 | 9139 | 2281 | 423 | 1495 | 307 | 3242 | 710 | 86 | 17 | 487 | 91 | 0 | 0 | 0
21:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 175 |  | 0 | 240 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 100 | 12 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 25 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 100 | 88 | 50 | 19 | 25 | 0 | 0 | 80 | 140 | 270 | 213 | 8 | 130 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 19 | 11 | 33 | 9 | 89 | 53 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 72 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 278 | 153 | 0 | 195 | 0 | 130 | 0 | 90 | 0 | 133 | 0 | 115 | 105 | 105 | 0 | 150 | 36 | 110 | 0 | 117 | 100 | 400 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 26 | 0 | 0 | 0 | 0 | 50 | 28 | 100 | 0 | 43 | 32 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 184 | 0 | 415 | 105 | 20 | 113 | 0 | 111 | 0 | 0 | 113 | 560 | 201 | 0 | 0 | 0 | 0 | 0 |  | 6041 | 2968 | 9009 | 2298 | 423 | 1486 | 223 | 3207 | 759 | 86 | 0 | 438 | 89 | 0 | 0 | 0
22:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 172 |  | 0 | 240 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 102 | 64 | 11 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 25 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 100 | 88 | 50 | 19 | 22 | 0 | 0 | 80 | 140 | 270 | 215 | 8 | 130 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 9 | 83 | 53 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 72 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 280 | 0 | 0 | 195 | 0 | 93 | 0 | 90 | 0 | 137 | 0 | 85 | 105 | 105 | 0 | 150 | 36 | 110 | 0 | 118 | 100 | 401 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 26 | 0 | 0 | 0 | 0 | 50 | 16 | 58 | 0 | 43 | 13 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 181 | 0 | 384 | 105 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 530 | 210 | 0 | 0 | 0 | 0 | 0 |  | 5744 | 2769 | 8513 | 2295 | 423 | 1458 | 0 | 3151 | 730 | 86 | 0 | 287 | 83 | 0 | 0 | 98.67
23:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 179 |  | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 11 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 25 | 9 | 25 | 25 | 16 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 60 | 88 | 50 | 19 | 37 | 0 | 0 | 80 | 140 | 270 | 220 | 8 | 131 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 9 | 79 | 53 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 70 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 195 | 0 | 0 | 195 | 0 | 63 | 0 | 90 | 0 | 140 | 0 | 45 | 105 | 105 | 0 | 100 | 36 | 110 | 0 | 117 | 100 | 400 | 104 | 0 | 108 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 181 | 0 | 408 | 105 | 0 | 70 | 0 | 112 | 0 | 0 | 113 | 510 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5186 | 2577 | 7763 | 2301 | 423 | 1512 | 0 | 2602 | 710 | 86 | 0 | 50 | 79 | 0 | 0 | 98.66
24:00 | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 194 |  | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 12 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 25 | 9 | 25 | 25 | 0 | 0 | 46 | 40 | 0 | 10 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 88 | 50 | 19 | 40 | 0 | 0 | 80 | 140 | 265 | 212 | 8 | 132 | 10 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 9 | 73 | 53 | 0 | 22 | 0 | 42 | 30 | 53 | 0 | 163 | 0 | 72 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 195 | 0 | 0 | 195 | 0 | 18 | 0 | 90 | 0 | 143 | 0 | 25 | 105 | 105 | 0 | 65 | 36 | 110 | 0 | 75 | 100 | 400 | 58 | 0 | 108 | 51 | 0 | 17 | 0 | 0 | 55 |  | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 414 | 105 | 0 | 35 | 0 | 112 | 0 | 0 | 113 | 400 | 131 | 0 | 0 | 0 | 0 | 0 |  | 4938 | 2346 | 7284 | 2298 | 424 | 1445 | 0 | 2308 | 600 | 86 | 0 | 50 | 73 | 0 | 0 | 98.66
KWH | 0 | 0 | 2430000 | 0 | 5496145 | 0 | 0 | 0 | 4714000 |  | 0 | 5850000 | 0 | 0 | 0 | 464402 | 0 | 0 | 0 | 0 | 1556640 | 1589280 | 193077 | 0 | 0 | 289056 | 835200 | 1230322 | 429453 | 373536 | 600000 | 106560 | 563200 | 679500 | 634560 | 0 | 1063680 | 976000 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 |  | 594480 | 0 | 261989 | 789720 | 2002560 | 1212000 | 423648 | 427200 | 0 | 0 | 1953510 | 3600200 | 6816000 | 4597000 | 217454 | 3237490 | 451152 | 155040 | 0 | 1217112 | 0 | 445536 | 865166 | 459504 | 248760 | 708800 | 234720 | 1754880 | 1235520 | 0 | 414720 | 6000 | 1011000 | 694320 | 1225200 | 0 | 3752345 | 0 | 1667520 | 1904640 | 0 | 695570 | 422000 | 0 | 232200 | 0 | 517728 | 219168 | 93696 | 5437198 | 1385520 | 110486 | 4209600 | 125712 | 1415376 | 117180 | 2114880 | 0 | 2795127 | 0 | 1035600 | 2127600 | 1814065 | 24959 | 2032364 | 901061 | 2397018 | 0 | 1857240 | 2033280 | 9325900 | 1488960 | 102950 | 2831040 | 1267091 | 0 | 444600 | 73033 | 0 | 981000 |  | 10114909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1408 | 0 | 1710067 | 425600 | 0 | 0 | 0 | 0 | 699472 | 128268 | 791136 | 0 | 657447 | 266368 | 1186171 | 326760 | 520800 | 0 | 241398 | 0 | 0 | 4852300 | 53000 | 17000 | 0 | 0 | 0 | 0 | 269861 | 407040 | 4446300 | 0 | 9447563 | 1849920 | 435118 | 1625472 | 0 | 2617200 | 0 | 6680 | 2316192 | 9868600 | 4941027 | 0 | 0 | 9600 | 339840 | 9854 |  | 125298999 | 60582371 | 185881370 | 55590936 | 10114909 | 35300042 | 2557572 | 58541992 | 14720900 | 2039680 | 70000 | 4510217 | 1754880 | 680242 | 0
Fuel Cost | 0 | 0 | 3547800 | 0 | 6100720.95 | 0 | 0 | 0 | 4855420 |  | 0 | 6376500 | 0 | 0 | 0 | 3928840.92 | 0 | 0 | 0 | 0 | 14196556.8 | 15638515.2 | 1780169.94 | 0 | 0 | 2627519.04 | 6096960 | 9510389.06 | 4234406.58 | 280152 | 450000 | 0 | 0 | 0 | 6136195.2 | 0 | 287193.6 | 263520 | 0 | 18100 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2541293.3 | 7541826 | 17422272 | 9599040 | 533796.48 | 1268784 | 0 | 0 | 2871659.7 | 2664148 | 6816000 | 4229240 | 280515.66 | 3723113.5 | 509801.76 | 217056 | 0 | 2081261.52 | 0 | 4499913.6 | 8262335.3 | 583570.08 | 186570 | 1240400 | 176040 | 13161600 | 1309651.2 | 0 | 526694.4 | 95640 | 1658040 | 1110912 | 2180856 | 0 | 4277673.3 | 0 | 3285014.4 | 3637862.4 | 0 | 1203336.1 | 924180 | 0 | 473688 | 0 | 388296 | 166567.68 | 1593768.96 | 41105216.88 | 23526129.6 | 1847325.92 | 21889920 | 2101904.64 | 13927299.84 | 1369834.2 | 17236272 | 0 | 19705645.35 | 0 | 9444672 | 20105820 | 15800506.15 | 0 | 15364671.84 | 7848241.31 | 21069788.22 | 0 | 15916546.8 | 13541644.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 58261875.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14755.84 | 0 | 1932375.71 | 659680 | 0 | 0 | 0 | 0 | 6882804.48 | 1303202.88 | 7001553.6 | 0 | 8888683.44 | 2581105.92 | 11493996.99 | 3169572 | 999936 | 0 | 182738.286 | 0 | 0 | 26299466 | 1836450 | 485010 | 0 | 0 | 0 | 0 | 404791.5 | 6923750.4 | 5202171 | 0 | 9353087.37 | 19313164.8 | 7401357.18 | 15425729.28 | 0 | 20309472 | 0 | 73814 | 17116658.88 | 43323154 | 0 | 0 | 0 | 0 | 0 | 0 |  | 461372816.18 | 276840357.396 | 738213173.576 | 51821089.246 | 58261875.84 | 37067111.75 | 43394236.7 | 416840461.42 | 69622620 | 550713.6 | 2321460 | 43632716.82 | 13161600 | 1539288.2 | 0
Yesterday Day Peak | 0 | 0 | 109 | 0 | 230 | 0 | 0 | 0 | 193 |  | 0 | 250 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 102 | 132 | 11 | 0 | 0 | 11 | 35 | 55 | 17 | 0 | 25 | 0 | 18 | 25 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 75 | 47 | 16 | 5 | 0 | 0 | 80 | 140 | 270 | 181 | 8 | 139 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 21 | 11 | 25 | 9 | 84 | 51 | 0 | 17 | 1 | 43 | 30 | 48 | 0 | 130 | 0 | 64 | 78 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 8 | 0 | 273 | 110 | 0 | 195 | 0 | 96 | 18 | 90 | 0 | 86 | 0 | 40 | 105 | 105 | 4 | 80 | 36 | 93 | 0 | 62 | 90 | 400 | 53 | 12 | 162 | 51 | 0 | 17 | 12 | 0 | 45 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 43 | 16 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 178 | 0 | 418 | 105 | 50 | 94 | 0 | 112 | 0 | 1 | 113 | 320 | 190 | 0 | 0 | 1 | 56 | 0 |  | 8046 | DayPeak
Yesterday Evening Peak | 0 | 0 | 101 | 0 | 230 | 0 | 0 | 0 | 175 | 0 | 0 | 250 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 150 | 11 | 0 | 0 | 51 | 35 | 55 | 17 | 19 | 25 | 0 | 25 | 26 | 42 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 100 | 88 | 50 | 19 | 7 | 0 | 0 | 80 | 140 | 270 | 218 | 8 | 131 | 10 | 5 | 0 | 51 | 0 | 42 | 52 | 19 | 11 | 25 | 9 | 90 | 51 | 0 | 20 | 0 | 43 | 30 | 53 | 0 | 163 | 0 | 69 | 81 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 20 | 280 | 209 | 30 | 185 | 26 | 131 | 0 | 90 | 0 | 113 | 0 | 115 | 105 | 105 | 0 | 225 | 36 | 110 | 0 | 117 | 100 | 401 | 104 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 50 | 28 | 100 | 0 | 43 | 32 | 52 | 29 | 22 | 0 | 11 | 0 | 0 | 200 | 17 | 8 | 0 | 0 | 0 | 0 | 11 | 95 | 185 | 0 | 415 | 105 | 100 | 110 | 0 | 111 | 0 | 0 | 113 | 540 | 220 | 0 | 0 | 0 | 0 | 0 |  | 9398 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 250 | 0 | 0 | 270 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 20 | 35 | 55 | 35 | 22 | 25 | 10 | 16 | 33 | 51 | 0 | 46 | 40 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 70 | 100 | 90 | 50 | 19 | 5 | 0 | 0 | 90 | 140 | 350 | 220 | 8 | 141 | 30 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 164 | 120 | 0 | 17 | 0 | 43 | 43 | 51 | 0 | 163 | 0 | 72 | 80 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 77 | 200 | 137 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 55 |  | 708 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 90 | 22 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 25 | 50 | 33 | 52 | 36 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 250 | 0 | 0 | 270 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 10 | 16 | 33 | 51 | 0 | 44 | 40 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 19 | 5 | 0 | 0 | 90 | 140 | 350 | 200 | 8 | 141 | 30 | 10 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 120 | 0 | 17 | 1.6 | 42 | 43 | 51 | 0 | 163 | 0 | 72 | 80 | 0 | 0 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 300 | 100 | 200 | 50 | 149 | 20 | 77 | 200 | 135 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 55 |  | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 25 | 50 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6 | 10
Generation at 08:00(Today) | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 0 | 212 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 6 | 0 | 0 | 0 | 35 | 53 | 17 | 20 | 25 | 9 | 25 | 32 | 2 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 89 | 46 | 19 | 8 | 0 | 0 | 80 | 160 | 315 | 193 | 8 | 138 | 10 | 5 | 0 | 51 | 0 | 0 | 34 | 16 | 8 | 33 | 9 | 64 | 53 | 0 | 20 | 0 | 42 | 30 | 51 | 0 | 163 | 0 | 72 | 78 | 0 | 0 | 18 | 0 | 10 | 0 | 21 | 5 | 0 | 180 | 0 | 0 | 194 | 0 | 6 | 7 | 90 | 0 | 117 | 0 | 16 | 90 | 42 | 0 | 45 | 36 | 93 | 0 | 25 | 70 | 400 | 80 | 5 | 42 | 51 | 0 | 17 | 11 | 0 | 55 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 161 | 0 | 404 | 80 | 0 | 1 | 0 | 112 | 0 | 0 | 80 | 350 | 201 | 0 | 0 | 0 | 7 | 0 | 0
199
| Minimum Generation |  | 5943 | 4:00
| Highest Generation |  | 9398 | 19:00
| Day Peak Generation |  | 8046 | 12:00
| Evening Peak Generation |  | 9398 | 19:00
| HVDC Max Flow |  | 437 | 15:00
| HVDC EvPeak Flow |  | 423 | 19:00
| Load factor L.F |  | 82.41%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-12-30
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-12-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8046 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5947 | MW
Evening Peak Generation : |  | 9398 | MW Hour : | 19:00 | Available Max Generation : |  | 12076 | MW
E.P. Demand (at gen end) : |  | 9398 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9398 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2576 | MW
Total Gen. (MKWH) : |  | 185.8814 | System Load Factor : | 82.41% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 12 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-12-30
Actual : | 98.63 | Ft.(MSL) , | Rule curve : | 103.2 | Ft.( MSL )
Gas Consumed : | Total = | 700.57 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 88888200.996
: |  | Coal : | 69622620 | Oil : | 506188874.94 | Total : | 664699695.936
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3411.885 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1156.3433 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1035.3528 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 935.2827 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 845.337 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 682.1472 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 386.4244 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 175.7669 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 526.0819 |  |  | 0 | 0%
Total | 0 |  | 9154.6213 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
2) Ghorasal-3,5
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit-1
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-2,3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Agargaon-Cantonment 132 kV Ckt-2 was under shut down from 11:43 to 12:48 for C/M.
b) Agargaon 132/33 kV T2 transformer was under shut down from 08:52 to 16:13 for A/M.
c) Ashuganj-Sirajganj 230 kV Ckt-2 was under shut down from 10:54 to 12:53 due to R/H maintenance at Ashuganj end.
d) Bagerhat-Bhandaria 132 kV Ckt was under shut down from 08:47 to 16:16 for A/M.
e) Bakulia-Sikalbaha 132 kV Ckt-2 was under shut down from 08:40 to 15:08 for A/M.
f) Baroiarhat 132/33 kV T1 transformer tripped at 10:21 showing buchholz relay.
g) Bhola P/S 230/33 kV transformer was under shut down from 10:01 to 15:40 for A/M. | [5 empty] | About 25 MW power interruption occurred under
Bhola P/S area from 10:01 to 15:40.
h) Bhulta 230 kV main Bus-2 was under shut down from 09:32 to 16:20 for A/M.
i) Cumilla(S) 132/33 kV T1 transformer along with 33 kV Bus were under shut down from 08:00 to 10:27 for A/M.
j) Faridpur S/S-Faridpur P/S 132 kV Ckt was under shut down from 09:06 to 15:53 for A/M.
k) Kamrangirchar 132/33 kV T2 transformer was under shut down from 08:56 to 13:28 for A/M.
l) Fenchuganj-Sreemangal 132 kV Ckt-2 was under shut down from 09:07 to 19:28 for A/M.
m) Sherpur 132/33 kV T3 transformer was under shut down from 08:51 to 14:52 for C/M.
n) Ghorashal-Norsingdi 132 kV Ckt-1 was under shut down from 09:28 to 16:47 for A/M.
o) Ghorashal-Joydebpur 132 kV Ckt-2 was under shut down from 07:46 to 13:25 for C/M.
p) Haripur-Ullon 132 kV Ckt tripped at 09:00 from Haripur end showing Dist. B-phase, Z1 and was switched on at 10:14.
q) Hasnabad-Shyampur 230 kV Ckt was under shut down from 07:23 to 20:26 for A/M.
r) Hathazari-Baroirhat 132 kV Ckt-1 was under shut down from 09:30 to 17:17 for A/M.
s) Ishwardi-Ruppur 132 kV Ckt-1 was under shut down from 08:43 to 18:10 for SCADA work.
t) Kabirpur-Tongi 132 kV Ckt-1 was under shut down from 09:31 to 13:22 for A/M.
u) Kaliakoir 400/132 kV T01 transformer was under shut down from 08:58 to 15:27 for A/M.
v) Madunaghat-Hathazari 132 kV Ckt-2 was under shut down from 09:43 to 12:01 due to Ckt Shifted from AIS to GIS.
w) Mohasthangarh-Polashbari 132 kV Ckt-1 was under shut down from 09:08 to 15:14 for A/M.
x) Kodda 132/33 kV T1 transformer was shut down at 13:43 for D/W.
y) Purbasadipur 132/33 kV T1 transformer along with 33 kV Bus were under shut down from 07:38 to 09:20 for C/M.
z) Purbasadipur-Thakurgaon P/S 132 kV Ckt-2 was under shut down from 08:40 to 16:56 for A/M.
aa) Rajendrapur-Kodda 132 kV Ckt-2 was under shut down from 12:30 to 13:10 for C/M.
ab) Ramganj 132/33 kV T1 transformer was under shut down from 08:51 to 17:37 for A/M.
ac) Rangamati-Chandraghona 132 kV Ckt-1 was under shut down from 11:04 to 13:47 for C/M.
ad) Rangamati-Khagrachari 132 kV Ckt-1 was under shut down from 13:56 to 15:01 for C/M.
ae) Savar-Manikganj P/S 132 kV Ckt-1 was under shut down from 09:19 to 16:55 for A/M.
af) Shajadpur 132/33 kV T4 transformer was under shut down from 08:38 to 15:21 for A/M.
ag) Sylhet-Chatak 132 kV Ckt-1 was under shut down from 10:30 to 11:54 for C/M.
ah) Thakurgaon S/S-Thakurgaon P/S 132 kV Ckt-2 was under shut down from 09:02 to 16:45 for A/M.
ai) Kodda 132/33 kV T4 transformer was switched on at 13:15.
aj) B.Baria-Shahzibazar 132 kV Ckt-2 was under shut down from 08:46 to 16:37 for A/M.
ak) HVDC 230 kV Bus-1 was under shut down from 09:53 to 17:13 for A/M.
al) Rangamati-Chandraghona 132 kV Ckt-2 was under shut down from 15:06 to 15:40 for C/M.
am) Rangamati-Khagrachari 132 kV Ckt-2 was under shut down from 15:45 to 16:12 for C/M.
an) Sreenagar 132/33 kV T1 transformer was under shut down from 15:01 to 16:04 due to R/H maintenance.
ao) Raozan Unit-2 was synchronized at 23:44.
ap) 33 kV side of Purbasadipur 132/33 kV T1 transformer tripped at 23:30 showing O/C due to 33 kV Sadar feeder | [5 empty] | About 25 MW power interruption occurred under
fault and was switched on at 23:50. | [5 empty] | Purbasadipur S/S area from 23:30 to 23:50.
aq) Payra unit-2 was shutdown at 00:47(30/12/2021).
ar) Naogaon 132/33 T-1 & T-2 transformers tripped at 02:25(30/12/2021) due to Joypurhat 33 kV PBS feeder fault | [5 empty] | About 24 MW power interruption occurred under
and were switched on at 23:50(30/12/2021). | [5 empty] | Naogaon S/S area from 23:30(30/12/2021) to 23:50.
as) Ashuganj 132 kV Bus-1 is under shut down since 07:37(30/12/2021) for A/M.
at) Polashbari-Mohasthangarh 132 kV Ckt-2 is under shut down since 07:39(30/12/2021) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-12-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 101 | 2430000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 230 | 5496145 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 175 | 4714000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 5850000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 464402 | High Voltage.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 11 | 193077 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 373536
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1556640
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 51 | 289056 | On test
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 835200 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1589280
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1230322
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 429453 | 33 kV feeder problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 25 | 706560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 563200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 679500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 42 | 634560 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 5437198 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 209 | 1385520
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 30 | 110486
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 26 | 125712
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 1415376 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2127600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1488960
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2831040
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 73033
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 55 | 981000
| Dhaka area Total |  |  |  | 5560 | 2446 | 44010856
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 10000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | High Voltage.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 117180
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1212000
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2039680 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1814065
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 261989 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 789720
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2114880 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 423648
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 7 | 427200
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 88 | 2002560 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24959
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 225 | 2032364 | High Voltage.
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 901061 | High Voltage.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2397018
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2033280
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 1267091 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1118 | 19868695
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1953510 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 4597000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 140 | 3600200
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6816000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 451152 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 155040 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1217112
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 113 | 2795127 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 445536
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 131 | 3237490 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | High Voltage.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 459504
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 248760
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 90 | 1754880
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 708800 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 865166
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 234720 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 93696
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | High Voltage.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 117 | 1857240
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444600 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3034 | 1428 | 32152987
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 51 | 1235520 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 414720 | Engine problem
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6000
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 185 | 4209600 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1035600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 102950
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 594480
| Mymensingh Area Total |  |  |  | 622 | 395 | 7598870
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1011000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 694320 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3752345
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1225200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 219168
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1667520
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1904640
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | On test
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 695570 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 422000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 517728
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 232200
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 401 | 9325900
| Sylhet Area Total |  |  |  | 2377 | 903 | 21667591
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 423 | 10114909
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | High Voltage.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | High Voltage.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 1408 | High Voltage.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 95 | 407040
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1849920
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 0 | 0 | 339840 | On test
| Khulna Area Total |  |  |  | 2129 | 623 | 12713117
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | High Voltage.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 23 | 425600 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1710067 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 269861 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 9868600 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4941027
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 859 | 17215155
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 699472
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 128268 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 657447
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 266368 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 185 | 4446300 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 9447563
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 326760 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 520800
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 241398
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1186171
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 791136
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 100 | 435118
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 110 | 1625472 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2316192
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 9600
| Rajshahi Area Total |  |  |  | 2179 | 1290 | 23098065
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4852300
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 53000
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 17000 | Engine problem
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 111 | 2617200
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 6680
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 9854 | On test
| Rangpur Area Total |  |  |  | 605 | 336 | 7556034
| Total |  |  |  | 20934 | 9398 | 185881370
| Eastern Grid Total |  |  |  | 13975 | 6290 | 125298999
| Western Grid Total |  |  |  | 6959 | 3108 | 60582371
| National Grid Total |  |  |  | 20934 | 9398 | 185881370
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-12-29
(a) ENTIRE EASTERN GRID : |  | 6212 | MW | (b) ENTIRE WESTERN GRID : |  | 2836 | MW
i) Dhaka area |  | 3294 | MW | i) Khulna area |  | 1083 | MW
ii) Chittagong area |  | 1116 | MW | ii) Rajshahi area |  | 883 | MW
iii) Comilla area |  | 753 | MW | iii) Barisal area |  | 256 | MW
iv) Mymensingh area |  | 716 | MW | iv) Rangpur area |  | 614 | MW
v) Sylhet area |  | 333 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9048 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 92 | 15:00 | Tangail | 133 | 18:30 | Noapara | 38 | 19:00
Munsiganj | 61 | 23:00 | Mymensing | 132 | 21:00 | Jessore | 76 | 18:00
Sonargaon | 68 | 16:00 | Kishoreganj | 94 | 19:30 | Benapol | 36 | 18:00
Shyampur | 170 | 10:00 | Netrokona | 83 | 18:00 | Jhenida(Old) | 81 | 18:30
Bhulta | 165 | 1:00 | Jamalpur | 99 | 18:00 | Bottail | 96 | 18:30
Madanganj | 29 | 17:00 | Sherpur | 106 | 18:00 | G.K Project | 36 | 19:00
Shitalakhya | 93 | 12:00 | Srimongal | 34 | 18:00 | Faridpur | 103 | 18:30
Rahim steel | 22 | 17:00 | Shahjibazar | 77 | 19:30 | Rajbari | 32 | 18:30
Matuail | 48 | 9:00 | Fenchuganj | 26 | 18:30 | Madaripur | 64 | 20:00
Ghorasal | 58 | 18:30 | Kulawara | 28 | 18:00 | Sariatpur | 42 | 20:00
Narsingdi | 127 | 19:00 | Sylhet | 92 | 19:00 | Gopalganj | 68 | 18:30
Haripur (SBU) | 90 | 21:00 | Chatak | 13 | 18:00 | Bagerhat | 78 | 19:30
Sreenagar | 27 | 20:00 | Sunamganj | 30 | 19:30 | Mongla | 44 | 12:00
Ullon | 137 | 7:00 | Biani Bazar | 39 | 18:00 | Satkhira | 74 | 18:30
Hasnabad | 137 | 6:00 | Comilla (S) | 85 | 18:00 | Gallamari | 47 | 13:00
Magbazar | 141 | 19:30 | Comilla(N) | 77 | 18:30 | Magura | 40 | 18:30
Maniknagar | 143 | 18:00 | Chandpur | 48 | 20:00 | Norail | 36 | 18:00
Bangabhaban | 143 | 18:00 | Feni | 79 | 19:30 | Chuadanga | 63 | 18:00
Motijheel | 143 | 18:00 | Chowmuhani | 134 | 20:00 | Barisal(N) | 27 | 19:00
Narinda | 143 | 18:00 | Ashuganj | 22 | 18:00 | Barisal (S) | 76 | 19:00
Kazla | 7 | 11:00 | Daudkandi | 96 | 21:00 | Patuakhali | 76 | 19:30
Dhanmondi | 122 | 13:00 | B.Baria | 98 | 20:00 | Bhandaria | 38 | 18:30
Lalbag | 38 | 11:00 | Ramganj | 52 | 18:00 | Borguna | 12 | 19:30
Madartek | 142 | 8:00 | Chaddagram | 40 | 10:00 | Borhan Uddin | 30 | 18:00
Dhaka University | 138 | 1:00 | PHP | 3 | 1:00 | Ishurdi | 52 | 18:30
Aftabnagar | 137 | 1:00 | Kochua | 38 | 19:00 | Ruppur Paromanobik | 3 | 9:00
Fatullah | 138 | 1:00 | Madunaghat | 41 | 19:00 | Natore | 88 | 18:30
Nawabganj | 138 | 1:00 | Hathazari | 69 | 18:00 | Bogra | 100 | 20:00
Keraniganj | 137 | 1:00 | Khulshi | 149 | 14:00 | Noagaon | 79 | 20:00
Banani | 140 | 1:00 | Halishahar | 63 | 20:00 | Rajshahi | 97 | 21:00
Mirpur | 79 | 18:00 | Baraulia | 135 | 14:00 | Rajshahi New | 14 | 18:00
Kalyanpur | 66 | 19:00 | Sikalbaha | 26 | 18:30 | C.Nawabganj | 41 | 18:00
Gulshan | 68 | 3:00 | Dohazari | 66 | 19:00 | Amnura | 34 | 19:30
Uttara | 40 | 13:00 | Cox'sbazar | 73 | 18:00 | Pabna | 68 | 18:00
Uttara New | 20 | 17:00 | Chandraghona | 22 | 18:00 | Shahjadpur | 71 | 18:30
Kamrangirchar | 59 | 17:00 | Kaptai | 3.5 | 18:00 | Serajganj | 68 | 19:00
Savar | 125 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 43 | 18:30
Bhasantec | 82 | 13:00 | Bakulia | 81 | 18:00 | Joypurhat | 47 | 19:00
Agargaon | 48 | 13:00 | Julda | 24 | 9:00 | Sherpur(Bogura) | 46 | 18:00
Satmosjid | 71 | 13:00 | TK chemical | 21 | 18:00 | Mohastangor | 42 | 18:30
Old Tongi | 92 | 11:00 | Modern Steel | 0 | 1:00 | Bhangura | 20 | 18:30
Kabirpur | 164 | 15:00 | Shahmirpur | 36 | 18:00 | Rangpur | 103 | 18:00
Bashundara | 127 | 18:00 | Khagrachhari | 18 | 21:00 | Lalmonirhat | 29 | 18:00
Manikgong | 62 | 20:00 | Matarbari | 25 | 17:00 | Saidpur | 87 | 18:00
Joydevpur | 130 | 18:30 | Baroiar Hat | 32 | 18:00 | Purbasadipur | 90 | 18:00
New Tongi | 63 | 12:00 | Rangamati | 10 | 18:00 | Thakurgaon | 66 | 18:00
Kodda | 224 | 12:00 | Abul Khair 230 | 138 | 9:00 | Palashbari | 73 | 18:00
Dhamrai | 90 | 12:00 | BSRM | 159 | 5:00 | Barapukuria | 43 | 19:30
Rajendrapur | 82 | 18:30 | GPH Ispat | 92 | 5:00 | Panchagar | 46 | 18:00
Purbachal | 11 | 20:00 | Agrabad | 56 | 18:00 | Joldhaka | 47 | 18:30
Tongi Millgate | 38 | 12:00 | Goalpara | 26 | 13:00 | Kurigram | 49 | 18:00
Valuka | 100 | 18:30 | Central S/S | 56 | 18:30 | Mithapukur | 36 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-12-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 1:00 | 408 | 10:00 | Kaliakoir | 416 | 0.20833 | 405 | 0.75
| Bheramara | 409 | 14:00 | 400 | 12:00 | Bhulta | 403 | 0.041667 | 391 | 0.41667
| Ashuganj(N) | 404 | 1:00 | 394 | 16:00 | Gopalganj | 420 | 0.625 | 399 | 0.95833
| Payra | 420 | 7:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 245 | 1:00 | 245 | 1:00 | Hathazari | 243 | 6:00 | 234 | 16:00
| Ishurdi | 245 | 5:00 | 233 | 23:00 | Megnaghat | 245 | 24:00 | 238 | 1:00
| Ashuganj | 252 | 6:00 | 246 | 12:00 | Fenchuganj | 248 | 1:00 | 242 | 16:00
| Serajganj | 243 | 1:00 | 239 | 8:00 | Siddhirganj | 243 | 1:00 | 236 | 12:00
| Baghabari | 242 | 14:00 | 236 | 19:30 | Maniknagar | 241 | 1:00 | 235 | 11:00
| Barapukuria | 240 | 4:00 | 231 | 18:00 | Agargaon | 243 | 5:00 | 235 | 16:00
| Bogra | 241 | 6:00 | 234 | 12:00 | Barisal | 247 | 17:00 | 239 | 21:00
| Rajshahi | 245 | 14:00 | 232 | 8:00 | Bhola 225 MW | 249 | 6:00 | 244 | 18:00
| Khulna South | 248 | 5:00 | 234 | 23:00 | AKSML | 245 | 17:00 | 232 | 4:00
| Rampura | 241 | 1:00 | 233 | 16:00 | BSRM | 244 | 21:00 | 233 | 10:00
| Haripur | 241 | 20:00 | 234 | 12:00 | Bibiyana | 249 | 24:00 | 239 | 10:00
| Hasnabad | 241 | 22:00 | 235 | 16:00 | Bhulta | 245 | 6:00 | 236 | 12:00
| Shyampur | 241 | 7:00 | 235 | 10:00 | Ashuganj (S) | 247 | 1:00 | 242 | 16:00
| Aminbazar | 244 | 1:00 | 237 | 2:00 | Kaliakoir | 243 | 1:00 | 234 | 7:00
| Tongi | 242 | 1:00 | 234 | 15:00 | GPH | 245 | 21:00 | 234 | 10:00
| Comilla (N) | 243 | 6:00 | 236 | 12:00 | Jhenaidah | 241 | 6:00 | 232 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 1:00 | 136 | 12:00 | Kachua | 143 | 0.041667 | 139 | 0.45833
| Munsiganj | 143 | 19:30 | 139 | 10:00 | Madanhat | 142 | 0.25 | 137 | 0.45833
| Sonargaon | 140 | 1:00 | 137 | 12:00 | Hathazari | 143 | 0.25 | 139 | 0.66667
| Shyampur | 139 | 1:00 | 135 | 12:00 | Khulshi | 141 | 0.25 | 135 | 0.41667
| Bhulta | 136 | 1:00 | 133 | 12:00 | Halishahar | 143 | 0.83333 | 136 | 0.41667
| Madanganj | 142 | 20:00 | 137 | 12:00 | Baraulia | 143 | 0.91667 | 136 | 0.41667
| Shitalakhya | 143 | 20:00 | 138 | 16:00 | Sikalbaha | 142 | 0.70833 | 137 | 0.91667
| Rahim steal | 140 | 19:00 | 137 | 10:00 | Dohazari | 142 | 0.91667 | 133 | 0.5
| Matuail | 140 | 1:00 | 136 | 12:00 | Cox'sbazar | 129 | 0.041667 | 122 | 0.77083
| Ghorasal | 145 | 1:00 | 145 | 1:00 | Chandraghona | 144 | 0.91667 | 137 | 0.66667
| Narsinghdi | 139 | 7:00 | 135 | 9:00 | Kaptai | 140 | 0.041667 | 140 | 0.041667
| Haripur (SBU) | 141 | 21:00 | 140 | 1:00 | A. Khaer Stl. | 141 | 0.083333 | 138 | 0.375
| Sreenagar | 138 | 1:00 | 134 | 16:00 | Bakulia | 142 | 0.875 | 135 | 0.66667
| Ullon | 137 | 6:00 | 132 | 16:00 | Julda | 142 | 0.66667 | 136 | 0.45833
| Hasnabad | 143 | 18:00 | 140 | 10:00 | TK Chemical | 143 | 0.8125 | 136 | 0.375
| Magbazar | 138 | 5:00 | 134 | 12:00 | Modern Steel | 142 | 0.83333 | 138 | 0.041667
| Maniknagar | 142 | 8:00 | 138 | 11:00 | Shahmirpur | 143 | 0.91667 | 137 | 0.41667
| Bangabhaban | 142 | 8:00 | 138 | 11:00 | Khagrachhari | 142 | 0.875 | 137 | 0.41667
| Motijheel | 142 | 8:00 | 138 | 11:00 | Matarbari | 131 | 0.25 | 128 | 0.29167
| Narinda | 142 | 8:00 | 138 | 11:00 | Baroiar Hat | 142 | 7:00 | 138 | 10:00
| Kazla | 142 | 8:00 | 138 | 11:00 | Rangamati | 143 | 22:00 | 137 | 10:00
| Dhanmondi | 141 | 19:30 | 136 | 16:00 | Agrabad | 142 | 22:00 | 134 | 0.5
| Lalbag | 138 | 1:00 | 133 | 16:00 | Goalpara S/S | 142 | 6:00 | 135 | 0.33333
| Madartek | 137 | 1:00 | 132 | 16:00 | Khulna Central S/S | 140 | 6:00 | 133 | 0.83333
| Dhaka University | 137 | 1:00 | 132 | 12:00 | Noapara | 140 | 1:00 | 134 | 0.5
| Aftabnagar | 138 | 1:00 | 132 | 12:00 | Jessore | 138 | 0.20833 | 132 | 0.33333
| Fatullah | 140 | 1:00 | 134 | 22:00 | Benapol | 139 | 4:00 | 132 | 0.75
| Nawabganj | 138 | 1:00 | 133 | 12:00 | Jhenida(Old) | 139 | 0.25 | 132 | 0.75
| Keraniganj | 138 | 1:00 | 134 | 16:00 | Bottail | 141 | 0.125 | 132 | 0.77083
| Banani | 137 | 1:00 | 133 | 16:00 | G.K Project | 141 | 0.041667 | 135 | 0.77083
| Mirpur | 140 | 7:00 | 136 | 15:00 | Faridpur | 140 | 0.29167 | 130 | 0.77083
| Kalyanpur | 140 | 1:00 | 138 | 7:00 | Rajbari | 140 | 0.20833 | 128 | 0.77083
| Gulshan | 137 | 3:00 | 132 | 16:00 | Madaripur | 144 | 5:00 | 138 | 0.83333
| Uttara | 141 | 1:00 | 137 | 11:00 | Shariyatpur S/S | 144 | 0.29167 | 137 | 0.77083
| Uttara New | 141 | 8:00 | 138 | 11:00 | Gopalganj | 142 | 5:00 | 136 | 0.75
| Kamrangirchar | 139 | 4:00 | 134 | 15:00 | Bagerhat | 140 | 6:00 | 134 | 0.33333
| Savar | 141 | 9:00 | 138 | 3:00 | Mongla | 139 | 10:00 | 130 | 9:00
| Bhasantec | 139 | 1:00 | 134 | 15:00 | Satkhira | 139 | 0.25 | 131 | 18:30
| Agargaon | 140 | 1:00 | 135 | 12:00 | Gallamari | 141 | 5:00 | 133 | 0.77083
| Satmosjid | 139 | 1:00 | 134 | 15:00 | Magura | 140 | 0.041667 | 132 | 0.75
| Old Tongi | 143 | 9:00 | 137 | 15:00 | Narail | 140 | 6:00 | 130 | 0.75
| Kabirpur | 139 | 1:00 | 132 | 15:00 | Chuadanga | 138 | 6:00 | 128 | 0.77083
| Bashundara | 142 | 1:00 | 136 | 12:00 | Barisal(N) | 145 | 5:00 | 139 | 18:00
| Manikgong | 138 | 24:00 | 130 | 12:00 | Barisal (S) | 143 | 0.25 | 138 | 0.79167
| Joydevpur | 143 | 22:00 | 137 | 15:00 | Patuakhali(S) | 142 | 0.125 | 135 | 0.77083
| New Tongi | 142 | 5:00 | 133 | 19:00 | Bhandaria | 142 | 0.041667 | 135 | 0.875
| Kodda | 142 | 13:00 | 137 | 11:00 | Borguna | 144 | 5:00 | 137 | 18:00
| Dhamrai | 141 | 1:00 | 134 | 18:00 | Jhenaidah(New) | 139 | 5:00 | 134 | 8:00
| Rajendrapur | 140 | 1:00 | 135 | 17:00 | Ishurdi | 142 | 14:00 | 136 | 18:00
| Purbachal | 138 | 6:00 | 133 | 14:00 | Ruppur Paromanobik | 141 | 13:00 | 135 | 18:00
| Tongi Millgate | 142 | 24:00 | 136 | 16:00 | Natore | 142 | 14:00 | 137 | 8:00
| Valuka | 133 | 1:00 | 127 | 12:00 | Bogra | 142 | 14:00 | 138 | 8:00
| Tangail | 137 | 2:00 | 131 | 12:00 | Noagaon | 138 | 1:00 | 134 | 12:00
| Mymensing | 135 | 1:00 | 129 | 18:00 | Rajshahi | 141 | 14:00 | 134 | 8:00
| Kishorganj | 136 | 1:00 | 132 | 12:00 | Rajshahi New | 141 | 17:00 | 133 | 8:00
| Netrokona | 135 | 5:00 | 129 | 18:00 | C.Nawabganj | 139 | 16:00 | 132 | 8:00
| Jamalpur | 141 | 13:00 | 137 | 8:00 | Amnura | 140 | 15:00 | 132 | 8:00
| Sherpur | 139 | 12:00 | 135 | 8:00 | Pabna | 142 | 5:00 | 135 | 18:00
| Srimongal | 140 | 1:00 | 137 | 16:00 | Shahjadpur | 147 | 3:00 | 141 | 8:00
| Shahjibazar | 139 | 1:00 | 136 | 12:00 | Serajganj | 141 | 1:00 | 137 | 8:00
| Fenchuganj | 138 | 1:00 | 135 | 11:00 | Niyamatpur | 139 | 3:00 | 131 | 8:00
| Khulawara | 138 | 1:00 | 135 | 12:00 | Joypurhat | 140 | 14:00 | 134 | 12:00
| Sylhet | 136 | 1:00 | 132 | 12:00 | Sherpur(Bogura) | 142 | 1:00 | 137 | 18:00
| Chatak | 137 | 1:00 | 132 | 11:00 | Mohastangor | 141 | 1:00 | 137 | 18:00
| Sunamganj | 135 | 1:00 | 130 | 19:00 | Bangura | 143 | 18:00 | 139 | 1:00
| Biani Bazar | 136 | 1:00 | 131 | 16:00 | Rangpur | 141 | 5:00 | 130 | 18:00
| Comilla(s) | 130 | 22:00 | 126 | 11:00 | Lalmonirhat | 138 | 3:00 | 130 | 18:00
| Comilla(n) | 146 | 4:00 | 142 | 12:00 | Saidpur | 137 | 4:00 | 128 | 18:00
| Chandpur | 143 | 4:00 | 141 | 11:00 | Purbasadipur | 135 | 3:00 | 125 | 18:00
| Feni | 143 | 7:00 | 137 | 11:00 | Thakurgaon | 133 | 2:00 | 121 | 18:00
| Chowmuhani | 142 | 7:00 | 137 | 10:00 | Palashbari | 140 | 1:00 | 133 | 12:00
| Ashuganj | 141 | 1:00 | 139 | 12:00 | Barapukuria | 140 | 0.16667 | 131 | 0.75
| Daudkandi | 144 | 18:00 | 139 | 10:00 | Panchagar | 135 | 0.16667 | 124 | 0.75
| B.Baria | 138 | 4:00 | 134 | 12:00 | Joldhaka | 137 | 0.20833 | 126 | 0.75
| Ramganj | 142 | 6:00 | 135 | 11:00 | Kurigram | 138 | 0.25 | 129 | 0.75
| Chaddagram | 145 | 21:00 | 138 | 11:00 | Mithapukur | 142 | 1:00 | 134 | 18:00
| PHP | 143 | 5:00 | 138 | 11:00

## L-Curve
Date | 2021-12-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 230 | 4938 | 2346 | 7284 |  |  |  | QF-LDC-11
0:30 | 161 | 4791.5 | 2216 | 7007.5 | Date: | 2021-12-29
1:00 | 92 | 4645 | 2086 | 6731
1:30 | 115 | 4511.5 | 2064.5 | 6576
2:00 | 138 | 4378 | 2043 | 6421
2:30 | 145 | 4257.5 | 2026 | 6283.5 | [5 empty] | Gen. at Eve. Peak | 9398 | 9398 MW (19:00 )
3:00 | 152 | 4137 | 2009 | 6146 | [6 empty] | 19:00
3:30 | 212 | 4036 | 2008.5 | 6044.5 | [5 empty] | Gen. at Day Peak | 8046 | 8046 MW (12:00 )
4:00 | 272 | 3935 | 2008 | 5943 | [6 empty] | 12:00
4:30 | 255 | 3965 | 1998 | 5963 | [5 empty] | Highest Generation | 9398
5:00 | 238 | 3995 | 1988 | 5983 | [6 empty] | 19:00
5:30 | 231 | 4030.5 | 2041 | 6071.5
6:00 | 224 | 4066 | 2094 | 6160
6:30 | 186 | 4255 | 2108 | 6363
7:00 | 148 | 4444 | 2122 | 6566
7:30 | 80 | 4579.5 | 2209.5 | 6789
8:00 | 12 | 4715 | 2297 | 7012
8:30 | 51 | 4883 | 2325 | 7208
9:00 | 90 | 5051 | 2353 | 7404
9:30 | 211 | 5181 | 2426 | 7607
10:00 | 332 | 5311 | 2499 | 7810
10:30 | 341 | 5272.5 | 2542.5 | 7815
11:00 | 350 | 5234 | 2586 | 7820
11:30 | 318 | 5341 | 2592 | 7933
12:00 | 286 | 5448 | 2598 | 8046
12:30 | 271 | 5499 | 2635 | 8134
13:00 | 256 | 5550 | 2672 | 8222
13:30 | 321 | 5432.5 | 2608 | 8040.5
14:00 | 386 | 5315 | 2544 | 7859
14:30 | 374 | 5271 | 2463 | 7734
15:00 | 362 | 5227 | 2382 | 7609
15:30 | 374 | 5189.5 | 2362 | 7551.5
16:00 | 386 | 5152 | 2342 | 7494
16:30 | 369 | 5286.5 | 2446.5 | 7733
17:00 | 352 | 5421 | 2551 | 7972
17:30 | 200 | 5851 | 2708.5 | 8559.5
18:00 | 48 | 6281 | 2866 | 9147
18:30 | 53 | 6285.5 | 2987 | 9272.5
19:00 | 58 | 6290 | 3108 | 9398
19:30 | 24 | 6345 | 3017 | 9362
20:00 | 46 | 6156 | 2983 | 9139 |  |  |  | Executive Engineer
20:30 | 94 | 6098.5 | 2975.5 | 9074 |  |  |  | Network Operation Division
21:00 | 142 | 6041 | 2968 | 9009
21:30 | 155 | 5892.5 | 2868.5 | 8761
22:00 | 168 | 5744 | 2769 | 8513 |  |  |  |  | Page 6 of 7
22:30 | 244 | 5465 | 2673 | 8138
23:00 | 320 | 5186 | 2577 | 7763
23:30 | 275 | 5062 | 2461.5 | 7523.5
24:00 | 230 | 4938 | 2346 | 7284
9398 MW (19:00 )
8046 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-12-29 |  | Energy |  | 185881370
[13 empty] | 2021-12-29 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2298 | 424 | 1445 | 0 | 2308 | 600 | 86 | 0 | 50 | 73 | 0 | 0
0:30 | 2324.5 | 407 | 1452.5 | 0 | 2070 | 560 | 83 | 0 | 42 | 68.5 | 0 | 0 | Date: | 2021-12-29
1:00 | 2351 | 390 | 1460 | 0 | 1832 | 520 | 80 | 0 | 34 | 64 | 0 | 0
1:30 | 2376.5 | 389.5 | 1482 | 0 | 1662 | 505 | 80 | 0 | 17 | 64 | 0 | 0 | [8 empty] | Total Energy | 185.8814 | Total Energy Gen 185.881 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.881 MKWHr
2:00 | 2402 | 389 | 1504 | 0 | 1492 | 490 | 80 | 0 | 0 | 64 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2387.5 | 388.5 | 1507.5 | 0 | 1372 | 485 | 80 | 0 | 0 | 63 | 0 | 0 | [8 empty] | Energy Requirement | 185.8814
3:00 | 2373 | 388 | 1511 | 0 | 1252 | 480 | 80 | 0 | 0 | 62 | 0 | 0
3:30 | 2379 | 388 | 1506 | 0 | 1155 | 475 | 80 | 0 | 0 | 61.5 | 0 | 0 | [6 empty] | Shortage
4:00 | 2385 | 388 | 1501 | 0 | 1058 | 470 | 80 | 0 | 0 | 61 | 0 | 0
4:30 | 2393 | 388.5 | 1486 | 0 | 1086 | 470 | 80 | 0 | 0 | 59.5 | 0 | 0
5:00 | 2401 | 389 | 1471 | 0 | 1114 | 470 | 80 | 0 | 0 | 58 | 0 | 0
5:30 | 2401.5 | 388.5 | 1497 | 0 | 1176.5 | 470 | 80 | 0 | 0 | 58 | 0 | 0
6:00 | 2402 | 388 | 1523 | 0 | 1239 | 470 | 80 | 0 | 0 | 58 | 0 | 0
6:30 | 2368 | 412 | 1446.5 | 0 | 1524 | 470 | 80 | 0 | 5 | 56 | 1.5 | 0 |  |  |  |  | Coal
7:00 | 2334 | 436 | 1370 | 0 | 1809 | 470 | 80 | 0 | 10 | 54 | 3 | 0
7:30 | 2335.5 | 436 | 1443 | 0 | 1920 | 480 | 80 | 0 | 29 | 48.5 | 17 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2337 | 436 | 1516 | 0 | 2031 | 490 | 80 | 0 | 48 | 43 | 31 | 0
8:30 | 2291 | 436 | 1469 | 56.5 | 2206.5 | 499.5 | 83 | 0 | 81.5 | 44 | 41 | 0
9:00 | 2245 | 436 | 1422 | 113 | 2382 | 509 | 86 | 0 | 115 | 45 | 51 | 0
9:30 | 2234.5 | 436 | 1473 | 145 | 2486 | 504 | 86 | 0 | 124.5 | 48 | 70 | 0
10:00 | 2224 | 436 | 1524 | 177 | 2590 | 499 | 86 | 0 | 134 | 51 | 89 | 0
10:30 | 2193.5 | 436 | 1508 | 173 | 2583.5 | 509 | 86 | 0 | 169 | 60.5 | 96.5 | 0
11:00 | 2163 | 436 | 1492 | 169 | 2577 | 519 | 86 | 0 | 204 | 70 | 104 | 0
11:30 | 2189 | 436 | 1463.5 | 169.5 | 2652 | 519 | 86 | 0 | 236.5 | 77 | 104.5 | 0
12:00 | 2215 | 436 | 1435 | 170 | 2727 | 519 | 86 | 0 | 269 | 84 | 105 | 0
12:30 | 2202 | 435.5 | 1455 | 168.5 | 2776.5 | 529 | 86 | 0 | 294.5 | 83.5 | 103.5 | 0
13:00 | 2189 | 435 | 1475 | 167 | 2826 | 539 | 86 | 0 | 320 | 83 | 102 | 0
13:30 | 2189 | 435 | 1475 | 167 | 2826 | 539 | 86 | 0 | 320 | 83 | 102 | 0
14:00 | 2189 | 435 | 1475 | 167 | 2826 | 539 | 86 | 0 | 320 | 83 | 102 | 0
14:30 | 2156.5 | 436 | 1425.5 | 83.5 | 2728 | 539 | 86 | 0 | 293.5 | 85 | 82.5 | 0
15:00 | 2124 | 437 | 1376 | 0 | 2630 | 539 | 86 | 0 | 267 | 87 | 63 | 0
15:30 | 2131.5 | 436.5 | 1369.5 | 0 | 2584.5 | 544 | 86 | 0 | 267 | 83 | 49.5 | 0
16:00 | 2139 | 436 | 1363 | 0 | 2539 | 549 | 86 | 0 | 267 | 79 | 36 | 0
16:30 | 2159.5 | 436 | 1412.5 | 10 | 2647 | 544 | 86 | 0 | 334.5 | 81 | 22.5 | 0
17:00 | 2180 | 436 | 1462 | 20 | 2755 | 539 | 86 | 0 | 402 | 83 | 9 | 0
17:30 | 2223 | 429.5 | 1479.5 | 314.5 | 2892.5 | 588.5 | 86 | 13.5 | 439 | 89 | 4.5 | 0
18:00 | 2266 | 423 | 1497 | 609 | 3030 | 638 | 86 | 27 | 476 | 95 | 0 | 0
18:30 | 2276 | 423 | 1495.5 | 544.5 | 3161 | 689 | 86 | 26 | 479 | 92.5 | 0 | 0
19:00 | 2286 | 423 | 1494 | 480 | 3292 | 740 | 86 | 25 | 482 | 90 | 0 | 0
19:30 | 2288 | 423 | 1499 | 493 | 3304 | 679 | 86 | 17 | 482 | 91 | 0 | 0
20:00 | 2281 | 423 | 1495 | 307 | 3242 | 710 | 86 | 17 | 487 | 91 | 0 | 0
20:30 | 2289.5 | 423 | 1490.5 | 265 | 3224.5 | 734.5 | 86 | 8.5 | 462.5 | 90 | 0 | 0
21:00 | 2298 | 423 | 1486 | 223 | 3207 | 759 | 86 | 0 | 438 | 89 | 0 | 0
21:30 | 2296.5 | 423 | 1472 | 111.5 | 3179 | 744.5 | 86 | 0 | 362.5 | 86 | 0 | 0
22:00 | 2295 | 423 | 1458 | 0 | 3151 | 730 | 86 | 0 | 287 | 83 | 0 | 0
22:30 | 2298 | 423 | 1485 | 0 | 2876.5 | 720 | 86 | 0 | 168.5 | 81 | 0 | 0
23:00 | 2301 | 423 | 1512 | 0 | 2602 | 710 | 86 | 0 | 50 | 79 | 0 | 0
23:30 | 2299.5 | 423.5 | 1478.5 | 0 | 2455 | 655 | 86 | 0 | 50 | 76 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 25.1° C
24:00 | 2298 | 424 | 1445 | 0 | 2308 | 600 | 86 | 0 | 50 | 73 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 185.881 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.881 MKWHr
Note on W13: Author:

## Generation
g | 2021-12-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1063680
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 976000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | [25 empty] | 10 | 10000
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7 | 12 | 16 | 18 | 18 | 17 | 15 | 11 | 6 | [10 empty] | 117180
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 51 | 51 |  |  | 261989
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 |  |  |  | 9 | 17 | 17 | 33 | 85 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1814065
| Daudkandi 200 MW PP (B.Trac) | [16 empty] | 10 | 60 |  | 20 | 20 | [5 empty] | 93696
14 | Titas 50 MW Peaking PP | [11 empty] | 42 | 45 | 50 | 50 | 50 | 50 | 50 |  | 42 | 42 | 42 | 42 |  |  | 0 | 445536
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 245 | 195 | 95 | 45 | 45 | 45 | 128 | 165 | 213 | 275 | 281 | 273 | 275 | 278 | 275 | 275 | 278 | 280 |  | 280 | 280 | 278 | 278 | 280 | 195 | 195 | 5437198
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 99 | 93 | 101 | 100 | 100 | 100 | 113 | 110 | 100 | 97 | 98 | 109 | 100 | 97 | 100 | 101 | 86 | 106 |  | 101 | 100 | 98 | 100 | 100 | 100 | 100 | 2430000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5496145
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1953510
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 23 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 451152
33 | Ashuganj 225 MW CCPP | 180 | 185 | 180 | 181 | 190 | 178 | 161 | 193 | 165 | 170 | 175 | 181 | 165 | 174 | 189 | 190 | 194 | 203 |  | 218 | 210 | 208 | 213 | 215 | 220 | 212 | 4597000
34 | Ashuganj 450 MW CCPP(South) | 265 | 310 | 265 | 270 | 270 | 275 | 300 | 320 | 280 | 275 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 265 | 6816000
| Ashuganj 450 MW CCPP(North) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3600200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 155040
36 | Chandpur 150 MW CCPP | 136 | 138 | 138 | 138 | 138 | 138 | 138 | 139 | 139 | 139 | 137 | 139 | 139 | 137 | 137 | 132 | 130 | 131 |  | 131 | 133 | 129 | 130 | 130 | 131 | 132 | 3237490
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 240 | 240 | 240 | 240 | 240 | 5850000
41 | Haripur 360MW CCPP(HPL) | 191 | 204 | 213 | 211 | 222 | 223 | 219 | 219 | 222 | 224 | 201 | 193 | 194 | 194 | 195 | 180 | 181 | 178 |  | 175 | 175 | 175 | 175 | 172 | 179 | 194 | 4714000
42 | RPCL 210MW CCPP | 53 | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 52 | 53 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 53 | 53 | 53 | 53 | 53 | 53 | 1235520
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 6 | 8 | 19 | 30 | 12 | 16 | 9 | 5 | 3 | 1 | [9 empty] | 102950
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 1011000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 694320
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 71 | 71 | 72 | 72 | 73 | 73 | 72 | 70 | 72 | 64 | 64 | 64 | 63 | 64 | 69 | 68 | 69 | 71 |  | 69 | 71 | 71 | 72 | 72 | 70 | 72 | 1667520
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 75 | 75 | 75 | 75 | 75 | 78 | 81 | 81 | 78 | 78 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1904640
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 88 | 79 | 79 | 79 | 79 | 79 | 79 | 40 | [17 empty] | 0 | 695570
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 422000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232200
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 219168
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 48 | 45 | 48 | 45 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1225200
56 | Shahjahanulla 25 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 517728
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 410 | 410 | 410 | 410 | 411 | 412 | 350 | 350 | 400 | 390 | 370 | 400 | 400 | 317 | 341 | 341 | 338 | 411 |  | 401 | 401 | 400 | 400 | 401 | 400 | 400 | 9325900
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 429453
59 | Tangail Palli Power Gen 22 MW | 24 | 25 | 25 | 24 | 24 | 24 | 25 | 23 | 23 | 25 | 24 | 24 | 24 | 24 | 22 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 594480
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 423648
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 19 |  |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 373536
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 414720
63 | Impoprt (Tripura) | 64 | 64 | 62 | 61 | 58 | 58 | 54 | 43 | 45 | 51 | 70 | 84 | 83 | 86 | 87 | 79 | 83 | 95 |  | 90 | 91 | 91 | 89 | 83 | 79 | 73 | 1754880
64 | Malancha, Ctg. EPZ (United) | 30 | 35 | 32 | 25 | 25 | 30 | 28 | 4 | 2 | 3 | 3 | 5 | 9 | 7 | 4 | 5 | 7 | 9 |  | 7 | 10 | 18 | 25 | 22 | 37 | 40 | 427200
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 459504
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 248760
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 25 |  | 25 | 25 | 26 | 33 | 33 | 33 | 33 | 708800
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 234720
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 6 | 9 | 9 | 9 | 9 | 9 | 106560
71 | Maona 33 MW PP(Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 563200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 26 | 26 | 26 |  | 26 | 26 | 24 | 25 | 25 | 25 | 25 | 679500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 45 | 45 | 45 | 17 | 17 | 17 | 77 | 75 | 35 | 35 | 41 | 62 | 84 | 88 | 55 | 55 | 73 | 104 |  | 117 | 118 | 118 | 117 | 118 | 117 | 75 | 1857240
| Manikgonj 162MW PP(MPGL) |  |  |  |  | 20 | 38 | 69 | 94 | 150 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 108 | 108 | 2831040
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 25 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 25 | 25 | 32 |  | 42 | 42 | 42 | 42 | 42 | 16 | 0 | 634560
79 | Kodda 150MW PP | [6 empty] | 10 | 48 | 115 | 115 | 132 | 132 | 132 | 82 | 64 | 64 | 133 | 150 |  | 150 | 150 | 150 | 100 | 64 |  | 0 | 1589280
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 13 | 42 | 46 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 865166
| Gazipur 100 MW PP | 70 | 17 |  |  | 18 | 39 | 88 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2127600
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24959
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 901061
| Karnaphuli Power Ltd. | 110 | 110 | 68 | 34 | 34 | 35 | 95 | 107 | 85 | 85 | 85 | 93 | 110 | 106 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2397018
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 6 | 11 | 12 | 11 | 11 | 12 | 11 | 12 | 11 | 12 | 11 |  | 11 | 11 | 11 | 12 | 11 | 11 | 12 | 193077
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 72 | 44 | 35 | 34 | 17 | 17 | 17 | 17 | 33 | 53 | 53 | 53 | 70 | 70 | 70 | 60 | 59 | 81 |  | 104 | 104 | 104 | 104 | 104 | 104 | 58 | 1488960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 10 | 10 | 45 | 100 |  | 100 | 100 | 100 | 100 | 100 | 60 | 0 | 789720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1217112
94 | Gagnagar 102 MW PP (Digital Power) | 58 | [6 empty] | 24 | 64 | 84 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 24 | 24 | 1556640
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1212000
96 | Chattogram 108 MW PP (ECPV) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 75 | 76 | 82 | 82 | 75 | 75 | 82 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2002560
97 | katpotti 52 MW | [11 empty] | 11 | 20 | 20 | 20 | 19 | 28 | 51 |  | 51 | 51 | 51 |  |  |  | 0 | 289056
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 1 | 15 | 15 | 28 | 30 | 30 | 30 | 30 | 30 | 40 |  | 30 | 35 | 35 | 40 | 45 |  | 0 | 464402
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1230322
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 163 | 163 | 130 | 163 | 110 | 130 | 130 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3752345
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [10 empty] | 6000
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 835200
104 | Keranigonj 300 MW PP (APR) | [8 empty] | 70 | 130 | 110 | 110 | 100 | 11 |  |  |  | 308 |  | 209 | 250 | 152 | 153 |  |  | 0 | 1385520
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 |  | 30 | 30 | 30 |  |  |  | 0 | 110486
106 | Mymensingh 200 MW PP (United) | 180 | 135 | 115 | 115 | 115 | 120 | 163 | 184 | 194 | 196 | 195 | 195 | 188 | 185 | 191 | 186 | 192 | 185 |  | 185 | 185 | 185 | 195 | 195 | 195 | 195 | 4209600
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 76 |  | 26 | 25 | 25 |  |  |  | 0 | 125712
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 10 | 32 | 63 | 72 | 94 | 96 | 110 | 90 | 68 | 52 | 52 | 60 |  | 131 | 131 | 145 | 130 | 93 | 63 | 18 | 1415376
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2114880
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | 137 | 132 | 115 | 128 | 125 | 122 | 120 | 117 | 123 | 115 | 46 | 86 | 95 | 115 | 110 | 102 | 107 | 108 |  | 113 | 116 | 117 | 133 | 137 | 140 | 143 | 2795127
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 16 | [6 empty] | 20 | 24 | 24 | 30 | 40 | 40 | 40 | 30 | 30 | 55 | 81 |  | 115 | 115 | 115 | 115 | 85 | 45 | 25 | 1035600
| Anwara 300 MW PP (United) |  |  |  |  | 15 | 15 | 45 | 45 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 155 |  | 225 | 225 | 150 | 150 | 150 | 100 | 65 | 2032364
| Juldah unit-2 (Acorn) | 60 | 60 | 60 | 60 | 60 | 80 | 100 | 80 | 100 | 70 | 70 | 90 | 90 | 90 | 90 | 96 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2033280
| Anlima Energy Ltd. | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1267091
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444600
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 6 | 5 | 12 | 6 | 12 | 8 | 15 | 5 | 4 | 1 | [9 empty] | 73033
Chandpur 115(Doreen)
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 |  |  |  |  | 7 | 28 | 27 | 16 | 45 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 981000
120 | Eastern Zone Total | 4645 | 4378 | 4137 | 3935 | 3995 | 4066 | 4444 | 4715 | 5051 | 5311 | 5234 | 5448 | 5550 | 5315 | 5227 | 5152 | 5421 | 6281 |  | 6290 | 6345 | 6156 | 6041 | 5744 | 5186 | 4938 | 125298999
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 |  |  |  | 14 | 35 | 70 | 70 | 94 | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 70 | 93 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1849920
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 0 | 10 | 22 | 36 | 44 | 56 | 54 | 46 | 38 | 21 | 7 | [8 empty] | 0 | 339840
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 220 | 221 | 220 | 217 | 221 | 200 | 220 | 220 | 220 | 215 | 190 | 190 | 190 | 190 | 190 | 190 | 221 |  | 220 | 220 | 220 | 201 | 210 | 220 | 131 | 4941027
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 269861
| Bhola 225 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 65 | 65 | 58 | 65 | 58 | 65 | 65 | 61 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 64 | 62 | 65 | 65 | 1710067
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 17 | 16 | 16 | 17 | 16 | 14 | 16 | 16 | 16 | 16 | 18 | 17 | 15 | 14 | 16 | 21 |  | 23 | 24 | 24 | 26 | 26 | 24 | 22 | 425600
141 | Noapara 100 MW PP (Bangla Trac) | [8 empty] | 23 | 27 | 20 | 10 | 17 | 10 |  |  |  | 35 |  | 95 | 98 | 50 | 50 |  |  | 0 | 407040
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [26 empty] | 1408
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 390 | 389 | 388 | 388 | 389 | 388 | 436 | 436 | 436 | 436 | 436 | 436 | 435 | 436 | 437 | 436 | 436 | 423 |  | 423 | 423 | 423 | 423 | 423 | 423 | 424 | 10114909
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 320 | 290 | 280 | 270 | 270 | 270 | 270 | 290 | 310 | 300 | 320 | 320 | 340 | 340 | 340 | 350 | 340 | 440 |  | 540 | 480 | 510 | 560 | 530 | 510 | 400 | 9868600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 198 |  | 200 | 199 | 200 | 199 | 200 | 200 | 200 | 4852300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [9 empty] | 14 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 699472
| Sirajgonj 6.55 MW Solar | [7 empty] | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 9600
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 137 | 152 | 163 | 173 | 179 | 185 | 184 | 175 | 177 | 178 | 177 | 178 | 178 | 169 | 150 | 159 | 186 | 185 |  | 185 | 185 | 185 | 184 | 181 | 181 | 182 | 4446300
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 349 | 410 | 410 | 411 | 373 | 414 | 295 | 414 | 353 | 414 | 417 | 418 | 418 | 352 | 354 | 356 | 414 | 414 |  | 415 | 416 | 414 | 415 | 384 | 408 | 414 | 9447563
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 18 | 18 |  | 28 | 28 | 28 | 28 | 16 |  |  | 128268
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520800
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 241398
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [5 empty] | 8 | 50 | 50 | 50 | 50 | 43 | 43 | 43 | 43 | 25 | 25 | 25 | 43 |  | 43 | 43 | 43 | 43 | 43 |  | 0 | 657447
167 | Katakhali 50 MW Peaking PP | [9 empty] | 5 | 16 | 16 | 16 | 20 | 24 | 24 | 24 | 28 |  | 32 | 32 | 32 | 32 | 13 |  |  | 266368
168 | Santahar 50 MW Peaking PP | [10 empty] | 6 | 29 | 29 | 29 | 29 | 29 | 28 | 29 |  | 29 | 29 | 34 | 35 | 35 |  |  | 326760
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 34 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1186171
170 | Chapainawabganj 100 MW Peaking PP | 34 | [11 empty] | 48 | 50 | 50 | 50 | 99 | 100 |  | 100 | 100 | 100 | 100 | 58 |  |  | 791136
171 | Baghabari 200 MW PP (Paramount) | [8 empty] | 20 | 20 | 39 | 50 | 50 | 10 |  |  | 10 | 80 |  | 100 | 70 | 50 | 20 |  |  | 0 | 435118
| Bagura 113 MW PP (Confidence)-2 | 35 |  |  |  |  | 1 | 18 | 31 | 52 | 86 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 110 | 113 | 113 | 113 | 113 | 70 | 35 | 1625472
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 35 | 35 | 35 | 60 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 100 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2316192
173 | Rangpur 20 MW GTPP | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 53000
175 | Saidpur 20 MW GTPP | [17 empty] | 10 |  | 8 | [6 empty] | 17000
176 | Rangpur 113 MW PP (Confidence) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 75 | 70 | 111 | 111 |  | 111 | 111 | 111 | 111 | 111 | 112 | 112 | 2617200
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 6680
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 5 | 9 |  |  |  | 9 | [10 empty] | 0 | 9854
178