## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-01-07 | Friday
|  | Date (day): | 2022-01-07 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11239.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12210 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-01-06 | 2022-01-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 100 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 0 | 0 | 365 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 228 | 250 | 200 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 180 | 180 | 180 | 180 | 270 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 11 | 11 | 11 |  | 89 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 40 | 40 |  | 11 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 100 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 34 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 20 | 20 |  | 13 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 52 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 280 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 197 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 60 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 30 | 0
| Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 55 | 55 | 55 | 55
| Dhaka area Total |  |  |  |  | 6178 | 5560 | 1903 | 2492 | 2555 | 2625 | 2115 | 890
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 17 | 25 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 46 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 78 | 40 | 40 |  | 190 | Low Water Level & Unit 4 & 5 U/M.
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 52 | 70 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 100 | 100
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 20 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 10 | 5 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 79 | 84 | 90 | 90 |  | 18 | Engine problem
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 50 | 100 | 300 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 54 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 104 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 870 | 971 | 1282 | 1301 | 180 | 903
60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 150 | 200
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 255 | 220 | 220 | 220 | 140 |  | ST S/D due to gas shortage.
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 270 | 270 | 270 |  |  | FGMO
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 30 | 30 | 15 |  | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 55 | 55 | 55
66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 8 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 127 | 145 | 150 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 122 | 131 | 130 | 131 |  | 32 | Machine problem.
71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 21 | 22 | 22
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 95 | 138 | 163
74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 15 | 25 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 0 | 200
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 85 | 113 | 113 | 113
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1283 | 1402 | 1903 | 2179 | 660 | 69
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 44 | 46 | 100 | 100 | 102 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 175 | 173 | 200 | 200
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 94 | 112 | 115 | 115
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 22 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 356 | 373 | 510.6 | 459 | 102 | 8
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maintenance
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 51 | 51 | 51
| Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 68 | 71 | 72 | 72
96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 81 | 81
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 190 | 190 | 190 | 190 |  | 41 | Machine problem
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 24 | 24 | 24
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 305 | 330 | 330
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1330 | 1367 | 1392 | 1392 | 0 | 989
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 663 | 711 | 676 | 724
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 32 | 0 | 35 |  | 19 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 10 | 0 | 40 |  | 69 | Engine problem
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 10 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 96 | 105 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 15 | 50 | 0 | 100
| Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 0 | 0 | 71 | 0 | 11 | 0
| Khulna Area Total |  |  |  |  | 2248 | 2129 | 849 | 918 | 842 | 1324 | 410 | 88
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 20 | 24 | 24 |  | 9 | Engine problem
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 91 | 91 | 91 | 103 |  | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 0 | 0 | 620 | 620
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 200 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 0 | 150
| Barisal Area Total |  |  |  |  | 2046 | 2046 | 373 | 393 | 1056 | 1226 | 187 | 9
121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 30 | 30 |  | 41 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 25 | 25 |  | 25 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 43 | 43 |  | 7 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 155 | 173 | 200 | 200 |  |  | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 336 | 394 | 400 | 400 |  |  | FGMO
131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Under maint
132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 43 | 43 | 52
136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 50 | 100 | 90 | 100
137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 50 | 200 | 200
138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 90 | 113 | 113
139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 95 | 113 | 113
140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 856 | 1111 | 1378 | 1391 | 600 | 141
141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74 |  | Coal shortage
143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 112 | 113 | 113
146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
| Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 316 | 311 | 321 | 313 | 74 | 210
| Total |  |  |  |  | 22031 | 20934 | 8136 | 9338 | 11239.6 | 12210 | 4328 | 3307
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7781.3896 | 8931 | 10749.7181 | 11677.8229
A. |  | 2022-01-06 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 9338 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5805 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9338 | MW
3 | Day peak Generation : |  |  | 8136 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8931 | MW
4 | Evening peak Generation : |  |  | 9338 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 184.5887 | MKWHr | By Solar | 0.85107 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 96.894 | MKWHr |  | By Oil: | 60.9797 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 6.9638 | MKWHr |  | By Hydro: | 1.9843 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4328 | MW | Dhaka | 3267 | 3267 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3307 | MW | Chittagong | 991 | 991 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 7635 | MW | Khulna | 1083 | 1083 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 737.42 | MMCFD |  |  | Rajshahi | 900 | 900 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 98411612.702 | ii) Oil : | Taka | 435684511.56 | Comilla | 755 | 755 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 35571732 | Total | Taka | 569667856.262 | Mymensingh | 767 | 767 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.649 | MKWHr. | Sylhet | 340 | 340 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -222 | MW (E to W) at | 19:00 | hrs | Barisal | 247 | 247 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -324 | MW at | 18:30 | hrs | Rangpur | 581 | 581 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.5° C |  |  | Total | 8931 | 8931 |  | 0
B. |  | 2022-01-07 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 26.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12210 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
4 | Reserve(Generation end) |  |  |  | 3710 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 168.0235 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5848 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.9651 | MKWHr. | ii) HVDC Flow at Peak Time |  | 711 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9507 | MKWHr. | iii) Maximum HVDC Flow : |  | 711 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.6 |  | (b) Today: | 97.48 |  | (c) Rule Curve: |  | 101.86
.

## YesterdayGen
2022-01-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 155 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 67 | 46 | 21 | 34 | 0 | 0 | 80 | 240 | 265 | 0 | 16 | 129 | 29 | 56 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 72 | 50 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 280 | 22 | 11 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 10 | 0 | 142 | 0 | 8 | 105 | 17 | 0 | 0 | 54 | 17 | 0 | 8 | 0 | 400 | 0 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 55 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 205 | 0 | 315 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4717 | 1995 | 6712 | 2488 | 484 | 1628 | 0 | 1451 | 500 | 86 | 0 | 3 | 72 | 0 | 0 | 97.62
2:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 153 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 50 | 41 | 21 | 34 | 0 | 0 | 80 | 240 | 265 | 0 | 16 | 127 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 70 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 285 | 21 | 8 | 0 | 95 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 142 | 0 | 8 | 35 | 17 | 0 | 0 | 54 | 17 | 0 | 8 | 0 | 400 | 0 | 0 | 108 | 51 | 0 | 17 | 0 | 0 | 55 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 168 | 0 | 296 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 300 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4332 | 1910 | 6242 | 2447 | 476 | 1590 | 0 | 1070 | 500 | 86 | 0 | 3 | 70 | 0 | 0 | 97.62
3:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 149 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 51 | 46 | 21 | 36 | 0 | 0 | 80 | 240 | 265 | 0 | 16 | 129 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 68 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 280 | 21 | 8 | 0 | 45 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 145 | 0 | 8 | 17 | 17 | 0 | 0 | 54 | 17 | 0 | 8 | 0 | 400 | 0 | 0 | 17 | 51 | 0 | 17 | 0 | 0 | 55 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 162 | 0 | 309 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 300 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4156 | 1881 | 6037 | 2444 | 477 | 1575 | 0 | 884 | 500 | 86 | 0 | 3 | 68 | 0 | 0 | 97.61
4:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 162 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 51 | 46 | 21 | 38 | 0 | 0 | 80 | 150 | 265 | 0 | 16 | 132 | 29 | 56 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 68 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 73 | 81 | 0 | 190 | 18 | 0 | 10 | 285 | 21 | 5 | 0 | 45 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 138 | 0 | 8 | 17 | 17 | 0 | 0 | 54 | 17 | 0 | 8 | 0 | 400 | 0 | 0 | 17 | 51 | 0 | 17 | 0 | 0 | 55 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 297 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 260 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4062 | 1800 | 5862 | 2334 | 476 | 1584 | 0 | 851 | 460 | 86 | 0 | 3 | 68 | 0 | 0 | 97.61
5:00 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 164 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 9 | 16 | 33 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 56 | 46 | 21 | 40 | 0 | 0 | 80 | 150 | 265 | 0 | 16 | 132 | 29 | 56 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 63 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 73 | 81 | 0 | 190 | 18 | 0 | 10 | 290 | 21 | 5 | 0 | 45 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 133 | 0 | 8 | 17 | 17 | 0 | 2 | 39 | 17 | 0 | 8 | 10 | 350 | 1 | 0 | 17 | 51 | 0 | 17 | 0 | 0 | 55 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 325 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 260 | 180 | 0 | 0 | 0 | 0 | 0 |  | 3974 | 1831 | 5805 | 2247 | 476 | 1621 | 0 | 849 | 460 | 86 | 0 | 3 | 63 | 0 | 0 | 97.6
6:00 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 171 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 0 | 16 | 0 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 46 | 21 | 40 | 0 | 0 | 80 | 150 | 275 | 0 | 16 | 130 | 29 | 56 | 0 | 51 | 0 | 0 | 8 | 16 | 11 | 33 | 9 | 61 | 53 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 305 | 21 | 5 | 0 | 45 | 0 | 0 | 69 | 0 | 0 | 0 | 80 | 0 | 128 | 0 | 8 | 20 | 17 | 0 | 16 | 36 | 20 | 0 | 23 | 10 | 350 | 17 | 0 | 20 | 76 | 0 | 17 | 0 | 0 | 0 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 379 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 230 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4038 | 1861 | 5899 | 2187 | 476 | 1698 | 0 | 959 | 429 | 86 | 0 | 3 | 61 | 0 | 0 | 97.6
7:00 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 168 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 6 | 16 | 16 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 46 | 21 | 38 | 0 | 0 | 80 | 180 | 305 | 0 | 16 | 129 | 29 | 56 | 0 | 51 | 0 | 0 | 8 | 16 | 11 | 33 | 9 | 64 | 53 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 110 | 0 | 40 | 78 | 0 | 190 | 18 | 0 | 10 | 280 | 21 | 5 | 0 | 90 | 0 | 0 | 130 | 0 | 12 | 0 | 70 | 0 | 135 | 0 | 8 | 70 | 17 | 0 | 16 | 36 | 74 | 0 | 46 | 10 | 300 | 17 | 0 | 144 | 116 | 0 | 17 | 1 | 0 | 25 |  | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 162 | 0 | 375 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 35 | 180 | 150 | 0 | 0 | 0 | 1 | 0 |  | 4433 | 1959 | 6392 | 2165 | 561 | 1611 | 0 | 1521 | 379 | 86 | 0 | 3 | 64 | 2 | 0 | 97.59
8:00 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 170 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 9 | 20 | 0 | 0 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 85 | 47 | 21 | 13 | 0 | 0 | 80 | 275 | 300 | 0 | 16 | 127 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 25 | 9 | 71 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 78 | 0 | 190 | 18 | 0 | 10 | 310 | 21 | 5 | 0 | 173 | 0 | 0 | 180 | 0 | 38 | 3 | 90 | 0 | 130 | 0 | 19 | 90 | 20 | 1 | 15 | 36 | 97 | 0 | 52 | 80 | 370 | 27 | 0 | 162 | 116 | 0 | 17 | 4 | 0 | 0 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 405 | 31 | 0 | 70 | 0 | 112 | 0 | 1 | 80 | 0 | 190 | 0 | 0 | 0 | 11 | 0 |  | 4985 | 2112 | 7097 | 2347 | 663 | 1707 | 0 | 2001 | 199 | 86 | 0 | 3 | 71 | 20 | 0 | 97.58
9:00 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 162 |  | 0 | 180 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 94 | 0 | 6 | 0 | 0 | 0 | 35 | 55 | 17 | 16 | 25 | 0 | 20 | 17 | 25 | 0 | 46 | 40 | 0 | 100 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 46 | 21 | 5 | 0 | 0 | 80 | 275 | 300 | 0 | 16 | 130 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 20 | 9 | 86 | 53 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 71 | 78 | 0 | 190 | 18 | 0 | 10 | 290 | 21 | 2 | 0 | 242 | 0 | 0 | 185 | 0 | 138 | 13 | 90 | 0 | 130 | 0 | 70 | 90 | 70 | 2 | 65 | 35 | 110 | 0 | 75 | 100 | 320 | 53 | 0 | 162 | 116 | 0 | 17 | 16 | 0 | 31 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 176 | 0 | 311 | 101 | 0 | 73 | 0 | 112 | 0 | 1 | 95 | 0 | 187 | 0 | 0 | 2 | 37 | 0 |  | 5493 | 2132 | 7625 | 2298 | 663 | 1607 | 0 | 2612 | 199 | 86 | 0 | 3 | 86 | 71 | 0 | 97.58
10:00 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 181 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 16 | 11 | 0 | 0 | 0 | 35 | 55 | 17 | 16 | 25 | 6 | 20 | 33 | 25 | 0 | 46 | 40 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 4 | 84 | 46 | 18 | 5 | 0 | 0 | 80 | 255 | 300 | 0 | 16 | 127 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 15 | 9 | 90 | 51 | 0 | 20 | 1 | 43 | 0 | 48 | 0 | 130 | 0 | 71 | 78 | 0 | 190 | 18 | 0 | 10 | 300 | 21 | 2 | 0 | 265 | 0 | 0 | 185 | 0 | 149 | 18 | 90 | 0 | 123 | 0 | 104 | 90 | 86 | 4 | 65 | 35 | 110 | 0 | 114 | 100 | 320 | 54 | 0 | 162 | 116 | 0 | 17 | 23 | 0 | 56 |  | 662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 92 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 30 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 335 | 105 | 0 | 92 | 0 | 112 | 0 | 2 | 95 | 0 | 180 | 0 | 0 | 3 | 57 | 0 |  | 5560 | 2226 | 7786 | 2146 | 662 | 1615 | 0 | 2830 | 200 | 86 | 0 | 49 | 90 | 108 | 0 | 97.58
11:00 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 215 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 48 | 11 | 0 | 0 | 0 | 35 | 55 | 17 | 16 | 25 | 9 | 20 | 33 | 52 | 0 | 46 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 10 | 82 | 46 | 18 | 3 | 0 | 0 | 80 | 200 | 265 | 0 | 16 | 122 | 29 | 53 | 0 | 51 | 0 | 0 | 34 | 16 | 8 | 15 | 9 | 85 | 46 | 0 | 20 | 2 | 42 | 0 | 48 | 0 | 110 | 0 | 71 | 78 | 0 | 190 | 18 | 0 | 10 | 280 | 21 | 0 | 0 | 265 | 0 | 0 | 173 | 0 | 149 | 20 | 76 | 0 | 128 | 0 | 104 | 90 | 105 | 4 | 100 | 35 | 110 | 0 | 108 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 28 | 0 | 55 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 92 | 14 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 154 | 0 | 298 | 90 | 0 | 93 | 0 | 112 | 0 | 3 | 95 | 0 | 190 | 0 | 1 | 4 | 68 | 0 |  | 5623 | 2238 | 7861 | 2037 | 663 | 1579 | 0 | 2973 | 199 | 86 | 0 | 110 | 85 | 129 | 0 | 97.57
12:00 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 228 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 16 | 12 | 0 | 0 | 0 | 35 | 55 | 17 | 16 | 25 | 9 | 20 | 17 | 52 | 0 | 46 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 79 | 46 | 18 | 3 | 0 | 0 | 80 | 255 | 285 | 0 | 16 | 122 | 29 | 52 | 0 | 51 | 0 | 0 | 25 | 16 | 11 | 15 | 9 | 88 | 44 | 0 | 20 | 2 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 79 | 0 | 190 | 18 | 0 | 10 | 285 | 21 | 2 | 0 | 275 | 0 | 0 | 175 | 0 | 149 | 20 | 90 | 0 | 127 | 0 | 94 | 90 | 105 | 4 | 50 | 35 | 110 | 0 | 85 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 29 | 0 | 55 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 17 | 16 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 336 | 96 | 0 | 70 | 15 | 112 | 0 | 4 | 70 | 0 | 221 | 0 | 17 | 4 | 71 | 0 |  | 5742 | 2394 | 8136 | 2187 | 663 | 1725 | 0 | 2901 | 200 | 86 | 0 | 152 | 88 | 134 | 0 | 97.57
13:00 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 234 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 16 | 11 | 0 | 0 | 0 | 35 | 55 | 25 | 16 | 25 | 9 | 20 | 25 | 52 | 0 | 46 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 80 | 46 | 18 | 11 | 0 | 0 | 100 | 265 | 290 | 0 | 16 | 122 | 29 | 56 | 0 | 51 | 0 | 0 | 30 | 19 | 11 | 15 | 9 | 94 | 45 | 0 | 20 | 2 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 78 | 0 | 190 | 18 | 0 | 10 | 300 | 21 | 2 | 0 | 277 | 0 | 0 | 175 | 0 | 149 | 18 | 90 | 0 | 125 | 0 | 103 | 90 | 105 | 4 | 80 | 35 | 110 | 0 | 85 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 31 | 0 | 55 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 91 | 17 | 16 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 377 | 105 | 0 | 70 | 15 | 111 | 0 | 4 | 70 | 0 | 215 | 0 | 17 | 4 | 68 | 0 |  | 5880 | 2447 | 8327 | 2244 | 663 | 1792 | 0 | 2962 | 199 | 86 | 0 | 156 | 94 | 131 | 0 | 97.56
14:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 238 |  | 0 | 180 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 0 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 25 | 25 | 0 | 40 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 81 | 46 | 18 | 9 | 0 | 0 | 120 | 220 | 265 | 0 | 16 | 122 | 29 | 56 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 15 | 9 | 96 | 45 | 0 | 20 | 2 | 43 | 0 | 51 | 0 | 110 | 0 | 66 | 81 | 0 | 165 | 18 | 0 | 10 | 275 | 21 | 2 | 0 | 277 | 0 | 0 | 184 | 0 | 149 | 16 | 90 | 0 | 135 | 0 | 80 | 90 | 105 | 3 | 65 | 35 | 110 | 0 | 85 | 100 | 320 | 104 | 0 | 162 | 116 | 0 | 17 | 23 | 0 | 55 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 17 | 16 | 0 | 0 | 0 | 50 | 0 | 41 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 164 | 0 | 326 | 90 | 0 | 35 | 15 | 112 | 0 | 4 | 35 | 0 | 219 | 0 | 17 | 3 | 60 | 0 |  | 5663 | 2293 | 7956 | 2186 | 663 | 1672 | 0 | 2822 | 199 | 80 | 0 | 127 | 96 | 111 | 0 | 97.56
15:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 242 |  | 0 | 180 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 102 | 0 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 25 | 25 | 0 | 35 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 46 | 18 | 3 | 0 | 0 | 120 | 220 | 270 | 0 | 16 | 121 | 29 | 56 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 15 | 9 | 84 | 44 | 0 | 20 | 1 | 43 | 0 | 50 | 0 | 110 | 0 | 68 | 81 | 0 | 165 | 18 | 0 | 10 | 290 | 21 | 2 | 0 | 275 | 0 | 0 | 184 | 0 | 149 | 13 | 90 | 0 | 133 | 0 | 80 | 90 | 68 | 2 | 65 | 35 | 110 | 0 | 85 | 30 | 350 | 75 | 0 | 162 | 116 | 0 | 17 | 17 | 0 | 55 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 15 | 16 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 159 | 0 | 305 | 60 | 0 | 35 | 15 | 112 | 0 | 2 | 35 | 0 | 219 | 0 | 17 | 2 | 42 | 4 |  | 5531 | 2227 | 7758 | 2216 | 663 | 1661 | 0 | 2645 | 199 | 75 | 0 | 136 | 84 | 79 | 0 | 97.55
16:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 240 |  | 0 | 180 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 60 | 0 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 25 | 25 | 0 | 38 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 46 | 21 | 2 | 0 | 0 | 120 | 220 | 270 | 0 | 16 | 125 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 21 | 11 | 15 | 9 | 82 | 44 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 110 | 0 | 40 | 81 | 0 | 165 | 18 | 0 | 10 | 295 | 21 | 5 | 0 | 277 | 0 | 0 | 183 | 0 | 137 | 8 | 50 | 0 | 100 | 0 | 60 | 90 | 34 | 1 | 30 | 35 | 110 | 0 | 85 | 20 | 350 | 35 | 0 | 162 | 116 | 0 | 17 | 9 | 0 | 55 |  | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 91 | 13 | 16 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 162 | 0 | 409 | 35 | 0 | 35 | 15 | 106 | 0 | 1 | 35 | 0 | 222 | 0 | 17 | 0 | 20 | 13 |  | 5235 | 2290 | 7525 | 2200 | 664 | 1768 | 0 | 2358 | 199 | 78 | 0 | 137 | 82 | 39 | 0 | 97.55
17:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 254 |  | 0 | 180 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 60 | 0 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 25 | 25 | 0 | 45 | 40 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 46 | 21 | 2 | 0 | 0 | 100 | 220 | 335 | 0 | 16 | 125 | 29 | 55 | 0 | 51 | 0 | 0 | 34 | 21 | 11 | 32 | 9 | 85 | 46 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 130 | 0 | 67 | 81 | 0 | 165 | 18 | 0 | 10 | 300 | 21 | 8 | 0 | 277 | 0 | 0 | 192 | 0 | 127 | 1 | 50 | 0 | 100 | 0 | 60 | 90 | 34 | 0 | 30 | 35 | 110 | 0 | 85 | 20 | 400 | 22 | 0 | 162 | 116 | 0 | 17 | 2 | 0 | 55 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 91 | 15 | 16 | 0 | 0 | 0 | 50 | 4 | 65 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 430 | 35 | 0 | 35 | 15 | 112 | 0 | 0 | 35 | 0 | 222 | 0 | 17 | 0 | 3 | 0 |  | 5414 | 2308 | 7722 | 2353 | 663 | 1830 | 0 | 2346 | 198 | 85 | 0 | 156 | 85 | 6 | 0 | 97.54
18:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 250 |  | 0 | 180 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 100 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 45 | 0 | 46 | 40 | 0 | 0 | 14 | 0 | 0 | 0 | 0 |  | 22 | 0 | 45 | 10 | 84 | 46 | 21 | 4 | 0 | 0 | 100 | 220 | 270 | 0 | 16 | 132 | 29 | 55 | 0 | 51 | 0 | 50 | 43 | 21 | 11 | 30 | 9 | 99 | 47 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 130 | 0 | 64 | 81 | 0 | 190 | 18 | 0 | 10 | 295 | 24 | 11 | 20 | 280 | 190 | 75 | 183 | 98 | 149 | 0 | 90 | 10 | 120 | 0 | 112 | 105 | 79 | 0 | 100 | 35 | 110 | 17 | 105 | 100 | 375 | 51 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 54 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 5 | 0 | 91 | 20 | 16 | 0 | 0 | 0 | 50 | 5 | 100 | 0 | 34 | 32 | 28 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 8 | 200 | 0 | 415 | 96 | 20 | 70 | 50 | 112 | 0 | 0 | 95 | 0 | 222 | 0 | 35 | 0 | 0 | 0 |  | 6464 | 2680 | 9144 | 2340 | 711 | 1813 | 411 | 3073 | 199 | 86 | 0 | 412 | 99 | 0 | 0 | 97.54
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 250 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 100 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 51 | 0 | 38 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 20 | 84 | 46 | 21 | 10 | 0 | 0 | 80 | 220 | 270 | 0 | 8 | 131 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 25 | 9 | 95 | 46 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 305 | 24 | 11 | 20 | 280 | 197 | 60 | 173 | 100 | 149 | 0 | 90 | 0 | 145 | 0 | 112 | 105 | 105 | 0 | 100 | 35 | 110 | 0 | 113 | 100 | 400 | 104 | 0 | 162 | 104 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 10 | 0 | 91 | 20 | 16 | 0 | 0 | 0 | 50 | 20 | 100 | 0 | 34 | 32 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 173 | 0 | 394 | 105 | 50 | 90 | 50 | 112 | 0 | 0 | 95 | 0 | 220 | 0 | 35 | 0 | 0 | 0 |  | 6605 | 2733 | 9338 | 2318 | 711 | 1831 | 437 | 3224 | 199 | 78 | 0 | 445 | 95 | 0 | 0 | 97.52
19:30 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 256 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 100 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 51 | 0 | 38 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 84 | 46 | 21 | 14 | 0 | 0 | 80 | 220 | 270 | 0 | 8 | 130 | 29 | 55 | 0 | 51 | 0 | 50 | 25 | 21 | 11 | 25 | 9 | 93 | 47 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 300 | 24 | 11 | 20 | 280 | 133 | 60 | 173 | 100 | 149 | 0 | 90 | 0 | 142 | 0 | 112 | 105 | 105 | 0 | 100 | 35 | 110 | 0 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 10 | 0 | 91 | 20 | 16 | 0 | 0 | 0 | 45 | 20 | 100 | 0 | 34 | 32 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 411 | 105 | 50 | 113 | 50 | 112 | 0 | 0 | 95 | 0 | 221 | 0 | 35 | 0 | 0 | 0 |  | 6516 | 2767 | 9283 | 2314 | 711 | 1854 | 363 | 3228 | 199 | 78 | 0 | 443 | 93 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 254 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 100 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 51 | 0 | 38 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 84 | 46 | 21 | 20 | 0 | 0 | 80 | 220 | 270 | 0 | 8 | 131 | 29 | 55 | 0 | 51 | 0 | 50 | 25 | 21 | 11 | 30 | 9 | 88 | 46 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 70 | 81 | 0 | 190 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 280 | 105 | 60 | 174 | 99 | 149 | 0 | 90 | 0 | 145 | 0 | 112 | 105 | 85 | 0 | 80 | 35 | 110 | 0 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 0 | 91 | 21 | 16 | 0 | 0 | 0 | 50 | 20 | 100 | 0 | 34 | 32 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 171 | 0 | 388 | 105 | 50 | 113 | 67 | 112 | 0 | 0 | 113 | 0 | 220 | 0 | 35 | 0 | 0 | 0 |  | 6424 | 2781 | 9205 | 2320 | 711 | 1835 | 314 | 3217 | 199 | 78 | 0 | 443 | 88 | 0 | 0 | 97.53
21:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 253 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 82 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 51 | 0 | 35 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 84 | 46 | 21 | 27 | 0 | 0 | 80 | 220 | 270 | 0 | 8 | 131 | 29 | 55 | 0 | 51 | 0 | 50 | 25 | 21 | 11 | 33 | 9 | 91 | 50 | 0 | 22 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 280 | 62 | 60 | 184 | 70 | 149 | 0 | 90 | 0 | 143 | 0 | 112 | 105 | 34 | 0 | 30 | 35 | 110 | 0 | 113 | 50 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 91 | 22 | 16 | 0 | 0 | 0 | 50 | 20 | 100 | 0 | 34 | 32 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 179 | 0 | 380 | 105 | 0 | 113 | 67 | 112 | 0 | 0 | 113 | 0 | 220 | 0 | 35 | 0 | 0 | 0 |  | 6204 | 2718 | 8922 | 2335 | 711 | 1834 | 192 | 3065 | 199 | 75 | 0 | 420 | 91 | 0 | 0 | 97.52
22:00 | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 233 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 32 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 13 | 25 | 9 | 20 | 22 | 51 | 0 | 40 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 84 | 46 | 21 | 30 | 0 | 0 | 80 | 220 | 270 | 0 | 8 | 130 | 29 | 55 | 0 | 51 | 0 | 50 | 8 | 21 | 11 | 33 | 9 | 86 | 50 | 0 | 22 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 280 | 0 | 25 | 185 | 0 | 149 | 0 | 90 | 0 | 143 | 0 | 112 | 105 | 17 | 0 | 16 | 54 | 68 | 0 | 113 | 20 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 91 | 22 | 16 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 34 | 32 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 176 | 0 | 344 | 105 | 0 | 113 | 67 | 112 | 0 | 0 | 113 | 0 | 220 | 0 | 35 | 0 | 0 | 0 |  | 5845 | 2663 | 8508 | 2317 | 711 | 1771 | 25 | 2974 | 199 | 80 | 0 | 345 | 86 | 0 | 0 | 97.52
23:00 | 0 | 0 | 150 | 0 | 122 | 0 | 0 | 0 | 213 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 46 | 21 | 34 | 0 | 0 | 80 | 220 | 275 | 28 | 8 | 131 | 29 | 55 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 75 | 50 | 0 | 22 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 70 | 81 | 0 | 190 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 280 | 0 | 0 | 184 | 0 | 139 | 0 | 90 | 0 | 142 | 0 | 65 | 105 | 17 | 0 | 0 | 54 | 68 | 0 | 55 | 20 | 402 | 70 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 91 | 20 | 16 | 0 | 0 | 0 | 50 | 0 | 42 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 171 | 0 | 347 | 70 | 0 | 113 | 15 | 112 | 0 | 0 | 113 | 0 | 220 | 0 | 17 | 0 | 0 | 0 |  | 5422 | 2407 | 7829 | 2332 | 711 | 1736 | 0 | 2595 | 199 | 82 | 0 | 99 | 75 | 0 | 0 | 97.51
24:00 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 203 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 37 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 46 | 21 | 34 | 0 | 0 | 80 | 220 | 260 | 32 | 8 | 133 | 29 | 10 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 69 | 50 | 0 | 0 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 280 | 21 | 11 | 0 | 285 | 0 | 0 | 193 | 0 | 110 | 0 | 90 | 0 | 137 | 0 | 40 | 105 | 17 | 0 | 0 | 54 | 68 | 0 | 55 | 20 | 400 | 53 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 170 | 0 | 342 | 35 | 0 | 70 | 0 | 112 | 0 | 0 | 113 | 0 | 220 | 0 | 17 | 0 | 0 | 0 |  | 5168 | 2086 | 7254 | 2195 | 539 | 1685 | 0 | 2440 | 199 | 77 | 0 | 50 | 69 | 0 | 0 | 97.51
KWH | 0 | 0 | 1306000 | 0 | 5373664 | 0 | 0 | 0 | 4908000 |  | 0 | 4185750 | 0 | 0 | 0 | 794016 | 0 | 0 | 0 | 0 | 1676592 | 506400 | 166421 | 0 | 0 | 0 | 877320 | 1336691 | 744978 | 382500 | 600000 | 199260 | 532200 | 663200 | 580320 | 0 | 1008300 | 976000 | 0 | 1000000 | 146944 | 0 | 0 | 0 | 0 |  | 529920 | 0 | 230121 | 47880 | 1862400 | 1106880 | 477120 | 483240 | 0 | 0 | 2103780 | 5487000 | 6812000 | 60000 | 384727 | 3059620 | 666936 | 1300800 | 0 | 1251568 | 0 | 236680 | 516557 | 456588 | 244980 | 627000 | 245630 | 1950720 | 1159680 | 0 | 468324 | 9150 | 1012000 | 0 | 1211400 | 0 | 3511472 | 0 | 1609728 | 1921920 | 0 | 4503980 | 423000 | 0 | 251640 | 7183500 | 532948 | 147024 | 45504 | 5304216 | 493900 | 280898 | 3787200 | 330805 | 2408400 | 132300 | 1617600 | 25920 | 3218313 | 0 | 1562400 | 1998000 | 1313927 | 27000 | 998618 | 1038107 | 1970460 | 18240 | 1781640 | 1191360 | 8878200 | 1422720 | 0 | 3350880 | 2480236 | 0 | 445680 | 180589 | 0 | 1280520 |  | 14965090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216960 | 19456 | 0 | 2220104 | 387800 | 201216 | 0 | 0 | 0 | 613005 | 58710 | 866168 | 0 | 420983 | 359823 | 708960 | 0 | 522720 | 0 | 190386 | 0 | 0 | 4855000 | 0 | 0 | 0 | 0 | 0 | 0 | 273541 | 33600 | 4322445 | 0 | 8419672 | 1472640 | 102036 | 1374624 | 435168 | 2567856 | 0 | 29291 | 1443168 | 2108800 | 4930991 | 0 | 340800 | 27780 | 444960 | 18816 |  | 129636102 | 54952569 | 184588671 | 55765297 | 14965090 | 41128741 | 1286743 | 56585587 | 6963800 | 1984300 | 0 | 3107323 | 1950720 | 851070 | 0
Fuel Cost | 0 | 0 | 1906760 | 0 | 5964767.04 | 0 | 0 | 0 | 5055240 |  | 0 | 4562467.5 | 0 | 0 | 0 | 6717375.36 | 0 | 0 | 0 | 0 | 15290519.04 | 4982976 | 1534401.62 | 0 | 0 | 0 | 6404436 | 10332621.43 | 7345483.08 | 286875 | 450000 | 0 | 0 | 0 | 5611694.4 | 0 | 272241 | 263520 | 0 | 1810000 | 1365109.76 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2232173.7 | 457254 | 16202880 | 8766489.6 | 601171.2 | 1435222.8 | 0 | 0 | 3092556.6 | 4060380 | 6812000 | 55200 | 496297.83 | 3518563 | 753637.68 | 1821120 | 0 | 2140181.28 | 0 | 2390468 | 4933119.35 | 579866.76 | 183735 | 1097250 | 184222.5 | 14630400 | 1229260.8 | 0 | 594771.48 | 145851 | 1659680 | 0 | 2156292 | 0 | 4003078.08 | 0 | 3171164.16 | 3670867.2 | 0 | 7791885.4 | 926370 | 0 | 513345.6 | 7255335 | 399711 | 111738.24 | 774023.04 | 40099872.96 | 8386422 | 4696614.56 | 19693440 | 5531059.6 | 23698656 | 1546587 | 13183440 | 281232 | 22689106.65 | 0 | 14249088 | 18881100 | 11444304.17 | 0 | 7549552.08 | 9041911.97 | 17320343.4 | 182035.2 | 15268654.8 | 7934457.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 86198918.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2275910.4 | 203898.88 | 0 | 2508717.52 | 601090 | 1963868.16 | 0 | 0 | 0 | 6031969.2 | 596493.6 | 7665586.8 | 0 | 5691690.16 | 3486684.87 | 6869822.4 | 0 | 1003622.4 | 0 | 144122.202 | 0 | 0 | 26314100 | 0 | 0 | 0 | 0 | 0 | 0 | 410311.5 | 571536 | 5057260.65 | 0 | 8335475.28 | 15374361.6 | 1735632.36 | 13045181.76 | 4107985.92 | 19926562.56 | 0 | 323665.55 | 10665011.52 | 9257632 | 0 | 0 | 0 | 0 | 0 | 0 |  | 432681927.52 | 240367111.692 | 673049039.212 | 54951666.232 | 86198918.4 | 43459946.47 | 21695287.56 | 384123062.55 | 35571732 | 535761 | 0 | 29866161.45 | 14630400 | 2016103.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 228 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 16 | 12 | 0 | 0 | 0 | 35 | 55 | 17 | 16 | 25 | 9 | 20 | 17 | 52 | 0 | 46 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 79 | 46 | 18 | 3 | 0 | 0 | 80 | 255 | 285 | 0 | 16 | 122 | 29 | 52 | 0 | 51 | 0 | 0 | 25 | 16 | 11 | 15 | 9 | 88 | 44 | 0 | 20 | 2 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 79 | 0 | 190 | 18 | 0 | 10 | 285 | 21 | 2 | 0 | 275 | 0 | 0 | 175 | 0 | 149 | 20 | 90 | 0 | 127 | 0 | 94 | 90 | 105 | 4 | 50 | 35 | 110 | 0 | 85 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 29 | 0 | 55 |  | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 17 | 16 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 336 | 96 | 0 | 70 | 15 | 112 | 0 | 4 | 70 | 0 | 221 | 0 | 17 | 4 | 71 | 0 |  | 8136 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 0 | 200 | 0 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 100 | 11 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 51 | 0 | 38 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 20 | 84 | 46 | 21 | 10 | 0 | 0 | 80 | 220 | 270 | 0 | 8 | 131 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 25 | 9 | 95 | 46 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 71 | 81 | 0 | 190 | 18 | 0 | 10 | 305 | 24 | 11 | 20 | 280 | 197 | 60 | 173 | 100 | 149 | 0 | 90 | 0 | 145 | 0 | 112 | 105 | 105 | 0 | 100 | 35 | 110 | 0 | 113 | 100 | 400 | 104 | 0 | 162 | 104 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 10 | 0 | 91 | 20 | 16 | 0 | 0 | 0 | 50 | 20 | 100 | 0 | 34 | 32 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 173 | 0 | 394 | 105 | 50 | 90 | 50 | 112 | 0 | 0 | 95 | 0 | 220 | 0 | 35 | 0 | 0 | 0 |  | 9338 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 40 | 35 | 55 | 35 | 19 | 25 | 10 | 20 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 70 | 100 | 90 | 50 | 21 | 30 | 0 | 0 | 80 | 220 | 270 | 200 | 8 | 131 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 163 | 100 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 330 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 55 |  | 724 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 35 | 40 | 0 | 91 | 24 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 25 | 43 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 11 | 0 | 0 | 40 | 35 | 55 | 35 | 19 | 25 | 10 | 20 | 33 | 51 | 0 | 0 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 52 | 100 | 90 | 50 | 20 | 5 | 0 | 0 | 80 | 220 | 270 | 150 | 8 | 130 | 30 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 100 | 0 | 22 | 1.6 | 42 | 0 | 51 | 0 | 163 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 330 | 24 | 11 | 0 | 300 | 300 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 55 |  | 676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 24 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 25 | 43 | 32 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6 | 11
Generation at 08:00(Today) | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 9 | 16 | 33 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 40 | 12 | 30 | 18 | 0 | 0 | 0 | 80 | 160 | 270 | 130 | 8 | 138 | 3 | 5 | 0 | 51 | 0 | 0 | 1 | 21 | 11 | 33 | 9 | 60 | 53 | 0 | 20 | 0 | 42 | 0 | 48 | 0 | 163 | 0 | 72 | 75 | 0 | 190 | 18 | 0 | 10 | 300 | 21 | 8 | 0 | 58 | 0 | 0 | 165 | 0 | 7 | 8 | 90 | 0 | 143 | 0 | 16 | 58 | 8 | 1 | 15 | 54 | 51 | 0 | 0 | 100 | 402 | 31 | 6 | 137 | 98 | 0 | 17 | 7 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 189 | 0 | 382 | 6 | 0 | 46 | 0 | 105 | 0 | 1 | 113 | 0 | 220 | 0 | 0 | 0 | 16 | 0 | 0
199
| Minimum Generation |  | 5805 | 5:00
| Highest Generation |  | 9338 | 19:00
| Day Peak Generation |  | 8136 | 12:00
| Evening Peak Generation |  | 9338 | 19:00
| HVDC Max Flow |  | 711 | 18:00
| HVDC EvPeak Flow |  | 711 | 19:00
| Load factor L.F |  | 82.36%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-01-07
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-01-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8136 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5848 | MW
Evening Peak Generation : |  | 9338 | MW Hour : | 19:00 | Available Max Generation : |  | 12210 | MW
E.P. Demand (at gen end) : |  | 9338 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 9338 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3710 | MW
Total Gen. (MKWH) : |  | 184.5887 | System Load Factor : | 82.36% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -324 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-01-07
Actual : | 97.48 | Ft.(MSL) , | Rule curve : | 101.86 | Ft.( MSL )
Gas Consumed : | Total = | 737.42 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 98411612.702
: |  | Coal : | 35571732 | Oil : | 435684511.56 | Total : | 569667856.262
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3038.9406 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1026.8177 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 918.8203 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 829.8147 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 750.1215 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 605.3049 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 346.9374 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 156.0742 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 466.8006 |  |  | 0 | 0%
Total | 0 |  | 8139.6318 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
2) Ghorasal-3,5,7
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit-1
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj(South)-Ashuganj(Network) 230 kV Ckt-2 was shut down at 09:29 for C/M.
b) Barishal-Bhola 230 kV Ckt-2 was under shut down from 09:02 to 17:13 for A/M.
c) Bheramara-Kustia 132 kV Ckt-2 was under shut down from 08:51 to 15:10 for A/M.
d) Cox's Bazar 132/33 kV T-2 transformer was under shut down from 08:13 to 13:24 for A/M.
e) Ashuganj-Cumilla(N) 230 kV Ckt-1 was under shut down from 10:09 to 16:46 for A/M.
f) Gopalganj-Faridpur 132 kV Ckt-2 was under shut down from 10:01 to 16:31 for C/M.
g) Bhulta-Haripur 132 kV Ckt was under shut down from 09:01 to 15:47 for A/M.
h) Hathazari-Kaptai 132 kV Ckt-2 was under shut down from 09:19 to 15:54 for A/M.
i) Kodda 132/33 kV T-3 transformer was under shut down at 09:17 for A/M.
j) Munshiganj 132/33 kV T-1 transformer was under shut down from 08:47 to13:32 for A/M.
k) Mymensing 132 kV Bus-A was under shut down from 09:40 to 19:50 for A/M.
l) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:16 to 13:36 for A/M.
m) Mymensing-Solar 132 kV Ckt was under shut down from 08:43 to 22:27 for A/M.
n) Gopalganj(N)-Payra 400 kV Ckt-2 was under shut down from 10:18 to 08:08(7/1/22) for D/W.
o) Savar-Manikganj-162 MW 132 kV Ckt-2 was under shut down from 10:11 to 16:28 for A/M.
p) Savar 132/33 kV T-1 transformer was under shut down from 09:18 to 19:14 for C/M.
q) Bogura-Mohastanghor 132 kV Ckt-2 was under shut down from 09:18 to 16:44 for A/M.
r) Shyampur 230/132 kV T-01 transformer was under shut down from 07:04 to 16:14 for A/M.
s) Magura-Narail 132 kV Ckt-2 was under shut down from 09:52 to 13:48 for A/M.
t) Ashuganj(S)-Ghorasal 230 kV Ckt-2 was under shut down from 07:25 to 17:26 for C/M.
u) Mymensing-Netrokona 132 kV Ckt-2 was under shut down from 13:45 to 19:30 for A/M.
v) Rangpur-Kurigram 132 kV Ckt tripped at 16:22 showing dist.Z1,B-phase due to PT burst at Kurigram end and was | [5 empty] | About 24 MW power interruption occurred under
switched on at 20:15. | [5 empty] | Kurigram S/S area from 16:22 to 20:15.
w) Kabirpur 132/33 kV T-2 transformer was under shut down from 15:05 to 16:20 for C/M. | [5 empty] | About 60 MW power interruption occurred under
Kabirpur S/S area from 15:05 to 16:20.
x) Aminbazar 230/132 kV T-3 transformer tripped at 20:50 showing gen.trip & lockout and was switched on at 21:41.
y) Ashuganj-225 MW CCPP GT & ST were synchronized at 22:17 & 02:51(7/2/22) respectively.
z) Ghorasal #7 was shut down at 23:59 due to gas shortage.
aa) Hathazari 132 kV Bus-1 is under shut down since 07:33(7/1/22) for D/W.
ab) Bogura-Confidenace-2 132 kV Ckt tripped at 00:27(7/1/22) showing over voltage and was switched on at 00:35(7/1/22).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-01-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 1306000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 5373664 | DP High
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 250 | 4908000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4185750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 794016
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 11 | 166421 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 382500
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1676592
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 877320 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 506400 | High Voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1336691
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 744978 | 33 kV feeder problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 799260 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 532200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 663200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 580320
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 5304216 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 197 | 493900
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 60 | 280898
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 330805
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2408400
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1998000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1422720
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3350880
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 180589
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 55 | 1280520
| Dhaka area Total |  |  |  | 5560 | 2492 | 41884240
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 1000000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 146944 | High Voltage
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 132300
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 1106880 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 78 | 1984300 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1313927
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 230121 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 47880 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1617600 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 477120
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 483240
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 1862400 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27000
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 100 | 998618 | High Voltage
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 1038107 | Engine problem
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1970460
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1191360
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 104 | 2480236 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 971 | 18108493
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2103780 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 60000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 220 | 5487000 | Machine problem
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6812000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 666936 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1300800
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 384727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1251568
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 145 | 3218313 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 236680
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 131 | 3059620 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 25920 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 456588
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244980
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 95 | 1950720
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 627000 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 516557
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 245630 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 45504
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 18240 | High Voltage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1781640
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 445680 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3034 | 1402 | 30939883
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 46 | 1159680 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 468324
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9150
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 173 | 3787200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 112 | 1562400
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 0
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 529920
| Mymensingh Area Total |  |  |  | 622 | 373 | 7516674
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1012000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3511472
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 1211400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 147024
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 71 | 1609728
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1921920
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 190 | 4503980 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 532948
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7183500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251640
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8878200
| Sylhet Area Total |  |  |  | 2377 | 1367 | 31186812
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 711 | 14965090
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 216960
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 10 | 19456
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 10 | 33600
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1472640
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 50 | 435168 | High Voltage
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 0 | 0 | 444960 | On test
| Khulna Area Total |  |  |  | 2129 | 918 | 17587874
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 201216 | High Voltage
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 387800 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2220104 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 273541 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 2108800 | Development work
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4930991
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 340800 | High Voltage
| Barisal Area Total |  |  |  | 2046 | 393 | 10463252
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 613005
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 58710 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 420983 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 359823 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 173 | 4322445 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 394 | 8419672 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 522720
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 190386
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 708960 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 866168
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 102036
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 90 | 1374624 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1443168 | Engine problem
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27780
| Rajshahi Area Total |  |  |  | 2179 | 1111 | 19430480
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4855000
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 2567856
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29291
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 18816 | On test
| Rangpur Area Total |  |  |  | 605 | 311 | 7470963
| Total |  |  |  | 20934 | 9338 | 184588671
| Eastern Grid Total |  |  |  | 13975 | 6605 | 129636102
| Western Grid Total |  |  |  | 6959 | 2733 | 54952569
| National Grid Total |  |  |  | 20934 | 9338 | 184588671
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-01-06
(a) ENTIRE EASTERN GRID : |  | 6120 | MW | (b) ENTIRE WESTERN GRID : |  | 2811 | MW
i) Dhaka area |  | 3267 | MW | i) Khulna area |  | 1083 | MW
ii) Chittagong area |  | 991 | MW | ii) Rajshahi area |  | 900 | MW
iii) Comilla area |  | 755 | MW | iii) Barisal area |  | 247 | MW
iv) Mymensingh area |  | 767 | MW | iv) Rangpur area |  | 581 | MW
v) Sylhet area |  | 340 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8931 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 92 | 9:00 | Tangail | 143 | 18:30 | Noapara | 37 | 18:30
Munsiganj | 66 | 19:30 | Mymensing | 163 | 18:30 | Jessore | 76 | 18:30
Sonargaon | 68 | 1:00 | Kishoreganj | 96 | 20:00 | Benapol | 38 | 18:30
Shyampur | 168 | 11:00 | Netrokona | 95 | 18:30 | Jhenida(Old) | 80 | 18:30
Bhulta | 136 | 20:00 | Jamalpur | 100 | 18:30 | Bottail | 94 | 18:30
Madanganj | 32 | 12:00 | Sherpur | 106 | 18:00 | G.K Project | 36 | 18:30
Shitalakhya | 81 | 12:00 | Srimongal | 35 | 19:00 | Faridpur | 98 | 19:00
Rahim steel | 30 | 15:00 | Shahjibazar | 76 | 18:00 | Rajbari | 40 | 18:00
Matuail | 46 | 12:00 | Fenchuganj | 28 | 17:00 | Madaripur | 66 | 20:00
Ghorasal | 55 | 19:30 | Kulawara | 30 | 18:00 | Sariatpur | 42 | 19:30
Narsingdi | 128 | 21:00 | Sylhet | 91 | 18:00 | Gopalganj | 69 | 18:30
Haripur (SBU) | 106 | 16:00 | Chatak | 18 | 18:30 | Bagerhat | 78 | 19:30
Sreenagar | 27 | 20:00 | Sunamganj | 31 | 18:30 | Mongla | 30 | 18:00
Ullon | 42 | 20:00 | Biani Bazar | 39 | 18:00 | Satkhira | 75 | 18:30
Hasnabad | 68 | 18:00 | Comilla (S) | 99 | 18:00 | Gallamari | 48 | 13:00
Magbazar | 61 | 13:00 | Comilla(N) | 82 | 18:00 | Magura | 40 | 18:30
Maniknagar | 40 | 12:00 | Chandpur | 46 | 19:00 | Norail | 36 | 18:00
Bangabhaban | 8 | 12:00 | Feni | 80 | 19:00 | Chuadanga | 68 | 18:30
Motijheel | 19 | 12:00 | Chowmuhani | 134 | 19:30 | Barisal(N) | 27 | 19:30
Narinda | 36 | 11:00 | Ashuganj | 20 | 18:30 | Barisal (S) | 76 | 19:00
Kazla | 69 | 10:00 | Daudkandi | 94 | 18:30 | Patuakhali | 76 | 21:00
Dhanmondi | 121 | 13:00 | B.Baria | 95 | 19:00 | Bhandaria | 38 | 20:00
Lalbag | 73 | 13:00 | Ramganj | 50 | 18:30 | Borguna | 12 | 19:30
Madartek | 41 | 13:00 | Chaddagram | 35 | 20:00 | Borhan Uddin | 29 | 21:00
Dhaka University | 18 | 12:00 | PHP | 7 | 9:00 | Ishurdi | 50 | 18:30
Aftabnagar | 10 | 12:00 | Kochua | 34 | 18:00 | Ruppur Paromanobik | 3 | 20:00
Fatullah | 50 | 12:00 | Madunaghat | 34 | 18:00 | Natore | 91 | 18:30
Nawabganj | 31 | 21:00 | Hathazari | 68 | 18:00 | Bogra | 103 | 18:30
Keraniganj | 33 | 18:00 | Khulshi | 151 | 16:00 | Noagaon | 82 | 19:30
Banani | 38 | 13:00 | Halishahar | 59 | 19:30 | Rajshahi | 100 | 20:00
Mirpur | 77 | 13:00 | Baraulia | 133 | 12:00 | Rajshahi New | 15 | 20:00
Kalyanpur | 56 | 12:00 | Sikalbaha | 24 | 18:00 | C.Nawabganj | 40 | 20:00
Gulshan | 78 | 5:00 | Dohazari | 66 | 18:00 | Amnura | 38 | 20:00
Uttara | 36 | 12:00 | Cox'sbazar | 64 | 14:00 | Pabna | 70 | 18:30
Uttara New | 22 | 17:00 | Chandraghona | 24 | 8:00 | Shahjadpur | 79 | 19:00
Kamrangirchar | 60 | 17:00 | Kaptai | 3.5 | 18:00 | Serajganj | 58 | 18:30
Savar | 112 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 53 | 18:30
Bhasantec | 78 | 13:00 | Bakulia | 84 | 18:00 | Joypurhat | 44 | 19:00
Agargaon | 46 | 13:00 | Julda | 24 | 9:00 | Sherpur(Bogura) | 45 | 20:00
Satmosjid | 69 | 14:00 | TK chemical | 22.5 | 18:00 | Mohastangor | 42 | 18:30
Old Tongi | 93 | 11:00 | Modern Steel | 0 | 1:00 | Bhangura | 16 | 18:30
Kabirpur | 175 | 18:00 | Shahmirpur | 27 | 6:00 | Rangpur | 98 | 18:00
Bashundara | 92 | 18:00 | Khagrachhari | 20 | 21:00 | Lalmonirhat | 30 | 19:00
Manikgong | 63 | 20:00 | Matarbari | 25 | 17:00 | Saidpur | 80 | 19:00
Joydevpur | 123 | 16:00 | Baroiar Hat | 32 | 18:00 | Purbasadipur | 88 | 18:30
New Tongi | 76 | 11:00 | Rangamati | 10 | 18:00 | Thakurgaon | 67 | 18:30
Kodda | 224 | 12:00 | Abul Khair 230 | 137 | 6:00 | Palashbari | 75 | 18:30
Dhamrai | 94 | 18:00 | BSRM | 157 | 9:00 | Barapukuria | 43 | 20:00
Rajendrapur | 86 | 18:30 | GPH Ispat | 13 | 4:00 | Panchagar | 45 | 18:00
Purbachal | 12 | 12:00 | Agrabad | 54 | 18:00 | Joldhaka | 45 | 18:00
Tongi Millgate | 36 | 0 | Goalpara | 23 | 13:00 | Kurigram | 35 | 8:00
Valuka | 84 | 15:00 | Central S/S | 56 | 18:30 | Mithapukur | 31 | 18:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-01-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 417 | 1:00 | 408 | 12:00 | Kaliakoir | 415 | 0.25 | 406 | 0.70833
| Bheramara | 405 | 22:00 | 395 | 11:00 | Bhulta | 403 | 0.041667 | 391 | 0.70833
| Ashuganj(N) | 410 | 8:00 | 395 | 17:00 | Gopalganj | 421 | 0.625 | 0 | 0.45833
| Payra | 423 | 21:00 | 0 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 246 | 1:00 | 240 | 7:00 | Hathazari | 243 | 21:00 | 230 | 17:00
| Ishurdi | 246 | 1:00 | 239 | 18:30 | Megnaghat | 248 | 22:00 | 246 | 11:00
| Ashuganj | 252 | 8:00 | 246 | 17:00 | Fenchuganj | 248 | 1:00 | 242 | 11:00
| Serajganj | 244 | 6:00 | 240 | 7:00 | Siddhirganj | 243 | 6:00 | 237 | 6:00
| Baghabari | 244 | 1:00 | 238 | 18:30 | Maniknagar | 242 | 6:00 | 234 | 12:00
| Barapukuria | 238 | 5:00 | 231 | 18:30 | Agargaon | 244 | 4:00 | 235 | 17:00
| Bogra | 241 | 17:00 | 236 | 13:00 | Barisal | 247 | 18:00 | 237 | 12:00
| Rajshahi | 246 | 22:00 | 238 | 12:00 | Bhola 225 MW | 248 | 3:00 | 243 | 18:00
| Khulna South | 248 | 4:00 | 236 | 12:00 | AKSML | 244 | 18:00 | 231 | 16:00
| Rampura | 241 | 6:00 | 233 | 12:00 | BSRM | 244 | 21:00 | 231 | 17:00
| Haripur | 242 | 21:00 | 234 | 12:00 | Bibiyana | 248 | 21:00 | 238 | 13:00
| Hasnabad | 243 | 7:00 | 235 | 10:00 | Bhulta | 243 | 5:00 | 236 | 12:00
| Shyampur | 244 | 21:00 | 234 | 17:00 | Ashuganj (S) | 248 | 8:00 | 242 | 17:00
| Aminbazar | 247 | 1:00 | 238 | 2:00 | Kaliakoir | 242 | 1:00 | 235 | 17:00
| Tongi | 242 | 23:00 | 232 | 15:00 | GPH | 243 | 21:00 | 232 | 16:00
| Comilla (N) | 244 | 22:00 | 239 | 11:00 | Jhenaidah | 242 | 4:00 | 234 | 18:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 21:00 | 133 | 16:00 | Kachua | 143 | 0.16667 | 139 | 0.70833
| Munsiganj | 140 | 20:00 | 133 | 17:00 | Madanhat | 142 | 0.375 | 137 | 0.041667
| Sonargaon | 139 | 0:00 | 133 | 16:00 | Hathazari | 143 | 0.8125 | 136 | 0.66667
| Shyampur | 137 | 21:00 | 130 | 12:00 | Khulshi | 140 | 0.25 | 132 | 0.70833
| Bhulta | 133 | 3:00 | 122 | 15:00 | Halishahar | 142 | 0.8125 | 132 | 0.70833
| Madanganj | 139 | 19:30 | 134 | 12:00 | Baraulia | 142 | 0.20833 | 136 | 0.041667
| Shitalakhya | 140 | 20:00 | 133 | 17:00 | Sikalbaha | 143 | 0.83333 | 138 | 0.041667
| Rahim steal | 138 | 5:00 | 132 | 17:00 | Dohazari | 141 | 0.25 | 130 | 0.70833
| Matuail | 139 | 21:00 | 133 | 16:00 | Cox'sbazar | 130 | 0.25 | 121 | 0.70833
| Ghorasal | 146 | 21:00 | 142 | 14:00 | Chandraghona | 143 | 0.8125 | 136 | 0.70833
| Narsinghdi | 137 | 7:00 | 132 | 11:00 | Kaptai | 142 | 0.041667 | 138 | 0.29167
| Haripur (SBU) | 139 | 20:00 | 134 | 12:00 | A. Khaer Stl. | 141 | 0.125 | 136 | 0.66667
| Sreenagar | 139 | 20:00 | 132 | 17:00 | Bakulia | 141 | 0.33333 | 135 | 0.66667
| Ullon | 139 | 4:00 | 132 | 17:00 | Julda | 142 | 0.25 | 134 | 0.625
| Hasnabad | 139 | 3:00 | 133 | 17:00 | TK Chemical | 143 | 0.25 | 135 | 0.70833
| Magbazar | 138 | 7:00 | 133 | 12:00 | Modern Steel | 141 | 0.25 | 134 | 0.70833
| Maniknagar | 143 | 6:00 | 132 | 16:00 | Shahmirpur | 142 | 0.33333 | 135 | 0.66667
| Bangabhaban | 143 | 6:00 | 132 | 16:00 | Khagrachhari | 142 | 0.875 | 134 | 0.70833
| Motijheel | 143 | 6:00 | 132 | 16:00 | Matarbari | 130 | 0.041667 | 126 | 0.75
| Narinda | 143 | 6:00 | 132 | 16:00 | Baroiar Hat | 141 | 6:00 | 138 | 1:00
| Kazla | 143 | 6:00 | 132 | 16:00 | Rangamati | 142 | 7:00 | 135 | 16:00
| Dhanmondi | 140 | 23:00 | 133 | 17:00 | Agrabad | 141 | 13:00 | 133 | 0.70833
| Lalbag | 139 | 21:00 | 132 | 12:00 | Goalpara S/S | 142 | 1:00 | 135 | 0.5
| Madartek | 138 | 8:00 | 132 | 12:00 | Khulna Central S/S | 141 | 10:00 | 134 | 0.75
| Dhaka University | 139 | 6:00 | 133 | 12:00 | Noapara | 140 | 2:00 | 135 | 0.5
| Aftabnagar | 138 | 5:00 | 133 | 11:00 | Jessore | 139 | 0.25 | 133 | 0.77083
| Fatullah | 138 | 20:00 | 131 | 17:00 | Benapol | 139 | 1:00 | 133 | 0.75
| Nawabganj | 139 | 18:30 | 132 | 12:00 | Jhenida(Old) | 140 | 0.041667 | 134 | 0.75
| Keraniganj | 139 | 20:00 | 132 | 12:00 | Bottail | 140 | 0.041667 | 135 | 0.5
| Banani | 139 | 6:00 | 132 | 17:00 | G.K Project | 142 | 0.083333 | 139 | 0.54167
| Mirpur | 136 | 3:00 | 130 | 11:00 | Faridpur | 141 | 0.375 | 134 | 0.5
| Kalyanpur | 136 | 6:00 | 132 | 11:00 | Rajbari | 140 | 0.16667 | 133 | 0.5
| Gulshan | 138 | 5:00 | 132 | 12:00 | Madaripur | 144 | 4:00 | 136 | 0.5
| Uttara | 139 | 19:30 | 134 | 12:00 | Shariyatpur S/S | 144 | 0.16667 | 135 | 0.54167
| Uttara New | 137 | 21:00 | 130 | 16:00 | Gopalganj | 144 | 4:00 | 135 | 0.70833
| Kamrangirchar | 139 | 20:00 | 132 | 10:00 | Bagerhat | 141 | 10:00 | 134 | 0.5
| Savar | 139 | 6:00 | 131 | 11:00 | Mongla | 139 | 6:00 | 134 | 12:00
| Bhasantec | 140 | 1:00 | 135 | 11:00 | Satkhira | 140 | 0.16667 | 133 | 12:00
| Agargaon | 141 | 2:00 | 135 | 12:00 | Gallamari | 140 | 4:00 | 135 | 0.29167
| Satmosjid | 140 | 1:00 | 135 | 11:00 | Magura | 142 | 0.16667 | 136 | 0.5
| Old Tongi | 140 | 1:00 | 135 | 18:00 | Narail | 139 | 1:00 | 134 | 0.5
| Kabirpur | 139 | 4.00 | 132 | 18:29 | Chuadanga | 139 | 3:00 | 131 | 0.75
| Bashundara | 140 | 18:30 | 133 | 12:00 | Barisal(N) | 146 | 5:00 | 138 | 11:00
| Manikgong | 137 | 7.00 | 130 | 17:00 | Barisal (S) | 143 | 0.083333 | 138 | 0.5
| Joydevpur | 144 | 4.00 | 138 | 12:00 | Patuakhali(S) | 142 | 0.20833 | 137 | 0.5
| New Tongi | 140 | 21:00 | 135 | 14:00 | Bhandaria | 144 | 0.16667 | 135 | 0.70833
| Kodda | 140 | 18:30 | 131 | 2:00 | Borguna | 144 | 3:00 | 138 | 12:00
| Dhamrai | 138 | 00:00 | 131 | 18:30 | Jhenaidah(New) | 140 | 4:00 | 135 | 12:00
| Rajendrapur | 139 | 20:00 | 132 | 3:00 | Ishurdi | 141 | 5:00 | 138 | 18:00
| Purbachal | 139 | 5.00 | 132 | 17:00 | Ruppur Paromanobik | 141 | 5:00 | 138 | 7:00
| Tongi Millgate | 140 | 21:00 | 135 | 15:00 | Natore | 141 | 6:00 | 138 | 18:00
| Valuka | 133 | 1:00 | 126 | 16:00 | Bogra | 142 | 10:00 | 138 | 18:30
| Tangail | 136 | 5:00 | 131 | 17:00 | Noagaon | 136 | 1:00 | 133 | 18:00
| Mymensing | 136 | 5:00 | 128 | 18:00 | Rajshahi | 140 | 15:00 | 137 | 18:00
| Kishorganj | 136 | 1:00 | 129 | 18:00 | Rajshahi New | 140 | 15:00 | 136 | 12:00
| Netrokona | 132 | 1:00 | 121 | 18:30 | C.Nawabganj | 138 | 19:00 | 134 | 7:00
| Jamalpur | 140 | 9:00 | 133 | 2:00 | Amnura | 140 | 20:00 | 134 | 8:00
| Sherpur | 139 | 10:00 | 132 | 3:00 | Pabna | 141 | 3:00 | 138 | 18:00
| Srimongal | 143 | 6:00 | 137 | 12:00 | Shahjadpur | 145 | 1:00 | 142 | 12:00
| Shahjibazar | 139 | 4:00 | 135 | 12:00 | Serajganj | 140 | 14:00 | 138 | 18:30
| Fenchuganj | 139 | 5:00 | 136 | 12:00 | Niyamatpur | 136 | 6:00 | 132 | 18:00
| Khulawara | 138 | 1:00 | 136 | 12:00 | Joypurhat | 139 | 2:00 | 134 | 13:00
| Sylhet | 136 | 1:00 | 134 | 15:00 | Sherpur(Bogura) | 141 | 1:00 | 137 | 18:30
| Chatak | 137 | 1:00 | 135 | 11:00 | Mohastangor | 141 | 6:00 | 137 | 18:30
| Sunamganj | 136 | 5:00 | 133 | 18:00 | Bangura | 144 | 4:00 | 140 | 18:30
| Biani Bazar | 137 | 3:00 | 134 | 12:00 | Rangpur | 138 | 7:00 | 130 | 18:00
| Comilla(s) | 131 | 1:00 | 126 | 10:00 | Lalmonirhat | 136 | 3:00 | 130 | 18:30
| Comilla(n) | 146 | 6:00 | 141 | 15:00 | Saidpur | 137 | 6:00 | 127 | 18:00
| Chandpur | 143 | 6:00 | 142 | 1:00 | Purbasadipur | 134 | 6:00 | 126 | 18:00
| Feni | 144 | 18:30 | 137 | 17:00 | Thakurgaon | 133 | 3:00 | 121 | 18:30
| Chowmuhani | 140 | 7:00 | 136 | 15:00 | Palashbari | 139 | 3:00 | 133 | 18:00
| Ashuganj | 142 | 7:00 | 139 | 12:00 | Barapukuria | 138 | 0.20833 | 131 | 0.77083
| Daudkandi | 142 | 5:00 | 135 | 17:00 | Panchagar | 135 | 0.66667 | 124 | 0.77083
| B.Baria | 139 | 6:00 | 133 | 12:00 | Joldhaka | 135 | 0.16667 | 125 | 0.77083
| Ramganj | 142 | 11:00 | 134 | 17:00 | Kurigram | 136 | 0.625 | 132 | 0.5
| Chaddagram | 144 | 6:00 | 137 | 17:00 | Mithapukur | 140 | 1:00 | 134 | 18:00
| PHP | 142 | 7:00 | 135 | 17:00

## L-Curve
Date | 2022-01-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 96 | 5168 | 2086 | 7254 |  |  |  | QF-LDC-11
0:30 | 49 | 4942.5 | 2040.5 | 6983 | Date: | 2022-01-06
1:00 | 2 | 4717 | 1995 | 6712
1:30 | 29 | 4524.5 | 1952.5 | 6477
2:00 | 56 | 4332 | 1910 | 6242
2:30 | 84 | 4244 | 1895.5 | 6139.5 | [5 empty] | Gen. at Eve. Peak | 9338 | 9338 MW (19:00 )
3:00 | 112 | 4156 | 1881 | 6037 | [6 empty] | 19:00
3:30 | 104 | 4109 | 1840.5 | 5949.5 | [5 empty] | Gen. at Day Peak | 8136 | 8136 MW (12:00 )
4:00 | 96 | 4062 | 1800 | 5862 | [6 empty] | 12:00
4:30 | 115 | 4018 | 1815.5 | 5833.5 | [5 empty] | Highest Generation | 9338
5:00 | 134 | 3974 | 1831 | 5805 | [6 empty] | 19:00
5:30 | 100 | 4006 | 1846 | 5852
6:00 | 66 | 4038 | 1861 | 5899
6:30 | 119 | 4235.5 | 1910 | 6145.5
7:00 | 172 | 4433 | 1959 | 6392
7:30 | 213 | 4709 | 2035.5 | 6744.5
8:00 | 254 | 4985 | 2112 | 7097
8:30 | 241 | 5239 | 2122 | 7361
9:00 | 228 | 5493 | 2132 | 7625
9:30 | 129 | 5526.5 | 2179 | 7705.5
10:00 | 30 | 5560 | 2226 | 7786
10:30 | 65 | 5591.5 | 2232 | 7823.5
11:00 | 100 | 5623 | 2238 | 7861
11:30 | 119 | 5682.5 | 2316 | 7998.5
12:00 | 138 | 5742 | 2394 | 8136
12:30 | 76 | 5811 | 2420.5 | 8231.5
13:00 | 14 | 5880 | 2447 | 8327
13:30 | 34 | 5771.5 | 2370 | 8141.5
14:00 | 54 | 5663 | 2293 | 7956
14:30 | 127 | 5597 | 2260 | 7857
15:00 | 200 | 5531 | 2227 | 7758
15:30 | 263 | 5383 | 2258.5 | 7641.5
16:00 | 326 | 5235 | 2290 | 7525
16:30 | 299 | 5324.5 | 2299 | 7623.5
17:00 | 272 | 5414 | 2308 | 7722
17:30 | 240 | 5939 | 2494 | 8433
18:00 | 208 | 6464 | 2680 | 9144
18:30 | 215 | 6534.5 | 2706.5 | 9241
19:00 | 222 | 6605 | 2733 | 9338
19:30 | 186 | 6516 | 2767 | 9283
20:00 | 168 | 6424 | 2781 | 9205 |  |  |  | Executive Engineer
20:30 | 142 | 6314 | 2749.5 | 9063.5 |  |  |  | Network Operation Division
21:00 | 116 | 6204 | 2718 | 8922
21:30 | 68 | 6024.5 | 2690.5 | 8715
22:00 | 20 | 5845 | 2663 | 8508 |  |  |  |  | Page 6 of 7
22:30 | 45 | 5633.5 | 2535 | 8168.5
23:00 | 70 | 5422 | 2407 | 7829
23:30 | 83 | 5295 | 2246.5 | 7541.5
24:00 | 96 | 5168 | 2086 | 7254
9338 MW (19:00 )
8136 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-01-06 |  | Energy |  | 184588671
[13 empty] | 2022-01-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2195 | 539 | 1685 | 0 | 2440 | 199 | 77 | 0 | 50 | 69 | 0 | 0
0:30 | 2341.5 | 511.5 | 1656.5 | 0 | 1945.5 | 349.5 | 81.5 | 0 | 26.5 | 70.5 | 0 | 0 | Date: | 2022-01-06
1:00 | 2488 | 484 | 1628 | 0 | 1451 | 500 | 86 | 0 | 3 | 72 | 0 | 0
1:30 | 2467.5 | 480 | 1609 | 0 | 1260.5 | 500 | 86 | 0 | 3 | 71 | 0 | 0 | [8 empty] | Total Energy | 184.5887 | Total Energy Gen 184.589 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.589 MKWHr
2:00 | 2447 | 476 | 1590 | 0 | 1070 | 500 | 86 | 0 | 3 | 70 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2445.5 | 476.5 | 1582.5 | 0 | 977 | 500 | 86 | 0 | 3 | 69 | 0 | 0 | [8 empty] | Energy Requirement | 184.5887
3:00 | 2444 | 477 | 1575 | 0 | 884 | 500 | 86 | 0 | 3 | 68 | 0 | 0
3:30 | 2389 | 476.5 | 1579.5 | 0 | 867.5 | 480 | 86 | 0 | 3 | 68 | 0 | 0 | [6 empty] | Shortage
4:00 | 2334 | 476 | 1584 | 0 | 851 | 460 | 86 | 0 | 3 | 68 | 0 | 0
4:30 | 2290.5 | 476 | 1602.5 | 0 | 850 | 460 | 86 | 0 | 3 | 65.5 | 0 | 0
5:00 | 2247 | 476 | 1621 | 0 | 849 | 460 | 86 | 0 | 3 | 63 | 0 | 0
5:30 | 2217 | 476 | 1659.5 | 0 | 904 | 444.5 | 86 | 0 | 3 | 62 | 0 | 0
6:00 | 2187 | 476 | 1698 | 0 | 959 | 429 | 86 | 0 | 3 | 61 | 0 | 0
6:30 | 2176 | 518.5 | 1654.5 | 0 | 1240 | 404 | 86 | 0 | 3 | 62.5 | 1 | 0 |  |  |  |  | Coal
7:00 | 2165 | 561 | 1611 | 0 | 1521 | 379 | 86 | 0 | 3 | 64 | 2 | 0
7:30 | 2256 | 612 | 1659 | 0 | 1761 | 289 | 86 | 0 | 3 | 67.5 | 11 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2347 | 663 | 1707 | 0 | 2001 | 199 | 86 | 0 | 3 | 71 | 20 | 0
8:30 | 2322.5 | 663 | 1657 | 0 | 2306.5 | 199 | 86 | 0 | 3 | 78.5 | 45.5 | 0
9:00 | 2298 | 663 | 1607 | 0 | 2612 | 199 | 86 | 0 | 3 | 86 | 71 | 0
9:30 | 2222 | 662.5 | 1611 | 0 | 2721 | 199.5 | 86 | 0 | 26 | 88 | 89.5 | 0
10:00 | 2146 | 662 | 1615 | 0 | 2830 | 200 | 86 | 0 | 49 | 90 | 108 | 0
10:30 | 2091.5 | 662.5 | 1597 | 0 | 2901.5 | 199.5 | 86 | 0 | 79.5 | 87.5 | 118.5 | 0
11:00 | 2037 | 663 | 1579 | 0 | 2973 | 199 | 86 | 0 | 110 | 85 | 129 | 0
11:30 | 2112 | 663 | 1652 | 0 | 2937 | 199.5 | 86 | 0 | 131 | 86.5 | 131.5 | 0
12:00 | 2187 | 663 | 1725 | 0 | 2901 | 200 | 86 | 0 | 152 | 88 | 134 | 0
12:30 | 2215.5 | 663 | 1758.5 | 0 | 2931.5 | 199.5 | 86 | 0 | 154 | 91 | 132.5 | 0
13:00 | 2244 | 663 | 1792 | 0 | 2962 | 199 | 86 | 0 | 156 | 94 | 131 | 0
13:30 | 2244 | 663 | 1792 | 0 | 2962 | 199 | 86 | 0 | 156 | 94 | 131 | 0
14:00 | 2244 | 663 | 1792 | 0 | 2962 | 199 | 86 | 0 | 156 | 94 | 131 | 0
14:30 | 2230 | 663 | 1726.5 | 0 | 2803.5 | 199 | 80.5 | 0 | 146 | 89 | 105 | 0
15:00 | 2216 | 663 | 1661 | 0 | 2645 | 199 | 75 | 0 | 136 | 84 | 79 | 0
15:30 | 2208 | 663.5 | 1714.5 | 0 | 2501.5 | 199 | 76.5 | 0 | 136.5 | 83 | 59 | 0
16:00 | 2200 | 664 | 1768 | 0 | 2358 | 199 | 78 | 0 | 137 | 82 | 39 | 0
16:30 | 2276.5 | 663.5 | 1799 | 0 | 2352 | 198.5 | 81.5 | 0 | 146.5 | 83.5 | 22.5 | 0
17:00 | 2353 | 663 | 1830 | 0 | 2346 | 198 | 85 | 0 | 156 | 85 | 6 | 0
17:30 | 2346.5 | 687 | 1821.5 | 205.5 | 2709.5 | 198.5 | 85.5 | 0 | 284 | 92 | 3 | 0
18:00 | 2340 | 711 | 1813 | 411 | 3073 | 199 | 86 | 0 | 412 | 99 | 0 | 0
18:30 | 2329 | 711 | 1822 | 424 | 3148.5 | 199 | 82 | 0 | 428.5 | 97 | 0 | 0
19:00 | 2318 | 711 | 1831 | 437 | 3224 | 199 | 78 | 0 | 445 | 95 | 0 | 0
19:30 | 2314 | 711 | 1854 | 363 | 3228 | 199 | 78 | 0 | 443 | 93 | 0 | 0
20:00 | 2320 | 711 | 1835 | 314 | 3217 | 199 | 78 | 0 | 443 | 88 | 0 | 0
20:30 | 2327.5 | 711 | 1834.5 | 253 | 3141 | 199 | 76.5 | 0 | 431.5 | 89.5 | 0 | 0
21:00 | 2335 | 711 | 1834 | 192 | 3065 | 199 | 75 | 0 | 420 | 91 | 0 | 0
21:30 | 2326 | 711 | 1802.5 | 108.5 | 3019.5 | 199 | 77.5 | 0 | 382.5 | 88.5 | 0 | 0
22:00 | 2317 | 711 | 1771 | 25 | 2974 | 199 | 80 | 0 | 345 | 86 | 0 | 0
22:30 | 2324.5 | 711 | 1753.5 | 12.5 | 2784.5 | 199 | 81 | 0 | 222 | 80.5 | 0 | 0
23:00 | 2332 | 711 | 1736 | 0 | 2595 | 199 | 82 | 0 | 99 | 75 | 0 | 0
23:30 | 2263.5 | 625 | 1710.5 | 0 | 2517.5 | 199 | 79.5 | 0 | 74.5 | 72 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 26.5° C
24:00 | 2195 | 539 | 1685 | 0 | 2440 | 199 | 77 | 0 | 50 | 69 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 184.589 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.589 MKWHr
Note on W13: Author:

## Generation
g | 2022-01-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 35 | 38 | 45 | 46 |  | 38 | 38 | 38 | 35 | 40 | 42 | 37 | 1008300
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 976000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | [16 empty] | 1000000
5 | Raozan 25 MW PP | [9 empty] | 2 | 8 | 8 | 8 | 8 |  |  | 3 | 14 |  | 17 | 17 | 17 | 17 | 17 |  |  | 146944
| Teknaf 20MW PP (Solartech) | [7 empty] | 3 | 13 | 18 | 20 | 20 | 18 | 16 | 13 | 8 | 1 | [9 empty] | 132300
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 45 |  | 51 | 51 | 51 | 51 | 51 |  |  | 230121
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 70 | 86 | 105 | 105 | 105 | 105 | 68 | 34 | 34 | 79 |  | 105 | 105 | 85 | 34 | 17 | 17 | 17 | 1313927
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 20 |  | 20 | 20 | [5 empty] | 45504
14 | Titas 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 50 |  |  | 236680
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 250 | 95 | 45 | 45 | 45 | 45 | 90 | 173 | 242 | 265 | 265 | 275 | 277 | 277 | 275 | 277 | 277 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 285 | 5304216
19 | Ashuganj 195MW PP (APSCL-United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 384727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | [13 empty] | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 150 | 172 | 1306000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 320 | 320 | 320 | 320 | 280 | 240 | 220 | 220 | 220 | 190 | 190 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 122 | 0 | 5373664
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 120 | 120 | 120 | 100 | 100 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2103780
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 666936
33 | Ashuganj 225 MW CCPP | [24 empty] | 28 | 32 | 60000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 275 | 305 | 300 | 300 | 300 | 265 | 285 | 290 | 265 | 270 | 270 | 335 | 270 |  | 270 | 270 | 270 | 270 | 270 | 275 | 260 | 6812000
| Ashuganj 450 MW CCPP(North) | 240 | 240 | 240 | 150 | 150 | 150 | 180 | 275 | 275 | 255 | 200 | 255 | 265 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5487000
35 | Ashuganj 55 MW PP (Precision) | 56 | 55 | 55 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 53 | 52 | 56 | 56 | 56 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 10 | 1300800
36 | Chandpur 150 MW CCPP | 129 | 127 | 129 | 132 | 132 | 130 | 129 | 127 | 130 | 127 | 122 | 122 | 122 | 122 | 121 | 125 | 125 | 132 |  | 131 | 130 | 131 | 131 | 130 | 131 | 133 | 3059620
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4185750
41 | Haripur 360MW CCPP(HPL) | 155 | 153 | 149 | 162 | 164 | 171 | 168 | 170 | 162 | 181 | 215 | 228 | 234 | 238 | 242 | 240 | 254 | 250 |  | 250 | 256 | 254 | 253 | 233 | 213 | 203 | 4908000
42 | RPCL 210MW CCPP | 50 | 52 | 52 | 52 | 52 | 53 | 53 | 52 | 53 | 51 | 46 | 44 | 45 | 45 | 44 | 44 | 46 | 47 |  | 46 | 47 | 46 | 50 | 50 | 50 | 50 | 1159680
43 | Sutiakhali 50 MW Solar PP
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 1012000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 71 | 71 | 72 | 73 | 73 | 72 | 40 | 72 | 71 | 71 | 71 | 68 | 68 | 66 | 68 | 40 | 67 | 64 |  | 71 | 71 | 70 | 71 | 71 | 70 | 71 | 1609728
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 79 | 78 | 81 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1921920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 165 | 165 | 165 | 165 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4503980
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251640
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 2 | 2 |  | 2 | 2 | 2 | 2 | 5 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 147024
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 48 | 51 | 51 | 51 | 50 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1211400
56 | Shahjahanulla 25 MW PP | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 532948
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 280 | 285 | 290 | 305 | 280 | 310 | 290 | 300 | 280 | 285 | 300 | 275 | 290 | 295 | 300 | 295 |  | 305 | 300 | 300 | 300 | 290 | 270 | 280 | 7183500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 350 | 350 | 300 | 370 | 320 | 320 | 320 | 400 | 400 | 320 | 350 | 350 | 400 | 375 |  | 400 | 400 | 400 | 400 | 400 | 402 | 400 | 8878200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 744978
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 21 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 529920
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477120
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 |  | 19 | 19 | 19 | 16 | 13 | 19 | 19 | 382500
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 22 | 22 | 22 | 0 | 468324
63 | Impoprt (Tripura) | 72 | 70 | 68 | 68 | 63 | 61 | 64 | 71 | 86 | 90 | 85 | 88 | 94 | 96 | 84 | 82 | 85 | 99 |  | 95 | 93 | 88 | 91 | 86 | 75 | 69 | 1950720
64 | Malancha, Ctg. EPZ (United) | 34 | 34 | 36 | 38 | 40 | 40 | 38 | 13 | 5 | 5 | 3 | 3 | 11 | 9 | 3 | 2 | 2 | 4 |  | 10 | 14 | 20 | 27 | 30 | 34 | 34 | 483240
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 456588
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244980
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 30 |  | 25 | 25 | 30 | 33 | 33 | 33 | 33 | 627000
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 245630
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 0 | 6 | 9 | 0 | 6 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 199260
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 532200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 |  | 16 |  | 17 | 33 | 33 | 17 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 22 | 33 | 33 | 663200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [17 empty] | 17 | [8 empty] | 18240
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 23 | 46 | 52 | 75 | 114 | 108 | 85 | 85 | 85 | 85 | 85 | 85 | 105 |  | 113 | 113 | 113 | 113 | 113 | 55 | 55 | 1781640
| Manikgonj 162MW PP(MPGL) | 162 | 108 | 17 | 17 | 17 | 20 | 144 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3350880
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 25 | 25 | 52 | 52 | 52 | 25 | 25 | 25 | 25 | 45 |  | 51 | 51 | 51 | 51 | 51 |  |  | 580320
79 | Kodda 150MW PP | [9 empty] | 16 | 48 | 16 | 16 |  |  |  |  | 100 |  | 100 | 100 | 100 | 82 | 32 |  |  | 506400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 | 25 | 30 | 34 | 34 | 34 | 34 | 43 |  | 52 | 25 | 25 | 25 | 8 | 8 | 8 | 516557
| Gazipur 100 MW PP | 105 | 35 | 17 | 17 | 17 | 20 | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1998000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27000
| Jodiac Power | 54 | 54 | 54 | 54 | 39 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 1038107
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 20 | 74 | 97 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 68 | 68 | 68 | 1970460
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 6 | 11 | 11 | 12 | 11 | 11 | 12 | 12 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 166421
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) |  |  |  |  | 1 | 17 | 17 | 27 | 53 | 54 | 104 | 104 | 104 | 104 | 75 | 35 | 22 | 51 |  | 104 | 104 | 104 | 104 | 104 | 70 | 53 | 1422720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 4 | 10 | [6 empty] | 10 |  | 20 | 10 | [5 empty] | 47880
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1251568
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 7 | 7 | 7 | 7 | 40 | 72 | 94 | 102 | 102 | 102 | 102 | 102 | 102 | 60 | 60 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1676592
95 | Patenga 50MW PP (Baraka) | 46 | 41 | 46 | 46 | 46 | 46 | 46 | 47 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1106880
96 | Chattogram 108 MW PP (ECPV) | 67 | 50 | 51 | 51 | 56 | 83 | 84 | 85 | 84 | 84 | 82 | 79 | 80 | 81 | 77 | 77 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 90 | 90 | 1862400
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 35 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 40 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 794016
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1336691
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 130 | 163 | 130 | 110 | 163 | 163 | 110 | 110 | 110 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3511472
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 9150
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 877320
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 190 |  | 197 | 133 | 105 | 62 |  |  |  | 493900
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 75 |  | 60 | 60 | 60 | 60 | 25 |  |  | 280898
106 | Mymensingh 200 MW PP (United) | 160 | 80 | 60 | 60 | 60 | 69 | 130 | 180 | 185 | 185 | 173 | 175 | 175 | 184 | 184 | 183 | 192 | 183 |  | 173 | 173 | 174 | 184 | 185 | 184 | 193 | 3787200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 98 |  | 100 | 100 | 99 | 70 |  |  |  | 330805
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 12 | 38 | 138 | 149 | 149 | 149 | 149 | 149 | 149 | 137 | 127 | 149 |  | 149 | 149 | 149 | 149 | 149 | 139 | 110 | 2408400
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 80 | 70 | 90 | 90 | 90 | 76 | 90 | 90 | 90 | 90 | 50 | 50 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1617600
116 | Chandpur 200MW (Desh energy) | [17 empty] | 10 | [8 empty] | 25920
117 | Ashuganj 150MW PP (Midland) | 142 | 142 | 145 | 138 | 133 | 128 | 135 | 130 | 130 | 123 | 128 | 127 | 125 | 135 | 133 | 100 | 100 | 120 |  | 145 | 142 | 145 | 143 | 143 | 142 | 137 | 3218313
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 19 | 70 | 104 | 104 | 94 | 103 | 80 | 80 | 60 | 60 | 112 |  | 112 | 112 | 112 | 112 | 112 | 65 | 40 | 1562400
| Anwara 300 MW PP (United) |  |  |  |  | 2 | 16 | 16 | 15 | 65 | 65 | 100 | 50 | 80 | 65 | 65 | 30 | 30 | 100 |  | 100 | 100 | 80 | 30 | 16 |  |  | 998618
| Juldah unit-2 (Acorn) |  |  |  |  | 10 | 10 | 10 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 30 | 20 | 20 | 100 |  | 100 | 100 | 100 | 50 | 20 | 20 | 20 | 1191360
| Anlima Energy Ltd. | 51 | 51 | 51 | 51 | 51 | 76 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 104 | 116 | 116 | 116 | 116 | 116 | 116 | 2480236
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445680
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 4 | 16 | 23 | 28 | 29 | 31 | 23 | 17 | 9 | 2 | [9 empty] | 180589
Chandpur 115(Doreen)
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 |  | 25 |  | 31 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1280520
120 | Eastern Zone Total | 4717 | 4332 | 4156 | 4062 | 3974 | 4038 | 4433 | 4985 | 5493 | 5560 | 5623 | 5742 | 5880 | 5663 | 5531 | 5235 | 5414 | 6464 |  | 6605 | 6516 | 6424 | 6204 | 5845 | 5422 | 5168 | 129636102
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 8 | 4 | 4 | 5 | 5 | 25 |  | 32 | 35 | 35 | 35 | 30 | 7 |  | 216960
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 31 | 101 | 105 | 90 | 96 | 105 | 90 | 60 | 35 | 35 | 96 |  | 105 | 105 | 105 | 105 | 105 | 70 | 35 | 1472640
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 11 | 37 | 57 | 68 | 71 | 68 | 60 | 42 | 20 | 3 | [9 empty] | 444960
131
132 | United Payra Power Ltd. | [10 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 340800
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 200 | 180 | 180 | 180 | 180 | 150 | 190 | 187 | 180 | 190 | 221 | 215 | 219 | 219 | 222 | 222 | 222 |  | 220 | 221 | 220 | 220 | 220 | 220 | 220 | 4930991
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [11 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 201216
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 273541
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 92 | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2220104
140 | Bhola 33 MW PP (Venture) | 16 | 15 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 13 | 14 | 17 | 17 | 17 | 15 | 13 | 15 | 20 |  | 20 | 20 | 21 | 22 | 22 | 20 | 19 | 387800
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 8 |  | 10 | [6 empty] | 33600
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 5 |  | 10 | 10 | 5 |  |  |  |  | 19456
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [11 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 50 |  | 50 | 50 | 67 | 67 | 67 | 15 |  | 435168
146 | Bheramara HVDC | 484 | 476 | 477 | 476 | 476 | 476 | 561 | 663 | 663 | 662 | 663 | 663 | 663 | 663 | 663 | 664 | 663 | 711 |  | 711 | 711 | 711 | 711 | 711 | 711 | 539 | 14965090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 300 | 300 | 300 | 260 | 260 | 230 | 180 | [19 empty] | 2108800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 200 | 199 | 200 | 199 | 199 | 199 | 199 | 198 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4855000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [11 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 45 | 50 | 50 | 50 | 50 | 50 | 613005
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 27780
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 205 | 168 | 162 | 160 | 163 | 163 | 162 | 175 | 176 | 163 | 154 | 155 | 165 | 164 | 159 | 162 | 165 | 200 |  | 173 | 169 | 171 | 179 | 176 | 171 | 170 | 4322445
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 315 | 296 | 309 | 297 | 325 | 379 | 375 | 405 | 311 | 335 | 298 | 336 | 377 | 326 | 305 | 409 | 430 | 415 |  | 394 | 411 | 388 | 380 | 344 | 347 | 342 | 8419672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [10 empty] | 5 | [5 empty] | 4 | 5 |  | 20 | 20 | 20 | 20 |  |  |  | 58710
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 522720
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190386
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [9 empty] | 16 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 |  |  | 420983
167 | Katakhali 50 MW Peaking PP | [9 empty] | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 |  |  | 359823
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 12 | 34 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 |  | 43 | 52 | 52 | 43 | 52 | 52 | 52 | 708960
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 22 | 50 | 50 | 41 | 50 | 50 | 65 | 100 |  | 100 | 100 | 100 | 100 | 100 | 42 |  | 866168
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 20 |  | 50 | 50 | 50 |  |  |  |  | 102036
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 70 | 73 | 92 | 93 | 70 | 70 | 35 | 35 | 35 | 35 | 70 |  | 90 | 113 | 113 | 113 | 113 | 113 | 70 | 1374624
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 35 | 80 | 95 | 95 | 95 | 70 | 70 | 35 | 35 | 35 | 35 | 95 |  | 95 | 95 | 113 | 113 | 113 | 113 | 113 | 1443168
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 112 | 112 | 96 | 70 | 70 | 72 | 112 | 112 | 112 | 112 | 112 | 112 | 111 | 112 | 112 | 106 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2567856
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 1 | 2 | 3 | 4 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 29291
178 | Energypac Power Venture Thakurgaon Ltd. | [14 empty] | 4 | 13 | [10 empty] | 18816
178