## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:November 2021
Sl. | Items | Current Month |  | Current Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-11-01 |  | 2021-10-01 |  | 2020-11-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10389 | 2021-11-03 | 13482 | 2021-10-11 | 11572 | 02-11-2020 | 13792 | 2021-04-27
|  |  | 19:00 |  | 21:00 |  | 19:00 |  | 20:00
2 | Minimum Generation (MW) | 5609 | 2021-11-27 | 7486 | 2021-10-22 | 5330 | 28/11/20 | - | -
|  |  | 6:00 |  | 19:30 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10389 | 2021-11-03 | 13482 | 2021-10-11 | 11572 | 02-11-2020 | 13792 | 2021-04-27
|  |  | 19:00 |  | 21:00 |  | 19:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 9044 | 2021-11-01 | 11987 | 2021-10-14 | 9280 | 02-11-2020 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Demand (MW) Estimated | 10389 | 2021-11-03 | 13482 | 2021-10-11 | 11572 | 02/11/20 | 14097 | 2021-04-27
|  |  | 12:00 |  | 21:00 |  | 19:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 9579.6333 |  | 12110.3871 |  | 9501.5333 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 8132.4 |  | 10238.1935 |  | 7762.9 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 747 | 2021-11-09 | 733 | 2021-10-27 | 915 | 01/11/2020 | 956 | 27/3/2019
|  |  | 3:00 |  | 22:00 |  | 19:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 138 | 2021-11-11 | 160 | 2021-10-10 | 152 | 03/11/2020 | 194 | 12/06/19
|  |  | 11:30 |  | 18:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | 0 | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - |  |  |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | 0 | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | 0 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1073.0634 |  | 1492.9513 |  | 3010.001 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 70.8056 |  | 83.4403 |  | 92.709
22 | Net Generation of BPDB (MKWH) | 1002.2577 |  | 1409.5109 |  | 2917.292
23 | Net Generation of IPP (MKWH) | 3794.4574 |  | 5175.3075 |  | 1607.0453
24 | Net Generation of REB (MKWH) | 137.7806 |  | 147.564 |  | 122.2164
24 | Net Generation of Rental Power Plant (MKWH) | 293.2499 |  | 437.4456 |  | 280.216
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5227.7456 |  | 7169.8281 |  | 4926.7697 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 3922.3382 |  | 4548.5962 |  | 3705.2202 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 176.6325 |  | 480.4616 |  | 139.7118 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 802.3956 |  | 1701.026 |  | 634.4156 |  | 1701.026 | 2021-11-01
29 | Energy Generation by Hydro (MKWH) | 65.2371 |  | 111.4727 |  | 103.6451 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 19.3572 |  | 20.1353 |  | 4.6869 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 312.5907 |  | 391.5767 |  | 431.7992 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 537.3749 |  | 617.2962 |  | 536.2305 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 75.5028 |  | 78.4655 |  | 66.6805 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:November 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10389 | 2021-11-03 | 19:00
Generation Period
| Dhaka | MW | 3840
| Chattogram | MW | 1222
| Cumilla | MW | 843
| Mymensingh | MW | 745
| Sylhet | MW | 384
a) | Total supply in East zone | MW | 7034
| Khulna | MW | 1115
| Barisal | MW | 254
| Rajshahi | MW | 928
| Rangpur | MW | 576
b) | Total supply in West zone | MW | 2873
c) | Total supply in both zone ( a+b) | MW | 9907
Ref: | 27.21.0000.603.16.087.20.447 | Date: 18/10/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 500 | 25--11-21 | 8:00
| b) Ishurdi end | MW | 270 | 2021-11-01 | 2:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 680 | 2021-11-25 | 15:00
| b) Ishurdi end | MW | 196 | 25--11-21 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.12
| b) Ishurdi end | MKWH | 74.02
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 71.79
| b) Ishurdi end | MKWH | 3.04
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 220 | 2021-11-02 | 18:00
| b)Serajganj end | MW | 340 | 2021-11-10 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 330 | 2021-11-30 | 15:00
| b)Sirajganj end | MW | 270 | 2021-11-25 | 8:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.026 | 2021-11-25
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 1.04 | 2021-11-25
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 11.53
| b)Sirajganj end | MKWH | 53.7
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 52.21
| b)Sirajganj end | MKWH | 11.69
30 | Transmission loss of EWI /NO-2 | % | 2.021
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
2nd East-West Interconnector Loss:
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062
| Difference (-) : | 3516000
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: November2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Uttara 3rd phase | 132/33 kV transformer GT-2 | 2021-11-08 06:23 | 2021-11-08 07:08 | 0:45 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-1 | 2021-11-12 02:52 | 2021-11-12 02:52 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-11-12 14:00 | 2021-11-12 14:00 | 0:00 | T | Tripped showing OSR trip | 0 | 0 | No interruption
Tongi(N) | 132/33 kV transformers T-1,&T-2 | 2021-11-23 22:50 | 2021-11-23 23:28 | 0:38 | T | Tripped showing O/C & E/F relay at 33 kV side | 55 | 34.8333 | Power interruption
Sherpur | 132/33 kV transformer T-2 | 2021-11-30 11:48 | 2021-11-30 15:45 | 3:57 | E/O | Due to Oil leakage at 33 kV PT | 0 | 0 | No interruption
|  |  | Total : | 5:20 |  | Unserved Energy: |  | 34.8333
Dhaka (South) Grid Circle :
Hasnabad | 33 kV reserve Bus | 2021-11-08 03:11 | 2021-11-08 03:35 | 0:24 | T | Due to 33 kV feeder fault | 40 | 16 | Power interruption
Ghoarshal | 132/33 kV transformers T-1,&T-2 | 2021-11-17 17:17 | 2021-11-17 17:17 | 0:00 | T | Tripped showing E/F relay at 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformers T-1 | 2021-11-21 17:20 | 2021-11-21 17:38 | 0:18 | T | Due to 33 kV feeder fault | 58 | 17.4 | Power interruption
| 132/33 kV transformers T-2 | 2021-11-21 17:20 | 2021-11-21 18:02 | 0:42 | T
Nawabganj | 33 kV Bus | 2021-11-23 08:04 | 2021-11-23 08:47 | 0:43 | T | Due to red-hot maint at 33 kV Bus | 20 | 14.3333 | Power interruption
Siddhirganj | 132/33 kV transformers T-1,&T-2 | 2021-11-29 14:28 | 2021-11-29 15:19 | 0:51 | T | Due to bursting of L/A | 90 | 76.5 | Power interruption
|  |  | Total : | 0:24 |  | Unserved Energy: |  | 124.2333
Chattogram Grid Circle :
Dohazari | 132/33 kV transformer T-2 | 2021-11-11 07:28 | 2021-11-11 07:57 | 0:29 | T | Due to red-hot maint | 0 | 0 | No interruption
Bakulia | 132/33 kV transformers T-1,&T-2 | 2021-11-29 15:15 | 2021-11-29 15:35 | 0:20 | T | Tripped showing O/C & E/F relay at 33kV feeder fault | 50 | 16.6667 | Power interruption
|  |  | Total : | 0:49 |  | Unserved Energy: |  | 16.6667
Cumilla Grid Circle :
Shahjibazar | 132/33 kV transformer T-2 | 2021-11-03 23:37 | 2021-11-04 00:01 | 0:24 | E/O | Tripped showing 33 kV feeder fault | 30 | 12 | Power interruption
Cumilla(N) | 230/132 kV transformer T-2 | 2021-11-15 05:41 | 2021-11-15 09:54 | 4:13 | T | Tripped showing lock out relay | 0 | 0 | No interruption
Ashuganj | 230/132 kV transformer OAT-12 | 2021-11-22 17:04 | 2021-11-22 19:36 | 2:32 | T | Tripped showing master protection relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T-2 | 2021-11-23 14:50 | 2021-11-23 16:03 | 1:13 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 8:22 |  |  |  | 12
Khulna Grid Circle :
Gopalganj(O) | 132/33 kV transformer T-1 | 2021-11-04 13:38 | 2021-11-04 15:08 | 1:30 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| 132/33 kV transformers T-1 | 2021-11-10 05:46 | 2021-11-10 07:15 | 1:29 | T | Tripped showing O/V relay
| 132/33 kV transformers T-2 | 2021-11-10 05:46 | 2021-11-10 07:07 | 1:21 | T |  | 35 | 47.25 | Power interruption 05:46 to 07:07
Faripur | 132/33 kV transformers T-1 | 2021-11-16 06:55 | 2021-11-16 07:26 | 0:31 | T | Due to 33 kV feeder fault | 60 | 31 | Power interruption 06:55 to 7:26
| 132/33 kV transformers T-2 | 2021-11-16 06:55 | 2021-11-16 09:24 | 2:29 | T
Mongla | 132/33 kV transformers T-1 & T2 | 2021-11-21 11:58 | 2021-11-21 12:18 | 0:20 | T | Due to gas pressure low at 33 kV Breaker | 30 | 10 | Power interruption
Bhandaria | 132/33 kV transformer T-2 | 2021-11-26 07:10 | 2021-11-26 07:54 | 0:44 | E/O | Due to red-hot maint | 12 | 8.8 | Power interruption
|  |  | Total : | 8:24 |  | Unserved Energy: |  | 97.05
HVDC Grid Circle :
HVDC | 230 kV 20DF32 filter | 2021-11-15 09:04 | 2021-11-15 16:31 | 7:27 | T | Tripped showing differential relay | 0 | 0 | No interruption
| 400 kV 10 CF25 | 2021-11-26 11:02 | 2021-11-26 20:30 | 9:28 | T | Tripped showing pole discrepancy | 0 | 0 | No interruption
|  |  | Total : | 16:55 |  |  |  | 0
Bogura Grid Circle:
Naogaon | 132/33 kV transformer T-2 | 2021-11-08 18:15 | 2021-11-08 19:14 | 0:59 | E/O | Due to red-hot maint | 16 | 15.7333 | Power interruption
Natore | 132/33 kV transformer T-4 | 2021-11-21 06:23 | 2021-11-21 06:58 | 0:35 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T-2 | 2021-11-21 08:05 | 2021-11-21 13:03 | 4:58 | T | Tripped showing O/C & E/F relay at 33 kV feeder fault | 7 | 34.7667 | Power interruption
Naogaon | 132/33 kV transformers T-2 | 2021-11-21 09:39 | 2021-11-21 10:05 | 0:26 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformers T-3 | 2021-11-21 09:39 | 2021-11-21 10:09 | 0:30 | T |  | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformers T-2 | 2021-11-30 10:05 | 2021-11-30 10:15 | 0:10 | T | Due to 33 kV feeder fault | 25 | 4.1667 | Power interruption
|  |  | Total : | 7:38 |  |  |  | 54.6667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 47:52 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: November2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Uttara 3rd phase 132 kV Ckt | 2021-11-12 22:38 | 2021-11-13 14:31 | 15:53 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-11-16 10:06 | 2021-11-16 15:40 | 5:34 | T | Due to opeartion SPS during relay test | 0 | 0
| Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-16 10:06 | 2021-11-16 10:13 | 0:07 | T |  | 25 | 2.9167 | Power interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV Ckt-2 | 2021-11-19 06:52 | 2021-11-19 06:59 | 0:07 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-1 | 2021-11-22 03:44 | 2021-11-22 04:13 | 0:29 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2021-11-24 11:57 | 2021-11-24 12:05 | 0:08 | T | Tripped showing Dist. Z1 relay. | 200 | 26.6667 | Power interruption
| Tongi-Kabirpur 132 kV Ckt-1 | 2021-11-24 11:59 | 2021-11-24 12:05 | 0:06 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-24 11:57 | 2021-11-24 12:35 | 0:38 | T | Tripped showing Dist. Z1 relay. | 15 | 9.5 | Power interruption
|  |  | Total : | 7:09 |  | Unserved Energy: |  | 39.0833
Dhaka (South) Grid Circle :
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV Ckt-1 | 2021-11-01 06:25 | 2021-11-01 07:06 | 0:41 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
| Shyampur(N)-Shyampur(O) 132 kV Ckt-2 | 2021-11-01 06:25 | 2021-11-01 07:04 | 0:39 | T |  |  |  | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV Ckt-2 | 2021-11-12 11:36 | 2021-11-12 11:59 | 0:23 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV Ckt-1 | 2021-11-13 18:59 | 2021-11-14 09:11 | 14:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV Ckt-1 & 2 | 2021-11-19 09:43 | 2021-11-19 10:03 | 0:20 | T | Tripped showing O/C & E/F. relay at 33 kV side | 0 | 0 | No interruption
Ghorashal P/S | Ghorashal-Ghorashal regent Power 230 kV Ckt | 2021-11-25 15:50 | 2021-11-26 08:55 | 17:05 | T | Tripped showing O/C & E/F. relay | 0 | 0 | Power interruption
APR | APR-Shyampur 230 kV Ckt | 2021-11-29 06:40 | 2021-11-29 06:56 | 0:16 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV Ckt-2 | 2021-11-29 08:19 | 2021-11-29 09:12 | 0:53 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 34:29 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Abul Khair 230 kV Ckt | 2021-11-05 14:03 | 2021-11-05 14:46 | 0:43 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Abul khair | Abul khair -BSRM 230 kV Ckt | 2021-11-07 09:50 | 2021-11-07 10:35 | 0:45 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-11-09 09:54 | 2021-11-09 10:11 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV Ckt-2 | 2021-11-15 12:44 | 2021-11-15 13:05 | 0:21 | T |  | 125 | 43.75 | Power interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-11-15 12:04 | 2021-11-15 12:43 | 0:39 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-15 12:04 | 2021-11-15 17:17 | 5:13 | E/O |  | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-2 | 2021-11-17 13:06 | 2021-11-17 13:14 | 0:08 | T | Tripped showing Dist.relay | 137 | 18.2667 | Power interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-2 | 2021-11-26 05:43 | 2021-11-26 06:41 | 0:58 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 9:04 |  | Unserved Energy: |  | 62.0167
Cumilla Grid Circle :
Fenchuganj | Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt | 2021-11-02 23:29 | 2021-11-02 23:37 | 0:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-11-03 05:06 | 2021-11-03 05:17 | 0:11 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2021-11-04 09:06 | 2021-11-04 09:43 | 0:37 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt-3 | 2021-11-06 20:36 | 2021-11-07 10:46 | 14:10 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt-3 | 2021-11-08 02:07 | 2021-11-08 09:18 | 7:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt-3 | 2021-11-15 03:25 |  |  | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Feni | Feni-PHP132 kV Ckt-2 | 2021-11-15 12:04 | 2021-11-15 12:27 | 0:23 | T | Tripped showing Dist. relay | 7.5 | 2.875 | Power interruption
Ashuganj | Ashuganj-Ghorashal 132 kV Ckt-2 | 2021-11-15 11:02 | 2021-11-15 13:59 | 2:57 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-11-19 11:02 | 2021-11-19 17:47 | 6:45 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 & 2 | 2021-11-21 04:23 | 2021-11-21 05:24 | 1:01 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 33:23 |  | Unserved Energy: |  | 2.875
Khulna Grid Circle :
Barisal | Barisal-Bhandaria 132 kV Ckt | 2021-11-13 14:14 | 2021-11-13 14:22 | 0:08 | T | Tripped showing Dist. Z1 relay | 22 | 2.9333 | Power interruption
|  |  | Total : | 0:08 |  | Unserved Energy: |  | 2.9333
HVDC Grid Circle :
Baghabari | Baghabari-Sirajganj 230 kV Ckt-1 | 2021-11-29 08:53 | 2021-11-29 08:53 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Thaurgaon | Thakurgaon-Panchaghar 132 kV Ckt | 2021-11-03 21:05 | 2021-11-03 21:37 | 0:32 | T | Tripped showing Dist. relay | 38 | 20.2667 | Power interruption
|  |  | Total : | 0:32 |  | Unserved Energy: |  | 20.2667
Others :
Haripur | Haripur-Ullon 132 kV Ckt | 2021-11-05 12:05 | 2021-11-05 15:17 | 3:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 3:12 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 87:57 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: November2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | 230/132 kV transformer T-03 | 2021-11-01 10:08 | 2021-11-01 16:42 | 6:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherur | 132/33 kV transformer T-3 | 2021-11-01 08:27 | 2021-11-01 16:19 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2021-11-01 14:29 | 2021-11-01 20:16 | 5:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2021-11-02 11:40 | 2021-11-02 16:19 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2021-11-02 08:18 | 2021-11-02 14:10 | 5:52 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-11-02 08:28 | 2021-11-02 11:17 | 2:49 | S/O | Due to D/W work | 20 | 56.3333 | Power interruption
Netrakona | 132/33 kV transformer T-1 | 2021-11-02 09:11 | 2021-11-02 15:50 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 33 kV Bus-2 | 2021-11-02 13:29 | 2021-11-02 13:29 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2021-11-03 10:14 | 2021-11-03 16:18 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 | 2021-11-03 09:04 | 2021-11-03 15:22 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2021-11-04 10:53 | 2021-11-04 16:16 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 | 2021-11-04 09:13 | 2021-11-04 15:14 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 & 33 kV Bus | 2021-11-06 06:21 | 2021-11-06 13:40 | 7:19 | S/O | Due to C/M work | 5 | 36.5833 | Power interruption
Aminbazar | 230/132 kV transformer T-03 | 2021-11-06 10:35 | 2021-11-06 12:35 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-01 | 2021-11-06 08:23 | 2021-11-06 16:04 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2021-11-07 08:26 | 2021-11-07 20:50 | 12:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2021-11-08 08:23 | 2021-11-08 10:05 | 1:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 main Bus | 2021-11-08 10:44 | 2021-11-08 19:04 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 | 2021-11-08 12:03 | 2021-11-08 15:42 | 3:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-1 | 2021-11-08 08:50 | 2021-11-08 15:50 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV transformer GT-1 | 2021-11-08 10:55 | 2021-11-08 16:16 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-2 | 2021-11-08 16:27 | 2021-11-08 17:41 | 1:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-11-09 10:10 | 2021-11-09 13:15 | 3:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-02 & 33 kV Bus | 2021-11-09 09:55 | 2021-11-09 11:40 | 1:45 | S/O | Due to isolator maint. | 60 | 105 | Power interruption
| 132/33 kV transformer T-2 | 2021-11-09 08:13 | 2021-11-09 15:55 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2021-11-09 08:50 | 2021-11-09 15:50 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-11-10 08:26 | 2021-11-10 16:45 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-3 | 2021-11-11 08:39 | 2021-11-11 08:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 main Bus | 2021-11-11 08:57 | 2021-11-11 22:21 | 13:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132 main Bus coupler | 2021-11-11 08:25 | 2021-11-11 16:18 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-2 | 2021-11-11 09:58 | 2021-11-11 16:20 | 6:22 | S/O |  | 0 | 0 | No interruption
Rajendrapur | 132/33 kV transformer T-1 | 2021-11-11 11:47 | 2021-11-11 17:10 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-02 | 2021-11-11 08:10 | 2021-11-11 13:45 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV transformer T-1 & 33 kV Bus | 2021-11-12 07:46 | 2021-11-12 07:46 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-3 | 2021-11-13 09:18 | 2021-11-13 16:07 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer GT-3 | 2021-11-13 09:17 | 2021-11-13 17:37 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV transformer T-1 | 2021-11-14 09:18 | 2021-11-14 11:03 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-3 | 2021-11-14 09:23 | 2021-11-14 15:31 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensing | 132 kV reserve Bus | 2021-11-15 10:25 | 2021-11-15 16:25 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-11-15 10:10 | 2021-11-15 15:45 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-1 | 2021-11-15 12:43 | 2021-11-15 17:05 | 4:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-1 | 2021-11-16 09:34 | 2021-11-16 16:13 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-1 | 2021-11-16 19:58 | 2021-11-16 21:51 | 1:53 | S/O | Due to cable connection | 0 | 0 | No interruption
Rajendrapur | 132/33 kV transformer T-2 | 2021-11-18 10:53 | 2021-11-18 16:42 | 5:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 400/230 kV transformer ATR-2 |  | 2021-11-18 14:25 |  | S/O | After maint. | 0 | 0 | No interruption
| 400/230 kV transformer ATR-3 |  | 2021-11-18 16:19 |  |  |  | 0 | 0 | No interruption
Dhamrai | 230/132 kV transformer T02 | 2021-11-20 08:43 | 2021-11-20 14:01 | 5:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-4 | 2021-11-20 09:22 | 2021-11-20 15:13 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajendrapur | 132/33 kV transformer T-3 | 2021-11-20 09:22 | 2021-11-20 15:13 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2021-11-20 09:35 | 2021-11-20 14:26 | 4:51 | S/O |  | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-4 | 2021-11-21 09:30 | 2021-11-21 15:06 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2021-11-21 09:45 | 2021-11-21 16:35 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-11-21 09:53 | 2021-11-21 16:06 | 6:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-3 | 2021-11-21 11:22 | 2021-11-21 12:25 | 1:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhangura | 132/33 kV transformer T-2 | 2021-11-21 18:34 | 2021-11-21 19:02 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T-3 | 2021-11-21 08:58 | 2021-11-21 17:03 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-2 | 2021-11-22 08:11 | 2021-11-22 08:11 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-3 | 2021-11-22 10:13 | 2021-11-22 11:40 | 1:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-AB | 2021-11-22 09:31 | 2021-11-22 15:18 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-2 | 2021-11-23 08:20 | 2021-11-23 16:52 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-2 | 2021-11-23 09:30 | 2021-11-23 15:55 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangal | 132/33 kV transformer T-4 | 2021-11-24 08:45 | 2021-11-24 14:48 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2021-11-24 11:17 | 2021-11-24 12:05 | 0:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2021-11-25 09:25 | 2021-11-25 10:15 | 0:50 | S/O | Due to relay test | 0 | 0 | No interruption
Cantonment | 132/33 kV transformer T-2 | 2021-11-26 07:48 | 2021-11-26 17:13 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-3 | 2021-11-27 09:37 | 2021-11-27 16:10 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-4 | 2021-11-29 09:34 | 2021-11-29 16:26 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV transformer GT-1 | 2021-11-29 08:58 | 2021-11-29 14:50 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 | 2021-11-29 14:24 | 2021-11-29 16:57 | 2:33 | S/O | Due to replacemeent work | 8 | 20.4 | Power interruption
Kallyanpur | 132/33 kV transformer GT-1 | 2021-11-30 08:21 | 2021-11-30 14:44 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajendrapur | 132 kV Bus-2 | 2021-11-30 11:31 | 2021-11-30 11:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformers T-1 & T3 | 2021-11-30 10:51 | 2021-11-30 11:07 | 0:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T01 | 2021-11-30 08:59 | 2021-11-30 16:55 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 366:14 |  | Unserved Energy: |  | 218.3167
Dhaka (South) Grid Circle :
Kamrangirchar | 132/33 kV transformer T1 | 2021-11-01 08:35 | 2021-11-01 15:50 | 7:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer T01 | 2021-11-01 09:46 | 2021-11-01 11:49 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 132/33 kV transformer T4 | 2021-11-01 10:54 | 2021-11-01 16:42 | 5:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer GT2 | 2021-11-02 08:30 | 2021-11-02 16:50 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T5 | 2021-11-03 08:13 | 2021-11-03 17:05 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer T1 | 2021-11-03 08:35 | 2021-11-03 15:50 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T5 | 2021-11-04 07:40 | 2021-11-04 07:40 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T5 | 2021-11-05 08:07 | 2021-11-05 12:31 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2021-11-07 07:47 | 2021-11-07 17:05 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer T01 | 2021-11-07 08:55 | 2021-11-07 16:37 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T01 | 2021-11-07 09:21 | 2021-11-07 16:29 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132 kV Bus-1 | 2021-11-07 09:45 | 2021-11-07 15:16 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T1 | 2021-11-08 07:40 | 2021-11-08 07:40 | 0:00 |  | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer ATR2 | 2021-11-08 08:54 | 2021-11-08 08:54 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer T01 | 2021-11-08 08:46 | 2021-11-08 15:59 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T01 | 2021-11-08 08:15 | 2021-11-08 15:13 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundahara | 132/33 kV transformer GT01 | 2021-11-09 09:45 | 2021-11-09 16:17 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T2 | 2021-11-10 07:21 | 2021-11-10 16:36 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-11-11 07:48 | 2021-11-11 07:48 | 0:00 |  |  | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer T02 | 2021-11-11 09:04 | 2021-11-11 16:58 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T02 | 2021-11-11 08:35 | 2021-11-11 13:42 | 5:07 | S/O |  | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer T02 | 2021-11-11 09:02 | 2021-11-11 17:54 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132 kV reserve Bus | 2021-11-15 08:52 | 2021-11-15 08:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 33/0.4 kV NLDC | 2021-11-14 08:28 | 2021-11-14 18:11 | 9:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundahara | 132/33 kV transformer T2 | 2021-11-15 08:38 | 2021-11-15 16:34 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T01 | 2021-11-16 08:45 | 2021-11-16 17:13 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbachal | 132/33 kV transformer T2 | 2021-11-17 10:22 | 2021-11-17 14:44 | 4:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Aftabnagar | 132/33 kv transformer T-1 | 2021-11-18 10:10 | 2021-11-18 14:26 | 4:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghangat | 230 kV Bus-1 | 2021-11-19 09:10 | 2021-11-19 15:55 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV transformer T2 | 2021-11-19 08:56 | 2021-11-19 20:37 | 11:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T03 | 2021-11-20 07:42 | 2021-11-20 16:16 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T03A T-3B | 2021-11-20 10:10 | 2021-11-20 15:33 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-1 | 2021-11-20 10:42 | 2021-11-20 14:35 | 3:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-2 & 33 kV Bus-2 | 2021-11-21 07:15 | 2021-11-21 08:32 | 1:17 | S/O | Due to PBS work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T03 | 2021-11-24 11:43 | 2021-11-24 11:43 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundahara | 132/33 kV transformer T3 | 2021-11-24 08:51 | 2021-11-24 12:51 | 4:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer TR1 |  | 2021-11-25 17:04 |  | S/O | After maint.work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer TR3 |  | 2021-11-25 20:09 |  |  |  | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer TR-1 | 2021-11-27 09:32 | 2021-11-27 12:36 | 3:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer TR2 | 2021-11-27 10:01 | 2021-11-27 16:47 | 6:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Gulshan | 132/33 kv transformer T-1 | 2021-11-27 08:26 | 2021-11-27 15:18 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | 132 kV Bus-1 | 2021-11-27 10:10 | 2021-11-27 15:55 | 5:45 | S/O | Due to A/M work | 0 | 0
Rampura | 230/132 kV transformer T01 | 2021-11-30 10:16 | 2021-11-30 17:52 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 231:48 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Juldah | 132/33 kv transformer T-1 | 2021-11-03 09:03 | 2021-11-03 15:29 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kv transformer T-2 | 2021-11-03 08:55 | 2021-11-03 15:55 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | 132/33 kv transformer T-2 | 2021-11-07 07:35 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari S/S-Rampur Bay-1 | 2021-11-07 15:22 | 2021-11-07 17:02 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | 230/132 kV transformer T01 | 2021-11-08 09:38 | 2021-11-08 20:34 | 10:56 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus- 1 & 2 | 2021-11-08 16:41 | 2021-11-08 20:30 | 3:49 | S/O |  | 0 | 0 | No interruption
Mirsorai | 230/132 kV transformer T01 | 2021-11-10 11:00 | 2021-11-10 17:12 | 6:12 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2021-11-10 11:02 | 2021-11-10 17:13 | 6:11 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2021-11-11 10:18 | 2021-11-11 17:10 | 6:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T1 | 2021-11-12 06:33 | 2021-11-12 11:26 | 4:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kv transformer T-3 | 2021-11-13 07:50 | 2021-11-13 13:15 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | 230/132 kV transformer MTR02 | 2021-11-13 10:28 | 2021-11-13 17:28 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Baraulia | 132/33 kv transformer T-2 |  | 2021-11-13 05:07 |  |  | After maint. | 0 | 0 | No interruption
Halishahar | 132/33 kv transformer T-3 | 2021-11-14 12:19 | 2021-11-14 15:51 | 3:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirsorai | 230/33/11 kV transformer T01 |  | 2021-11-16 19:24 |  |  | After maint. | 0 | 0 | No interruption
| 230/33/11 kV transformer T02 |  | 2021-11-17 19:23 |  |  |  | 0 | 0 | No interruption
Hathazari | Hathazari S/S-Rampur 230 Bay | 2021-11-17 09:50 | 2021-11-17 19:50 | 10:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirsorai | 230 kV Bus | 2021-11-17 10:14 | 2021-11-17 20:20 | 10:06 | S/O |  | 0 | 0 | No interruption
Mirsorai | 230/33/11 kV transformer T01 & T02 | 2021-11-17 10:11 | 2021-11-17 20:01 | 9:50 | S/O
Madunaghat | 33 kV Bus-1 | 2021-11-19 06:53 | 2021-11-19 07:32 | 0:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T2 | 2021-11-19 07:42 | 2021-11-19 07:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 & 33 kV Bus-2 | 2021-11-20 07:04 | 2021-11-20 07:04 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | 132/33 kV transformer T1 | 2021-11-20 07:09 | 2021-11-20 13:10 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer T1 | 2021-11-21 09:06 | 2021-11-21 13:10 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T1 | 2021-11-22 07:15 | 2021-11-22 13:04 | 5:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T2 | 2021-11-24 07:36 | 2021-11-24 07:36 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampur | 132 kV Bus-1 | 2021-11-26 12:30 | 2021-11-26 12:30 | 0:00
Mirsorai | 230/33/11 kV transformer T01 & T02 | 2021-11-30 10:12 | 2021-11-30 10:12 | 0:00 | S/O | Due to SAS work | 0 | 0 | No interruption
Juldah | 132/33 kV transformer T2 | 2021-11-30 08:48 | 2021-11-30 14:12 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 121:49 |  | Unserved Energy : |  | 0
Cumilla Grid Circle :
Cumilla (N) | 132/33 kV transformer T4 | 2021-11-01 09:02 | 2021-11-01 15:57 | 6:55 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T1 | 2021-11-02 08:43 | 2021-11-02 12:04 | 3:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV transformer T3 | 2021-11-03 10:19 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T2 | 2021-11-03 11:25 | 2021-11-03 12:12 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T2 | 2021-11-03 09:27 | 2021-11-03 13:25 | 3:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T2 | 2021-11-03 08:37 | 2021-11-03 16:16 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T5 | 2021-11-03 15:01 | 2021-11-03 16:55 | 1:54 | S/O | Due to connection work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T2 | 2021-11-04 09:15 | 2021-11-04 11:55 | 2:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T1 | 2021-11-04 08:32 | 2021-11-04 13:25 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T2 | 2021-11-04 08:47 | 2021-11-04 16:30 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T1 & T3 | 2021-11-04 13:35 | 2021-11-04 16:48 | 3:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132 kV Bus-A | 2021-11-06 09:40 | 2021-11-06 15:58 | 6:18 | S/O | Due to Doren P/P work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T1 | 2021-11-07 08:32 | 2021-11-07 16:40 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer ICT T1 | 2021-11-07 09:08 | 2021-11-07 13:57 | 4:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T1 | 2021-11-07 09:39 | 2021-11-07 15:19 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T1 | 2021-11-07 08:30 | 2021-11-07 12:14 | 3:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-11-07 12:22 | 2021-11-07 15:12 | 2:50 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2021-11-08 08:48 | 2021-11-08 15:44 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T1 | 2021-11-08 08:43 | 2021-11-08 15:55 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer ICT01 | 2021-11-09 08:40 | 2021-11-09 14:12 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Chattak | 132 kV Bus-A | 2021-11-09 09:06 | 2021-11-09 14:01 | 4:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T1 | 2021-11-09 08:26 | 2021-11-10 17:15 | 32:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Chattak | 132 kV Bus-B | 2021-11-09 14:30 | 2021-11-09 16:06 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T1 | 2021-11-10 08:31 | 2021-11-10 16:50 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T6 | 2021-11-11 09:58 | 2021-11-11 16:38 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T1 | 2021-11-11 08:22 | 2021-11-11 16:30 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T1 | 2021-11-13 09:20 | 2021-11-13 09:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T1 | 2021-11-13 08:21 | 2021-11-13 16:20 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T1 | 2021-11-13 08:57 | 2021-11-13 16:46 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV transformer T1 | 2021-11-14 07:35 | 2021-11-14 10:46 | 3:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 & 33 kV Bus | 2021-11-14 07:35 | 2021-11-14 10:46 | 3:11 |  | Due to C/M work | 0 | 0 | Power interruption
Fenchuganj | 132/33 kV transformer T1 | 2021-11-14 09:13 | 2021-11-14 16:35 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2021-11-14 08:22 | 2021-11-14 11:09 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformers T2 & T3 | 2021-11-14 08:40 | 2021-11-14 16:25 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer AT-02 | 2021-11-15 09:01 | 2021-11-15 17:13 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T2 | 2021-11-15 09:15 | 2021-11-15 14:34 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T2 | 2021-11-16 08:31 | 2021-11-16 16:59 | 8:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T4 | 2021-11-16 09:10 | 2021-11-16 09:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformers T2 & T3 | 2021-11-16 08:56 | 2021-11-16 16:40 | 7:44 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T3 | 2021-11-17 08:36 | 2021-11-17 16:59 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer T2 | 2021-11-17 09:58 | 2021-11-17 16:02 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T3 | 2021-11-17 08:39 | 2021-11-17 15:40 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer T2 | 2021-11-18 09:50 | 2021-11-18 16:50 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Comilla(N) | 230/132 kV transformer T-01 | 2021-11-20 09:11 | 2021-11-20 15:26 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T2 | 2021-11-21 08:52 | 2021-11-21 16:26 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformers T1 & T2 & 33 kV Bus | 2021-11-21 09:01 | 2021-11-21 11:07 | 2:06 | S/O | Due to C/M work | 25 | 52.5 | Power interruption
Beanibazar | 132/33 kV transformer T1 | 2021-11-21 09:34 | 2021-11-21 16:55 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132 kV Bus-A | 2021-11-22 10:53 | 2021-11-22 15:10 | 4:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T2 | 2021-11-22 14:58 | 2021-11-22 17:06 | 2:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 400/230 kV transformer ICT-2 | 2021-11-23 08:43 | 2021-11-23 16:00 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T2 | 2021-11-23 08:36 | 2021-11-23 16:48 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2021-11-23 08:42 | 2021-11-23 16:13 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T5 | 2021-11-23 09:10 | 2021-11-23 13:45 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(N) | 400/230 kV transformer IBT-1 | 2021-11-24 08:36 | 2021-11-24 08:36 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/230 kV transformer IBT-2 | 2021-11-24 08:50 | 2021-11-24 08:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T2 | 2021-11-23 14:12 | 2021-11-23 17:05 | 2:53 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2021-11-24 08:53 | 2021-11-24 13:54 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer ICT-2 | 2021-11-24 08:48 | 2021-11-24 15:29 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T1 | 2021-11-24 09:35 | 2021-11-24 14:15 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T2 | 2021-11-24 08:52 | 2021-11-24 16:18 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer ICT-2 | 2021-11-25 09:20 | 2021-11-25 14:12 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T1 with 132 kV bus | 2021-11-25 09:25 | 2021-11-25 16:59 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | 132/33 kV transformer T1 | 2021-11-27 10:01 | 2021-11-27 12:44 | 2:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132 kV Bus-2 | 2021-11-28 08:28 | 2021-11-28 19:35 | 11:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230 kV Bus-2 | 2021-11-29 09:28 | 2021-11-29 16:44 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-11-30 08:31 | 2021-11-30 17:21 | 2021-11-01 07:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV transformer T4 | 2021-11-30 12:45 | 2021-11-30 12:45 | 0:00 | S/O | Due to 33 kV DS of Jangalia | 0 | 0 | No interruption
|  |  | Total : | 49:21 |  | Unserved Energy : |  | 52.5
Khulna Grid Circle :
Madaripur | 132/33 kV transformer T2 | 2021-11-01 07:27 | 2021-11-01 07:27 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | 230/132 kV transformer T-01 | 2021-11-01 08:44 | 2021-11-01 17:40 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 | 2021-11-01 09:02 | 2021-11-01 13:58 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-01 | 2021-11-02 08:07 | 2021-11-02 16:31 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-02 | 2021-11-02 08:06 | 2021-11-02 16:49 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-03 | 2021-11-02 09:03 | 2021-11-02 12:58 | 3:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-01 | 2021-11-03 08:16 | 2021-11-03 16:40 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-03 | 2021-11-03 09:04 | 2021-11-03 13:27 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-03 | 2021-11-04 07:35 | 2021-11-04 17:17 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T-03 | 2021-11-04 07:26 | 2021-11-04 16:48 | 9:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Banapole | 132/33 kV transformer T-02 | 2021-11-04 08:17 | 2021-11-04 15:42 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-01 | 2021-11-04 08:55 | 2021-11-04 13:40 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Banapole | 132/33 kV transformer T-02 | 2021-11-05 08:02 | 2021-11-05 15:35 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T-01 | 2021-11-06 07:30 | 2021-11-06 07:30 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132 kV Bus coupler | 2021-11-06 07:30 | 2021-11-06 07:30 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T-02 | 2021-11-06 07:56 | 2021-11-06 16:07 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-02 | 2021-11-06 09:18 | 2021-11-06 17:02 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Norail | 132/33 kV transformer T-01 | 2021-11-06 09:31 | 2021-11-06 14:54 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-02 | 2021-11-06 09:05 | 2021-11-06 14:29 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-02 | 2021-11-07 08:10 | 2021-11-07 16:28 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Norail | 132/33 kV transformer T-01 | 2021-11-07 09:18 | 2021-11-07 14:42 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-02 | 2021-11-07 09:02 | 2021-11-07 13:40 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-02 | 2021-11-08 08:39 | 2021-11-08 20:23 | 11:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Norail | 132/33 kV transformer T-02 | 2021-11-08 09:05 | 2021-11-08 15:06 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-02 | 2021-11-08 09:02 | 2021-11-08 15:19 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV transformer T-01 | 2021-11-09 08:42 | 2021-11-09 15:27 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-01 | 2021-11-09 08:26 | 2021-11-09 16:14 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-02 | 2021-11-09 09:49 | 2021-11-09 14:53 | 5:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV transformer T-03 | 2021-11-11 09:16 | 2021-11-11 15:30 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T-01 | 2021-11-11 14:29 | 2021-11-11 14:43 | 0:14 | S/O | Due to protection test | 0 | 0 | No interruption
Basishal(N) | 132/33 kV transformer T-04 | 2021-11-13 08:35 | 2021-11-13 16:51 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-A | 2021-11-13 09:50 | 2021-11-13 16:52 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-03 | 2021-11-13 08:30 | 2021-11-13 17:07 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Basishal(N) | 132/33 kV transformer T-04 | 2021-11-14 08:28 | 2021-11-14 17:17 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-B | 2021-11-14 08:21 | 2021-11-14 16:36 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Basishal(N) | 132/33 kV transformer T-04 | 2021-11-15 09:19 | 2021-11-15 16:34 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-03 | 2021-11-15 09:42 | 2021-11-15 18:10 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-01 | 2021-11-16 08:18 | 2021-11-16 16:49 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Basishal(N) | 132/33 kV transformer T-05 | 2021-11-16 08:20 | 2021-11-16 20:29 | 12:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-01 |  | 2021-11-16 09:24 |  |  | After maint. | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer T-01 | 2021-11-16 10:54 | 2021-11-16 13:59 | 3:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-01 | 2021-11-16 14:45 | 2021-11-16 16:44 | 1:59 | S/O | Due to C/M work | 22 | 43.6333 | Power interruption
Bagerhat | 132/33 kV transformer T-01 | 2021-11-17 08:09 | 2021-11-17 15:08 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Basishal(N) | 132/33 kV transformer T-05 | 2021-11-17 09:07 | 2021-11-17 17:22 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Benapole | 132 kV Bus coupler | 2021-11-17 08:18 | 2021-11-17 15:34 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-02 | 2021-11-18 10:36 | 2021-11-18 13:42 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Benapole | 132 kV Bus -A | 2021-11-18 08:21 | 2021-11-18 15:07 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-02 | 2021-11-20 08:14 | 2021-11-20 16:28 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 230/132 kV transformer T-01 | 2021-11-20 08:41 | 2021-11-20 16:55 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132 kV Bus -A | 2021-11-20 09:19 | 2021-11-20 14:34 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | 33 kV Bus section-3 | 2021-11-20 08:56 | 2021-11-20 20:37 | 11:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(C) | 132 kV Bus | 2021-11-20 08:10 | 2021-11-20 13:15 | 5:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-02 | 2021-11-21 08:14 | 2021-11-21 12:38 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132 kV Bus coupler | 2021-11-21 08:01 | 2021-11-21 14:10 | 6:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 230/132 kV transformer T-01 | 2021-11-21 08:59 | 2021-11-21 16:25 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2021-11-22 09:18 | 2021-11-22 13:27 | 4:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2021-11-23 09:23 | 2021-11-23 16:08 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-03 | 2021-11-24 08:33 | 2021-11-24 15:47 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 230/132 kV transformer T-01 | 2021-11-24 08:52 | 2021-11-24 16:08 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T-06 | 2021-11-24 08:10 | 2021-11-24 14:15 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T-01 | 2021-11-24 08:40 | 2021-11-24 13:17 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-03 | 2021-11-25 07:48 | 2021-11-25 16:23 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T-06 | 2021-11-25 08:35 | 2021-11-25 15:10 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | 230/132 kV transformer T-02 | 2021-11-25 09:07 | 2021-11-25 16:16 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | 230/132 kV transformer T-02 | 2021-11-27 08:53 | 2021-11-27 16:41 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR-2 | 2021-11-28 09:21 | 2021-11-28 16:44 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV transformer TR-3 | 2021-11-28 08:30 | 2021-11-28 15:49 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 230 kV Bus-1 | 2021-11-29 08:54 | 2021-11-29 15:32 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | 230 kV Bus-2 | 2021-11-30 09:07 | 2021-11-30 16:32 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 447:51 |  | Unserved Energy : |  | 43.6333
HVDC Grid Circle
Bheramara GK | 132/33 kV transformer T1 | 2021-11-01 08:06 | 2021-11-01 16:52 | 8:46 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | HVDC 10CF12 reactor | 2021-11-02 09:18 | 2021-11-02 16:03 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara GK | 132/33 kV transformer T2 | 2021-11-02 08:11 | 2021-11-02 15:27 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-11-03 08:20 | 2021-11-03 14:33 | 6:13 | S/O |  | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC 400 kV 10CF22 | 2021-11-03 12:43 | 2021-11-03 17:01 | 4:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara HVDC 400 kV pole-1 | 2021-11-04 07:24 |  |  | S/O | Due to maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T4 | 2021-11-04 08:35 | 2021-11-04 14:15 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC 10CF24 filter | 2021-11-09 09:54 | 2021-11-09 16:16 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/33 kV transformer T2 | 2021-11-11 10:17 | 2021-11-11 16:40 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | 230 kV 20DF22 filter | 2021-11-14 11:15 | 2021-11-14 15:54 | 4:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| 33/04 kV auxiliary | 2021-11-14 11:06 | 2021-11-14 15:05 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T1 | 2021-11-26 10:48 | 2021-11-26 12:09 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T1 | 2021-11-27 09:27 | 2021-11-27 15:52 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | 230/132 kV transformer TR-1 | 2021-11-29 08:29 | 2021-11-29 12:06 | 3:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T2 | 2021-11-30 09:20 | 2021-11-30 16:24 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 78:48 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Niyamatpur | 132/33 kV transformer T3 | 2021-11-01 08:47 | 2021-11-01 17:15 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T1 | 2021-11-01 08:30 | 2021-11-01 16:50 | 8:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T1 | 2021-11-01 10:33 | 2021-11-01 11:33 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-11-01 11:36 | 2021-11-01 12:15 | 0:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Panchaghar | 132/33 kV transformer T3 | 2021-11-02 08:08 | 2021-11-02 17:02 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T1 | 2021-11-02 08:12 | 2021-11-02 16:40 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T1 | 2021-11-03 07:56 | 2021-11-03 16:19 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchaghar | 132/33 kV transformer T3 | 2021-11-03 08:00 | 2021-11-03 08:00 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T1 | 2021-11-03 08:08 | 2021-11-03 15:42 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132 kV Bus-1 | 2021-11-03 08:38 | 2021-11-03 12:33 | 3:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2021-11-04 08:19 | 2021-11-04 16:49 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T01 | 2021-11-04 08:45 | 2021-11-04 17:40 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchaghar | 132/33 kV transformer T01 | 2021-11-04 16:22 | 2021-11-04 16:22 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T1 | 2021-11-05 11:03 | 2021-11-05 18:01 | 6:58 | S/O | Due to CB change | 0 | 0 | No interruption
Bogura | 132 kV main& transfer Bus | 2021-11-06 06:22 | 2021-11-06 07:25 | 1:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T02 | 2021-11-06 07:56 | 2021-11-06 16:07 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformers T01 &T0 2 | 2021-11-06 07:38 | 2021-11-06 09:53 | 2:15 | S/O | Due to A/M work | 25 | 56.25 | Power interruption
Rajshahi | 132/33 kV transformer T3 | 2021-11-07 09:10 | 2021-11-07 16:20 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132 kV Bus coupler | 2021-11-07 09:05 | 2021-11-07 16:33 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T01 | 2021-11-07 10:31 | 2021-11-07 15:29 | 4:58 | S/O | Due to A/M work | 0 | 0 | Power interruption
Sherpur | 132/33 kV transformer T03 | 2021-11-07 15:28 | 2021-11-07 17:02 | 1:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T06 | 2021-11-08 08:40 | 2021-11-08 15:40 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV transformer T04 | 2021-11-08 08:30 | 2021-11-08 15:02 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T01 | 2021-11-08 08:05 | 2021-11-08 16:06 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T3 | 2021-11-08 08:27 | 2021-11-08 16:20 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T01 | 2021-11-09 08:26 | 2021-11-09 18:25 | 9:59 | S/O | Due to A/M work | 0 | 0 | Power interruption
Rajshahi | 132/33 kV transformer T3 | 2021-11-09 08:42 | 2021-11-09 15:57 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T2 | 2021-11-09 09:55 | 2021-11-09 16:15 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T02 | 2021-11-10 07:18 | 2021-11-10 16:30 | 9:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T03 | 2021-11-10 08:39 | 2021-11-10 15:59 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T01 | 2021-11-10 08:02 | 2021-11-11 16:22 | 32:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV transformer T02 | 2021-11-10 08:14 | 2021-11-10 16:18 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T02 | 2021-11-11 08:30 | 2021-11-11 15:55 | 7:25 | S/O |  | 0 | 0 | No interruption
Naoapara | 132 kV Bus-B | 2021-11-11 09:05 | 2021-11-11 13:05 | 4:00 | S/O |  | 0 | 0 | No interruption
Natore | 132/33 kV transformer T01 | 2021-11-11 08:10 | 2021-11-11 14:17 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformers T03 & T04 & 33 kV Bus | 2021-11-12 07:05 | 2021-11-12 08:05 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T02 | 2021-11-12 08:16 | 2021-11-12 13:49 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T03 | 2021-11-13 08:37 | 2021-11-13 16:12 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T02 | 2021-11-13 08:02 | 2021-11-13 16:13 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T03 | 2021-11-13 08:14 | 2021-11-13 16:42 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV transformer T3 | 2021-11-13 08:01 | 2021-11-13 17:01 | 9:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 230 kV Bus-1 | 2021-11-13 10:50 | 2021-11-13 14:29 | 3:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj | 230 kV Bus-1 | 2021-11-13 09:48 | 2021-11-13 16:40 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T02 | 2021-11-14 09:20 | 2021-11-14 15:10 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(N) | 230/ kV transformer T1 | 2021-11-14 09:29 | 2021-11-14 17:10 | 7:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-11-14 09:55 | 2021-11-14 17:05 | 7:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T03 | 2021-11-14 12:15 | 2021-11-14 14:50 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T05 | 2021-11-15 08:34 | 2021-11-15 14:52 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T03 | 2021-11-15 08:17 | 2021-11-15 16:58 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T02 | 2021-11-17 09:24 | 2021-11-17 17:02 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2021-11-17 09:45 | 2021-11-17 16:51 | 7:06 | S/O |  | 0 | 0 | No interruption
Barapukuria | 132 kV Bus coupler | 2021-11-17 09:22 | 2021-11-17 15:30 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T03 | 2021-11-17 08:25 | 2021-11-17 17:16 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV transformer T01 | 2021-11-18 10:59 | 2021-11-18 12:22 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T02 | 2021-11-18 12:30 | 2021-11-18 13:26 | 0:56 | S/O |  | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T02 | 2021-11-18 09:15 | 2021-11-18 16:21 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-11-18 09:40 | 2021-11-18 11:32 | 1:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T02 & 33 kV Bus-2 | 2021-11-18 15:02 | 2021-11-18 15:46 | 0:44 | S/O | Due to construction works | 14 | 10.2667 | Power interruption
C.nawabganj | 132/33 kV transformer T02 | 2021-11-19 08:35 | 2021-11-19 09:53 | 1:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T02 with 33 kV Bus | 2021-11-19 09:23 | 2021-11-19 11:23 | 2:00 | S/O | Due to C/M work | 0 | 0
| 230 kV Bus coupler | 2021-11-20 09:04 | 2021-11-20 17:33 | 8:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 | 2021-11-20 08:15 | 2021-11-20 16:55 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 230 kV Bus -2 | 2021-11-21 10:16 | 2021-11-21 15:26 | 5:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 | 2021-11-21 07:56 | 2021-11-21 16:53 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T03 | 2021-11-21 12:13 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 | 2021-11-23 08:12 | 2021-11-23 14:30 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T3 | 2021-11-24 08:25 | 2021-11-24 14:15 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T3 | 2021-11-24 19:10 | 2021-11-24 20:30 | 1:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(N) | 132 kV Busbar | 2021-11-25 06:38 | 2021-11-25 06:38 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132 kV bus | 2021-11-26 06:58 | 2021-11-26 08:26 | 1:28 | S/O | Due to A/M work | 125 | 183.3333 | Power interruption
| 132 kV bus section-1 | 2021-11-26 08:27 | 2021-11-26 16:10 | 7:43 | S/O | Due to maint.work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T02 | 2021-11-26 09:08 | 2021-11-26 11:11 | 2:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Chaddagram | 132/33 kV transformer T02 & 33 kV Bus | 2021-11-26 09:43 | 2021-11-26 11:56 | 2:13 | S/O | Due to D/W work | 5 | 11.0833 | Power interruption
Purbasadipur | 132 kV full bus | 2021-11-27 06:37 | 2021-11-27 09:01 | 2:24 | S/O | Due to D/W work | 121 | 290.4 | Power interruption
Barapukuria | 132 kV Bus-2 | 2021-11-27 07:45 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV transformer T1 | 2021-11-27 08:18 | 2021-11-27 15:56 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T04 | 2021-11-27 10:55 | 2021-11-27 12:44 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T01 | 2021-11-28 10:34 | 2021-11-28 10:34 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132 kV full bus | 2021-11-28 14:31 | 2021-11-28 15:45 | 1:14 | S/O | Due to C/M work | 120 | 148 | Power interruption
Amnura | 132/33 kV transformer T1 | 2021-11-28 08:15 | 2021-11-28 13:24 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2021-11-30 08:33 | 2021-11-30 13:12 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(O) | 132/33 kV transformer T3 | 2021-11-30 10:02 | 2021-11-30 15:36 | 5:34 | S/O | Due to C/M work | 25 | 139.1667 | Power interruption
Chaddagram | 132/33 kV transformer T01 | 2021-11-30 09:22 | 2021-11-30 17:25 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 468:27 |  | Unserved Energy : |  | 838.5
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1764:18 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: November2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | Mirpur-Aminbazar 230 kV Ckt-2 | 2021-11-01 07:38 | 2021-11-01 07:38 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-11-01 08:58 | 2021-11-01 17:38 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2021-11-02 07:23 | 2021-11-02 07:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2021-11-02 09:44 | 2021-11-02 17:37 | 7:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-11-02 09:15 | 2021-11-02 17:19 | 8:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-11-03 09:17 | 2021-11-03 15:50 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2021-11-06 11:33 | 2021-11-06 16:16 | 4:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-11-06 08:47 | 2021-11-06 17:03 | 8:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-11-07 10:30 | 2021-11-07 13:33 | 3:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Kodda 132 kV Ckt-1 | 2021-11-07 09:02 | 2021-11-07 13:11 | 4:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV Ckt-2 | 2021-11-07 09:23 | 2021-11-07 17:34 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi (N) 132 kV Ckt-1 | 2021-11-07 09:32 | 2021-11-07 16:02 | 6:30 | S/O |  |  |  | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2021-11-08 08:25 | 2021-11-08 14:52 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi (N) 132 kV Ckt-1 | 2021-11-08 09:16 | 2021-11-08 12:39 | 3:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi S/S | TongiS/S-Kodda P.P 230 kkV Ckt- | 2021-11-08 11:53 | 2021-11-08 11:53 | 0:00 | S/O | Due to protection test | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2021-11-08 15:04 | 2021-11-08 19:01 | 3:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2021-11-09 07:27 | 2021-11-09 07:27 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda -Kabirpur 132 kV Ckt-2 | 2021-11-09 08:47 | 2021-11-09 14:54 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-1 | 2021-11-09 10:36 | 2021-11-09 13:19 | 2:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2021-11-09 07:30 | 2021-11-09 17:09 | 9:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-11-09 09:35 | 2021-11-09 17:20 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2021-11-10 07:27 | 2021-11-10 07:27 | 0:00 |  | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-11-10 08:50 | 2021-11-10 15:55 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
|  | 2021-11-11 08:50 | 2021-11-11 15:55 | 7:05 | S/O | Due to A/M work |  |  | No interruption
Tongi | Tongi-Tongi (N) 132 kV Ckt-2 | 2021-11-10 09:49 | 2021-11-10 16:11 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda -Rajendrapur 132 kV Ckt-1 | 2021-11-11 09:26 | 2021-11-11 11:44 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2021-11-11 09:37 | 2021-11-11 17:19 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi (N) | Tongi (N)-Tongi 132 kV Ckt-2 | 2021-11-11 09:23 | 2021-11-11 13:46 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
RPCL | RPCL-Mymensingh 132 kV Ckt-2 | 2021-11-13 09:53 | 2021-11-13 17:10 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV Ckt | 2021-11-13 09:12 | 2021-11-13 16:56 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi -Kabirpur 132 kV Ckt-1 | 2021-11-14 08:52 | 2021-11-14 10:58 | 2:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV Ckt-1 | 2021-11-14 09:37 | 2021-11-14 16:39 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh RPCL-Mymensingh 132 kV Ckt-1 | 2021-11-14 09:20 | 2021-11-14 16:59 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-1 | 2021-11-14 08:50 | 2021-11-14 16:08 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2021-11-15 09:50 | 2021-11-15 16:52 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV Ckt-1 | 2021-11-15 09:05 | 2021-11-15 16:40 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-15 10:47 | 2021-11-15 17:52 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda -Joydevpur 132 kV Ckt-2 | 2021-11-15 08:43 | 2021-11-15 16:47 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV Ckt-1 | 2021-11-15 09:40 | 2021-11-15 16:22 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-1 | 2021-11-15 09:25 | 2021-11-15 17:10 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-1 | 2021-11-15 08:29 | 2021-11-15 16:31 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2021-11-16 07:32 | 2021-11-16 07:32 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2021-11-16 09:55 | 2021-11-16 18:15 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydepur | Joydepur-Kodda 132 kV Ckt-1 | 2021-11-16 08:24 | 2021-11-16 15:57 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh S/S-Mymensingh RPCL 132 kV Ckt-1 | 2021-11-16 09:52 | 2021-11-16 16:22 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-1 | 2021-11-16 08:41 | 2021-11-16 18:42 | 10:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sherpur-UMPL 132 kV Ckt-1 | 2021-11-17 08:51 | 2021-11-17 16:13 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh S/S-Mymensingh RPCL 132 kV Ckt-2 | 2021-11-17 08:18 | 2021-11-17 16:05 | 7:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh S/S-Mymensingh RPCL 132 kV Ckt-1 | 2021-11-18 09:41 | 2021-11-18 20:33 | 10:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajendrapur | Rajendrapur-Kodda 132 kV Ckt-2 | 2021-11-18 08:56 | 2021-11-18 10:48 | 1:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-2 | 2021-11-18 10:37 | 2021-11-18 17:20 | 6:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-1 | 2021-11-18 08:40 | 2021-11-18 16:18 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
|  | 2021-11-18 08:51 | 2021-11-18 16:21 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-2 |  | 2021-11-19 14:38 |  |  | After maint.work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-11-20 15:22 |  |  | S/O | ue to load test | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-11-20 07:35 | 2021-11-20 07:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-1 | 2021-11-20 09:25 | 2021-11-20 10:21 | 0:56 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 132 kV Ckt-2 | 2021-11-20 10:30 | 2021-11-20 16:01 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-11-20 09:25 | 2021-11-20 17:11 | 7:46 | S/O | Due to C/M work | 0 | 0 | No interruption
RPCL | RPCL-Mymensingh 132 kV Ckt-2 | 2021-11-20 09:43 | 2021-11-20 17:11 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 132 kV Ckt-2 | 2021-11-20 08:43 | 2021-11-20 16:30 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2021-11-21 07:58 | 2021-11-21 07:58 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-11-21 07:44 | 2021-11-21 07:44 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 132 kV Ckt-2 | 2021-11-21 08:39 | 2021-11-21 17:05 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| UMPL -Jamalpur 132 kV kt-2 | 2021-11-21 08:39 | 2021-11-21 16:50 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV Ckt-1 | 2021-11-21 09:11 | 2021-11-21 10:50 | 1:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2021-11-21 10:25 | 2021-11-21 10:25 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
RPCL | RPCL-Mymensingh 132 kV Ckt-2 | 2021-11-21 11:42 | 2021-11-21 17:26 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-11-22 07:37 | 2021-11-22 07:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Narinda 132 kV Ckt-1 | 2021-11-22 09:02 | 2021-11-22 17:46 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2021-11-22 08:32 | 2021-11-22 17:15 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-2 | 2021-11-22 08:47 | 2021-11-22 16:34 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-1 | 2021-11-22 09:20 | 2021-11-22 10:56 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV Ckt-2 | 2021-11-22 11:06 | 2021-11-22 12:16 | 1:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV Ckt-1 | 2021-11-22 09:17 | 2021-11-22 16:37 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-1 | 2021-11-22 09:20 | 2021-11-22 10:56 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-11-23 07:36 | 2021-11-23 07:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2021-11-23 08:24 | 2021-11-23 23:54 | 15:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh RPCL-Tangail 132 kV Ckt-2 | 2021-11-23 09:22 | 2021-11-23 15:50 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV Ckt-2 | 2021-11-23 08:52 | 2021-11-23 16:54 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-2 | 2021-11-23 09:04 | 2021-11-23 16:05 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2021-11-23 10:00 | 2021-11-23 13:28 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Kodda 132 kV Ckt-2 | 2021-11-23 13:30 | 2021-11-23 15:26 | 1:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-1 | 2021-11-24 09:15 | 2021-11-24 10:33 | 1:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV Ckt-2 | 2021-11-24 08:42 | 2021-11-24 17:43 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-11-24 08:54 | 2021-11-24 16:34 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-2 | 2021-11-24 08:32 | 2021-11-24 16:42 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV Ckt-2 | 2021-11-24 09:38 | 2021-11-24 11:45 | 2:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV Ckt-2 | 2021-11-25 09:31 | 2021-11-25 16:38 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-25 08:19 | 2021-11-25 16:44 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Tangail 132 kV Ckt-1 | 2021-11-25 10:30 | 2021-11-25 15:36 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-2 | 2021-11-25 09:11 | 2021-11-25 16:04 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-2 | 2021-11-25 12:50 | 2021-11-25 15:36 | 2:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-27 07:41 | 2021-11-27 07:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-1 | 2021-11-27 14:56 | 2021-11-27 17:19 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-28 08:25 | 2021-11-28 18:19 | 9:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Tangail 132 kV Ckt-1 | 2021-11-28 09:03 | 2021-11-28 10:55 | 1:52 | S/O | Due to protection test | 0 | 0 | No interruption
Uttara | Uttara-Mirpur 132 kV Ckt | 2021-11-28 08:35 | 2021-11-28 17:11 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-29 07:25 | 2021-11-29 16:33 | 9:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara (O)132 kV Ckt-1 | 2021-11-29 08:10 | 2021-11-29 16:25 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2021-11-29 09:24 | 2021-11-29 15:32 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Bhaluka 132 kV Ckt-2 | 2021-11-29 15:33 | 2021-11-29 16:49 | 1:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-2 | 2021-11-30 09:25 | 2021-11-30 11:10 | 1:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Manikganj 132 kV Ckt-2 | 2021-11-30 08:19 | 2021-11-30 15:55 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Rajendrapur 132 kV Ckt-1 | 2021-11-30 10:33 | 2021-11-30 10:33 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2021-11-30 09:05 | 2021-11-30 16:56 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 570:33 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur S/S | Haripur S/S-Haripur P/S 230 kV Ckt-2 | 2021-11-01 10:40 | 2021-11-01 12:36 | 1:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2021-11-01 08:23 | 2021-11-01 16:53 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Fatulla 132 kV Ckt-1 | 2021-11-01 09:04 | 2021-11-01 15:01 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2021-11-02 08:25 | 2021-11-02 13:56 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon -IE 132 kV Ckt-2 | 2021-11-02 08:35 | 2021-11-02 15:45 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2021-11-03 08:16 | 2021-11-03 17:27 | 9:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bhulta-Haripur 230 kV Ckt-1 | 2021-11-04 08:43 | 2021-11-04 17:38 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-2 | 2021-11-04 08:23 | 2021-11-04 13:36 | 5:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2021-11-06 08:25 | 2021-11-06 17:14 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 132 kV Ckt-1 | 2021-11-06 08:37 | 2021-11-06 18:48 | 10:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-1 | 2021-11-06 08:17 | 2021-11-06 16:32 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur S/S-Bhulta P/S 230 kV Ckt-2 | 2021-11-07 08:54 | 2021-11-07 17:36 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-1 | 2021-11-08 07:37 | 2021-11-08 07:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-1 | 2021-11-08 08:13 | 2021-11-08 16:54 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-2 | 2021-11-08 08:54 | 2021-11-08 16:31 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Cumilla(N) 230 kV Ckt-2 | 2021-11-09 08:18 | 2021-11-09 15:56 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-1 | 2021-11-09 09:54 | 2021-11-09 16:50 | 6:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur -Bhulta 230 kV Ckt-1 | 2021-11-10 07:12 | 2021-11-10 07:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-2 | 2021-11-10 08:31 | 2021-11-10 14:50 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-2 | 2021-11-10 08:03 | 2021-11-10 16:27 | 8:24 | S/O |  | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV Ckt |  | 2021-11-10 17:09 |  |  | After maint.work | 0 | 0 | No interruption
| Hasnabad-APR 230 kV Ckt |  | 2021-11-10 17:18 |  |  | After maint.work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2021-11-11 08:37 | 2021-11-11 08:37 | 0:00 |  | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-2 | 2021-11-11 09:04 | 2021-11-11 16:58 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Maniknagar-Siddhirganj 230 kV Ckt-2 | 2021-11-11 08:20 | 2021-11-11 17:54 | 9:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-1 | 2021-11-13 08:19 | 2021-11-13 16:32 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt | 2021-11-13 09:52 | 2021-11-13 14:32 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2021-11-16 08:17 | 2021-11-16 16:06 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV Ckt-1 | 2021-11-16 10:01 | 2021-11-16 15:37 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-2 | 2021-11-17 07:42 | 2021-11-17 07:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV Ckt-1 |  | 2021-11-17 17:13 |  |  | After maint.work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-1 | 2021-11-17 08:36 | 2021-11-17 17:02 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Bramangaon 132 kV Ckt | 2021-11-17 10:08 | 2021-11-17 11:44 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV Ckt-2 | 2021-11-17 09:38 | 2021-11-17 15:36 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV Ckt-1 | 2021-11-18 09:13 | 2021-11-18 19:34 | 10:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Sitalakhya 132 kV Ckt | 2021-11-18 09:39 | 2021-11-18 17:09 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Bramangaon 132 kV Ckt | 2021-11-18 09:46 | 2021-11-19 23:01 | 37:15 | S/O |  | 0 | 0 | No interruption
| Hasnabad-Sitalakhya 132 kV Ckt | 2021-11-19 09:15 | 2021-11-19 22:57 | 13:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 Ckt-1 | 2021-11-19 08:58 | 2021-11-19 15:59 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-3 | 2021-11-20 07:41 | 2021-11-20 07:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj S/S | Madanganj S/S-Madanganj Summit 132 kV Ckt-1 | 2021-11-20 09:48 | 2021-11-20 14:35 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-2 | 2021-11-20 08:22 | 2021-11-20 17:19 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghanghat | Meghanghat-Haripur 230 kV Bus-2 | 2021-11-20 23:22 | 2021-11-21 05:08 | 5:46 | S/O | Due to VT fail | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-3 | 2021-11-21 08:30 | 2021-11-21 16:35 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV Ckt | 2021-11-21 10:45 | 2021-11-21 17:17 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Sitalakhya 132 kV Ckt | 2021-11-23 09:39 | 2021-11-23 15:46 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-4 | 2021-11-24 07:37 | 2021-11-24 07:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV Ckt-2 | 2021-11-24 07:37 | 2021-11-24 16:24 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-4 | 2021-11-25 08:22 | 2021-11-25 16:37 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Madanganj Summit 132 kV Ckt | 2021-11-27 11:15 | 2021-11-27 15:22 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Keraniganj (N) 132 kV Ckt | 2021-11-28 09:08 | 2021-11-28 17:06 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Lalbagh 132 kV Ckt-3 | 2021-11-28 14:54 | 2021-11-28 15:46 | 0:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Keraniganj-Nawabganj 132 kV Ckt-1 | 2021-11-29 12:18 | 2021-11-29 12:42 | 0:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV Ckt-2 | 2021-11-29 10:41 | 2021-11-29 17:34 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2021-11-29 15:08 | 2021-11-29 16:03 | 0:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Aftabnagar | Aftabnagar-Rampura 132 kV Ckt-2 | 2021-11-30 11:34 | 2021-11-30 14:52 | 3:18 | S/O | Due to SCADA test | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV Ckt-1 | 2021-11-30 09:19 | 2021-11-30 17:01 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV Ckt-1 | 2021-11-30 10:44 | 2021-11-30 10:44 | 0:00 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 358:55 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-11-01 08:15 | 2021-11-01 08:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV Ckt-1 | 2021-11-02 08:45 | 2021-11-02 15:17 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madunaghat-Sikalbaha 132 kV Ckt-1 | 2021-11-03 09:15 | 2021-11-03 16:40 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madunaghat-Sikalbaha 132 kV Ckt-1 | 2021-11-04 09:04 | 2021-11-04 16:23 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-2 | 2021-11-04 08:50 | 2021-11-04 12:41 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV both Ckts | 2021-11-05 07:08 | 2021-11-05 07:08 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV Ckts-1 & 2 | 2021-11-06 09:09 | 2021-11-08 17:07 | 55:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV Ckt | 2021-11-06 08:24 | 2021-11-07 13:14 | 28:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madunaghat-T.k chemical 132 kV Ckt | 2021-11-07 09:09 | 2021-11-07 14:44 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-1 | 2021-11-09 09:23 | 2021-11-09 16:27 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV Ckt | 2021-11-09 08:30 | 2021-11-10 16:59 | 32:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Hathazari 230 kV Ckt-1 | 2021-11-09 09:52 | 2021-11-09 19:38 | 9:46 | S/O | Due to D/W work | 0 | 0 | No interruption
TK.chemical | TK.chemical-Sikalbaha 132 kV Ckt | 2021-11-10 07:50 | 2021-11-10 07:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-11-10 08:52 | 2021-11-10 19:27 | 10:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirsarai EPZ | Mirsarai EPZ-BSRM 230 kV Ckt-1 | 2021-11-10 11:18 | 2021-11-10 17:08 | 5:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampur | Rampur-Khulshi 132 kV Ckt-1 | 2021-11-10 10:50 | 2021-11-10 18:04 | 7:14 | S/O |  | 0 | 0 | Power interruption
BSRM | BSRM Mirsharai 230 kV Ckt-1 | 2021-11-11 10:21 | 2021-11-11 17:07 | 6:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-11-11 08:48 | 2021-11-11 16:22 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV Ckt | 2021-11-11 11:58 | 2021-11-11 14:56 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
TK.chemical | TK.chemical-Sikalbaha 132 kV Ckt | 2021-11-11 08:47 | 2021-11-11 16:05 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirsarai EPZ | Mirsarai EPZ-BSRM 230 kV Ckt-1 | 2021-11-13 10:25 | 2021-11-13 17:11 | 6:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV Ckt-1 | 2021-11-13 08:56 | 2021-11-14 15:45 | 30:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-11-13 09:05 | 2021-11-13 19:28 | 10:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2021-11-14 09:07 | 2021-11-14 16:10 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2021-11-14 09:10 | 2021-11-14 16:04 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirsarai EPZ | Mirsarai EPZ-BSRM 230 kV Ckt-1 | 2021-11-14 11:23 | 2021-11-14 18:28 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2021-11-15 09:36 | 2021-11-15 15:52 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM Mirsharai 230 kV Ckt-1 | 2021-11-16 11:14 | 2021-11-16 19:17 | 8:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2021-11-16 08:58 | 2021-11-16 16:12 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-16 08:45 | 2021-11-16 16:29 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV Ckt | 2021-11-16 09:11 | 2021-11-16 09:11 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-2 | 2021-11-16 16:49 | 2021-11-16 19:33 | 2:44 | S/O | Due to trimming of 11 kV pole | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV Ckt | 2021-11-16 14:22 | 2021-11-16 15:11 | 0:49 | S/O |  | 0 | 0 | No interruption
BSRM | BSRM Mirsharai 230 kV Ckt-1 | 2021-11-17 09:57 | 2021-11-17 19:55 | 9:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2021-11-17 09:11 | 2021-11-17 16:16 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-17 09:08 | 2021-11-17 09:08 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-1 | 2021-11-17 10:07 | 2021-11-17 19:49 | 9:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-18 08:58 | 2021-11-18 21:36 | 12:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-2 | 2021-11-18 09:47 | 2021-11-18 19:34 | 9:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2021-11-18 08:34 | 2021-11-18 15:40 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-20 09:17 | 2021-11-20 15:37 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV Ckt-1 |  | 2021-11-20 16:00 |  |  | After maint work | 0 | 0 | No interruption
| Sikalbaha-Bakulia 132 kV Ckt-2 |  | 2021-11-20 16:03 |  |  |  | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-21 08:41 | 2021-11-21 16:25 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-22 09:08 | 2021-11-22 16:38 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-23 08:52 | 2021-11-23 16:43 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-2 | 2021-11-23 09:25 | 2021-11-23 16:55 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Dohazari-Sikalbaha 132 kV Ckt-2 | 2021-11-24 09:05 | 2021-11-24 16:27 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2021-11-24 09:10 | 2021-11-24 17:32 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2021-11-24 17:16 | 2021-11-24 20:26 | 3:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-2 | 2021-11-25 09:25 | 2021-11-25 16:23 | 6:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV Ckt |  | 2021-11-25 09:30 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2021-11-25 07:30 | 2021-11-25 18:53 | 11:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2021-11-27 09:07 | 2021-11-27 17:11 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV Ckt-1 | 2021-11-29 09:08 | 2021-11-29 17:52 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV Ckt-2 | 2021-11-30 09:19 | 2021-11-30 16:53 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 469:42 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Daudkandi S/S | Daudkandi S/S-Daudkandi P/S 132 kV Ckt | 2021-11-01 08:51 | 2021-11-01 16:16 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla (N) | Cumilla (N)-Kachua 132 kV Ckt-2 | 2021-11-01 10:00 | 2021-11-01 13:48 | 3:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-11-02 09:25 | 2021-11-03 00:28 | 15:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-11-03 09:07 | 2021-11-03 20:38 | 11:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-PHP 132 kV Ckt | 2021-11-03 08:24 | 2021-11-03 15:15 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV Ckt-1 | 2021-11-04 11:53 | 2021-11-04 15:32 | 3:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt-3 | 2021-11-07 07:17 | 2021-11-07 10:46 | 3:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla (N)-Meghnaghat 230 kV Ckt-1 | 2021-11-07 08:12 | 2021-11-07 16:05 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-11-08 09:47 | 2021-11-08 11:35 | 1:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-11-09 09:48 | 2021-11-09 12:55 | 3:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 | 2021-11-09 13:02 | 2021-11-09 16:28 | 3:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(S)-Tripura 132 kV Ckt-2 | 2021-11-09 13:39 | 2021-11-09 14:08 | 0:29 | S/O | Due to C/M work | 100 | 48.3333 | Power interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-11-09 14:15 | 2021-11-09 14:25 | 0:10 | S/O |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 | 2021-11-10 09:44 | 2021-11-10 16:28 | 6:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV Ckt-1 | 2021-11-10 09:49 | 2021-11-10 13:38 | 3:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV Ckt-2 | 2021-11-10 13:51 | 2021-11-10 15:45 | 1:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt-1 | 2021-11-13 08:27 | 2021-11-13 14:50 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Kachua 132 kV Ckt-1 | 2021-11-14 08:29 | 2021-11-14 15:51 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV Ckt-1 | 2021-11-15 08:35 | 2021-11-15 17:22 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Kochua 132 kV Ckt-1 | 2021-11-17 09:00 | 2021-11-17 16:10 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandpur-Kochua 132 kV Ckt-2 | 2021-11-18 16:49 | 2021-11-18 19:33 | 2:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandpur-Kochua 132 kV Ckt-2 | 2021-11-20 09:13 | 2021-11-20 16:51 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-11-21 07:51 | 2021-11-21 07:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-11-21 08:39 | 2021-11-21 17:22 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Kochua 132 kV Ckt-2 | 2021-11-21 08:53 | 2021-11-21 15:38 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2021-11-21 09:17 | 2021-11-21 12:35 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 | 2021-11-21 08:39 | 2021-11-21 18:08 | 9:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-11-21 07:53 | 2021-11-21 07:53 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghanaghat 230 kV Ckt-1 | 2021-11-22 09:08 | 2021-11-22 10:23 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi -Sonargaon 132 kV Ckt-1 | 2021-11-22 08:52 | 2021-11-22 15:59 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV Ckt-1 | 2021-11-22 12:06 | 2021-11-22 13:00 | 0:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Cumilla(N)-Meghanaghat 230 kV Ckt-2 | 2021-11-22 10:28 | 2021-11-22 13:50 | 3:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Shahjibazar 230 kV Ckt-2 | 2021-11-22 13:09 | 2021-11-22 13:54 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(N)-Meghanaghat 230 kV Ckt-1 | 2021-11-22 09:08 | 2021-11-22 10:25 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-11-23 08:34 | 2021-11-23 17:10 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 k Ckt-2 | 2021-11-23 09:18 | 2021-11-23 10:42 | 1:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi -Sonargaon 132 kV Ckt-1 | 2021-11-23 08:38 | 2021-11-23 15:35 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Sreemongal 132 kV Ckt-1 | 2021-11-23 10:44 | 2021-11-23 12:14 | 1:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj S/S-Sreemongal 132 kV Ckt-2 | 2021-11-23 12:16 | 2021-11-23 12:58 | 0:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(N) | Ashuganj(N)-Bhulta 400 kV Ckt-1 & 2 | 2021-11-24 14:54 | 2021-11-24 14:54 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Kulaura 132 kV Ckt-2 | 2021-11-23 14:39 | 2021-11-23 16:00 | 1:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj S/S-Fenchuganj P/S 132 k Ckt-3 | 2021-11-24 10:45 | 2021-11-24 12:25 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj -Sylhet 132 kV Ckt | 2021-11-24 09:27 | 2021-11-24 10:43 | 1:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-11-24 11:11 | 2021-11-24 17:10 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi -Sonargaon 132 kV Ckt-2 | 2021-11-24 08:20 | 2021-11-24 15:31 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-11-25 08:52 | 2021-11-25 17:03 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi -Sonargaon 132 kV Ckt-2 | 2021-11-25 08:30 | 2021-11-25 15:34 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV Ckt | 2021-11-25 09:46 | 2021-11-25 14:31 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 kV Ckt-2 | 2021-11-26 07:21 | 2021-11-26 07:21 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt-2 | 2021-11-27 08:30 | 2021-11-27 17:28 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-11-27 08:22 | 2021-11-27 16:48 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj -Bibiyana 230 kV Ckt-1 | 2021-11-27 09:08 | 2021-11-27 17:06 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-11-28 07:28 | 2021-11-28 07:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghangaht 230 kV Ckt-2 | 2021-11-28 08:36 | 2021-11-28 11:55 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj -Bibiyana 230 kV Ckt-1 | 2021-11-28 09:06 | 2021-11-28 16:50 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chaddagram 132 kV Ckt-1 | 2021-11-28 09:06 | 2021-11-28 10:48 | 1:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt-1 | 2021-11-29 11:31 | 2021-11-29 12:21 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj -Bibiyana 230 kV Ckt-1 | 2021-11-29 09:10 | 2021-11-29 16:43 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj -Bibiyana 230 kV Ckt-1 | 2021-11-30 08:46 | 2021-11-30 17:04 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Keraniganj 132 kV Ckt-1 | 2021-11-30 10:58 | 2021-11-30 11:20 | 0:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sreemongal-Keraniganj 132 kV Ckt-2 | 2021-11-30 12:04 | 2021-11-30 12:35 | 0:31 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 276:22 |  | Unserved Energy: |  | 48.3333
Khulna Grid Circle :
Faridpur | Faridpur-Gopalganj (N) 132 kv Ckt-1 | 2021-11-01 09:20 | 2021-11-01 18:35 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV Ckt-3 | 2021-11-04 09:45 | 2021-11-04 19:55 | 10:10 | S/O | Due to relay test | 0 | 0 | No interruption
| Gopalganj(N)-Gopalganj(O) 132 kV Ckt-1 & 2 | 2021-11-06 06:40 | 2021-11-06 06:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal S/S | Barisal S/S-Barisal P.P 132 kV Ckt | 2021-11-06 08:36 | 2021-11-06 17:00 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Faridpur P.P 132 kV Ckt | 2021-11-11 08:27 | 2021-11-11 20:11 | 11:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Modhumoti 132 kV Ckt | 2021-11-11 15:47 | 2021-11-11 15:54 | 0:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna | Khulna-Jhenidah 230 kV Ckt-1 | 2021-11-16 09:05 | 2021-11-16 17:13 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna-Jhenidah 230 kV Ckt-1 | 2021-11-17 08:44 | 2021-11-17 15:17 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | Gallamari-Gopalganj (O) 132 kV Ckt-1 | 2021-11-20 08:37 | 2021-11-20 17:30 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Jhenaidah 230 kV Ckt-2 | 2021-11-20 08:57 | 2021-11-20 15:53 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna(S)-Jhenaidah 230 kV Ckt-2 | 2021-11-21 09:28 | 2021-11-21 15:22 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal (S) | Barisal (S)-Bhandaria 132 kV Ckt | 2021-11-23 09:34 | 2021-11-23 15:55 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-1,2 | 2021-11-23 09:07 | 2021-11-23 17:21 | 8:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Magura | Magura-Jhenaidah 132 kV Ckt-1 | 2021-11-23 08:45 | 2021-11-23 14:48 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-1,2 | 2021-11-24 08:01 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal (N) | Barisal (N)-Madaripur 132 kV Ckt-2 | 2021-11-24 17:08 | 2021-11-24 18:18 | 1:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj S/S-Gopalganj P/S 132 kV Ckt |  | 2021-11-25 12:40 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gopalganj(O)-Gallamari 132 kV Ckt-1 |  | 2021-11-25 12:40 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gopalganj S/S-Gopalganj (N) 132 kV Ckt-1 |  | 2021-11-25 11:15 |  | S/O |  | 0 | 0 | No interruption
| Gopalganj(N)-Madaripur 132 kV Ckt-4 | 2021-11-25 17:43 | 2021-11-25 20:02 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gopalganj(N)-Madaripur 132 kV Ckt-1 & 2 | 2021-11-30 07:28 | 2021-11-30 07:34 | 0:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Jhenaidah 230 kV Ckt-1 | 2021-11-30 08:01 | 2021-11-30 13:38 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 96:39 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari | Baghabari-Ishurdi 132 kV Ckt | 2021-11-01 08:30 | 2021-11-01 19:02 | 10:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-G.K 132 kV Ckt-1 & 2 | 2021-11-05 08:30 | 2021-11-05 14:46 | 6:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bogura 132 kV Ckt-1 | 2021-11-06 08:14 | 2021-11-06 17:51 | 9:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| Baghabari-Bogura 132 kV Ckt-2 | 2021-11-06 09:32 | 2021-11-06 17:51 | 8:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| Baghabari-Bogura 132 kV Ckt-1 | 2021-11-07 08:07 | 2021-11-07 15:15 | 7:08 | S/O | Due to A/M work | 20 | 142.6667 | Power interruption
Bheramara | Bheramara-GK 132 kV Ckt | 2021-11-07 08:15 | 2021-11-07 14:40 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah(O) | Jhenidah(O)-Jhenidah (N) 132 kV Ckt-3 | 2021-11-09 08:19 | 2021-11-09 15:37 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV Ckt-2 | 2021-11-10 10:04 | 2021-11-10 16:26 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | HVDC-Jhenidah 230 kV Ckt-2 | 2021-11-10 08:54 | 2021-11-10 16:52 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC-Bharamara 230 kV Ckt-1 | 2021-11-13 09:33 | 2021-11-13 15:59 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Rajshahi 230 kV Ckt-1 | 2021-11-13 09:24 | 2021-11-13 17:38 | 8:14 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara HVDC-Bahrampur 400 kV Ckt-1 |  | 2021-11-13 12:36 |  | S/O | After maint. | 0 | 0 | No interruption
| Bheramara HVDC-Bahrampur 400 kV Ckt-2 |  | 2021-11-13 14:06 |  | S/O |  | 0 | 0 | No interruption
| HVDC-Rajshahi 230 kV Ckt-1 | 2021-11-22 10:08 | 2021-11-22 13:44 | 3:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenidah(O) | Jhenidah(O)-Magura 132 kV Ckt-1 | 2021-11-24 08:44 | 2021-11-24 15:51 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenidah(O)-Magura 132 kV Ckt-2 | 2021-11-27 08:14 | 2021-11-27 15:45 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Jhenidah 230 kV Ckt-1 | 2021-11-28 08:05 | 2021-11-28 17:11 | 9:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV Ckt-1 | 2021-11-29 08:53 | 2021-11-29 15:52 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Bahrampur 400 kV Ckt-1 | 2021-11-29 09:24 | 2021-11-29 15:19 | 5:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV Ckt-2 | 2021-11-29 09:08 | 2021-11-29 15:51 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenidah-Khulna(S) 230 kV Ckt-1 | 2021-11-29 12:33 | 2021-11-29 16:55 | 4:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-2 | 2021-11-30 09:39 | 2021-11-30 09:39 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 135:54 |  | Unserved Energy: |  | 142.6667
Bogura Grid Circle :
Bogura | Bogura-Sherpur 132 kV Ckt-2 | 2021-11-01 09:42 | 2021-11-01 14:36 | 4:54 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV Ckt-1 | 2021-11-03 08:23 | 2021-11-03 17:00 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur P/P 132 Ckt | 2021-11-03 11:35 | 2021-11-03 11:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur(Bogura) | Sherpur-Sirajganj 132 kV Ckt-1 | 2021-11-03 08:12 | 2021-11-03 16:10 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV Ckt-1 | 2021-11-04 08:31 | 2021-11-04 13:41 | 5:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur P/P 132 Ckt-1 | 2021-11-05 08:28 | 2021-11-05 16:36 | 8:08 | S/O |  | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV Ckt-2 | 2021-11-05 08:25 | 2021-11-05 15:53 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi 132 kV Ckt-1 | 2021-11-06 08:01 | 2021-11-06 16:21 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Conf.P/P 132 kV Ckt-1 | 2021-11-06 09:35 | 2021-11-06 15:48 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-2 | 2021-11-06 08:23 | 2021-11-06 15:59 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV Ckt | 2021-11-07 08:29 | 2021-11-07 17:23 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Conf.P/P 132 Ckt | 2021-11-07 09:07 | 2021-11-07 16:49 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(new) | Rajshahi(new)-Amnura 132 kV Ckt | 2021-11-08 07:42 | 2021-11-08 15:18 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Conf.132 kV Ckt-2 | 2021-11-08 09:30 | 2021-11-08 15:56 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV Ckt-1 | 2021-11-08 08:21 | 2021-11-08 20:15 | 11:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palshbari-Mithapukur 132 kV Ckt-1 | 2021-11-08 11:42 | 2021-11-08 16:56 | 5:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV Ckt | 2021-11-09 07:35 | 2021-11-09 07:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Palashbari 132 kV Ckt-1 | 2021-11-09 08:15 | 2021-11-09 16:01 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar 132 kV Ckt | 2021-11-10 08:30 | 2021-11-10 17:02 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palshbari-Mithapukur 132 kV Ckt-1 | 2021-11-10 08:26 | 2021-11-10 15:54 | 7:28 | S/O |  | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV Ckt-2 | 2021-11-11 08:17 | 2021-11-11 18:36 | 10:19 | S/O
Naogaon | Naogaon-Santahar 132 kV Ckt-1 | 2021-11-11 08:35 | 2021-11-11 12:10 | 3:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Palashbari 132 kV Ckt-1 | 2021-11-11 08:33 | 2021-11-11 15:52 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mithapukur-Palashbari 132 kV Ckt-2 | 2021-11-12 08:18 | 2021-11-12 15:26 | 7:08 | S/O | Due to A/M work | 0 | 0
Rajshahi | Rajshahi(O)-Rajshahi(N) 132 kV Ckt-1 | 2021-11-12 07:36 | 2021-11-12 07:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Palashbari 132 kV Ckt-2 | 2021-11-13 08:18 | 2021-11-13 15:33 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-1 | 2021-11-14 08:28 | 2021-11-14 16:22 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palshbari-Mithapukur 132 kV Ckt-2 | 2021-11-14 09:42 | 2021-11-14 15:32 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi(O)-Rajshahi(N) 132 kV Ckt-2 | 2021-11-15 07:38 | 2021-11-15 07:38 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Natore 132 kV Ckt-1 | 2021-11-15 13:28 | 2021-11-15 13:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-1 | 2021-11-15 08:38 | 2021-11-15 16:08 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-1 | 2021-11-15 08:28 | 2021-11-15 14:37 | 6:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-1 | 2021-11-16 08:54 | 2021-11-16 16:49 | 7:55 | S/O |  | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-1 | 2021-11-16 08:41 | 2021-11-16 17:17 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-2 | 2021-11-17 08:40 | 2021-11-17 16:09 | 7:29 | S/O |  | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-1 | 2021-11-17 08:36 | 2021-11-17 16:56 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-2 | 2021-11-18 08:15 | 2021-11-18 16:24 | 8:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-2 | 2021-11-18 08:55 | 2021-11-18 16:56 | 8:01 | S/O |  | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC Bheramara 230 kV Ckt-1 | 2021-11-19 09:00 | 2021-11-19 16:34 | 7:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-2 | 2021-11-19 08:37 | 2021-11-19 17:30 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-HVDC Bheramara 230 kV Ckt-2 | 2021-11-19 16:49 | 2021-11-19 21:04 | 4:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajshahi-HVDC Bheramara 230 kV Ckt-1 | 2021-11-20 09:00 | 2021-11-20 16:34 | 7:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV Ckt-2 | 2021-11-20 08:15 | 2021-11-20 15:31 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-2 | 2021-11-20 08:27 | 2021-11-20 08:27 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-2 | 2021-11-20 08:49 | 2021-11-20 16:03 | 7:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur-Barapukuria 132 kV Ckt-1 | 2021-11-20 08:37 | 2021-11-20 15:41 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur-Barapukuria 132 kV Ckt-1 | 2021-11-21 08:53 | 2021-11-21 15:45 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV Ckt-1 | 2021-11-21 09:06 | 2021-11-21 16:24 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV Ckt-2 | 2021-11-22 08:52 | 2021-11-22 15:59 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV Ckt-1 | 2021-11-22 09:02 | 2021-11-22 16:15 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV Ckt-1 | 2021-11-22 08:44 | 2021-11-22 16:48 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV Ckt-2 | 2021-11-22 09:05 | 2021-11-22 16:45 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV Ckt-2 | 2021-11-24 08:37 | 2021-11-24 16:40 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV Ckt-2 | 2021-11-24 09:15 | 2021-11-24 16:47 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV Ckt-2 | 2021-11-25 08:56 | 2021-11-25 17:10 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV Ckt-2 | 2021-11-25 09:20 | 2021-11-25 16:18 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV Ckt | 2021-11-26 08:05 | 2021-11-26 14:40 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV Ckt-1 | 2021-11-27 08:01 | 2021-11-27 16:05 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Saidpur-Barapukuria 132 kV Ckt-1 | 2021-11-29 08:26 | 2021-11-29 16:21 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur P/S 132 kV Ckt | 2021-11-30 11:40 | 2021-11-30 12:12 | 7:55 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 410:06 |  | Unserved Energy: |  | 0
Others :
Haripur | Haripur-Ullon 132 kV Ckt-1 | 2021-11-30 10:44 | 2021-11-30 10:44 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2318:11 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:November 2021
| Area | Previous Month (October' 2021) |  |  |  | Current Month (November '2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 16 | 2 | 115 | 133 | 11 | 2 | 175 | 188
2 | Dhaka (South) Grid Circle. | 14 | 6 | 26 | 46 | 14 |  | 96 | 110
3 | Chattogram Grid Circle. | 18 | 3 | 71 | 92 | 8 | 2 | 106 | 116
4 | Cumilla Grid Circle. | 26 | 8 | 26 | 60 | 11 | 3 | 129 | 143
5 | Khulna Grid Circle. | 16 | 7 | 61 | 84 | 6 | 2 | 87 | 95
6 | HVDC Grid Circle | 1 | 0 | 35 | 36 | 3 |  | 36 | 39
7 | Bogura Grid Circle. |  | 6 | 99 | 105 | 6 |  | 143 | 149
8 | Others | 1 |  | 1 | 2 | 1 |  | 1 | 2
9 | Total | 92 | 32 | 434 | 558 | 60 | 9 | 773 | 842
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:November 2021
| Area | Previous Month (October' 2021) |  |  |  | Current Month (November '2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 291 | 58.6667 | 495 | 844.6667 | 73.91 |  | 218.32 | 292.23
2 | Dhaka (South) Grid Circle. | 60.17 | 30.9 | 0 | 91.07 | 124.23 | - | - | 124.23
3 | Chattogram Grid Circle. | 72.64 | 0 | 103.05 | 175.69 | 78.69 | - | - | 78.69
4 | Cumilla Grid Circle. | 90.08 | 157.4 | 325.5 | 572.98 | 2.88 | 12 | 100.83 | 115.71
5 | Khulna Grid Circle. | 180.9 | 125.8 | 81.87 | 388.57 | 91.18 | 8.8 | 43.63 | 143.61
6 | HVDC Grid Circle | 0 | 0 | 140.72 | 140.72 | - | - | 142.67 | 142.67
7 | Bogura Grid Circle. | 162.33 | 253.27 | 209.22 | 624.82 | 59.2 | 15.73 | 838.5 | 913.43
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 857.12 | 626.0367 | 1355.36 | 2838.5167 | 430.09 | 36.53 | 1343.95 | 1810.57
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:November 2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 1 | 4 | 5 |  | 1 | 4 | 253.15
2 | Dhaka (South) | 5031.6 | 4 | - | 4 | 2 | 2 | - | 124.23
3 | Chattogram | 2042 | 1 | - | 1 | 1 | - | - | 16.6667
4 | Khulna | 2434 | 4 | 1 | 5 | 1 | 3 | 1 | 140.68
5 | HVDC | 5954.3 | - | - | - | - | - | - | 0
6 | Bogura | 3145.6 | 3 | 7 | 10 | 1 | 2 | 7 | 893.17
7 | Cumilla | 2981 | 1 | 1 | 2 | 1 | - | 1 | 64.5
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 1492.3967
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.95%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.96% | [6 empty] | Information Management Division
7 | Cumilla | 99.93% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:November 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 |  | 3 | 1 | 1 |  | 39.08
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | 2 |  | 2 | 2 |  |  | 62.02
4 | Khulna | 1238.4 | - | 1 |  | 1 | 1 | - | - | 2.93 | -
5 | HVDC | 1325 | 501 | 1 | - | 1 | 1 | - | - | 142.67 | -
6 | Bogura | 1803.3 | - | 1 | - | 1 |  | 1 | - | 20.27
7 | Cumilla | 1648.16 | - | 1 | 1 | 2 | 2 |  |  | 51.21
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | - | [6 empty] | 318.18
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.95%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.96% | [7 empty] | Information Management Division
7 | Cumilla | 99.93% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:November 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-11-18 | 10 | - | 3 | 2hr 34 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:November 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tongi(N) | 1 | 0:38 | 55 | 34.8333 | Due to tripping of 132/33 kV Transformers-T1 & T2
Kabirpur | 1 | 0:07 | 25 | 2.9167 | Due to tripping of Kabirpur-Manikganj 132 kV line-1 & 2
Tongi | 1 | 0:08 | 200 | 26.6667 | Due to tripping of Tongi-Kabirpur 132 kV line-2
Kabirpur | 1 | 0:38 | 15 | 9.5 | Due to tripping of Kabirpur-Manikganj 132 kV line-2
Dhamrai | 1 | 2:49 | 20 | 56.3333 | Due to S/D of 132/33 kV Transformer-T2
Netrakona | 1 | 7:19 | 5 | 36.5833 | Due to S/D of 132/33 kV Transformer-T2 & 33 kV Bus
Tangail | 1 | 1:45 | 60 | 105 | Due to S/D of 132/33 kV Transformer T2 & 33 kV Bus
Jamalpur | 1 | 2:33 | 8 | 20.4 | Due to S/D of 132/33 kV Transformer T4
Hasnabad | 1 | 0:24 | 40 | 16 | Due to tripping of 33 kV feeder fault
Ghoarshal | 1 | 0:18 | 58 | 17.4 | Due to tripping of 132/33 kV Transformers-T1 & T2
Nawabganj | 1 | 0:43 | 20 | 14.3333 | Due to red-hot maint.of 33 kV Bus
Siddhirganj | 1 | 0:51 | 90 | 76.5 | Due to tripping of 132/33 kV Transformers-T1 & T2
Bakulia |  | 0:20 | 50 | 16.6667 | Due to tripping of 132/33 kV Transformers-T1 & T2
Sikalbaha | 1 | 0:21 | 125 | 43.75 | Due to tripping of Sikalbaha-Dohazari 132 kV line-2
Dohazari | 1 | 0:08 | 137 | 18.2667 | Due to tripping of Dohazari-Sikalbaha 132 kV line-2
Shahjibazar | 1 | 0:24 | 30 | 12 | Due to tripping of 33 kV feeder fault
Feni | 1 | 0:23 | 7.5 | 2.875 | Due to tripping of Feni-PHP132 kV Ckt-2
Baroierhat | 1 | 2:06 | 25 | 52.5 | Due to S/D of 132/33 kV Transformers T1 & T2 & 33 kV Bus
Cumilla(S) | 1 | 0:29 | 100 | 48.3333 | Due to S/D of Cumilla(S)-Trpura 132 kV Ckt-2
Gopalganj(O) | 1 | 1:21 | 35 | 47.25 | Due to tripping of 132/33 kV Transformers-T1 & T2
Faripur | 1 | 0:31 | 60 | 31
Mongla | 1 | 0:20 | 30 | 10 | Due to tripping of 132/33 kV Transformers-T1 & T2
Bhandaria | 1 | 0:44 | 12 | 8.8 | Due to tripping of 132/33 kV Transformer-T1
Barisal | 1 | 0:08 | 22 | 2.9333 | Due to tripping of Barisal-Bhandaria kV Ckt
Faridpur | 1 | 1:59 | 22 | 43.6333 | Due to S/D of 132/33 kV Transformer T01
Baghabari |  | 7:08 | 20 | 142.6667 | Due to S/D of Baghabari-Bogura 132 kV Ckt-1
Naogaon | 1 | 0:59 | 16 | 15.7333 | Due to red-hot maint.of 132/33 kV Transformer T2
Bogura | 1 | 4:58 | 7 | 34.7667 | Due to of tripping of 132/33 kV Transformer-T2
Thakurgaon | 2 | 0:10 | 25 | 4.1667 | Due to tripping of 33 kV feeder fault
|  | 0:32 | 38 | 20.2667 | Due to tripping of Thakurgaon -Panchuagar 132 kV Ckt
Natore | 1 | 2:15 | 25 | 56.25 | Due to S/D of 132/33 kV Transformers T01 & T02
Naogaon | 1 | 0:44 | 14 | 10.2667 | Due to S/D of 132/33 kV Transformer T02
Purbasadipur | 1 | 1:28 | 125 | 183.3333 | Due to S/D of 132 kV Bus
Chaddagram | 1 | 2:13 | 5 | 11.0833 | Due to S/D of 132/33 kV Transformer T02
Purbasadipur | 2 | 2:24 | 121 | 290.4 | Due to S/D of 132 kV full Bus
|  | 1:14 | 120 | 148
Bogura(O) | 1 | 5:34 | 25 | 139.1667 | Due to S/D of 132/33 kV Transformer T03
| Total Unserved energy : |  |  | 1810.575 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: November '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 110 | 2 | 2021-11-01 | 12:00
2 | Munsiganj | 80 | 3 | 2021-11-01 | 18:00
3 | Sonargaon | 69 | 1 | 2021-11-01 | 23:00
4 | Shyampur | 192 | 10 | 2021-11-01 | 13:00
5 | Bhulta | 195 | 8 | 2021-11-01 | 10:00
6 | Madanganj | 53 | 4 | 2021-11-01 | 18:30
7 | Shitalakhya | 112 | 1 | 2021-11-01 | 14:00
8 | Rahim steel | 29 | 9 | 2021-11-01 | 11:00
9 | Matuail | 70 | 2 | 2021-11-01 | 22:00
10 | Ghorasal | 75 | 2 | 2021-11-01 | 8:00
11 | Narsingdi | 134 | 1 | 2021-11-01 | 19:30
12 | Haripur (SBU) | 122 | 3 | 2021-11-01 | 14:00
13 | Sreenagar | 36 | 5 | 2021-11-01 | 4:00
14 | Ullon | 57 | 2 | 2021-11-01 | 18:00
15 | Hasnabad | 72 | 1 | 2021-11-01 | 19:00
16 | Magbazar | 88 | 1 | 2021-11-01 | 11:00
17 | Maniknagar | 62 | 1 | 2021-11-01 | 13:00
18 | Bangabhaban | 10 | 1 | 2021-11-01 | 10:00
19 | Narinda | 66 | 13 | 2021-11-01 | 13:00
20 | Dhanmondi | 174 | 1 | 2021-11-01 | 13:00
21 | Lalbag | 88 | 24 | 2021-11-01 | 17:00
22 | Madartek | 61 | 7 | 2021-11-01 | 18:00
23 | Dhaka University | 30 | 11 | 2021-11-01 | 13:00
24 | Aftabnagar | 19 | 23 | 2021-11-01 | 12:00
25 | Fatullah | 58 | 22 | 2021-11-01 | 18:30
26 | Nawabganj | 52 | 25 | 2021-11-01 | 14:00
27 | Mirpur | 106 | 2 | 2021-11-01 | 18:00
28 | Kalyanpur | 95 | 23 | 2021-11-01 | 18:30
29 | Gulshan | 98 | 1 | 2021-11-01 | 11:00
30 | Uttara | 81 | 1 | 2021-11-01 | 20:00
31 | Uttara(new) | 24 | 1 | 2021-11-01 | 15:00
32 | Kamrangirchar | 91 | 8 | 2021-11-01 | 19:00
33 | Savar | 164 | 2 | 2021-11-01 | 15:00
34 | Bhasantec | 109 | 9 | 2021-11-01 | 13:00
35 | Agargaon | 87 | 10 | 2021-11-01 | 13:00
36 | Satmosjid | 90 | 1 | 2021-11-01 | 13:00
37 | Tongi | 112 | 1 | 2021-11-01 | 18:00
38 | Kabirpur | 231 | 4 | 2021-11-01 | 3336:00
39 | Basundhara | 173 | 2 | 2021-11-01 | 15:00
40 | Manikganj | 64 | 20 | 2021-11-01 | 8:00
41 | Joydevpur | 157 | 1 | 2021-11-01 | 18:00
42 | New Tongi | 79 | 1 | 2021-11-01 | 12:00
43 | Kodda | 235 | 6 | 2021-11-01 | 15:00
44 | Dhamrai | 100 | 3 | 2021-11-01 | 15:00
45 | Rajendrapur | 96 | 3 | 2021-11-01 | 18:30
46 | Valuka | 106 | 3 | 2021-11-01 | 16:00
47 | Tangail | 158 | 2 | 2021-11-01 | 18:00
48 | Mymensing | 167 | 6 | 2021-11-01 | 18:00
49 | Kishorganj | 100 | 3 | 2021-11-01 | 20:00
50 | Netrokona | 84 | 3 | 2021-11-01 | 18:00
51 | Jamalpur | 108 | 10 | 2021-11-01 | 18:00
52 | Sherpur | 98 | 3 | 2021-11-01 | 18:00
53 | Srimongal | 45 | 27 | 2021-11-01 | 18:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: November '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
54 | Shahjibazar | 93 | 10 | 2021-11-01 | 21:00
56 | Fenchuganj | 35 | 1 | 2021-11-01 | 17:00
57 | Kulawara | 36 | 1 | 2021-11-01 | 19:00
58 | Sylhet | 116 | 1 | 2021-11-01 | 18:00
59 | Chatak | 20 | 1 | 2021-11-01 | 18:00
60 | Sunamganj | 34 | 1 | 2021-11-01 | 19:00
61 | Bianibazar | 47 | 2 | 2021-11-01 | 18:00
62 | Cumilla (S) | 140 | 25 | 2021-11-01 | 18:00
63 | Cumilla(N) | 99 | 23 | 2021-11-01 | 17:00
64 | Chandpur | 51 | 1 | 2021-11-01 | 18:30
65 | Feni | 99 | 10 | 2021-11-01 | 18:00
66 | Chowmuhani | 150 | 1 | 2021-11-01 | 18:00
67 | Ashuganj | 62 | 7 | 2021-11-01 | 6:00
68 | Daudkandi | 112 | 1 | 2021-11-01 | 18:00
69 | B.Baria | 120 | 12 | 2021-11-01 | 21:00
70 | Ramganj | 66 | 11 | 2021-11-01 | 21:00
71 | Chaddagram | 35 | 15 | 2021-11-01 | 20:00
72 | PHP | 11 | 9 | 2021-11-01 | 12:00
73 | Kochua | 46 | 10 | 2021-11-01 | 20:00
74 | Madanhat | 54 | 1 | 2021-11-01 | 18:00
75 | Hathazari | 83 | 1 | 2021-11-01 | 18:00
76 | Khulshi | 195 | 10 | 2021-11-01 | 15:00
77 | Halishahar | 100 | 1 | 2021-11-01 | 18:00
78 | Baraulia | 156 | 7 | 2021-11-01 | 12:00
79 | Sikalbaha | 41 | 2 | 2021-11-01 | 18:00
80 | Dohazari | 88 | 11 | 2021-11-01 | 18:00
81 | Cox'sbazar | 101 | 13 | 2021-11-01 | 18:00
82 | Chandraghona | 26 | 12 | 2021-11-01 | 18:00
83 | Kaptai | 4.2 | 9 | 2021-11-01 | 18:00
84 | A. Khaer Stl. | 15 | 1 | 2021-11-01 | 7:00
85 | Bakulia | 118 | 10 | 2021-11-01 | 19:00
86 | Julda | 26 | 4 | 2021-11-01 | 10:00
87 | TK chemical | 28.5 | 8 | 2021-11-01 | 18:30
88 | Modern Steel | 14 | 9 | 2021-11-01 | 12:00
89 | Shahmirpur | 30.3 | 11 | 2021-11-01 | 18:30
90 | Khagrachhari | 24 | 10 | 2021-11-01 | 19:00
91 | Matarbari | 39 | 14 | 2021-11-01 | 18:30
92 | Baroiar Hat | 54 | 13 | 2021-11-01 | 23:00
93 | Rangamati | 12 | 1 | 2021-11-01 | 18:30
94 | Abul Khair 230 | 154 | 23 | 2021-11-01 | 15:00
95 | BSRM | 165 | 23 | 2021-11-01 | 18:00
96 | GPH Ispat | 99 | 1 | 2021-11-01 | 0:00
97 | Goalpara | 28 | 22 | 2021-11-01 | 13:00
98 | Central s/s | 90 | 1 | 2021-11-01 | 18:30
99 | Noapara | 42 | 2 | 2021-11-01 | 20:00
100 | Jashore | 89 | 1 | 2021-11-01 | 18:00
101 | Benapol | 42 | 22 | 2021-11-01 | 18:00
101 | Jhenidah | 85 | 1 | 2021-11-01 | 18:00
102 | Bottail | 98 | 30 | 2021-11-01 | 18:00
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: November '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
103 | G.K Project | 69 | 1 | 2021-11-01 | 18:00
104 | Faridpur | 107 | 10 | 2021-11-01 | 18:00
105 | Madaripur | 68 | 1 | 2021-11-01 | 18:30
106 | Sariatpur | 44 | 1 | 2021-11-01 | 20:00
107 | Gopalganj | 71 | 1 | 2021-11-01 | 18:00
108 | Bagerhat | 77 | 1 | 2021-11-01 | 18:00
109 | Mongla | 54 | 21 | 2021-11-01 | 11:00
110 | Satkhira | 80 | 3 | 2021-11-01 | 18:30
111 | Gallamari | 33 | 30 | 2021-11-01 | 13:00
112 | Magura | 40 | 1 | 2021-11-01 | 18:00
113 | Norail | 38 | 3 | 2021-11-01 | 18:00
114 | Chuadanga | 70 | 1 | 2021-11-01 | 18:00
115 | Barsal(N) | 34 | 10 | 2021-11-01 | 18:00
116 | Barsal(S) | 86 | 10 | 2021-11-01 | 18:00
117 | Patuakhali | 83 | 24 | 2021-11-01 | 21:00
118 | Bhandaria | 40 | 11 | 2021-11-01 | 18:30
119 | Borguna | 12 | 1 | 2021-11-01 | 18:00
120 | Borhan Uddin | 30 | 13 | 2021-11-01 | 21:00
121 | Ishurdi | 55 | 3 | 2021-11-01 | 18:00
122 | Ruppur Paromanobik | 4 | 1 | 2021-11-01 | 12:00
123 | Natore | 95 | 3 | 2021-11-01 | 18:00
124 | Bogura | 126 | 7 | 2021-11-01 | 19:00
125 | Naogaon | 84 | 23 | 2021-11-01 | 18:30
126 | Rajshahi | 106 | 1 | 2021-11-01 | 18:00
127 | Rajshahi New | 16 | 25 | 2021-11-01 | 13:00
128 | C.Nawabganj | 49 | 8 | 2021-11-01 | 19:30
129 | Amnura | 34 | 2 | 2021-11-01 | 18:00
130 | Pabna | 98 | 9 | 2021-11-01 | 18:00
131 | Shahjadpur | 76 | 30 | 2021-11-01 | 18:30
132 | Serajganj | 74 | 2 | 2021-11-01 | 18:30
133 | Niyamatpur | 47 | 2 | 2021-11-01 | 18:00
134 | Joypurhat | 46 | 27 | 2021-11-01 | 18:00
135 | Sherpur(Bogura) | 50 | 24 | 2021-11-01 | 18:00
136 | Mohastangar | 48 | 5 | 2021-11-01 | 19:00
137 | Bangura | 22 | 1 | 2021-11-01 | 19:30
138 | Rangpur | 103 | 9 | 2021-11-01 | 18:30
139 | Lalmonirhat | 46 | 9 | 2021-11-01 | 18:30
140 | Saidpur | 83 | 6 | 2021-11-01 | 18:00
141 | Purbasadipur | 90 | 27 | 2021-11-01 | 18:00
142 | Thakurgaon | 75 | 26 | 2021-11-01 | 18:00
143 | Palshbari | 88 | 2 | 2021-11-01 | 18:00
144 | Barapukuria | 40 | 2 | 2021-11-01 | 18:30
145 | Panchugar | 48 | 30 | 2021-11-01 | 18:00
146 | Joldhaka | 29 | 3 | 2021-11-01 | 18:30
147 | Kurigram | 47 | 2 | 2021-11-01 | 18:00
148 | Mitha Pukur | 34 | 24 | 2021-11-01 | 18:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:November 2021
Area | MW | Date | Hour | Remarks
Dhaka | 4149 | 25.11.2021 | 16:00
Chattogram | 1443 | 11.11.2021 | 18:00
Khulna | 1155 | 01.11.2021 | 21:00
Rajshahi | 954 | 03.11.2021 | 20:00
Cumilla | 891 | 01.11.2021 | 21:00
Mymensingh | 774 | 01.11.2021 | 20:00
Sylhet | 403 | 10.11.2021 | 22:00
Barisal | 265 | 10.11.2021 | 22:00
Rangpur | 634 | 27.11.2021 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November '2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 417 | 19 | 2021-11-01 | 19:00 | 402 | 11 | 2021-11-01 | 15:00
2 | Bheramara | 400 | 416 | 19 | 2021-11-01 | 19:30 | 392 | 12 | 2021-11-01 | 18:00
3 | Ashuganj(N) | 400 | 402 | 19 | 2021-11-01 | 19:00 | 379 | 11 | 2021-11-01 | 16:00
4 | Payra | 400 | 419 | 20 | 2021-11-01 | 4:00 | 145 | 11 | 2021-11-01 | 1:00
5 | Kaliakoir | 400 | 409 | 20 | 2021-11-01 | 4:00 | 387 | 1 | 2021-11-01 | 12:00
6 | Bhulta | 400 | 397 | 19 | 2021-11-01 | 18:30 | 88 | 15 | 2021-11-01 | 18:00
7 | Gopalganj | 400 | 419 | 20 | 2021-11-01 | 15:00 | 395 | 2 | 2021-11-01 | 18:30
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2021-11-01 | 20:00 | 227 | 2 | 2021-11-01 | 10:00
2 | Ishurdi | 230 | 245 | 20 | 2021-11-01 | 4:00 | 226 | 25 | 2021-11-01 | 7:00
3 | Ashuganj | 230 | 247 | 28 | 2021-11-01 | 22:00 | 235 | 1 | 2021-11-01 | 16:00
4 | Serajganj | 230 | 240 | 27 | 2021-11-01 | 14:00 | 230 | 3 | 2021-11-01 | 7:00
5 | Baghabari | 230 | 240 | 19 | 2021-11-01 | 5:00 | 228 | 3 | 2021-11-01 | 13:00
6 | Barapukuria | 230 | 239 | 5 | 2021-11-01 | 6:00 | 221 | 3 | 2021-11-01 | 8:00
7 | Bogura | 230 | 238 | 25 | 2021-11-01 | 14:00 | 219 | 17 | 2021-11-01 | 11:00
8 | Rajshahi | 230 | 240 | 20 | 2021-11-01 | 5:00 | 219 | 25 | 2021-11-01 | 7:00
9 | Khulna South | 230 | 250 | 27 | 2021-11-01 | 14:00 | 221 | 3 | 2021-11-01 | 12:00
10 | Rampura | 230 | 234 | 5 | 2021-11-01 | 7:00 | 221 | 28 | 2021-11-01 | 16:00
11 | Haripur | 230 | 236 | 5 | 2021-11-01 | 18:00 | 222 | 28 | 2021-11-01 | 12:00
12 | Hasnabad | 230 | 236 | 17 | 2021-11-01 | 20:00 | 220 | 1 | 2021-11-01 | 11:00
13 | Shyampur | 230 | 236 | 4 | 2021-11-01 | 21:00 | 222 | 28 | 2021-11-01 | 6:00
14 | Aminbazar | 230 | 238 | 19 | 2021-11-01 | 1:00 | 223 | 1 | 2021-11-01 | 2:00
15 | Tongi | 230 | 234 | 25 | 2021-11-01 | 19:30 | 215 | 28 | 2021-11-01 | 16:00
16 | Comilla (N) | 230 | 239 | 26 | 2021-11-01 | 18:30 | 225 | 13 | 2021-11-01 | 12:00
17 | Hathazari | 230 | 243 | 27 | 2021-11-01 | 18:00 | 216 | 30 | 2021-11-01 | 6:00
18 | Megnaghat | 230 | 241 | 13 | 2021-11-01 | 20:00 | 228 | 30 | 2021-11-01 | 11:00
19 | Fenchuganj | 230 | 248 | 3 | 2021-11-01 | 22:00 | 234 | 30 | 2021-11-01 | 13:00
20 | Siddhirganj | 230 | 239 | 19 | 2021-11-01 | 6:00 | 223 | 24 | 2021-11-01 | 11:00
21 | Maniknagar | 230 | 236 | 5 | 2021-11-01 | 8:00 | 222 | 28 | 2021-11-01 | 12:00
22 | Old Airport | 230 | 236 | 19 | 2021-11-01 | 4:00 | 220 | 3 | 2021-11-01 | 11:00
23 | Barisal | 230 | 249 | 5 | 2021-11-01 | 13:00 | 231 | 25 | 2021-11-01 | 17:00
24 | Bhola 225 MW | 230 | 250 | 5 | 2021-11-01 | 8:00 | 239 | 4 | 2021-11-01 | 21:00
25 | AKSML | 230 | 242 | 27 | 2021-11-01 | 14:00 | 214 | 12 | 2021-11-01 | 15:00
26 | BSRM | 230 | 238 | 6 | 2021-11-01 | 9:00 | 217 | 13 | 2021-11-01 | 12:00
27 | Bibiyana | 230 | 248 | 26 | 2021-11-01 | 18:30 | 238 | 11 | 2021-11-01 | 16:00
28 | Bhulta | 230 | 240 | 5 | 2021-11-01 | 8:00 | 221 | 24 | 2021-11-01 | 12:00
29 | Ashuganj (S) | 230 | 232 | 30 | 2021-11-01 | 12:00 | 231 | 13 | 2021-11-01 | 12:00
30 | Kaliakoir | 230 | 336 | 9 | 2021-11-01 | 12:00 | 219 | 20 | 2021-11-01 | 17:00
31 | GPH | 230 | 240 | 27 | 2021-11-01 | 13:00 | 217 | 2 | 2021-11-01 | 4:00
132 kV Substation
1 | Siddhirganj | 132 | 138 | 5 | 2021-11-01 | 0.25 | 130 | 24 | 2021-11-01 | 0.5
2 | Munsiganj | 132 | 140 | 5 | 2021-11-01 | 0.75 | 131 | 3 | 2021-11-01 | 0.45833
3 | Sonargaon | 132 | 140 | 5 | 2021-11-01 | 0.75 | 129 | 1 | 2021-11-01 | 0.5
4 | Shyampur | 132 | 141 | 5 | 2021-11-01 | 0.33333 | 133 | 1 | 2021-11-01 | 0.45833
5 | Bhulta | 132 | 135 | 5 | 2021-11-01 | 0.75 | 126 | 1 | 2021-11-01 | 0.45833
6 | Madanganj | 132 | 140 | 14 | 2021-11-01 | 0.83333 | 130 | 28 | 2021-11-01 | 0.66667
7 | Shitalakhya | 132 | 141 | 14 | 2021-11-01 | 0.83333 | 130 | 3 | 2021-11-01 | 0.45833
8 | Rahim Steal | 132 | 139 | 5 | 2021-11-01 | 0.75 | 130 | 23 | 2021-11-01 | 0.5
9 | Matuail | 132 | 138 | 5 | 2021-11-01 | 0.25 | 130 | 24 | 2021-11-01 | 0.5
10 | Ghorasal | 132 | 142 | 5 | 2021-11-01 | 0.041667 | 134 | 24 | 2021-11-01 | 0.45833
11 | Narsinghdi | 132 | 139 | 5 | 2021-11-01 | 0.33333 | 126 | 11 | 2021-11-01 | 0.66667
12 | Haripur (SBU) | 132 | 139 | 19 | 2021-11-01 | 0.70833 | 131 | 1 | 2021-11-01 | 0.5
13 | Sreenagar | 132 | - |  | - | - | - | - | - | -
14 | Ullon | 132 | 137 | 5 | 2021-11-01 | 0.33333 | 125 | 24 | 2021-11-01 | 0.5
15 | Hasnabad | 132 | 141 | 14 | 2021-11-01 | 0.8125 | 130 | 2 | 2021-11-01 | 0.375
16 | Magbazar | 132 | 138 | 5 | 2021-11-01 | 0.33333 | 126 | 24 | 2021-11-01 | 0.45833
17 | Maniknagar | 132 | 139 | 5 | 2021-11-01 | 0.33333 | 127 | 11 | 2021-11-01 | 0.5
18 | Bangabhaban | 132 | 139 | 5 | 2021-11-01 | 0.33333 | 127 | 11 | 2021-11-01 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November '2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
19 | Narinda | 132 | 139 | 5 | 2021-11-01 | 0.33333 | 127 | 11 | 2021-11-01 | 0.5
20 | Dhanmondi | 132 | 140 | 12 | 2021-11-01 | 0.70833 | 130 | 1 | 2021-11-01 | 0.5
21 | Lalbag | 132 | 136 | 17 | 2021-11-01 | 0.875 | 122 | 2 | 2021-11-01 | 0.41667
22 | Madartek | 132 | 137 | 5 | 2021-11-01 | 0.25 | 125 | 24 | 2021-11-01 | 0.5
23 | Dhaka University | 132 | - | - | - | - | - | - | - | -
24 | Aftabnagar | 132 | 137 | 5 | 2021-11-01 | 0.29167 | 125 | 24 | 2021-11-01 | 0.5
25 | Fatullah | 132 | 141 | 5 | 2021-11-01 | 0.75 | 132 | 1 | 2021-11-01 | 0.5
26 | Nawabganj | 133 | 139 | 5 | 2021-11-01 | 0.25 | 129 | 1 | 2021-11-01 | 0.5
27 | Mirpur | 132 | 135 | 13 | 2021-11-01 | 0.75 | 123 | 2 | 2021-11-01 | 0.375
28 | Kalyanpur | 132 | 135 | 13 | 2021-11-01 | 0.75 | 124 | 2 | 2021-11-01 | 0.375
29 | Gulshan | 132 | 136 | 22 | 2021-11-01 | 0.29167 | 125 | 24 | 2021-11-01 | 0.5
30 | Uttara | 132 | 138 | 10 | 2021-11-01 | 0.33333 | 122 | 3 | 2021-11-01 | 0.41667
31 | Uttara(New) | 132 | 139 | 22 | 2021-11-01 | 0.41667 | 123 | 1 | 2021-11-01 | 0.41667
32 | Kamrangirchar | 132 | 139 | 5 | 2021-11-01 | 0.77083 | 124 | 28 | 2021-11-01 | 0.625
33 | Savar | 132 | 137 | 5 | 2021-11-01 | 0.75 | 122 | 2 | 2021-11-01 | 0.375
34 | Bhasantec | 132 | 138 | 19 | 2021-11-01 | 0.77083 | 128 | 6 | 2021-11-01 | 0.45833
35 | Agargaon | 132 | 138 | 2 | 2021-11-01 | 0.8125 | 127 | 19 | 2021-11-01 | 0.5
36 | Satmosjid | 132 | 138 | 2 | 2021-11-01 | 0.8125 | 129 | 6 | 2021-11-01 | 0.45833
37 | Tongi | 132 | 143 | 10 | 2021-11-01 | 0.8125 | 129 | 22 | 2021-11-01 | 18:00
38 | Kabirpur | 132 | 141 | 19 | 2021-11-01 | 0.25 | 130 | 24 | 2021-11-01 | 0.45833
39 | Basundhara | 132 | 140 | 10 | 2021-11-01 | 0.83333 | 126 | 21 | 2021-11-01 | 0.5
40 | Manikganj | 132 | 144 | 19 | 2021-11-01 | 0.58333 | 128 | 22 | 2021-11-01 | 11:00
41 | Joydevpur | 132 | 140 | 5 | 2021-11-01 | 18:00 | 127 | 28 | 2021-11-01 | 0.66667
42 | New Tongi | 132 | 141 | 9 | 2021-11-01 | 0.75 | 123 | 22 | 2021-11-01 | 11:00
43 | Kodda | 132 | 140 | 10 | 2021-11-01 | 0.75 | 124 | 1 | 2021-11-01 | 16:00
44 | Dhamrai | 132 | 142 | 5 | 2021-11-01 | 8:00 | 120 | 22 | 2021-11-01 | 12:00
45 | Rajendrapur | 132 | 141 | 12 | 2021-11-01 | 0.75 | 121 | 4 | 2021-11-01 | 16:00
46 | Valuka | 132 | 134 | 19 | 2021-11-01 | 0.25 | 118 | 3 | 2021-11-01 | 0.54167
47 | Tangail | 132 | 139 | 19 | 2021-11-01 | 0.375 | 128 | 21 | 2021-11-01 | 0.66667
48 | Mymensing | 132 | 135 | 5 | 2021-11-01 | 0.25 | 123 | 3 | 2021-11-01 | 0.54167
49 | Kishorganj | 132 | 137 | 5 | 2021-11-01 | 0.33333 | 126 | 11 | 2021-11-01 | 0.66667
50 | Netrokona | 132 | 134 | 5 | 2021-11-01 | 0.25 | 122 | 20 | 2021-11-01 | 0.70833
51 | Jamalpur | 132 | 141 | 25 | 2021-11-01 | 0.375 | 118 | 1 | 2021-11-01 | 0.29167
52 | Sherpur | 132 | 140 | 25 | 2021-11-01 | 0.375 | 116 | 1 | 2021-11-01 | 0.29167
53 | Srimongal | 132 | 142 | 5 | 2021-11-01 | 0.33333 | 134 | 11 | 2021-11-01 | 15:0
54 | Shahjibazar | 132 | 141 | 5 | 2021-11-01 | 0.29167 | 130 | 11 | 2021-11-01 | 0.66667
55 | Fenchuganj | 132 | 139 | 4 | 2021-11-01 | 0.83333 | 132 | 15 | 2021-11-01 | 0.5
56 | Khulawara | 132 | 139 | 12 | 2021-11-01 | 23:0 | 133 | 11 | 2021-11-01 | 0.66667
57 | Sylhet | 132 | 136 | 9 | 2021-11-01 | 0.29167 | 130 | 17 | 2021-11-01 | 0.66667
58 | Chattak | 132 | 137 | 3 | 2021-11-01 | 0.375 | 130 | 17 | 2021-11-01 | 0.625
59 | Sunamganj | 132 | 135 | 13 | 2021-11-01 | 0.25 | 129 | 17 | 2021-11-01 | 0.54167
60 | Biani Bazar | 132 | 136 | 5 | 2021-11-01 | 0.33333 | 124 | 4 | 2021-11-01 | 0.95833
61 | Comilla(South) | 132 | 130 | 2 | 2021-11-01 | 0.95833 | 123 | 25 | 2021-11-01 | 0.58333
62 | Comilla (North) | 132 | 144 | 27 | 2021-11-01 | 0.75 | 134 | 1 | 2021-11-01 | 0.66667
63 | Chandpur | 132 | 143 | 7 | 2021-11-01 | 0.70833 | 132 | 1 | 2021-11-01 | 0.5
64 | Feni | 132 | 142 | 29 | 2021-11-01 | 0.75 | 128 | 1 | 2021-11-01 | 0.041667
65 | Chowmuhani | 132 | 141 | 28 | 2021-11-01 | 0.70833 | 127 | 1 | 2021-11-01 | 0.5
66 | Ashuganj | 132 | 142 | 5 | 2021-11-01 | 0.33333 | 136 | 8 | 2021-11-01 | 0.625
67 | Daudkandi | 132 | 140 | 26 | 2021-11-01 | 0.77083 | 130 | 1 | 2021-11-01 | 0.5
68 | Brahminbaria | 132 | 137 | 2 | 2021-11-01 | 0.75 | 127 | 11 | 2021-11-01 | 0.66667
69 | Ramganj | 132 | 140 | 26 | 2021-11-01 | 0.77083 | 128 | 1 | 2021-11-01 | 0.66667
70 | Chaddagram | 132 | 142 | 26 | 2021-11-01 | 0.75 | 130 | 1 | 2021-11-01 | 0.041667
71 | PHP | 132 | 140 | 26 | 2021-11-01 | 0.77083 | 126 | 2 | 2021-11-01 | 0.20833
72 | Kochua | 132 | 142 | 25 | 2021-11-01 | 0.45833 | 131 | 1 | 2021-11-01 | 0.5
73 | Madanhat | 132 | 142 | 27 | 2021-11-01 | 0.70833 | 128 | 1 | 2021-11-01 | 0.33333
74 | Hathazari | 132 | 142 | 27 | 2021-11-01 | 0.75 | 128 | 1 | 2021-11-01 | 0.375
75 | Khulshi | 132 | 139 | 29 | 2021-11-01 | 0.75 | 118 | 7 | 2021-11-01 | 0
76 | Halishahar | 132 | 140 | 27 | 2021-11-01 | 0.54167 | 124 | 2 | 2021-11-01 | 0.16667
77 | Baraulia | 132 | 142 | 26 | 2021-11-01 | 0.77083 | 125 | 1 | 2021-11-01 | 0.375
78 | Sikalbaha | 132 | 141 | 28 | 2021-11-01 | 0.70833 | 125 | 1 | 2021-11-01 | 0.33333
79 | Dohazari | 132 | 138 | 4 | 2021-11-01 | 0.83333 | 120 | 12 | 2021-11-01 | 0.625
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November '2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
80 | Cox'sbazar | 132 | 126 | 25 | 2021-11-01 | 0.375 | 101 | 15 | 2021-11-01 | 0.625
81 | Chandraghona | 132 | 141 | 27 | 2021-11-01 | 0.54167 | 128 | 13 | 2021-11-01 | 0.41667
82 | Kaptai | 132 | 140 | 27 | 2021-11-01 | 0.79167 | 128 | 12 | 2021-11-01 | 0.45833
83 | A. Khaer Stl. | 132 | 138 | 24 | 2021-11-01 | 0.66667 | 125 | 1 | 2021-11-01 | 0.66667
84 | Bakulia | 132 | 139 | 23 | 2021-11-01 | 0.91667 | 124 | 1 | 2021-11-01 | 0.66667
85 | Julda | 132 | 140 | 4 | 2021-11-01 | 0.75 | 126 | 12 | 2021-11-01 | 0.54167
86 | TK Chemical | 132 | 140 | 17 | 2021-11-01 | 0.54167 | 125 | 12 | 2021-11-01 | 0.45833
87 | Modern Steel | - | - | - | - | - | - | - | - | -
88 | Shahmirpur | 132 | 140 | 23 | 2021-11-01 | 0.79167 | 125 | 2 | 2021-11-01 | 0.375
89 | Khagrachhari | 132 | 140 | 29 | 2021-11-01 | 0.75 | 126 | 13 | 2021-11-01 | 0.5
90 | Matarbari | 132 | 135 | 21 | 2021-11-01 | 0.875 | 110 | 1 | 2021-11-01 | 0.083333
91 | Baroiar Hat | 132 | 141 | 29 | 2021-11-01 | 0.83333 | 128 | 1 | 2021-11-01 | 0.041667
92 | Rangamati | 132 | 140 | 27 | 2021-11-01 | 0.54167 | 126 | 12 | 2021-11-01 | 0.625
93 | Goalpara | 132 | 139 | 1 | 2021-11-01 | 0.041667 | 122 | 6 | 2021-11-01 | 0.5
94 | Khulna Central | 132 | 1126 | 0 | 2021-11-01 | 0.5 | 123 | 6 | 2021-11-01 | 0.5
95 | Noapara | 132 | 140 | 27 | 2021-11-01 | 0.58333 | 123 | 6 | 2021-11-01 | 0.5
96 | Jessore | 132 | 139 | 2 | 2021-11-01 | 0.16667 | 124 | 6 | 2021-11-01 | 0.5
97 | Benapol | 132 | 140 | 29 | 2021-11-01 | 0.70833 | 121 | 3 | 2021-11-01 | 0.54167
98 | Jhenida | 132 | 142 | 2 | 2021-11-01 | 0.20833 | 128 | 25 | 2021-11-01 | 0.29167
99 | Bottail | 132 | 141 | 19 | 2021-11-01 | 0.25 | 129 | 30 | 2021-11-01 | 0.54167
100 | G.K Project | 132 | 145 | 20 | 2021-11-01 | 0.16667 | 129 | 13 | 2021-11-01 | 0.5
101 | Faridpur | 132 | 144 | 6 | 2021-11-01 | 0.25 | 130 | 29 | 2021-11-01 | 0.58333
102 | Madaripur | 132 | 147 | 6 | 2021-11-01 | 0.33333 | 138 | 3 | 2021-11-01 | 0.125
103 | Sariatpur | 132 | 146 | 6 | 2021-11-01 | 0.16667 | 137 | 10 | 2021-11-01 | 0.75
104 | Gopalganj | 132 | 149 | 5 | 2021-11-01 | 0.25 | 122 | 6 | 2021-11-01 | 0.5
105 | Bagerhat | 132 | 139 | 2 | 2021-11-01 | 0.25 | 119 | 6 | 2021-11-01 | 0.5
106 | Mongla | 132 | 137 | 2 | 2021-11-01 | 0.041667 | 117 | 21 | 2021-11-01 | 0.875
107 | Satkhira | 132 | 138 | 1 | 2021-11-01 | 0.25 | 121 | 10 | 2021-11-01 | 0.45833
108 | Gallamari | 132 | 146 | 8 | 2021-11-01 | 0.16667 | 121 | 6 | 2021-11-01 | 0.5
109 | Magura | 132 | 142 | 2 | 2021-11-01 | 0.041667 | 130 | 3 | 2021-11-01 | 0.54167
110 | Norail | 132 | 141 | 2 | 2021-11-01 | 0.25 | 126 | 30 | 2021-11-01 | 0.77083
111 | Chuadanga | 132 | 141 | 20 | 2021-11-01 | 0.20833 | 124 | 30 | 2021-11-01 | 0.77083
112 | Barisal(N) | 132 | 146 | 3 | 2021-11-01 | 0.16667 | 137 | 2 | 2021-11-01 | 0.83333
113 | Barisal(S) | 132 | 144 | 5 | 2021-11-01 | 0.20833 | 136 | 12 | 2021-11-01 | 0.875
114 | Patuakhali | 132 | 144 | 6 | 2021-11-01 | 0.33333 | 133 | 12 | 2021-11-01 | 0.83333
115 | Bhandaria | 132 | 144 | 3 | 2021-11-01 | 0.25 | 125 | 23 | 2021-11-01 | 0.41667
116 | Borguna | 132 | 144 | 3 | 2021-11-01 | 0.375 | 135 | 12 | 2021-11-01 | 0.83333
117 | Ishurdi | 132 | 142 | 20 | 2021-11-01 | 0.125 | 130 | 25 | 2021-11-01 | 0.29167
118 | Ruppur paromanobik | 132 | 141 | 2 | 2021-11-01 | 0.25 | 130 | 30 | 2021-11-01 | 0.5
118 | Natore | 132 | 140 | 6 | 2021-11-01 | 0.25 | 127 | 25 | 2021-11-01 | 0.29167
119 | Bogra | 132 | 141 | 10 | 2021-11-01 | 0.8125 | 126 | 25 | 2021-11-01 | 0.33333
120 | Noagaon | 132 | 137 | 6 | 2021-11-01 | 0.25 | 119 | 25 | 2021-11-01 | 0.29167
121 | Rajshahi | 132 | 140 | 7 | 2021-11-01 | 0.79167 | 129 | 25 | 2021-11-01 | 0.29167
122 | Rajshahi New | 132 | 141 | 7 | 2021-11-01 | 0.79167 | 128 | 25 | 2021-11-01 | 0.29167
123 | C.Nawabganj | 132 | 141 | 7 | 2021-11-01 | 0.79167 | 126 | 6 | 2021-11-01 | 0.45833
124 | Amnura | 132 | 142 | 18 | 2021-11-01 | 0.75 | 127 | 4 | 2021-11-01 | 0.77083
125 | Pabna | 132 | 141 | 20 | 2021-11-01 | 0.16667 | 130 | 25 | 2021-11-01 | 0.29167
126 | Shahjadpur | 132 | 144 | 11 | 2021-11-01 | 0.16667 | 135 | 3 | 2021-11-01 | 0.5
127 | Serajganj | 132 | 140 | 12 | 2021-11-01 | 0.25 | 127 | 5 | 2021-11-01 | 0.45833
128 | Niyamatpur | 132 | 136 | 6 | 2021-11-01 | 0.25 | 123 | 25 | 2021-11-01 | 0.33333
129 | Joypurhat | 132 | 139 | 10 | 2021-11-01 | 0.8125 | 123 | 2 | 2021-11-01 | 0.375
130 | Sherpur(Bogura) | 132 | 141 | 27 | 2021-11-01 | 0.58333 | 130 | 1 | 2021-11-01 | 0.5
132 | Mohastangor | 132 | 140 | 10 | 2021-11-01 | 0.83333 | 123 | 25 | 2021-11-01 | 0.41667
133 | Bangura | 132 | 142 | 20 | 2021-11-01 | 0.16667 | 132 | 8 | 2021-11-01 | 0.5
134 | Rangpur | 132 | 138 | 6 | 2021-11-01 | 0.25 | 120 | 21 | 2021-11-01 | 0.8125
135 | Lalmonirhat | 132 | 137 | 25 | 2021-11-01 | 0.58333 | 120 | 3 | 2021-11-01 | 0.33333
136 | Saidpur | 132 | 137 | 25 | 2021-11-01 | 0.58333 | 120 | 7 | 2021-11-01 | 0.5
137 | Purbasadipur | 132 | 137 | 7 | 2021-11-01 | 0.16667 | 115 | 8 | 2021-11-01 | 0.5
138 | Thakurgaon | 132 | 136 | 1 | 2021-11-01 | 0.25 | 118 | 8 | 2021-11-01 | 0.5
139 | Palashbari | 132 | 138 | 6 | 2021-11-01 | 0.25 | 125 | 21 | 2021-11-01 | 0.8125
140 | Barapukuria | 132 | 139 | 5 | 2021-11-01 | 0.25 | 121 | 3 | 2021-11-01 | 0.33333
141 | Panchagar | 132 | 138 | 2 | 2021-11-01 | 0.70833 | 116 | 8 | 2021-11-01 | 0.5
142 | Joldhaka | 132 | 138 | 6 | 2021-11-01 | 0.25 | 117 | 8 | 2021-11-01 | 0.5
143 | Kurigram | 132 | 137 | 25 | 2021-11-01 | 0.58333 | 118 | 3 | 2021-11-01 | 0.33333
144 | Mithapukur | 132 | 140 | 6 | 2021-11-01 | 0.25 | 123 | 3 | 2021-11-01 | 0.33333
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:November 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 33 | 90
Hasnabad | TR2 | 225 | 33 | 90 | 27/11/2021 | 9:00
| TR3 | 225 | 33 | 90
| TR1 | 225 | 170 | 485 | 01.11.2021 | 17:00
Tongi | TR2 | 225 | 170 | 485 | 01.11.2021 | 17:00
| TR3 | 225 | 170 | 485 | 01.11.2021 | 17:00
Haripur | TR1 | 225 | 78 | 220
| TR2 | 225 | 78 | 220 | 2021-01-11 | 16:00
| TR3 | 225 | 78 | 220
| TR1 | 225 | 158 | 405
Rampura | TR2 | 225 | 158 | 405 | 2021-01-11 | 16:00
| TR3 | 225 | 158 | 405
Keraniganj | ATR1 | 300 | 67 | 178
| ATR2 | 300 | 67 | 178 | 2021-11-11 | 19:00
| ATR3 | 300 | 67 | 178
| TR1 | 225 | 131 | 370
Aminbazar | TR2 | 225 | 131 | 370 | 2021-02-11 | 10:00
| TR3 | 225 | 135 | 380
Agargaon | TR1 | 300 | 133 | 340
| TR2 | 300 | 133 | 340 | 2021-01-11 | 13:00
Maniknagar | TR1 | 300 | 113 | 320 | 2021-02-11 | 13:00
| TR2 | 300 | 113 | 320
Cumilla (N) | dx | 225 | 40 | 479 | 23/11/21 | 19:00
| TR2 | 225 | 40 | 467
Fenchuganj | AT2 | 300 | 164 | 427 | 17/11/2021 | 18:00
| MT1 | 150 | 93 | 428
Hathazari | MT2 | 150 | 93 | 428 | 2021-12-11 | 20:00
| MT3 | 150 | 93 | 428
| MT4 | 150 | 93 | 428
| TR1 | 225 | 71 | 195
Ishurdi | TR2 | 225 | 71 | 195 | 25/11/2021 | 7:26
| TR3 | 225 | 71 | 195
Khulna(S) | TR1 | 225 | 75 | 195
| TR2 | 225 | 75 | 195 | 21/11/2021 | 21:00
| TR3 | 300 | 95 | 255
Bogura | TR1 | 225 | 87 | 237 | 27.11.21 | 8:00
| TR2 | 225 | 87 | 237 | 27.11.21 | 8:00
| TR3 | 225 | 118 | 297 | 27.11.21 | 8:00
Baghabari | TR1 | 300 | 116 | 300 | 30/11/21 | 19:30
| TR2 | 225 | 78 | 210
Rajshahi | ATR-01 | 300 | 145 | 245 | 01.11.2021 | 21:00
| ATR-02 | 300 | 145 | 245 | 01.11.2021 | 21:00
Barapukuria | TR1 | 225 | 114 | 490 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 122 | 560 | 2021-01-11 | 18:00 | 132 kV current is being provided
| TR6 | 300 | 152 | 670
Bheramara | Transformer-1 | 225 | 50 | 130 | 2021-11-30 | 19:30
| Transformer-2 | 225 | 50 | 130 | 2021-11-30 | 19:30
Shyampur | ATR-01 | 300 | 101 | 310 | 24/11/2021 | 2:00
| ATR-02 | 300 | 101 | 310
Kaliakoir | TR1 | 300 | 101 | 265 | 2021-03-11 | 12:00
Sikalbaha | ATR-1 | 300 | 172 | 480 | 2021-12-11 | 20:00
| ATR-2 | 300 | 172 | 480
Jhenaidah | T1(230/132 kV) | 300 | 119 | 318 | 30/11/2021 | 18:00
| T2(230/132 kV) | 300 | 119 | 318
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:September 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 245.7 | 374 | 2021-04-11 | 10:00
| TR2(400/230 kV) | 520 | 248.6 | 377
| TR1(400/132 kV) | 325 | 239.7 | 374 | 2021-04-11 | 17:30
| TR2(400/132 kV) | 325 | 240.7 | 376
Bibiyana | ICT1(400/230 kV) | 520 | 118.5 | 171 | 2021-02-11 | 4:00
| ICT2(400/230kV) | 520 | 113 | 165 | 2021-02-11 | 4:00
Bhulta | ATR1(400/230 kV) | 520 | 187 | 326 | 2021-11-11 | 11:30
| ATR2(400/230kV) | 520 | 187 | 326 | 2021-11-12 | 12:30
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 380 | 605 | 2021-08-11 | 17:45
Gopalganj | ATR1(400/138 kV) | 325 | 231 | 342 | 09.11.2021 | 21:00
| ATR2(400/138kV) | 325 | 231 | 342 | 09.11.2021 | 21:00
Payra | GSUT1 | 270 | 151 | 634 | 21/11/2021 | 21:00
| GSUT2 | 270 | 151 | 652
| GSUT3 | 270 | 151 | 640
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:October 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:October 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-11-01 | 10331 | 10331 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-01 | 9044 | 9044 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-02 | 10274 | 10274 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-02 | 8757 | 8757 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-03 | 10389 | 10389 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-03 | 8791 | 8791 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-04 | 10114 | 10114 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-04 | 8919 | 8919 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-05 | 8681 | 8681 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-05 | 7413 | 7413 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-06 | 9659 | 9659 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-06 | 7845 | 7845 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-07 | 9785 | 9785 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-07 | 8399 | 8399 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-08 | 9853 | 9853 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-08 | 8471 | 8471 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-09 | 10228 | 10228 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-09 | 8626 | 8626 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-10 | 10254 | 10254 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-10 | 8827 | 8827 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-11 | 10067 | 10067 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-11 | 8739 | 8739 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-12 | 8907 | 8907 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-12 | 7487 | 7487 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-13 | 9174 | 9174 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-13 | 7938 | 7938 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-14 | 9240 | 9240 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-14 | 8043 | 8043 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-15 | 9519 | 9519 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-15 | 8203 | 8203 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-16 | 9504 | 9504 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-16 | 8298 | 8298 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-17 | 9614 | 9614 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-17 | 8059 | 8059 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-18 | 9747 | 9747 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-18 | 8362 | 8362 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-19 | 8271 | 8271 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-19 | 7051 | 7051 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-20 | 9598 | 9598 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-20 | 7762 | 7762 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-21 | 9464 | 9464 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-21 | 8129 | 8129 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-22 | 9734 | 9734 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-22 | 8210 | 8210 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-23 | 10026 | 10026 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-23 | 8396 | 8396 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-24 | 9668 | 9668 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-24 | 7982 | 7982 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-25 | 9664 | 9664 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-25 | 8221 | 8221 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-26 | 8261 | 8261 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-26 | 6648 | 6648 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-27 | 9338 | 9338 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-27 | 7520 | 7520 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-28 | 9173 | 9173 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-28 | 7811 | 7811 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-29 | 9456 | 9456 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-29 | 8035 | 8035 | - | - | - | - | - | - | - | - | - | - | - | -
2021-11-30 | 9396 | 9396 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-11-30 | 7986 | 7986 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:November 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10389 | 2021-11-03 | 19:00
2 | Maximum Day Peak Genaration | MW | 9044 | 2021-11-01 | 12:00
3 | Maximum Demand | MW | 10389 | 2021-11-03 | 12:00
4 | Minimum Generation | MW | 5609 | 2021-11-27 | 6:00
5 | Average of the daily evening peak Genaration | MW | 9579.6333
6 | Average of the daily day peak Genaration | MW | 8132.4
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 5835.9262
12 | Total Generation by BPDB | MkWh | 1073.0634 | % of total Gen. | 18.39%
13 | Total Generation by IPP | MkWh | 1805.5503 | '' | 30.94%
14 | A) Total Generation by Generation Companies | MkWh | 1988.9071 | '' | 34.08%
| B) Total Generation by REB | MkWh | 137.7806 | " | 2.361%
| C) Total Generation by RENTAL | MkWh | 293.2499 | " | 5.025%
| D) Total Imported from India (BIPTC) | MkWh | 473.2633 | " | 8.109%
| E) Total Imported from Tripura, India (A.C) | MkWh | 64.1117 | " | 1.099%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3922.3382 | % of total Gen. | 67.21%
| B) Oil | MkWh | 979.0282 | '' | 16.78%
| C) Hydro | MkWh | 65.2371 | '' | 1.118%
| D) Solar | MkWh | 19.3572 | '' | 0.3317%
| E) Coal | MkWh | 312.5907 | '' | 5.356%
| F) BIPTC (Import from India) | MkWh | 473.2633 | '' | 8.109%
| G) A.C (Import from Tripura, India) | MkWh | 64.1117 | '' | 1.099%
16 | Maximun of the daily total Generation . | MkWh | 269.0334
17 | Monthly Load factor | % | 75.5028
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 15084.5037
| A) Gas | M.Taka | 4227.5014
| B) Liquid fuel | M.Taka | 6492.8184
| C) Coal | M.Taka | 1469.7037
| D) BIPTC (Import from India) | M.Taka | 2413.6426
| E) Tripura(Import from India) | M.Taka | 480.8376
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 526.8048 | 2021-11-18
| A) Gas | M.Taka | 211.4865 | 2021-11-23
| B) Liquid fuel | M.Taka | 351.4111 | 2021-11-18
| C) Coal | M.Taka | 63.9404 | 2021-11-23
| D) BIPTC (Import from India) | M.Taka | 88.6584 | 2021-11-04
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 2.94
| B) Excluding Hydro & Solar | Taka/kWhR | 2.9829
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 106.1 | 30/11/2021 | 06:00
b) | Actual | FT (MSL) | 100.9 | 30/11/2021 | 06:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.