## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-01-10 | Monday
|  | Date (day): | 2022-01-10 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11115.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11907 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-01-09 | 2022-01-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 240 | 251 | 250 | 250
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 170 | 167 | 250 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 180 | 180 | 180 | 180 | 270 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 27 | 24 | 35 | 40 |  | 60 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 47 | 48 | 51 | 51
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 98 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 34 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 32 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 285 | 299 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 258 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 100 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 0 | 0 | 55 | 55 | 55 | 55
| Dhaka area Total |  |  |  |  | 6178 | 5560 | 2010 | 2494 | 2723 | 2748 | 2115 | 837
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 0 | 25 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 3 | 20 | 20 |  | 30 | Engine problem
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 85 | 82 | 83 | 83 |  | 147 | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 68 | 91 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 52 | 70 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 30 | 100 | 100
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 4 | 5 | 10
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 87 | 90 | 90 | 90 | 18 |  | Engine problem
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 50 | 150 | 300 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 54 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 786 | 992 | 1296 | 1294 | 378 | 692
60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 175 | 142 | 170 | 170 | 51 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 140 | 140 | 150 | 150 | 210 |  | Gas shortage.
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 360 | 360 |  |  | FGMO
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 138 | 128 | 150 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 132 | 137 | 137 |  | 26 | Machine problem.
71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 44 | 200 | 200
72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 22 | 22
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 101 | 138 | 163
74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 31 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 26 | 52 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 0 | 200
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 73 | 113 | 113 | 113
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1297 | 1457 | 1875 | 2100 | 856 | 63
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 48 | 50 | 55 | 55 | 147 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 173 | 192 | 200 | 200
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 112 | 108 | 115 | 115
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 22 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 622 | 423 | 392 | 465.6 | 414 | 147 | 8
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maintenance
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 51 | 51 | 51
| Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 66 | 68 | 72 | 72
96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 81 | 81
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 177 | 177 | 190 | 190 |  | 41 | Machine problem
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 24 | 24
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 320 | 330 | 330
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1283 | 1355 | 1392 | 1392 | 0 | 989
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 469 | 471 | 489 | 489
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35 |  | 19 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 6 | 0 | 40 |  | 69 | Engine problem
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 60 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 0 | 0 | 75 | 0 | 16 | 0
| Khulna Area Total |  |  |  |  | 2248 | 2129 | 614 | 642 | 660 | 1089 | 410 | 88
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 25 | 25 | 25 |  | 8 | Engine problem
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 92 | 91 | 91 | 103 |  | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 11 | 11 | 11 | 84 |  | Gas shortage
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 290 | 400 | 620 | 620
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 150 | 222 | 200 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
| Barisal Area Total |  |  |  |  | 2046 | 2046 | 558 | 750 | 1057 | 1227 | 187 | 8
121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 43 | 50 | 50
123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 38 | 30 | 30 |  | 41 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 168 | 194 | 200 | 200 |  |  | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 343 | 410 | 400 | 400 |  |  | FGMO
131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Under maint
132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 16 | 16 | 25 | 25 | 25 |  | Fuel shortage
136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 90 | 100
137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 20 | 200 | 200
138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 864 | 1143 | 1326 | 1330 | 625 | 175
141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 200 | 200 | 74 |  | Coal shortage
143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 105 | 113 | 113 | 113
146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
| Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 6 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 314 | 312 | 321 | 313 | 74 | 210
| Total |  |  |  |  | 22031 | 20934 | 8149 | 9537 | 11115.6 | 11907 | 4792 | 3070
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8037.92 | 9407 | 10964.0819 | 11744.6942
A. |  | 2022-01-09 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 9537 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6018 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9537 | MW
3 | Day peak Generation : |  |  | 8149 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9407 | MW
4 | Evening peak Generation : |  |  | 9537 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 189.6729 | MKWHr | By Solar | 1.1449 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 94.3822 | MKWHr |  | By Oil: | 65.1454 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 13.6161 | MKWHr |  | By Hydro: | 1.9098 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4792 | MW | Dhaka | 3552 | 3552 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3070 | MW | Chittagong | 1028 | 1028 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 7862 | MW | Khulna | 1087 | 1087 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 744.11 | MMCFD |  |  | Rajshahi | 950 | 950 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 95175171.178 | ii) Oil : | Taka | 465861788.56 | Comilla | 759 | 759 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 64791706 | Total | Taka | 625828665.738 | Mymensingh | 808 | 808 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.358 | MKWHr. | Sylhet | 340 | 340 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -202 | MW (E to W) at | 19:00 | hrs | Barisal | 249 | 249 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -310 | MW at | 8:00 | hrs | Rangpur | 634 | 634 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.6° C |  |  | Total | 9407 | 9407 |  | 0
B. |  | 2022-01-10 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 27.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11907 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 2307 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 190.9259 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6007 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.4364 | MKWHr. | ii) HVDC Flow at Peak Time |  | 471 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0381 | MKWHr. | iii) Maximum HVDC Flow : |  | 477 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.12 |  | (b) Today: | 97 |  | (c) Rule Curve: |  | 101.29
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-01-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 201 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 79 | 0 | 21 | 25 | 0 | 0 | 80 | 140 | 275 | 181 | 8 | 136 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 71 | 51 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 76 | 0 | 177 | 18 | 0 | 10 | 280 | 22 | 8 | 0 | 195 | 0 | 0 | 192 | 0 | 0 | 0 | 76 | 0 | 150 | 0 | 24 | 105 | 0 | 0 | 0 | 54 | 34 | 0 | 35 | 70 | 401 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 162 | 0 | 310 | 35 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 290 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4847 | 2018 | 6865 | 2269 | 472 | 1579 | 0 | 1905 | 489 | 80 | 0 | 0 | 71 | 0 | 0 | 97.14
2:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 201 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 36 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 85 | 0 | 21 | 25 | 0 | 0 | 80 | 140 | 275 | 180 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 68 | 53 | 0 | 22 | 0 | 42 | 0 | 48 | 0 | 130 | 0 | 72 | 76 | 0 | 177 | 18 | 0 | 10 | 280 | 22 | 8 | 0 | 110 | 0 | 0 | 160 | 0 | 0 | 0 | 76 | 0 | 150 | 0 | 0 | 105 | 0 | 0 | 0 | 54 | 17 | 0 | 8 | 40 | 400 | 35 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 17 |  | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 161 | 0 | 326 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 290 | 201 | 0 | 0 | 0 | 0 | 0 |  | 4475 | 1996 | 6471 | 2270 | 470 | 1592 | 0 | 1506 | 489 | 76 | 0 | 0 | 68 | 0 | 0 | 97.14
3:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 201 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 35 | 0 | 0 | 80 | 140 | 275 | 185 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 65 | 53 | 0 | 22 | 0 | 42 | 0 | 48 | 0 | 130 | 0 | 71 | 76 | 0 | 177 | 18 | 0 | 10 | 295 | 22 | 8 | 0 | 110 | 0 | 0 | 160 | 0 | 0 | 0 | 76 | 0 | 145 | 0 | 0 | 70 | 0 | 0 | 0 | 36 | 17 | 0 | 8 | 10 | 400 | 17 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 18 |  | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 167 | 0 | 318 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 290 | 181 | 0 | 0 | 0 | 0 | 0 |  | 4353 | 1903 | 6256 | 2280 | 470 | 1588 | 0 | 1282 | 489 | 82 | 0 | 0 | 65 | 0 | 0 | 97.13
4:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 212 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 45 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 37 | 0 | 0 | 80 | 140 | 305 | 193 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 64 | 53 | 0 | 22 | 0 | 42 | 0 | 48 | 0 | 110 | 0 | 40 | 40 | 0 | 177 | 18 | 0 | 10 | 285 | 22 | 8 | 0 | 80 | 0 | 0 | 100 | 0 | 0 | 0 | 90 | 0 | 147 | 0 | 0 | 35 | 0 | 0 | 0 | 36 | 17 | 0 | 8 | 10 | 400 | 17 | 0 | 126 | 68 | 0 | 17 | 0 | 0 | 18 |  | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 335 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 290 | 161 | 0 | 0 | 0 | 0 | 0 |  | 4164 | 1896 | 6060 | 2283 | 470 | 1532 | 0 | 1137 | 489 | 85 | 0 | 0 | 64 | 0 | 0 | 97.13
5:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 212 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 85 | 0 | 21 | 39 | 0 | 0 | 80 | 140 | 290 | 199 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 65 | 53 | 0 | 22 | 0 | 42 | 0 | 11 | 0 | 110 | 0 | 40 | 40 | 0 | 177 | 18 | 0 | 10 | 300 | 22 | 5 | 0 | 80 | 0 | 0 | 100 | 0 | 0 | 0 | 90 | 0 | 150 | 0 | 0 | 35 | 0 | 0 | 0 | 36 | 17 | 0 | 8 | 10 | 400 | 17 | 0 | 126 | 68 | 0 | 17 | 0 | 0 | 17 |  | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 159 | 0 | 332 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 290 | 161 | 0 | 0 | 0 | 0 | 0 |  | 4131 | 1887 | 6018 | 2267 | 470 | 1508 | 0 | 1139 | 489 | 80 | 0 | 0 | 65 | 0 | 0 | 97.12
6:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 222 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 41 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 39 | 0 | 0 | 80 | 140 | 275 | 195 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 14 | 21 | 11 | 33 | 9 | 70 | 53 | 0 | 22 | 0 | 42 | 0 | 11 | 0 | 130 | 0 | 40 | 40 | 0 | 177 | 18 | 0 | 10 | 310 | 21 | 5 | 0 | 80 | 0 | 0 | 106 | 0 | 0 | 0 | 90 | 0 | 150 | 0 | 2 | 35 | 7 | 0 | 7 | 36 | 17 | 0 | 21 | 50 | 400 | 17 | 0 | 126 | 92 | 0 | 17 | 0 | 0 | 17 |  | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 332 | 0 | 0 | 1 | 0 | 112 | 0 | 0 | 15 | 290 | 161 | 0 | 0 | 0 | 0 | 0 |  | 4321 | 1901 | 6222 | 2303 | 470 | 1550 | 0 | 1259 | 489 | 81 | 0 | 0 | 70 | 0 | 0 | 97.12
7:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 222 |  | 0 | 180 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 44 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 34 | 0 | 0 | 80 | 140 | 310 | 198 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 9 | 71 | 51 | 0 | 22 | 0 | 42 | 0 | 11 | 0 | 130 | 0 | 40 | 76 | 0 | 177 | 18 | 0 | 10 | 300 | 21 | 5 | 0 | 125 | 0 | 0 | 140 | 0 | 1 | 1 | 90 | 0 | 147 | 0 | 8 | 70 | 17 | 0 | 15 | 36 | 50 | 0 | 46 | 70 | 400 | 45 | 1 | 126 | 116 | 0 | 17 | 1 | 0 | 17 |  | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 152 | 0 | 346 | 14 | 0 | 25 | 0 | 112 | 0 | 0 | 50 | 290 | 161 | 0 | 0 | 0 | 0 | 0 |  | 4690 | 1983 | 6673 | 2334 | 470 | 1583 | 0 | 1639 | 489 | 84 | 0 | 0 | 71 | 3 | 0 | 97.11
8:00 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 200 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 74 | 0 | 8 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 36 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 4 | 0 | 0 | 80 | 140 | 280 | 188 | 8 | 136 | 5 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 9 | 71 | 53 | 0 | 22 | 0 | 42 | 0 | 45 | 0 | 163 | 0 | 72 | 76 | 0 | 177 | 18 | 0 | 10 | 300 | 21 | 5 | 0 | 225 | 0 | 0 | 182 | 0 | 42 | 9 | 90 | 0 | 135 | 0 | 50 | 86 | 39 | 1 | 15 | 36 | 99 | 0 | 46 | 100 | 400 | 82 | 9 | 158 | 116 | 0 | 17 | 9 | 0 | 29 |  | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 152 | 0 | 296 | 60 | 0 | 70 | 0 | 112 | 0 | 1 | 113 | 290 | 160 | 0 | 0 | 0 | 17 | 0 |  | 5237 | 2112 | 7349 | 2331 | 470 | 1547 | 0 | 2319 | 489 | 76 | 0 | 0 | 71 | 46 | 0 | 97.11
9:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 201 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 0 | 24 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 9 | 25 | 33 | 25 | 0 | 33 | 40 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 280 | 167 | 8 | 136 | 5 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 25 | 9 | 85 | 51 | 0 | 22 | 1 | 42 | 0 | 45 | 0 | 163 | 0 | 70 | 76 | 0 | 177 | 18 | 0 | 10 | 290 | 21 | 5 | 0 | 292 | 0 | 0 | 184 | 0 | 149 | 13 | 90 | 0 | 132 | 0 | 112 | 90 | 68 | 2 | 15 | 36 | 110 | 0 | 46 | 100 | 400 | 104 | 22 | 162 | 116 | 0 | 0 | 18 | 0 | 55 |  | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 156 | 0 | 318 | 85 | 0 | 110 | 0 | 112 | 0 | 3 | 113 | 290 | 200 | 0 | 0 | 2 | 40 | 0 |  | 5616 | 2294 | 7910 | 2302 | 469 | 1597 | 0 | 2794 | 489 | 73 | 0 | 0 | 85 | 101 | 0 | 97.1
10:00 | 0 | 0 | 241 | 0 | 0 | 0 | 0 | 0 | 196 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 32 | 25 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 25 | 0 | 33 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 265 | 178 | 8 | 136 | 5 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 22 | 9 | 84 | 51 | 0 | 22 | 2 | 42 | 0 | 45 | 0 | 163 | 0 | 70 | 76 | 0 | 177 | 18 | 0 | 10 | 290 | 21 | 5 | 0 | 295 | 0 | 0 | 184 | 0 | 149 | 17 | 90 | 0 | 143 | 0 | 112 | 91 | 68 | 4 | 15 | 36 | 110 | 0 | 46 | 90 | 400 | 104 | 35 | 162 | 116 | 0 | 16 | 25 | 0 | 55 |  | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 34 | 30 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 280 | 105 | 0 | 113 | 0 | 110 | 0 | 5 | 113 | 280 | 130 | 0 | 0 | 4 | 60 | 0 |  | 5695 | 2310 | 8005 | 2306 | 469 | 1484 | 0 | 2853 | 479 | 73 | 0 | 105 | 84 | 152 | 0 | 97.1
11:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 182 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 32 | 25 | 0 | 0 | 20 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 20 | 25 | 0 | 33 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 270 | 182 | 8 | 138 | 5 | 5 | 0 | 51 | 0 | 0 | 25 | 18 | 11 | 20 | 9 | 93 | 50 | 0 | 22 | 2 | 43 | 0 | 45 | 0 | 130 | 0 | 40 | 76 | 0 | 177 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 281 | 0 | 0 | 173 | 0 | 149 | 19 | 90 | 0 | 135 | 0 | 112 | 105 | 68 | 4 | 15 | 36 | 110 | 0 | 46 | 90 | 340 | 104 | 41 | 162 | 116 | 0 | 17 | 29 | 0 | 55 |  | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 34 | 32 | 25 | 0 | 18 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 316 | 70 | 0 | 70 | 0 | 105 | 0 | 5 | 113 | 280 | 130 | 0 | 0 | 4 | 71 | 3 |  | 5550 | 2284 | 7834 | 2205 | 469 | 1451 | 0 | 2775 | 479 | 73 | 0 | 114 | 93 | 175 | 0 | 97.09
12:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 170 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 48 | 27 | 0 | 0 | 47 | 35 | 55 | 35 | 16 | 25 | 6 | 25 | 22 | 32 | 0 | 45 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 87 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 300 | 175 | 8 | 138 | 5 | 5 | 0 | 43 | 0 | 0 | 26 | 18 | 8 | 16 | 9 | 98 | 48 | 0 | 20 | 2 | 43 | 0 | 50 | 0 | 130 | 0 | 66 | 78 | 0 | 177 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 285 | 0 | 0 | 173 | 0 | 149 | 19 | 90 | 0 | 138 | 0 | 112 | 105 | 68 | 4 | 50 | 36 | 110 | 0 | 73 | 90 | 390 | 104 | 44 | 162 | 116 | 0 | 17 | 30 | 0 | 55 |  | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 34 | 32 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 168 | 0 | 343 | 70 | 0 | 70 | 0 | 105 | 0 | 4 | 113 | 290 | 150 | 0 | 0 | 4 | 75 | 6 |  | 5799 | 2350 | 8149 | 2294 | 469 | 1517 | 0 | 2880 | 489 | 85 | 0 | 135 | 98 | 182 | 0 | 97.09
13:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 173 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 48 | 32 | 0 | 0 | 47 | 35 | 55 | 35 | 16 | 25 | 9 | 25 | 33 | 51 | 0 | 34 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 90 | 0 | 21 | 4 | 0 | 0 | 80 | 140 | 270 | 158 | 8 | 136 | 5 | 5 | 0 | 51 | 0 | 0 | 35 | 18 | 11 | 16 | 9 | 98 | 48 | 0 | 20 | 2 | 43 | 0 | 51 | 0 | 163 | 0 | 66 | 78 | 0 | 177 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 285 | 0 | 0 | 173 | 0 | 149 | 18 | 90 | 0 | 143 | 0 | 112 | 92 | 77 | 4 | 80 | 36 | 110 | 0 | 113 | 90 | 400 | 104 | 40 | 162 | 116 | 0 | 17 | 30 | 0 | 55 |  | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 50 | 22 | 0 | 0 | 34 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 197 | 0 | 385 | 105 | 0 | 90 | 0 | 105 | 0 | 5 | 113 | 330 | 170 | 0 | 0 | 4 | 72 | 0 |  | 5915 | 2549 | 8464 | 2301 | 469 | 1630 | 0 | 3036 | 529 | 74 | 0 | 152 | 98 | 175 | 0 | 97.08
14:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 171 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 48 | 16 | 36 | 0 | 0 | 47 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 33 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 90 | 0 | 21 | 4 | 0 | 0 | 80 | 140 | 270 | 170 | 8 | 130 | 5 | 5 | 0 | 51 | 0 | 0 | 46 | 18 | 11 | 16 | 9 | 99 | 43 | 0 | 20 | 2 | 43 | 0 | 48 | 0 | 130 | 0 | 66 | 78 | 0 | 177 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 295 | 0 | 0 | 172 | 0 | 149 | 16 | 90 | 0 | 138 | 0 | 75 | 105 | 91 | 3 | 45 | 36 | 110 | 0 | 113 | 90 | 340 | 104 | 34 | 108 | 116 | 0 | 17 | 27 | 0 | 55 |  | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 50 | 31 | 41 | 0 | 34 | 32 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 176 | 0 | 283 | 105 | 0 | 70 | 0 | 98 | 0 | 3 | 70 | 320 | 170 | 0 | 0 | 4 | 61 | 0 |  | 5618 | 2384 | 8002 | 2224 | 472 | 1463 | 0 | 2832 | 519 | 73 | 0 | 170 | 99 | 150 | 0 | 97.08
15:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 173 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 48 | 16 | 36 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 90 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 305 | 169 | 8 | 130 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 16 | 9 | 93 | 45 | 0 | 20 | 1 | 43 | 0 | 48 | 0 | 163 | 0 | 64 | 78 | 0 | 177 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 288 | 0 | 0 | 171 | 0 | 149 | 13 | 90 | 0 | 142 | 0 | 75 | 105 | 91 | 2 | 45 | 36 | 106 | 0 | 113 | 90 | 340 | 104 | 22 | 108 | 110 | 0 | 17 | 19 | 0 | 55 |  | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 50 | 39 | 48 | 0 | 8 | 32 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 340 | 70 | 0 | 35 | 0 | 60 | 0 | 2 | 35 | 320 | 174 | 0 | 0 | 2 | 43 | 0 |  | 5597 | 2262 | 7859 | 2173 | 471 | 1580 | 0 | 2648 | 519 | 86 | 0 | 185 | 93 | 104 | 0 | 97.07
16:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 174 |  | 0 | 180 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 48 | 16 | 24 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 6 | 25 | 33 | 51 | 0 | 38 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 90 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 270 | 159 | 8 | 132 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 9 | 89 | 49 | 0 | 20 | 0 | 43 | 0 | 48 | 0 | 163 | 0 | 65 | 78 | 0 | 178 | 18 | 0 | 10 | 310 | 16 | 5 | 0 | 280 | 0 | 0 | 169 | 0 | 149 | 8 | 90 | 0 | 128 | 0 | 75 | 105 | 91 | 1 | 45 | 36 | 107 | 0 | 113 | 100 | 340 | 104 | 10 | 108 | 100 | 0 | 17 | 9 | 0 | 55 |  | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 16 | 0 | 0 | 0 | 0 | 50 | 38 | 48 | 0 | 8 | 32 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 332 | 70 | 0 | 35 | 0 | 49 | 0 | 1 | 35 | 320 | 170 | 0 | 0 | 0 | 20 | 0 |  | 5497 | 2217 | 7714 | 2155 | 471 | 1579 | 0 | 2590 | 519 | 78 | 0 | 184 | 89 | 49 | 0 | 97.07
17:00 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 168 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 75 | 48 | 24 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 90 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 270 | 155 | 8 | 130 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 9 | 92 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 78 | 0 | 178 | 18 | 0 | 10 | 305 | 16 | 5 | 0 | 280 | 0 | 0 | 181 | 0 | 149 | 1 | 90 | 0 | 123 | 0 | 85 | 105 | 91 | 0 | 65 | 36 | 110 | 0 | 113 | 100 | 400 | 104 | 1 | 125 | 101 | 0 | 17 | 2 | 0 | 55 |  | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 16 | 0 | 0 | 0 | 0 | 50 | 38 | 48 | 0 | 8 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 300 | 70 | 0 | 37 | 0 | 58 | 0 | 0 | 70 | 320 | 140 | 0 | 0 | 0 | 4 | 3 |  | 5673 | 2188 | 7861 | 2213 | 471 | 1510 | 0 | 2746 | 519 | 86 | 0 | 216 | 92 | 8 | 0 | 97.06
18:00 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 172 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 19 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 51 | 30 | 90 | 0 | 21 | 3 | 0 | 0 | 80 | 140 | 300 | 152 | 8 | 132 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 20 | 11 | 28 | 9 | 108 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 78 | 0 | 177 | 18 | 0 | 10 | 300 | 16 | 5 | 20 | 285 | 212 | 50 | 191 | 100 | 149 | 0 | 90 | 13 | 128 | 0 | 95 | 105 | 91 | 0 | 120 | 40 | 110 | 4 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 92 | 25 | 0 | 0 | 0 | 0 | 43 | 38 | 100 | 0 | 34 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 20 | 177 | 0 | 414 | 105 | 20 | 96 | 0 | 113 | 0 | 0 | 113 | 340 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6530 | 2714 | 9244 | 2332 | 471 | 1713 | 422 | 3160 | 540 | 82 | 0 | 416 | 108 | 0 | 0 | 97.06
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 167 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 24 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 30 | 90 | 3 | 21 | 4 | 0 | 0 | 80 | 140 | 280 | 142 | 8 | 132 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 31 | 9 | 101 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 78 | 0 | 177 | 18 | 0 | 10 | 320 | 16 | 11 | 20 | 299 | 258 | 50 | 192 | 100 | 149 | 0 | 90 | 44 | 128 | 0 | 108 | 105 | 91 | 0 | 150 | 54 | 110 | 17 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 92 | 25 | 0 | 0 | 0 | 0 | 43 | 38 | 100 | 0 | 34 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 60 | 194 | 0 | 410 | 105 | 20 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 222 | 0 | 0 | 0 | 0 | 0 |  | 6690 | 2847 | 9537 | 2331 | 471 | 1727 | 508 | 3300 | 599 | 82 | 0 | 418 | 101 | 0 | 0 | 97.04
19:30 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 167 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 12 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 90 | 12 | 21 | 8 | 0 | 0 | 80 | 140 | 280 | 154 | 8 | 131 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 33 | 9 | 102 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 65 | 78 | 0 | 177 | 18 | 0 | 10 | 305 | 16 | 11 | 0 | 300 | 257 | 50 | 191 | 100 | 149 | 0 | 90 | 17 | 128 | 0 | 108 | 105 | 68 | 0 | 120 | 54 | 110 | 0 | 119 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 92 | 26 | 0 | 0 | 0 | 0 | 43 | 38 | 100 | 0 | 34 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 177 | 0 | 410 | 105 | 20 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 222 | 0 | 0 | 0 | 0 | 0 |  | 6544 | 2841 | 9385 | 2323 | 472 | 1717 | 497 | 3176 | 600 | 82 | 0 | 416 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 168 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 12 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 91 | 12 | 21 | 12 | 0 | 0 | 80 | 140 | 275 | 163 | 8 | 132 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 33 | 9 | 103 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 78 | 0 | 177 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 300 | 153 | 50 | 192 | 100 | 149 | 0 | 90 | 17 | 128 | 0 | 109 | 105 | 68 | 0 | 100 | 54 | 110 | 0 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 26 | 0 | 0 | 0 | 0 | 43 | 38 | 100 | 0 | 34 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 179 | 0 | 409 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6430 | 2828 | 9258 | 2342 | 475 | 1709 | 373 | 3153 | 609 | 82 | 0 | 412 | 103 | 0 | 0 | 97.05
21:00 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 170 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 12 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 91 | 17 | 21 | 19 | 0 | 0 | 80 | 140 | 265 | 173 | 8 | 132 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 33 | 9 | 93 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 69 | 78 | 0 | 177 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 298 | 78 | 25 | 192 | 25 | 149 | 0 | 90 | 17 | 130 | 0 | 115 | 105 | 68 | 0 | 45 | 54 | 68 | 0 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 27 | 0 | 0 | 0 | 0 | 43 | 38 | 100 | 0 | 34 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 190 | 0 | 410 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 420 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6172 | 2781 | 8953 | 2354 | 475 | 1725 | 128 | 3067 | 619 | 80 | 0 | 412 | 93 | 0 | 0 | 97.04
22:00 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 170 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 48 | 12 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 25 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 6 | 0 | 93 | 20 | 21 | 19 | 0 | 0 | 80 | 140 | 265 | 176 | 8 | 130 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 93 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 140 | 0 | 69 | 78 | 0 | 177 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 0 | 90 | 17 | 130 | 0 | 85 | 105 | 68 | 0 | 45 | 54 | 68 | 0 | 119 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 25 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 34 | 12 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 189 | 0 | 353 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 420 | 223 | 0 | 0 | 0 | 0 | 0 |  | 5834 | 2666 | 8500 | 2354 | 475 | 1646 | 0 | 3024 | 619 | 80 | 0 | 209 | 93 | 0 | 0 | 97.04
23:00 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 170 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 0 | 12 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 22 | 33 | 0 | 0 | 33 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 20 | 21 | 30 | 0 | 0 | 80 | 140 | 265 | 169 | 8 | 74 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 33 | 9 | 89 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 140 | 0 | 70 | 79 | 0 | 163 | 18 | 0 | 10 | 270 | 22 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 149 | 0 | 90 | 0 | 150 | 0 | 85 | 105 | 68 | 0 | 15 | 54 | 68 | 0 | 25 | 100 | 400 | 54 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 330 | 53 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 400 | 207 | 0 | 0 | 0 | 0 | 0 |  | 5466 | 2442 | 7908 | 2266 | 477 | 1588 | 0 | 2766 | 599 | 73 | 0 | 50 | 89 | 0 | 0 | 97.03
24:00 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 170 |  | 0 | 180 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 33 | 0 | 0 | 36 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 35 | 0 | 0 | 80 | 140 | 265 | 168 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 46 | 21 | 11 | 33 | 9 | 81 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 140 | 0 | 71 | 79 | 0 | 163 | 18 | 0 | 10 | 270 | 22 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 135 | 0 | 90 | 0 | 150 | 0 | 65 | 105 | 34 | 0 | 15 | 54 | 34 | 0 | 25 | 60 | 400 | 54 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 0 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 345 | 53 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 370 | 223 | 0 | 0 | 0 | 0 | 0 |  | 5051 | 2357 | 7408 | 2179 | 477 | 1622 | 0 | 2404 | 569 | 76 | 0 | 0 | 81 | 0 | 0 | 97.03
KWH | 0 | 0 | 5282000 | 0 | 0 | 0 | 0 | 0 | 4500000 |  | 0 | 4422450 | 0 | 0 | 0 | 963555 | 0 | 0 | 0 | 0 | 1586448 | 680160 | 371378 | 0 | 0 | 600864 | 876240 | 1337875 | 885183 | 419292 | 600000 | 198000 | 654900 | 803900 | 621120 | 0 | 933780 | 976000 | 0 | 0 | 54714 | 0 | 0 | 0 | 0 |  | 552960 | 0 | 206086 | 56160 | 2075520 | 92640 | 478368 | 391680 | 0 | 0 | 1953510 | 3583100 | 6860000 | 4319000 | 217454 | 3113570 | 145512 | 144000 | 0 | 1235276 | 0 | 207768 | 831662 | 469584 | 245700 | 698700 | 241270 | 2038080 | 1180800 | 0 | 488232 | 11850 | 1011000 | 0 | 1061400 | 0 | 3633790 | 0 | 1525920 | 1749120 | 0 | 4332330 | 420000 | 0 | 252000 | 7242000 | 475464 | 146064 | 43008 | 5798507 | 726040 | 184189 | 4116000 | 302548 | 2515968 | 130545 | 2091840 | 120480 | 3375563 | 0 | 1689600 | 2319600 | 1326472 | 26881 | 1021200 | 1066167 | 1952900 | 21660 | 1750560 | 1892160 | 9272800 | 2084160 | 256660 | 3660480 | 2610709 | 0 | 436680 | 196241 | 0 | 1114920 |  | 11436363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8960 | 0 | 2215612 | 448700 | 0 | 0 | 0 | 0 | 568639 | 318435 | 824008 | 0 | 436651 | 354708 | 429600 | 0 | 510240 | 0 | 185814 | 0 | 0 | 4870900 | 0 | 0 | 0 | 0 | 0 | 0 | 269242 | 179520 | 4350755 | 0 | 8246545 | 1628160 | 40145 | 1638048 | 0 | 2537836 | 0 | 24452 | 1948224 | 8745200 | 4387145 | 0 | 0 | 29580 | 468720 | 10752 |  | 132559967 | 57112954 | 189672921 | 55671197 | 11436363 | 38711042 | 1475450 | 60501216 | 13616100 | 1909780 | 0 | 3168764 | 2038080 | 1144929 | 0
Fuel Cost | 0 | 0 | 7711720 | 0 | 0 | 0 | 0 | 0 | 4635000 |  | 0 | 4820470.5 | 0 | 0 | 0 | 8151675.3 | 0 | 0 | 0 | 0 | 14468405.76 | 6692774.4 | 3424105.16 | 0 | 0 | 5461853.76 | 6396552 | 10341773.75 | 8727904.38 | 314469 | 450000 | 0 | 0 | 0 | 6006230.4 | 0 | 252120.6 | 263520 | 0 | 0 | 508293.06 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1999034.2 | 536328 | 18057024 | 733708.8 | 602743.68 | 1163289.6 | 0 | 0 | 2871659.7 | 2651494 | 6860000 | 3973480 | 280515.66 | 3580605.5 | 164428.56 | 201600 | 0 | 2112321.96 | 0 | 2098456.8 | 7942372.1 | 596371.68 | 184275 | 1222725 | 180952.5 | 15285600 | 1251648 | 0 | 620054.64 | 188889 | 1658040 | 0 | 1889292 | 0 | 4142520.6 | 0 | 3006062.4 | 3340819.2 | 0 | 7494930.9 | 919800 | 0 | 514080 | 7314420 | 356598 | 111008.64 | 731566.08 | 43836712.92 | 12328159.2 | 3079640.08 | 21403200 | 5058602.56 | 24757125.12 | 1526071.05 | 17048496 | 1307208 | 23797719.15 | 0 | 15409152 | 21920220 | 11553571.12 | 0 | 7720272 | 9286314.57 | 17165991 | 216166.8 | 15002299.2 | 12601785.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65873450.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93900.8 | 0 | 2503641.56 | 695485 | 0 | 0 | 0 | 0 | 5595407.76 | 3235299.6 | 7292470.8 | 0 | 5903521.52 | 3437120.52 | 4162824 | 0 | 979660.8 | 0 | 140661.198 | 0 | 0 | 26400278 | 0 | 0 | 0 | 0 | 0 | 0 | 403863 | 3053635.2 | 5090383.35 | 0 | 8164079.55 | 16997990.4 | 682866.45 | 15545075.52 | 0 | 19693607.36 | 0 | 270194.6 | 14397375.36 | 38391428 | 0 | 0 | 0 | 0 | 0 | 0 |  | 460484290.64 | 249004221.228 | 709488511.868 | 54517753.308 | 65873450.88 | 40657417.87 | 24934469.57 | 410482854.11 | 64791706 | 515640.6 | 0 | 30444464.88 | 15285600 | 1985154.65 | 0
Yesterday Day Peak | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 170 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 48 | 27 | 0 | 0 | 47 | 35 | 55 | 35 | 16 | 25 | 6 | 25 | 22 | 32 | 0 | 45 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 87 | 0 | 21 | 2 | 0 | 0 | 80 | 140 | 300 | 175 | 8 | 138 | 5 | 5 | 0 | 43 | 0 | 0 | 26 | 18 | 8 | 16 | 9 | 98 | 48 | 0 | 20 | 2 | 43 | 0 | 50 | 0 | 130 | 0 | 66 | 78 | 0 | 177 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 285 | 0 | 0 | 173 | 0 | 149 | 19 | 90 | 0 | 138 | 0 | 112 | 105 | 68 | 4 | 50 | 36 | 110 | 0 | 73 | 90 | 390 | 104 | 44 | 162 | 116 | 0 | 17 | 30 | 0 | 55 |  | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 34 | 32 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 168 | 0 | 343 | 70 | 0 | 70 | 0 | 105 | 0 | 4 | 113 | 290 | 150 | 0 | 0 | 4 | 75 | 6 |  | 8149 | DayPeak
Yesterday Evening Peak | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 24 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 51 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 30 | 90 | 3 | 21 | 4 | 0 | 0 | 80 | 140 | 280 | 142 | 8 | 132 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 31 | 9 | 101 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 163 | 0 | 68 | 78 | 0 | 177 | 18 | 0 | 10 | 320 | 16 | 11 | 20 | 299 | 258 | 50 | 192 | 100 | 149 | 0 | 90 | 44 | 128 | 0 | 108 | 105 | 91 | 0 | 150 | 54 | 110 | 17 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 92 | 25 | 0 | 0 | 0 | 0 | 43 | 38 | 100 | 0 | 34 | 32 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 60 | 194 | 0 | 410 | 105 | 20 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 222 | 0 | 0 | 0 | 0 | 0 |  | 9537 | EvPeak
Forecast for Evening | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 40 | 0 | 0 | 51 | 35 | 55 | 35 | 19 | 25 | 10 | 33 | 33 | 51 | 0 | 43 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 70 | 100 | 90 | 20 | 21 | 10 | 0 | 0 | 80 | 150 | 360 | 170 | 8 | 137 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 163 | 55 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 330 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 55 |  | 489 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 35 | 40 | 0 | 91 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 35 | 0 | 0 | 51 | 35 | 55 | 35 | 19 | 25 | 10 | 33 | 33 | 51 | 0 | 43 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 52 | 100 | 90 | 20 | 21 | 5 | 0 | 0 | 80 | 150 | 360 | 170 | 8 | 137 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 55 | 0 | 22 | 1.6 | 42 | 0 | 51 | 0 | 163 | 0 | 72 | 81 | 0 | 190 | 18 | 0 | 10 | 330 | 24 | 11 | 0 | 300 | 300 | 100 | 200 | 50 | 149 | 20 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 55 |  | 489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 0 | 34 | 32 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 200 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6 | 16
Generation at 08:00(Today) | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 9 | 33 | 33 | 0 | 0 | 43 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 50 | 6 | 19 | 0 | 8 | 0 | 0 | 80 | 140 | 365 | 124 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 27 | 19 | 11 | 33 | 9 | 69 | 53 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 70 | 78 | 0 | 163 | 18 | 0 | 10 | 320 | 22 | 7 | 0 | 115 | 0 | 0 | 180 | 0 | 25 | 7 | 90 | 0 | 143 | 0 | 30 | 105 | 43 | 1 | 115 | 54 | 74 | 0 | 35 | 100 | 400 | 104 | 7 | 142 | 116 | 0 | 17 | 7 | 0 | 0 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 395 | 32 | 0 | 70 | 0 | 98 | 0 | 0 | 95 | 320 | 224 | 0 | 0 | 0 | 16 | 0 | 0
199
| Minimum Generation |  | 6018 | 5:00
| Highest Generation |  | 9537 | 19:00
| Day Peak Generation |  | 8149 | 12:00
| Evening Peak Generation |  | 9537 | 19:00
| HVDC Max Flow |  | 477 | 23:00
| HVDC EvPeak Flow |  | 471 | 19:00
| Load factor L.F |  | 82.87%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-01-10
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-01-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8149 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6007 | MW
Evening Peak Generation : |  | 9537 | MW Hour : | 19:00 | Available Max Generation : |  | 11907 | MW
E.P. Demand (at gen end) : |  | 9537 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9600 | MW
Maximum Generation : |  | 9537 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2307 | MW
Total Gen. (MKWH) : |  | 189.6729 | System Load Factor : | 82.87% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -310 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-01-10
Actual : | 97 | Ft.(MSL) , | Rule curve : | 101.29 | Ft.( MSL )
Gas Consumed : | Total = | 744.11 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 95175171.178
: |  | Coal : | 64791706 | Oil : | 465861788.56 | Total : | 625828665.738
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3528.3645 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1196.7973 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1071.7486 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 968.2228 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 875.0751 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 706.147 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 398.7572 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 181.9175 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 544.5969 |  |  | 0 | 0%
Total | 0 |  | 9471.6268 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
2) Ghorasal-3,5,7
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit-1 & 2
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Kaliakoir 230 kV Ckt-2 was under shut down from 09:55 to 16:53 for A/M.
b) Ashuganj-Comilla(N) 230 kV Ckt-2 was under shut down from 08:54 to 16:00 for A/M.
c) Agargaon 230/132 kV T-1 transformer was under shut down from 08:44 to 18:41 for A/M.
d) Bibiyana-Kaliakoir 400 kV Ckt-1 was under shut down from 08:49 to 17:27 for A/M.
e) Bakulia-Modern 132 kV Ckt was under shut down from 08:42 to 14:03 for protection test.
f) Dhamrai-Kaliakoir 132 kV Ckt-1 was under shut down from 08:27 to 18:00 for A/M.
g) Dhamrai 132/33 kV T-1 transformers was under shut down from 08:50 to 16:52 for A/M.
h) Raozan-Hathazari 230 kV Ckt-2 was under shut down from 10:03 to 17:25 for A/M.
i) Jamalpur 132/33 kV T-4 transformer was under shut down from 09:56 to 17:35 for A/M.
j) Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-2 was under shut down from 08:22 to 17:05 for A/M.
k) Jhenaidah(O)-Kustia 132 kV Ckt-1 was under shut down from 08:16 to 17:02 for A/M.
l) Madaripur-Gopalganj(N) 132 kV Ckt-3 was under shut down from 09:36 to 17:19 for D/W.
m) Madaripur-Gopalganj(N) 132 kV Ckt-4 was under shut down from 09:41 to 17:00 for D/W.
n) Mymensingh-Bhaluka 132 kV Ckt-2 was under shut down from 09:19 to 16:51 for A/M.
o) Rajshahi 132/33 kV T-2 transformers was under shut down from 11:49 to 17:26 for A/M.
p) Savar 132/33 kV T-1 transformers was under shut down from 09:40 to 17:02 for A/M.
q) Sylhet-Chatak 132 kV Ckt-2 was under shut down from 08:19 to 14:54 for A/M.
r) Chandpur CCPP was shut down at 23:46.
s) Madanganj-Bashundhara 132 kV Ckt tripped at 23:34 showing Dist. Relay and was switched on at 03:46(10-01-2022).
t) Satkhira 132 kV Bus-B was shut down at 07:28(10-01-2022) for D/W.
u) Satkhira 132 kV Bus CB was shut down at 07:30(10-01-2022) for D/W.
v) Sylhet-Chatak 132 kV Ckt-2 was shut down at 07:42(10-01-2022) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-01-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 251 | 5282000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gasshortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 167 | 4500000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4422450 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 963555
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 24 | 371378 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 419292 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1586448
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 48 | 600864
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 876240 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 680160 | High Voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1337875
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 885183 | Machine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 798000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 654900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 621120
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 299 | 5798507
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 258 | 726040 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 50 | 184189 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 302548
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2515968
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2319600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2084160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3660480
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 196241
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 0 | 55 | 1114920
| Dhaka area Total |  |  |  | 5560 | 2494 | 43706018
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 54714 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 130545
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 3 | 92640 | 33 kV feeder fault
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1909780 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 91 | 1326472 | Engine problem
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 206086 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 56160 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2091840 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 478368
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 4 | 391680
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 2075520 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26881
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 150 | 1021200 | High Voltage
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1066167
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1952900
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1892160
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2610709
| Chattogram area Total |  |  |  | 2382 | 992 | 17383822
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1953510 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 142 | 4319000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 140 | 3583100 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6860000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 145512 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 144000 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1235276
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 3375563 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 207768
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 132 | 3113570 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 44 | 120480 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 469584
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 101 | 2038080
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 31 | 698700
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 831662
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 241270 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 43008 | Low demand
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 21660 | High Voltage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1750560
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 436680 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3034 | 1457 | 32052137
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 50 | 1180800 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 488232
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11850
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 4116000 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 108 | 1689600 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 256660
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 552960
| Mymensingh Area Total |  |  |  | 622 | 392 | 8296102
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1011000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3633790
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 1061400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 146064
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1525920
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1749120
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 177 | 4332330 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 420000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 475464 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7242000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252000
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9272800
| Sylhet Area Total |  |  |  | 2377 | 1355 | 31121888
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 471 | 11436363
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 6 | 8960
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 60 | 179520 | Low demand
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1628160
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 0 | 0 | 468720 | On test
| Khulna Area Total |  |  |  | 2129 | 642 | 13721723
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | High Voltage
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 448700 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 92 | 2215612 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 269242 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 400 | 8745200
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 4387145
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 750 | 16065899
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 568639
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 38 | 318435 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 436651 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 354708 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 194 | 4350755 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 410 | 8246545 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 510240
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 185814
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 429600 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 824008
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 20 | 40145 | Low demand
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1638048
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1948224
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29580
| Rajshahi Area Total |  |  |  | 2179 | 1143 | 19881392
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4870900
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2537836
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24452
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 10752 | On test
| Rangpur Area Total |  |  |  | 605 | 312 | 7443940
| Total |  |  |  | 20934 | 9537 | 189672921
| Eastern Grid Total |  |  |  | 13975 | 6690 | 132559967
| Western Grid Total |  |  |  | 6959 | 2847 | 57112954
| National Grid Total |  |  |  | 20934 | 9537 | 189672921
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-01-09
(a) ENTIRE EASTERN GRID : |  | 6487 | MW | (b) ENTIRE WESTERN GRID : |  | 2920 | MW
i) Dhaka area |  | 3552 | MW | i) Khulna area |  | 1087 | MW
ii) Chittagong area |  | 1028 | MW | ii) Rajshahi area |  | 950 | MW
iii) Comilla area |  | 759 | MW | iii) Barisal area |  | 249 | MW
iv) Mymensingh area |  | 808 | MW | iv) Rangpur area |  | 634 | MW
v) Sylhet area |  | 340 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9407 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 89 | 14:00 | Tangail | 145 | 18:00 | Noapara | 36 | 18:30
Munsiganj | 59 | 20:00 | Mymensing | 145 | 18:30 | Jessore | 81 | 18:30
Sonargaon | 51 | 12:00 | Kishoreganj | 100 | 20:00 | Benapol | 38 | 18:30
Shyampur | 162 | 12:00 | Netrokona | 103 | 18:00 | Jhenida(Old) | 85 | 18:30
Bhulta | 147 | 1:00 | Jamalpur | 107 | 19:00 | Bottail | 98 | 18:30
Madanganj | 35 | 18:30 | Sherpur | 112 | 18:00 | G.K Project | 36 | 18:30
Shitalakhya | 90 | 16:00 | Srimongal | 33 | 19:30 | Faridpur | 100 | 20:20
Rahim steel | 21 | 0:00 | Shahjibazar | 79 | 18:30 | Rajbari | 40 | 18:30
Matuail | 51 | 15:00 | Fenchuganj | 30 | 17:00 | Madaripur | 64 | 20:00
Ghorasal | 60 | 19:00 | Kulawara | 26 | 18:00 | Sariatpur | 42 | 20:00
Narsingdi | 128 | 18:30 | Sylhet | 93 | 18:30 | Gopalganj | 69 | 18:30
Haripur (SBU) | 99 | 13:00 | Chatak | 19 | 20:00 | Bagerhat | 80 | 18:30
Sreenagar | 28 | 20:00 | Sunamganj | 31 | 20:00 | Mongla | 36 | 18:30
Ullon | 38 | 21:00 | Biani Bazar | 39 | 19:00 | Satkhira | 18 | 18:30
Hasnabad | 65 | 11:00 | Comilla (S) | 108 | 18:00 | Gallamari | 46 | 13:00
Magbazar | 71 | 13:00 | Comilla(N) | 85 | 18:30 | Magura | 40 | 18:00
Maniknagar | 47 | 13:00 | Chandpur | 47 | 19:30 | Norail | 33 | 18:30
Bangabhaban | 8 | 13:00 | Feni | 79 | 18:00 | Chuadanga | 65 | 18:30
Motijheel | 20 | 13:00 | Chowmuhani | 132 | 19:00 | Barisal(N) | 28 | 21:00
Narinda | 37 | 18:30 | Ashuganj | 20 | 12:00 | Barisal (S) | 78 | 19:30
Kazla | 63 | 13:00 | Daudkandi | 90 | 20:00 | Patuakhali | 78 | 18:30
Dhanmondi | 128 | 13:00 | B.Baria | 98 | 19:30 | Bhandaria | 38 | 20:00
Lalbag | 72 | 13:00 | Ramganj | 52 | 18:00 | Borguna | 12 | 19:30
Madartek | 43 | 21:00 | Chaddagram | 29 | 18:00 | Borhan Uddin | 28 | 20:00
Dhaka University | 21 | 14:00 | PHP | 9 | 9:00 | Ishurdi | 50 | 18:30
Aftabnagar | 13 | 14:00 | Kochua | 36 | 20:00 | Ruppur Paromanobik | 4 | 17:00
Fatullah | 52 | 12:00 | Madunaghat | 38 | 18:00 | Natore | 91 | 18:30
Nawabganj | 32 | 20:00 | Hathazari | 69 | 18:00 | Bogra | 108 | 18:30
Keraniganj | 48 | 13:00 | Khulshi | 139 | 15:00 | Noagaon | 86 | 20:00
Banani | 43 | 14:00 | Halishahar | 61 | 14:00 | Rajshahi | 94 | 20:00
Mirpur | 80 | 18:30 | Baraulia | 142 | 9:00 | Rajshahi New | 20 | 18:30
Kalyanpur | 63 | 18:00 | Sikalbaha | 20 | 1:00 | C.Nawabganj | 43 | 8:00
Gulshan | 78 | 3:00 | Dohazari | 78 | 18:00 | Amnura | 42 | 19:00
Uttara | 39 | 18:30 | Cox'sbazar | 81 | 22:00 | Pabna | 75 | 18:30
Uttara New | 22 | 18:30 | Chandraghona | 28 | 17:00 | Shahjadpur | 74 | 18:30
Kamrangirchar | 64 | 13:00 | Kaptai | 3.5 | 18:00 | Serajganj | 68 | 19:00
Savar | 137 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 62 | 20:00
Bhasantec | 81 | 18:00 | Bakulia | 88 | 18:00 | Joypurhat | 46 | 20:00
Agargaon | 49 | 13:00 | Julda | 24 | 9:00 | Sherpur(Bogura) | 48 | 18:00
Satmosjid | 68 | 13:00 | TK chemical | 14.4 | 19:00 | Mohastangor | 50 | 18:00
Old Tongi | 102 | 11:00 | Modern Steel | 0 | 1:00 | Bhangura | 20 | 18:30
Kabirpur | 188 | 15:00 | Shahmirpur | 34 | 16:00 | Rangpur | 94 | 18:00
Bashundara |  |  | Khagrachhari | 22 | 6:00 | Lalmonirhat | 29 | 18:30
Manikgong | 80 | 19:30 | Matarbari | 26 | 17:00 | Saidpur | 82 | 18:30
Joydevpur | 134 | 15:00 | Baroiar Hat | 34 | 18:00 | Purbasadipur | 90 | 19:00
New Tongi | 69 | 12:00 | Rangamati | 10 | 18:00 | Thakurgaon | 65 | 19:00
Kodda | 231 | 18:00 | Abul Khair 230 | 144 | 5:00 | Palashbari | 73 | 19:00
Dhamrai | 68 | 8:00 | BSRM | 162 | 12:00 | Barapukuria | 43 | 19:00
Rajendrapur | 94 | 18:30 | GPH Ispat | 23 | 23:00 | Panchagar | 44 | 18:30
Purbachal | 12 | 21:00 | Agrabad | 58 | 18:00 | Joldhaka | 44 | 18:00
Tongi Millgate | 38 | 18:30 | Goalpara | 24 | 13:00 | Kurigram | 47 | 18:00
Valuka | 106 | 18:00 | Central S/S | 56 | 18:30 | Mithapukur | 42 | 18:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-01-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 417 | 6:00 | 408 | 13:00 | Kaliakoir | 416 | 0.41667 | 397 | 0.5
| Bheramara | 408 | 1:00 | 397 | 18:00 | Bhulta | 401 | 0.25 | 384 | 0.625
| Ashuganj(N) | 404 | 8:00 | 388 | 15:00 | Gopalganj | 417 | 0.625 | 402 | 0.75
| Payra | 415 | 6:00 | 407 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 248 | 1:00 | 240 | 15:00 | Hathazari | 243 | 19:00 | 232 | 12:00
| Ishurdi | 244 | 1:00 | 232 | 8:00 | Megnaghat | 249 | 23:00 | 242 | 12:00
| Ashuganj | 250 | 1:00 | 243 | 15:00 | Fenchuganj | 249 | 4:00 | 242 | 12:00
| Serajganj | 242 | 1:00 | 234 | 12:00 | Siddhirganj | 243 | 1:00 | 233 | 12:00
| Baghabari | 243 | 3:00 | 234 | 12:00 | Maniknagar | 241 | 1:00 | 231 | 15:00
| Barapukuria | 238 | 6:00 | 230 | 18:00 | Agargaon | 244 | 4:00 | 233 | 12:00
| Bogra | 240 | 3:00 | 232 | 18:30 | Barisal | 244 | 22:00 | 236 | 12:00
| Rajshahi | 242 | 3:00 | 231 | 8:00 | Bhola 225 MW | 248 | 8:00 | 242 | 21:00
| Khulna South | 247 | 4:00 | 232 | 18:00 | AKSML | 242 | 22:00 | 231 | 4:00
| Rampura | 240 | 4:00 | 230 | 12:00 | BSRM | 243 | 22:00 | 231 | 3:00
| Haripur | 242 | 2:00 | 232 | 12:00 | Bibiyana | 247 | 1:00 | 240 | 13:00
| Hasnabad | 243 | 1:00 | 233 | 15:00 | Bhulta | 243 | 1:00 | 233 | 12:00
| Shyampur | 242 | 6:00 | 231 | 12:00 | Ashuganj (S) | 246 | 1:00 | 239 | 15:00
| Aminbazar | 245 | 1:00 | 234 | 2:00 | Kaliakoir | 243 | 1:00 | 232 | 12:00
| Tongi | 240 | 21:00 | 230 | 11:00 | GPH | 244 | 22:00 | 231 | 3:00
| Comilla (N) | 243 | 1:00 | 233 | 12:00 | Jhenaidah | 239 | 1:00 | 231 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 1:00 | 132 | 12:00 | Kachua | 142 | 0.083333 | 138 | 0.5
| Munsiganj | 140 | 22:00 | 133 | 15:00 | Madanhat | 141 | 0.20833 | 136 | 0.45833
| Sonargaon | 139 | 20:00 | 133 | 12:00 | Hathazari | 144 | 0.79167 | 137 | 0.33333
| Shyampur | 136 | 8:00 | 129 | 12:00 | Khulshi | 140 | 0.041667 | 134 | 0.45833
| Bhulta | 134 | 1:00 | 127 | 12:00 | Halishahar | 141 | 0.25 | 134 | 0.5
| Madanganj | 139 | 23:00 | 133 | 12:00 | Baraulia | 142 | 0.20833 | 136 | 0.5
| Shitalakhya | 140 | 22:00 | 133 | 15:00 | Sikalbaha | 142 | 0.29167 | 136 | 0.5
| Rahim steal | 138 | 2:00 | 132 | 12:00 | Dohazari | 138 | 0.58333 | 133 | 0.5
| Matuail | 138 | 1:00 | 132 | 12:00 | Cox'sbazar | 128 | 0.29167 | 121 | 0.8125
| Ghorasal | 145 | 1:00 | 140 | 13:00 | Chandraghona | 143 | 0.79167 | 136 | 0.5
| Narsinghdi | 137 | 8:00 | 131 | 12:00 | Kaptai | 140 | 0.041667 | 137 | 0.33333
| Haripur (SBU) | 138 | 22:00 | 132 | 12:00 | A. Khaer Stl. | 141 | 0.29167 | 135 | 0.5
| Sreenagar | 138 | 1:00 | 131 | 12:00 | Bakulia | 142 | 0.70833 | 135 | 0.5
| Ullon | 138 | 4:00 | 130 | 12:00 | Julda | 140 | 0.25 | 135 | 0.083333
| Hasnabad | 139 | 23:00 | 132 | 15:00 | TK Chemical | 142 | 0.79167 | 136 | 0.5
| Magbazar | 137 | 6:00 | 130 | 15:00 | Modern Steel | 142 | 0.79167 | 135 | 0.5
| Maniknagar | 137 | 0:00 | 0 | 0:00 | Shahmirpur | 141 | 0.25 | 135 | 0.5
| Bangabhaban | 137 | 0:00 | 130 | 12:00 | Khagrachhari | 141 | 0.25 | 135 | 0.5
| Motijheel | 137 | 1:00 | 130 | 12:00 | Matarbari | 131 | 0.77083 | 128 | 0.70833
| Narinda | 137 | 1:00 | 130 | 12:00 | Baroiar Hat | 141 | 17:00 | 136 | 12:00
| Kazla | 137 | 2:00 | 129 | 13:00 | Rangamati | 142 | 22:00 | 136 | 12:00
| Dhanmondi | 140 | 4:00 | 132 | 12:00 | Agrabad | 141 | 18:30 | 134 | 0.5
| Lalbag | 138 | 8:00 | 131 | 12:00 | Goalpara S/S | 140 | 1:00 | 135 | 0.33333
| Madartek | 137 | 0:00 | 130 | 12:00 | Khulna Central S/S | 139 | 1:00 | 132 | 0.29167
| Dhaka University | 138 | 8:00 | 130 | 12:00 | Noapara | 140 | 3:00 | 133 | 0.5
| Aftabnagar | 138 | 4:00 | 131 | 14:00 | Jessore | 138 | 0.041667 | 131 | 0.5
| Fatullah | 137 | 21:00 | 130 | 12:00 | Benapol | 140 | 3:00 | 130 | 0.33333
| Nawabganj | 138 | 1:00 | 131 | 12:00 | Jhenida(Old) | 139 | 0.041667 | 131 | 0.77083
| Keraniganj | 138 | 8:00 | 130 | 12:00 | Bottail | 139 | 0.125 | 131 | 0.77083
| Banani | 138 | 3:00 | 130 | 12:00 | G.K Project | 141 | 0.041667 | 135 | 0.54167
| Mirpur | 137 | 2:00 | 13 | 14:00 | Faridpur | 140 | 0.41667 | 133 | 0.75
| Kalyanpur | 137 | 1:00 | 130 | 12:00 | Rajbari | 140 | 0.41667 | 132 | 0.75
| Gulshan | 137 | 3:00 | 130 | 12:00 | Madaripur | 143 | 6:00 | 135 | 0.5
| Uttara | 138 | 0:00 | 131 | 15:00 | Shariyatpur S/S | 142 | 0.041667 | 135 | 0.625
| Uttara New | 138 | 4:00 | 129 | 14:00 | Gopalganj | 143 | 10:00 | 135 | 0.77083
| Kamrangirchar | 138 | 0:00 | 131 | 12:00 | Bagerhat | 131 | 7:00 | 140 | 0.91667
| Savar | 137 | 23:00 | 130 | 12:00 | Mongla | 130 | 7:00 | 139 | 22:00
| Bhasantec | 135 | 1:00 | 126 | 15:00 | Satkhira | 138 | 0.041667 | 131 | 18:00
| Agargaon | 136 | 8:00 | 127 | 15:00 | Gallamari | 140 | 2:00 | 134 | 0.75
| Satmosjid | 136 | 8:00 | 127 | 12:00 | Magura | 140 | 0.041667 | 131 | 0.77083
| Old Tongi | 138 | 21:00 | 133 | 12:00 | Narail | 140 | 4:00 | 130 | 0.5
| Kabirpur | 137 | 23:00 | 130 | 12:00 | Chuadanga | 138 | 4:00 | 128 | 0.75
| Bashundara | 138 | 8:00 | 132 | 12:00 | Barisal(N) | 143 | 3:00 | 136 | 18:00
| Manikgong | 136 | 1:00 | 129 | 11:00 | Barisal (S) | 142 | 0.125 | 135 | 0.77083
| Joydevpur | 144 | 1:00 | 137 | 15:00 | Patuakhali(S) | 141 | 0.16667 | 132 | 0.875
| New Tongi | 140 | 5:00 | 132 | 12:00 | Bhandaria | 139 | 0.41667 | 130 | 0.29167
| Kodda | 141 | 10:00 | 132 | 12:00 | Borguna | 143 | 3:00 | 134 | 18:30
| Dhamrai | 138 | 23:00 | 131 | 15:00 | Jhenaidah(New) | 138 | 1:00 | 131 | 18:30
| Rajendrapur | 139 | 14:00 | 132 | 18:30 | Ishurdi | 141 | 6:00 | 134 | 10:00
| Purbachal | 139 | 1:00 | 130 | 12:00 | Ruppur Paromanobik | 140 | 3:00 | 136 | 12:00
| Tongi Millgate | 139 | 8:00 | 131 | 13:00 | Natore | 140 | 3:00 | 135 | 9:00
| Valuka | 131 | 1:00 | 118 | 15:00 | Bogra | 142 | 24:00 | 136 | 18:00
| Tangail | 136 | 1:00 | 130 | 13:00 | Noagaon | 137 | 2:00 | 130 | 18:30
| Mymensing | 133 | 1:00 | 124 | 18:30 | Rajshahi | 138 | 4:00 | 133 | 12:00
| Kishorganj | 134 | 1:00 | 127 | 18:30 | Rajshahi New | 138 | 3:00 | 132 | 12:00
| Netrokona | 132 | 1:00 | 122 | 18:30 | C.Nawabganj | 138 | 4:00 | 132 | 12:00
| Jamalpur | 140 | 11:00 | 134 | 18:30 | Amnura | 138 | 5:00 | 129 | 12:00
| Sherpur | 138 | 10:00 | 131 | 6:00 | Pabna | 141 | 4:00 | 134 | 12:00
| Srimongal | 140 | 23:00 | 136 | 16:00 | Shahjadpur | 145 | 3:00 | 140 | 15:00
| Shahjibazar | 137 | 5:00 | 134 | 12:00 | Serajganj | 142 | 3:00 | 135 | 12:00
| Fenchuganj | 139 | 23:00 | 136 | 2:00 | Niyamatpur | 134 | 4:00 | 128 | 18:00
| Khulawara | 138 | 4:00 | 135 | 12:00 | Joypurhat | 139 | 23:00 | 130 | 12:00
| Sylhet | 135 | 1:00 | 133 | 13:00 | Sherpur(Bogura) | 141 | 3:00 | 136 | 12:00
| Chatak | 137 | 6:00 | 134 | 11:00 | Mohastangor | 141 | 1:00 | 134 | 18:00
| Sunamganj | 134 | 1:00 | 131 | 13:00 | Bangura | 143 | 3:00 | 138 | 12:00
| Biani Bazar | 139 | 6:00 | 133 | 13:00 | Rangpur | 138 | 4:00 | 128 | 18:30
| Comilla(s) | 131 | 2:00 | 127 | 9:00 | Lalmonirhat | 137 | 23:00 | 128 | 18:30
| Comilla(n) | 146 | 6:00 | 140 | 12:00 | Saidpur | 135 | 4:00 | 126 | 18;30
| Chandpur | 142 | 1:00 | 141 | 15:00 | Purbasadipur | 134 | 3:00 | 121 | 18:30
| Feni | 142 | 6:00 | 137 | 2:00 | Thakurgaon | 133 | 4:00 | 119 | 18:00
| Chowmuhani | 143 | 22:00 | 133 | 5:00 | Palashbari | 138 | 23:00 | 130 | 18:30
| Ashuganj | 140 | 1:00 | 138 | 12:00 | Barapukuria | 138 | 0.25 | 130 | 0.75
| Daudkandi | 141 | 8:00 | 136 | 15:00 | Panchagar | 134 | 0.20833 | 121 | 0.77083
| B.Baria | 136 | 4:00 | 132 | 15:00 | Joldhaka | 135 | 0.25 | 122 | 0.77083
| Ramganj | 143 | 19:00 | 134 | 11:00 | Kurigram | 136 | 0.16667 | 126 | 0.75
| Chaddagram | 144 | 19:00 | 139 | 11:00 | Mithapukur | 139 | 5:00 | 131 | 18:30
| PHP | 142 | 8:00 | 136 | 11:00

## L-Curve
Date | 2022-01-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 98 | 5051 | 2357 | 7408 |  |  |  | QF-LDC-11
0:30 | 77.5 | 4949 | 2187.5 | 7136.5 | Date: | 2022-01-09
1:00 | 57 | 4847 | 2018 | 6865
1:30 | 58.5 | 4661 | 2007 | 6668
2:00 | 60 | 4475 | 1996 | 6471
2:30 | 51 | 4414 | 1949.5 | 6363.5 | [5 empty] | Gen. at Eve. Peak | 9537 | 9537 MW (19:00 )
3:00 | 42 | 4353 | 1903 | 6256 | [6 empty] | 19:00
3:30 | 65 | 4258.5 | 1899.5 | 6158 | [5 empty] | Gen. at Day Peak | 8149 | 8149 MW (12:00 )
4:00 | 88 | 4164 | 1896 | 6060 | [6 empty] | 12:00
4:30 | 87 | 4147.5 | 1891.5 | 6039 | [5 empty] | Highest Generation | 9537
5:00 | 86 | 4131 | 1887 | 6018 | [6 empty] | 19:00
5:30 | 45 | 4226 | 1894 | 6120
6:00 | 4 | 4321 | 1901 | 6222
6:30 | 98 | 4505.5 | 1942 | 6447.5
7:00 | 192 | 4690 | 1983 | 6673
7:30 | 251 | 4963.5 | 2047.5 | 7011
8:00 | 310 | 5237 | 2112 | 7349
8:30 | 192 | 5426.5 | 2203 | 7629.5
9:00 | 74 | 5616 | 2294 | 7910
9:30 | 50 | 5655.5 | 2302 | 7957.5
10:00 | 26 | 5695 | 2310 | 8005
10:30 | 81 | 5622.5 | 2297 | 7919.5
11:00 | 136 | 5550 | 2284 | 7834
11:30 | 110 | 5674.5 | 2317 | 7991.5
12:00 | 84 | 5799 | 2350 | 8149
12:30 | 104 | 5857 | 2449.5 | 8306.5
13:00 | 124 | 5915 | 2549 | 8464
13:30 | 159 | 5766.5 | 2466.5 | 8233
14:00 | 194 | 5618 | 2384 | 8002
14:30 | 219 | 5607.5 | 2323 | 7930.5
15:00 | 244 | 5597 | 2262 | 7859
15:30 | 244 | 5547 | 2239.5 | 7786.5
16:00 | 244 | 5497 | 2217 | 7714
16:30 | 176 | 5585 | 2202.5 | 7787.5
17:00 | 108 | 5673 | 2188 | 7861
17:30 | 119 | 6101.5 | 2451 | 8552.5
18:00 | 130 | 6530 | 2714 | 9244
18:30 | 166 | 6610 | 2780.5 | 9390.5
19:00 | 202 | 6690 | 2847 | 9537
19:30 | 166 | 6544 | 2841 | 9385
20:00 | 168 | 6430 | 2828 | 9258 |  |  |  | Executive Engineer
20:30 | 140 | 6301 | 2804.5 | 9105.5 |  |  |  | Network Operation Division
21:00 | 112 | 6172 | 2781 | 8953
21:30 | 68 | 6003 | 2723.5 | 8726.5
22:00 | 24 | 5834 | 2666 | 8500 |  |  |  |  | Page 6 of 7
22:30 | 16 | 5650 | 2554 | 8204
23:00 | 8 | 5466 | 2442 | 7908
23:30 | 53 | 5258.5 | 2399.5 | 7658
24:00 | 98 | 5051 | 2357 | 7408
9537 MW (19:00 )
8149 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-01-09 |  | Energy |  | 189672921
[13 empty] | 2022-01-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2179 | 477 | 1622 | 0 | 2404 | 569 | 76 | 0 | 0 | 81 | 0 | 0
0:30 | 2224 | 474.5 | 1600.5 | 0 | 2154.5 | 529 | 78 | 0 | 0 | 76 | 0 | 0 | Date: | 2022-01-09
1:00 | 2269 | 472 | 1579 | 0 | 1905 | 489 | 80 | 0 | 0 | 71 | 0 | 0
1:30 | 2269.5 | 471 | 1585.5 | 0 | 1705.5 | 489 | 78 | 0 | 0 | 69.5 | 0 | 0 | [8 empty] | Total Energy | 189.6729 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 2270 | 470 | 1592 | 0 | 1506 | 489 | 76 | 0 | 0 | 68 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2275 | 470 | 1590 | 0 | 1394 | 489 | 79 | 0 | 0 | 66.5 | 0 | 0 | [8 empty] | Energy Requirement | 189.6729
3:00 | 2280 | 470 | 1588 | 0 | 1282 | 489 | 82 | 0 | 0 | 65 | 0 | 0
3:30 | 2281.5 | 470 | 1560 | 0 | 1209.5 | 489 | 83.5 | 0 | 0 | 64.5 | 0 | 0 | [6 empty] | Shortage
4:00 | 2283 | 470 | 1532 | 0 | 1137 | 489 | 85 | 0 | 0 | 64 | 0 | 0
4:30 | 2275 | 470 | 1520 | 0 | 1138 | 489 | 82.5 | 0 | 0 | 64.5 | 0 | 0
5:00 | 2267 | 470 | 1508 | 0 | 1139 | 489 | 80 | 0 | 0 | 65 | 0 | 0
5:30 | 2285 | 470 | 1529 | 0 | 1199 | 489 | 80.5 | 0 | 0 | 67.5 | 0 | 0
6:00 | 2303 | 470 | 1550 | 0 | 1259 | 489 | 81 | 0 | 0 | 70 | 0 | 0
6:30 | 2318.5 | 470 | 1566.5 | 0 | 1449 | 489 | 82.5 | 0 | 0 | 70.5 | 1.5 | 0 |  |  |  |  | Coal
7:00 | 2334 | 470 | 1583 | 0 | 1639 | 489 | 84 | 0 | 0 | 71 | 3 | 0
7:30 | 2332.5 | 470 | 1565 | 0 | 1979 | 489 | 80 | 0 | 0 | 71 | 24.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2331 | 470 | 1547 | 0 | 2319 | 489 | 76 | 0 | 0 | 71 | 46 | 0
8:30 | 2316.5 | 469.5 | 1572 | 0 | 2556.5 | 489 | 74.5 | 0 | 0 | 78 | 73.5 | 0
9:00 | 2302 | 469 | 1597 | 0 | 2794 | 489 | 73 | 0 | 0 | 85 | 101 | 0
9:30 | 2304 | 469 | 1540.5 | 0 | 2823.5 | 484 | 73 | 0 | 52.5 | 84.5 | 126.5 | 0
10:00 | 2306 | 469 | 1484 | 0 | 2853 | 479 | 73 | 0 | 105 | 84 | 152 | 0
10:30 | 2255.5 | 469 | 1467.5 | 0 | 2814 | 479 | 73 | 0 | 109.5 | 88.5 | 163.5 | 0
11:00 | 2205 | 469 | 1451 | 0 | 2775 | 479 | 73 | 0 | 114 | 93 | 175 | 0
11:30 | 2249.5 | 469 | 1484 | 0 | 2827.5 | 484 | 79 | 0 | 124.5 | 95.5 | 178.5 | 0
12:00 | 2294 | 469 | 1517 | 0 | 2880 | 489 | 85 | 0 | 135 | 98 | 182 | 0
12:30 | 2297.5 | 469 | 1573.5 | 0 | 2958 | 509 | 79.5 | 0 | 143.5 | 98 | 178.5 | 0
13:00 | 2301 | 469 | 1630 | 0 | 3036 | 529 | 74 | 0 | 152 | 98 | 175 | 0
13:30 | 2301 | 469 | 1630 | 0 | 3036 | 529 | 74 | 0 | 152 | 98 | 175 | 0
14:00 | 2301 | 469 | 1630 | 0 | 3036 | 529 | 74 | 0 | 152 | 98 | 175 | 0
14:30 | 2237 | 470 | 1605 | 0 | 2842 | 524 | 80 | 0 | 168.5 | 95.5 | 139.5 | 0
15:00 | 2173 | 471 | 1580 | 0 | 2648 | 519 | 86 | 0 | 185 | 93 | 104 | 0
15:30 | 2164 | 471 | 1579.5 | 0 | 2619 | 519 | 82 | 0 | 184.5 | 91 | 76.5 | 0
16:00 | 2155 | 471 | 1579 | 0 | 2590 | 519 | 78 | 0 | 184 | 89 | 49 | 0
16:30 | 2184 | 471 | 1544.5 | 0 | 2668 | 519 | 82 | 0 | 200 | 90.5 | 28.5 | 0
17:00 | 2213 | 471 | 1510 | 0 | 2746 | 519 | 86 | 0 | 216 | 92 | 8 | 0
17:30 | 2272.5 | 471 | 1611.5 | 211 | 2953 | 529.5 | 84 | 0 | 316 | 100 | 4 | 0
18:00 | 2332 | 471 | 1713 | 422 | 3160 | 540 | 82 | 0 | 416 | 108 | 0 | 0
18:30 | 2331.5 | 471 | 1720 | 465 | 3230 | 569.5 | 82 | 0 | 417 | 104.5 | 0 | 0
19:00 | 2331 | 471 | 1727 | 508 | 3300 | 599 | 82 | 0 | 418 | 101 | 0 | 0
19:30 | 2323 | 472 | 1717 | 497 | 3176 | 600 | 82 | 0 | 416 | 102 | 0 | 0
20:00 | 2342 | 475 | 1709 | 373 | 3153 | 609 | 82 | 0 | 412 | 103 | 0 | 0
20:30 | 2348 | 475 | 1717 | 250.5 | 3110 | 614 | 81 | 0 | 412 | 98 | 0 | 0
21:00 | 2354 | 475 | 1725 | 128 | 3067 | 619 | 80 | 0 | 412 | 93 | 0 | 0
21:30 | 2354 | 475 | 1685.5 | 64 | 3045.5 | 619 | 80 | 0 | 310.5 | 93 | 0 | 0
22:00 | 2354 | 475 | 1646 | 0 | 3024 | 619 | 80 | 0 | 209 | 93 | 0 | 0
22:30 | 2310 | 476 | 1617 | 0 | 2895 | 609 | 76.5 | 0 | 129.5 | 91 | 0 | 0
23:00 | 2266 | 477 | 1588 | 0 | 2766 | 599 | 73 | 0 | 50 | 89 | 0 | 0
23:30 | 2222.5 | 477 | 1605 | 0 | 2585 | 584 | 74.5 | 0 | 25 | 85 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 28.6° C
24:00 | 2179 | 477 | 1622 | 0 | 2404 | 569 | 76 | 0 | 0 | 81 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-01-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 36 | 42 | 45 | 40 | 41 | 44 | 36 | 33 | 33 | 33 | 45 | 34 | 33 | 46 | 38 | 46 | 42 |  | 42 | 42 | 42 | 40 | 40 | 33 | 36 | 933780
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 976000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 1 | 8 | 8 | 8 | 8 | 8 | [12 empty] | 54714
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 9 | 13 | 17 | 19 | 19 | 18 | 16 | 13 | 8 | 1 | [9 empty] | 130545
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 51 | 6 |  |  | 206086
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [5 empty] | 7 | 17 | 39 | 68 | 68 | 68 | 68 | 77 | 91 | 91 | 91 | 91 | 91 |  | 91 | 68 | 68 | 68 | 68 | 68 | 34 | 1326472
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 20 |  | 20 | [6 empty] | 43008
14 | Titas 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 |  |  |  | 207768
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 110 | 110 | 80 | 80 | 80 | 125 | 225 | 292 | 295 | 281 | 285 | 285 | 295 | 288 | 280 | 280 | 285 |  | 299 | 300 | 300 | 298 | 300 | 300 | 300 | 5798507
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 180 | 180 | 180 | 180 | 180 | 240 | 240 | 245 | 240 | 241 | 240 | 240 | 240 | 240 | 160 | 160 | 156 | 249 |  | 251 | 250 | 251 | 251 | 251 | 251 | 240 | 5282000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1953510
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 145512
33 | Ashuganj 225 MW CCPP | 181 | 180 | 185 | 193 | 199 | 195 | 198 | 188 | 167 | 178 | 182 | 175 | 158 | 170 | 169 | 159 | 155 | 152 |  | 142 | 154 | 163 | 173 | 176 | 169 | 168 | 4319000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 305 | 290 | 275 | 310 | 280 | 280 | 265 | 270 | 300 | 270 | 270 | 305 | 270 | 270 | 300 |  | 280 | 280 | 275 | 265 | 265 | 265 | 265 | 6860000
| Ashuganj 450 MW CCPP(North) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3583100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 144000
36 | Chandpur 150 MW CCPP | 136 | 138 | 138 | 138 | 138 | 138 | 138 | 136 | 136 | 136 | 138 | 138 | 136 | 130 | 130 | 132 | 130 | 132 |  | 132 | 131 | 132 | 132 | 130 | 74 | 0 | 3113570
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4422450
41 | Haripur 360MW CCPP(HPL) | 201 | 201 | 201 | 212 | 212 | 222 | 222 | 200 | 201 | 196 | 182 | 170 | 173 | 171 | 173 | 174 | 168 | 172 |  | 167 | 167 | 168 | 170 | 170 | 170 | 170 | 4500000
42 | RPCL 210MW CCPP | 51 | 53 | 53 | 53 | 53 | 53 | 51 | 53 | 51 | 51 | 50 | 48 | 48 | 43 | 45 | 49 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 1180800
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 9 | 22 | 35 | 41 | 44 | 40 | 34 | 22 | 10 | 1 | [9 empty] | 256660
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 1011000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 72 | 72 | 71 | 40 | 40 | 40 | 40 | 72 | 70 | 70 | 40 | 66 | 66 | 66 | 64 | 65 | 68 | 68 |  | 68 | 65 | 68 | 69 | 69 | 70 | 71 | 1525920
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 76 | 40 | 40 | 40 | 76 | 76 | 76 | 76 | 76 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 79 | 79 | 1749120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 178 | 178 | 177 |  | 177 | 177 | 177 | 177 | 177 | 163 | 163 | 4332330
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 420000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252000
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 146064
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 48 | 48 | 48 | 11 | 11 | 11 | 45 | 45 | 45 | 45 | 50 | 51 | 48 | 48 | 48 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1061400
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 24 | 24 | 24 | 22 | 22 | 475464
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 295 | 285 | 300 | 310 | 300 | 300 | 290 | 290 | 270 | 300 | 300 | 275 | 300 | 310 | 305 | 300 |  | 320 | 305 | 295 | 300 | 300 | 270 | 270 | 7242000
| Bibiyana South 400 MW | 401 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 340 | 390 | 400 | 340 | 340 | 340 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9272800
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 885183
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 24 | 24 | 24 | 24 | 25 | 24 | 23 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 552960
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 478368
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 419292
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 488232
63 | Impoprt (Tripura) | 71 | 68 | 65 | 64 | 65 | 70 | 71 | 71 | 85 | 84 | 93 | 98 | 98 | 99 | 93 | 89 | 92 | 108 |  | 101 | 102 | 103 | 93 | 93 | 89 | 81 | 2038080
64 | Malancha, Ctg. EPZ (United) | 25 | 25 | 35 | 37 | 39 | 39 | 34 | 4 | 2 | 2 | 2 | 2 | 4 | 4 | 2 | 2 | 2 | 3 |  | 4 | 8 | 12 | 19 | 19 | 30 | 35 | 391680
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 469584
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 22 | 20 | 16 | 16 | 16 | 16 | 33 | 33 | 28 |  | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 698700
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 241270
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 9 | 9 | 9 | 6 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 198000
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 22 | 20 | 654900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 20 | 22 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [17 empty] | 4 |  | 17 | [6 empty] | 21660
| Chowmuhani 113 MW | 35 | 8 | 8 | 8 | 8 | 21 | 46 | 46 | 46 | 46 | 46 | 73 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 119 | 113 | 113 | 119 | 25 | 25 | 1750560
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 126 | 126 | 126 | 126 | 158 | 162 | 162 | 162 | 162 | 162 | 108 | 108 | 108 | 125 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3660480
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 25 | 25 | 25 | 32 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 25 |  |  | 621120
79 | Kodda 150MW PP | [9 empty] | 32 | 32 | 48 | 48 | 16 | 16 | 16 | 48 | 98 |  | 98 | 98 | 98 | 98 | 48 |  |  | 680160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 14 | 25 | 25 | 25 | 25 | 25 | 26 | 35 | 46 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 46 | 831662
| Gazipur 100 MW PP | 105 | 105 | 70 | 35 | 35 | 35 | 70 | 86 | 90 | 91 | 105 | 105 | 92 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2319600
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26881
| Jodiac Power | 54 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 40 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1066167
| Karnaphuli Power Ltd. | 34 | 17 | 17 | 17 | 17 | 17 | 50 | 99 | 110 | 110 | 110 | 110 | 110 | 110 | 106 | 107 | 110 | 110 |  | 110 | 110 | 110 | 68 | 68 | 68 | 34 | 1952900
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 8 | 24 | 25 | 25 | 27 | 32 | 36 | 36 | 24 | 24 | 19 |  | 24 | 12 | 12 | 12 | 12 | 12 |  | 371378
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 35 | 17 | 17 | 17 | 17 | 45 | 82 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 54 | 54 | 2084160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 10 | 30 |  | 30 | [6 empty] | 56160
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1235276
94 | Gagnagar 102 MW PP (Digital Power) | 48 | 0 |  |  |  | 0 | 16 | 74 | 102 | 102 | 102 | 102 | 102 | 48 | 48 | 48 | 75 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 64 | 1586448
95 | Patenga 50MW PP (Baraka) | [19 empty] | 3 | 12 | 12 | 17 | 20 | 20 | 19 | 92640
96 | Chattogram 108 MW PP (ECPV) | 79 | 85 | 84 | 84 | 85 | 84 | 84 | 84 | 84 | 84 | 84 | 87 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 91 | 91 | 93 | 84 | 83 | 2075520
97 | katpotti 52 MW | [10 empty] | 20 | 47 | 47 | 47 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 |  | 600864
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 14 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 42 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 963555
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1337875
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 110 | 110 | 130 | 130 | 163 | 163 | 163 | 130 | 130 | 163 | 130 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 140 | 140 | 140 | 3633790
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 11850
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 876240
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 212 |  | 258 | 257 | 153 | 78 |  |  |  | 726040
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 |  | 50 | 50 | 50 | 25 |  |  |  | 184189
106 | Mymensingh 200 MW PP (United) | 192 | 160 | 160 | 100 | 100 | 106 | 140 | 182 | 184 | 184 | 173 | 173 | 173 | 172 | 171 | 169 | 181 | 191 |  | 192 | 191 | 192 | 192 | 192 | 192 | 192 | 4116000
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 100 |  | 100 | 100 | 100 | 25 |  |  |  | 302548
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 1 | 42 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 135 | 2515968
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2091840
116 | Chandpur 200MW (Desh energy) | [17 empty] | 13 |  | 44 | 17 | 17 | 17 | 17 |  |  | 120480
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 145 | 147 | 150 | 150 | 147 | 135 | 132 | 143 | 135 | 138 | 143 | 138 | 142 | 128 | 123 | 128 |  | 128 | 128 | 128 | 130 | 130 | 150 | 150 | 3375563
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 24 | 0 |  |  | 0 | 2 | 8 | 50 | 112 | 112 | 112 | 112 | 112 | 75 | 75 | 75 | 85 | 95 |  | 108 | 108 | 109 | 115 | 85 | 85 | 65 | 1689600
| Anwara 300 MW PP (United) |  |  |  |  | 0 | 7 | 15 | 15 | 15 | 15 | 15 | 50 | 80 | 45 | 45 | 45 | 65 | 120 |  | 150 | 120 | 100 | 45 | 45 | 15 | 15 | 1021200
| Juldah unit-2 (Acorn) | 70 | 40 | 10 | 10 | 10 | 50 | 70 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 1892160
| Anlima Energy Ltd. | 116 | 116 | 68 | 68 | 68 | 92 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 110 | 100 | 101 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2610709
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 436680
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 9 | 18 | 25 | 29 | 30 | 30 | 27 | 19 | 9 | 2 | [9 empty] | 196241
| Chandpur 115(Doreen) | [26 empty] | 0
| Kanchan Purbachal Power Generation Ltd. | 55 | 17 | 18 | 18 | 17 | 17 | 17 | 29 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 |  | 1114920
120 | Eastern Zone Total | 4847 | 4475 | 4353 | 4164 | 4131 | 4321 | 4690 | 5237 | 5616 | 5695 | 5550 | 5799 | 5915 | 5618 | 5597 | 5497 | 5673 | 6530 |  | 6690 | 6544 | 6430 | 6172 | 5834 | 5466 | 5051 | 132559967
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 |  |  |  | 0 | 14 | 60 | 85 | 105 | 70 | 70 | 105 | 105 | 70 | 70 | 70 | 105 |  | 105 | 105 | 105 | 105 | 105 | 53 | 53 | 1628160
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 17 | 40 | 60 | 71 | 75 | 72 | 61 | 43 | 20 | 4 | [9 empty] | 468720
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 201 | 181 | 161 | 161 | 161 | 161 | 160 | 200 | 130 | 130 | 150 | 170 | 170 | 174 | 170 | 140 | 220 |  | 222 | 222 | 220 | 220 | 223 | 207 | 223 | 4387145
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 269242
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 89 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 91 | 91 | 2215612
140 | Bhola 33 MW PP (Venture) | 19 | 18 | 17 | 17 | 16 | 18 | 16 | 16 | 15 | 15 | 17 | 17 | 19 | 18 | 16 | 16 | 16 | 25 |  | 25 | 26 | 26 | 27 | 25 | 24 | 22 | 448700
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [7 empty] | 20 |  | 60 | 70 | 70 |  |  |  |  | 179520
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 4 |  | 6 | 4 | [5 empty] | 8960
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 472 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 469 | 469 | 469 | 469 | 469 | 472 | 471 | 471 | 471 | 471 |  | 471 | 472 | 475 | 475 | 475 | 477 | 477 | 11436363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 280 | 280 | 290 | 330 | 320 | 320 | 320 | 320 | 340 |  | 400 | 400 | 410 | 420 | 420 | 400 | 370 | 8745200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 200 |  | 199 | 200 | 199 | 199 | 199 | 199 | 199 | 4870900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [9 empty] | 43 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 43 |  | 43 | 43 | 43 | 43 | 43 |  |  | 568639
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 4 | 4 | 4 | 4 | 4 | 2 | 0 | 0 | [9 empty] | 29580
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 161 | 167 | 163 | 159 | 155 | 152 | 152 | 156 | 163 | 163 | 168 | 197 | 176 | 173 | 175 | 175 | 177 |  | 194 | 177 | 179 | 190 | 189 | 182 | 182 | 4350755
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 310 | 326 | 318 | 335 | 332 | 332 | 346 | 296 | 318 | 280 | 316 | 343 | 385 | 283 | 340 | 332 | 300 | 414 |  | 410 | 410 | 409 | 410 | 353 | 330 | 345 | 8246545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 5 | 22 | 31 | 39 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 |  |  |  | 318435
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 21 | 22 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 185814
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 8 | 34 | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 |  | 436651
167 | Katakhali 50 MW Peaking PP | [9 empty] | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 12 |  |  | 354708
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 429600
170 | Chapainawabganj 100 MW Peaking PP | [13 empty] | 41 | 48 | 48 | 48 | 100 |  | 100 | 100 | 100 | 100 | 100 | 50 |  | 824008
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 20 |  | 20 | 20 | [5 empty] | 40145
| Bagura 113 MW PP (Confidence)-2 | [5 empty] | 1 | 25 | 70 | 110 | 113 | 70 | 70 | 90 | 70 | 35 | 35 | 37 | 96 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1638048
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 |  |  |  | 15 | 50 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 70 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1948224
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 112 | 112 | 112 | 112 | 112 | 110 | 105 | 105 | 105 | 98 | 60 | 49 | 58 | 113 |  | 113 | 113 | 113 | 113 | 113 | 112 | 112 | 2537836
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 3 | 5 | 5 | 4 | 5 | 3 | 2 | 1 | 0 | [9 empty] | 24452
178 | Energypac Power Venture Thakurgaon Ltd. | [10 empty] | 3 | 6 |  |  |  |  | 3 | [9 empty] | 10752
178