## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-01-12 | Wednesday
|  |  | Date (day): | 2022-01-12 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10254.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11250 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-01-11 | 2022-01-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 180 | 220 | 180 | 180
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 151 | 130 | 140 | 140 | 220 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 180 | 170 | 160 | 160 | 290 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 37 | 61 | 65 | 65 |  | 35 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 18 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 44 | 48 | 51 | 51
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 136 | 98 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 34 | 35 | 35 |  | 45 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 32 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 288 | 293 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 302 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2042 | 2519 | 2503 | 2573 | 2275 | 812
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Contract Expired
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 15 | 17 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 25 | 25 | 25 |  | 25 | 33 kV line problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 85 | 75 | 75 |  | 155 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 10 | 6 | 10
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 83 | 78 | 90 | 90 | 18 |  | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 140 | 135 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 946 | 1097 | 1293 | 1272 | 378 | 714
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 80 | 54 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 155 | 163 | 216 | 170 | 51 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 140 | 140 | 0 | 140 | 220 |  | Gas shortage.
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 295 | 0 | 250 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 29 | 5 | 40 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 50 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 0 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 125 | 135 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 44 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maintenance |  | 2022-01-19
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 34 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 97 | 101 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 16 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 25 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 150 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 98 | 109 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1207 | 1436 | 1455 | 1843 | 731 | 200
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 50 | 50 | 55 | 55 | 147 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 180 | 189 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 108 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 19 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 400 | 396 | 465.6 | 414 | 147 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 42 | 42 |  | 28 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maintenance
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 110 | 130 | 130 | 33 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 40 | 72 | 72
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 81 | 81
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 145 | 126 | 125 | 125 |  | 106 | Gas shortage+Machine problem
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 20 | 24 | 24
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 330 | 330
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 395 | 400 | 260 | 260 |  | 123 | Machhine problem
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1280 | 1196 | 1154 | 1154 | 33 | 1177
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 484 | 477 | 490 | 490
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 2 | 34 | 0 | 35 |  | 19 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 15 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 60 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 15 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 67 | 0 | 16 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 673 | 731 | 721 | 1090 | 410 | 88
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 21 | 25 | 25 |  | 8 | Engine problem
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 91 | 91 | 91 | 103 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 400 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 222 | 221 | 200 | 220
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 639 | 744 | 1057 | 1227 | 187 | 8
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 17 | 38 | 30 | 30 |  | 41 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Fuel shortage
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 50 | 34 | 50
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 32 | 32 | 32 |  | 18 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 189 | 150 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 377 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Under maint
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 34 | 34 | 34 | 43 | 9 |  | Engine problem
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 90 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 172 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 948 | 1295 | 1285 | 1364 | 609 | 159
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 111 | 113 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 7 | 0 | 0 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 322 | 312 | 321 | 313 | 74 | 210
|  | Total |  |  |  |  | 22066 | 21035 | 8457 | 9726 | 10254.6 | 11250 | 4844 | 3376
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8306.1374 | 9552.5 | 10071.6704 | 11049.3137
| A. |  | 2022-01-11 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 9726 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6210 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9726 | MW
| 3 | Day peak Generation : |  |  | 8457 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9552.5 | MW
| 4 | Evening peak Generation : |  |  | 9726 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 193.5815 | MKWHr | By Solar | 0.87394 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 89.6718 | MKWHr |  | By Oil: | 73.5945 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.7122 | MKWHr |  | By Hydro: | 1.9424 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4844 | MW | Dhaka | 3593.5 | 3593.5 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3376 | MW | Chittagong | 1098 | 1098 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 8220 | MW | Khulna | 1085 | 1085 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 687.89 | MMCFD |  |  | Rajshahi | 967 | 967 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 88857036.762 | ii) Oil : | Taka | 552461967.79 | Comilla | 795 | 795 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 65198444 | Total | Taka | 706517448.552 | Mymensingh | 816 | 816 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.031 | MKWHr. | Sylhet | 337 | 337 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 26 | MW (E to W) at | 19:00 | hrs | Barisal | 247 | 247 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -12 | MW at | 7:00 | hrs | Rangpur | 614 | 614 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.8° C |  |  | Total | 9552.5 | 9552.5 |  | 0
| B. |  | 2022-01-12 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 25.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9850 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 11250 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
| 4 | Reserve(Generation end) |  |  |  | 1400 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 196.0495 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5854 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.6429 | MKWHr. | ii) HVDC Flow at Peak Time |  | 477 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1437 | MKWHr. | iii) Maximum HVDC Flow : |  | 485 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.88 |  | (b) Today: | 96.73 |  | (c) Rule Curve: |  | 100.9
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-01-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 181 |  | 0 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 47 | 35 | 55 | 35 | 19 | 25 | 9 | 25 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 33 | 0 | 0 | 80 | 140 | 275 | 167 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 78 | 51 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 150 | 0 | 67 | 82 | 0 | 145 | 18 | 0 | 10 | 290 | 22 | 8 | 0 | 195 | 0 | 0 | 193 | 0 | 0 | 0 | 90 | 0 | 143 | 0 | 8 | 105 | 34 | 0 | 30 | 54 | 110 | 0 | 55 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 157 | 0 | 339 | 17 | 0 | 50 | 0 | 113 | 0 | 0 | 50 | 330 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4979 | 2139 | 7118 | 2119 | 480 | 1631 | 0 | 2160 | 530 | 80 | 0 | 40 | 78 | 0 | 0 | 96.9
2:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 187 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 34 | 0 | 0 | 80 | 140 | 275 | 170 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 76 | 51 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 110 | 0 | 67 | 82 | 0 | 145 | 18 | 0 | 10 | 280 | 22 | 8 | 0 | 95 | 0 | 0 | 192 | 0 | 0 | 0 | 90 | 0 | 142 | 0 | 8 | 50 | 34 | 0 | 30 | 54 | 51 | 0 | 55 | 100 | 400 | 104 | 0 | 54 | 116 | 0 | 17 | 0 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 151 | 0 | 378 | 0 | 0 | 50 | 0 | 113 | 0 | 0 | 50 | 310 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4560 | 2092 | 6652 | 2109 | 479 | 1626 | 0 | 1773 | 509 | 80 | 0 | 0 | 76 | 0 | 0 | 96.9
3:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 193 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 38 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 34 | 0 | 0 | 80 | 140 | 275 | 177 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 72 | 51 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 110 | 0 | 67 | 82 | 0 | 145 | 18 | 0 | 10 | 290 | 22 | 8 | 0 | 95 | 0 | 0 | 150 | 0 | 0 | 0 | 90 | 0 | 142 | 0 | 8 | 50 | 34 | 0 | 30 | 54 | 51 | 0 | 55 | 50 | 400 | 60 | 0 | 54 | 116 | 0 | 17 | 0 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 154 | 0 | 384 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 300 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4441 | 1983 | 6424 | 2119 | 479 | 1627 | 0 | 1550 | 499 | 78 | 0 | 0 | 72 | 0 | 0 | 96.89
4:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 193 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 17 | 35 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 36 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 34 | 0 | 0 | 80 | 140 | 280 | 181 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 69 | 51 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 110 | 0 | 66 | 82 | 0 | 145 | 18 | 0 | 10 | 290 | 22 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 0 | 0 | 90 | 0 | 148 | 0 | 8 | 50 | 34 | 0 | 30 | 54 | 51 | 0 | 55 | 50 | 401 | 54 | 0 | 54 | 116 | 0 | 17 | 0 | 0 | 17 |  | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 152 | 0 | 345 | 0 | 0 | 35 | 0 | 54 | 0 | 0 | 35 | 290 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4303 | 1932 | 6235 | 2126 | 480 | 1588 | 0 | 1406 | 490 | 76 | 0 | 0 | 69 | 0 | 0 | 96.89
5:00 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 188 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 17 | 35 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 38 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 34 | 0 | 0 | 80 | 140 | 280 | 181 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 9 | 69 | 51 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 110 | 0 | 67 | 82 | 0 | 145 | 18 | 0 | 10 | 275 | 22 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 0 | 0 | 90 | 0 | 150 | 0 | 8 | 50 | 34 | 0 | 30 | 54 | 51 | 0 | 55 | 50 | 400 | 54 | 0 | 54 | 116 | 0 | 17 | 0 | 0 | 17 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 150 | 0 | 344 | 0 | 0 | 35 | 0 | 54 | 0 | 0 | 35 | 280 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4292 | 1918 | 6210 | 2129 | 479 | 1567 | 0 | 1408 | 480 | 78 | 0 | 0 | 69 | 0 | 0 | 96.88
6:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 187 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 17 | 35 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 44 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 35 | 0 | 0 | 80 | 140 | 295 | 173 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 18 | 9 | 65 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 65 | 81 | 0 | 145 | 18 | 0 | 10 | 295 | 22 | 8 | 0 | 95 | 0 | 0 | 120 | 0 | 1 | 0 | 90 | 0 | 142 | 0 | 8 | 90 | 34 | 0 | 30 | 54 | 51 | 0 | 55 | 100 | 399 | 55 | 0 | 56 | 116 | 0 | 17 | 0 | 0 | 17 |  | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 385 | 1 | 0 | 37 | 0 | 56 | 0 | 0 | 50 | 290 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4437 | 2001 | 6438 | 2124 | 480 | 1681 | 0 | 1514 | 490 | 84 | 0 | 0 | 65 | 0 | 0 | 96.88
7:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 173 |  | 0 | 180 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 12 | 35 | 55 | 35 | 19 | 25 | 9 | 18 | 33 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 18 | 31 | 0 | 0 | 80 | 140 | 300 | 181 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 5 | 21 | 11 | 33 | 9 | 68 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 70 | 75 | 0 | 145 | 18 | 0 | 10 | 270 | 22 | 8 | 0 | 200 | 0 | 0 | 140 | 0 | 16 | 1 | 90 | 0 | 138 | 0 | 8 | 92 | 34 | 0 | 30 | 54 | 51 | 0 | 55 | 100 | 400 | 104 | 1 | 127 | 116 | 0 | 17 | 1 | 0 | 35 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 153 | 0 | 378 | 16 | 0 | 70 | 0 | 111 | 0 | 0 | 70 | 300 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4737 | 2116 | 6853 | 2148 | 479 | 1589 | 0 | 1986 | 500 | 80 | 0 | 0 | 68 | 3 | 0 | 96.87
8:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 167 |  | 0 | 180 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 64 | 0 | 21 | 0 | 0 | 22 | 35 | 55 | 35 | 19 | 25 | 9 | 18 | 33 | 2 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 21 | 9 | 0 | 0 | 80 | 140 | 275 | 168 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 9 | 81 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 163 | 0 | 68 | 76 | 0 | 145 | 18 | 0 | 10 | 315 | 16 | 8 | 0 | 300 | 0 | 0 | 161 | 0 | 42 | 4 | 90 | 0 | 132 | 0 | 49 | 90 | 51 | 1 | 30 | 54 | 76 | 0 | 63 | 100 | 400 | 104 | 4 | 162 | 116 | 0 | 0 | 4 | 0 | 55 |  | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 176 | 0 | 415 | 64 | 0 | 80 | 0 | 112 | 0 | 1 | 113 | 320 | 200 | 0 | 0 | 0 | 15 | 0 |  | 5133 | 2369 | 7502 | 2128 | 480 | 1697 | 0 | 2485 | 520 | 82 | 0 | 0 | 81 | 29 | 0 | 96.87
9:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 156 |  | 0 | 180 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 48 | 36 | 0 | 0 | 47 | 35 | 55 | 35 | 19 | 25 | 9 | 18 | 33 | 26 | 0 | 41 | 40 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 18 | 2 | 0 | 0 | 80 | 140 | 285 | 159 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 21 | 9 | 90 | 52 | 0 | 20 | 1 | 42 | 0 | 51 | 0 | 163 | 0 | 68 | 76 | 0 | 145 | 18 | 0 | 10 | 310 | 16 | 0 | 0 | 300 | 0 | 0 | 184 | 0 | 133 | 7 | 90 | 0 | 135 | 0 | 94 | 90 | 81 | 2 | 65 | 54 | 110 | 0 | 98 | 100 | 400 | 104 | 8 | 162 | 116 | 0 | 16 | 0 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 7 | 20 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 203 | 0 | 395 | 105 | 0 | 112 | 0 | 112 | 0 | 2 | 113 | 330 | 222 | 0 | 0 | 0 | 36 | 0 |  | 5580 | 2514 | 8094 | 2133 | 479 | 1677 | 0 | 2993 | 530 | 81 | 0 | 55 | 90 | 56 | 0 | 96.86
10:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 154 |  | 0 | 180 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 102 | 64 | 36 | 0 | 0 | 48 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 51 | 0 | 38 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 16 | 2 | 0 | 0 | 80 | 140 | 280 | 166 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 17 | 9 | 91 | 52 | 0 | 20 | 1 | 42 | 0 | 51 | 0 | 163 | 0 | 68 | 76 | 0 | 145 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 295 | 0 | 0 | 184 | 0 | 149 | 10 | 90 | 0 | 135 | 0 | 93 | 90 | 85 | 3 | 65 | 54 | 110 | 0 | 98 | 100 | 400 | 104 | 13 | 162 | 116 | 0 | 17 | 13 | 0 | 55 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 19 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 215 | 0 | 340 | 105 | 0 | 113 | 15 | 112 | 0 | 3 | 113 | 300 | 222 | 0 | 0 | 1 | 51 | 8 |  | 5644 | 2514 | 8158 | 2141 | 484 | 1600 | 0 | 3086 | 500 | 78 | 0 | 83 | 91 | 95 | 0 | 96.86
11:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 155 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 36 | 0 | 0 | 48 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 0 | 0 | 36 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 16 | 2 | 0 | 0 | 80 | 140 | 275 | 164 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 12 | 21 | 8 | 16 | 9 | 95 | 51 | 0 | 20 | 1 | 42 | 0 | 51 | 0 | 130 | 0 | 65 | 78 | 0 | 145 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 286 | 0 | 0 | 190 | 0 | 149 | 11 | 90 | 0 | 127 | 0 | 96 | 90 | 101 | 4 | 120 | 54 | 110 | 0 | 98 | 90 | 400 | 104 | 26 | 162 | 116 | 0 | 17 | 25 | 0 | 55 |  | 485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 14 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 34 | 24 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 178 | 0 | 326 | 105 | 0 | 113 | 15 | 112 | 0 | 4 | 113 | 300 | 222 | 0 | 0 | 2 | 62 | 10 |  | 5635 | 2488 | 8123 | 2049 | 485 | 1555 | 0 | 3101 | 500 | 76 | 0 | 127 | 95 | 135 | 0 | 96.85
12:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 151 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 136 | 37 | 0 | 0 | 44 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 18 | 2 | 0 | 0 | 80 | 140 | 345 | 155 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 11 | 16 | 9 | 97 | 50 | 0 | 20 | 1 | 42 | 0 | 51 | 0 | 163 | 0 | 62 | 78 | 0 | 145 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 288 | 0 | 0 | 180 | 0 | 149 | 14 | 90 | 0 | 125 | 0 | 108 | 90 | 105 | 4 | 140 | 54 | 110 | 0 | 98 | 90 | 395 | 104 | 19 | 162 | 116 | 0 | 17 | 30 | 0 | 55 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 34 | 24 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 414 | 105 | 0 | 113 | 15 | 111 | 0 | 4 | 113 | 300 | 222 | 0 | 0 | 3 | 67 | 7 |  | 5875 | 2582 | 8457 | 2096 | 484 | 1683 | 0 | 3190 | 500 | 86 | 0 | 179 | 97 | 142 | 0 | 96.85
13:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 153 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 136 | 48 | 0 | 0 | 45 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 51 | 0 | 37 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 83 | 19 | 18 | 6 | 0 | 0 | 80 | 140 | 275 | 144 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 12 | 24 | 21 | 11 | 18 | 9 | 95 | 49 | 0 | 20 | 1 | 43 | 0 | 51 | 0 | 163 | 0 | 62 | 78 | 0 | 126 | 18 | 0 | 10 | 310 | 16 | 0 | 0 | 300 | 83 | 0 | 180 | 26 | 149 | 19 | 90 | 12 | 128 | 0 | 108 | 90 | 105 | 4 | 155 | 54 | 110 | 0 | 98 | 90 | 400 | 104 | 18 | 162 | 116 | 0 | 17 | 21 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 31 | 41 | 0 | 34 | 24 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 39 | 198 | 0 | 398 | 105 | 0 | 113 | 15 | 62 | 0 | 4 | 113 | 340 | 210 | 0 | 0 | 3 | 64 | 0 |  | 5956 | 2654 | 8610 | 2032 | 479 | 1671 | 148 | 3187 | 539 | 77 | 0 | 248 | 95 | 134 | 0 | 96.84
14:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 148 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 98 | 52 | 0 | 0 | 48 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 51 | 0 | 33 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 80 | 14 | 18 | 3 | 0 | 0 | 80 | 140 | 275 | 165 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 24 | 21 | 11 | 16 | 9 | 98 | 49 | 0 | 20 | 1 | 43 | 0 | 51 | 0 | 130 | 0 | 40 | 78 | 0 | 126 | 18 | 0 | 10 | 270 | 16 | 0 | 0 | 300 | 0 | 0 | 184 | 0 | 149 | 17 | 90 | 34 | 127 | 0 | 108 | 102 | 105 | 3 | 100 | 54 | 110 | 0 | 103 | 100 | 360 | 104 | 20 | 162 | 115 | 0 | 17 | 23 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 50 | 36 | 48 | 0 | 34 | 30 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 193 | 0 | 285 | 105 | 0 | 113 | 15 | 93 | 0 | 2 | 113 | 320 | 200 | 0 | 0 | 2 | 52 | 0 |  | 5704 | 2552 | 8256 | 1984 | 479 | 1468 | 0 | 3216 | 519 | 73 | 0 | 299 | 98 | 120 | 0 | 96.84
15:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 134 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 64 | 61 | 0 | 0 | 48 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 32 | 51 | 0 | 40 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 20 | 18 | 2 | 0 | 0 | 80 | 140 | 280 | 170 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 41 | 24 | 21 | 11 | 16 | 9 | 91 | 49 | 0 | 20 | 1 | 43 | 0 | 51 | 0 | 110 | 0 | 40 | 78 | 0 | 126 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 300 | 0 | 0 | 184 | 0 | 149 | 13 | 90 | 17 | 125 | 0 | 107 | 100 | 105 | 2 | 100 | 54 | 110 | 0 | 110 | 100 | 340 | 104 | 12 | 162 | 100 | 0 | 17 | 10 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 50 | 38 | 48 | 0 | 0 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 302 | 105 | 0 | 70 | 15 | 103 | 0 | 2 | 113 | 300 | 170 | 0 | 0 | 1 | 37 | 10 |  | 5623 | 2435 | 8058 | 1955 | 479 | 1448 | 0 | 3146 | 500 | 80 | 0 | 281 | 91 | 78 | 0 | 96.83
16:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 132 |  | 0 | 180 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 102 | 64 | 62 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 32 | 51 | 0 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 24 | 18 | 2 | 0 | 0 | 80 | 140 | 275 | 169 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 41 | 24 | 21 | 11 | 16 | 9 | 94 | 49 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 110 | 0 | 66 | 78 | 0 | 126 | 18 | 0 | 10 | 295 | 16 | 2 | 0 | 300 | 0 | 0 | 187 | 0 | 149 | 7 | 90 | 17 | 122 | 0 | 98 | 105 | 105 | 1 | 100 | 54 | 110 | 0 | 108 | 100 | 400 | 104 | 6 | 162 | 100 | 0 | 17 | 7 | 0 | 55 |  | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 50 | 38 | 48 | 0 | 0 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 174 | 0 | 313 | 35 | 0 | 35 | 15 | 39 | 0 | 2 | 35 | 300 | 170 | 0 | 0 | 0 | 18 | 13 |  | 5678 | 2185 | 7863 | 2039 | 478 | 1452 | 0 | 2888 | 500 | 85 | 0 | 286 | 94 | 41 | 0 | 96.83
17:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 132 |  | 0 | 180 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 64 | 48 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 32 | 51 | 0 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 81 | 20 | 21 | 2 | 0 | 0 | 80 | 140 | 280 | 159 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 35 | 28 | 21 | 11 | 24 | 9 | 95 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 130 | 0 | 66 | 78 | 0 | 126 | 18 | 0 | 10 | 320 | 16 | 5 | 0 | 300 | 0 | 0 | 187 | 0 | 149 | 1 | 90 | 22 | 127 | 0 | 108 | 105 | 105 | 0 | 100 | 54 | 110 | 0 | 112 | 100 | 394 | 104 | 1 | 162 | 105 | 0 | 17 | 1 | 0 | 55 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 50 | 38 | 60 | 0 | 8 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 178 | 0 | 398 | 35 | 0 | 37 | 15 | 90 | 0 | 0 | 60 | 300 | 202 | 0 | 0 | 0 | 4 | 0 |  | 5767 | 2378 | 8145 | 2047 | 477 | 1614 | 0 | 2973 | 500 | 85 | 0 | 347 | 95 | 7 | 0 | 96.82
18:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 132 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 98 | 60 | 0 | 0 | 48 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 32 | 51 | 0 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 50 | 76 | 25 | 21 | 5 | 0 | 0 | 80 | 140 | 270 | 173 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 42 | 43 | 21 | 11 | 20 | 9 | 107 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 110 | 0 | 40 | 78 | 0 | 126 | 18 | 0 | 10 | 295 | 16 | 8 | 120 | 300 | 304 | 80 | 189 | 100 | 149 | 0 | 90 | 51 | 130 | 0 | 115 | 105 | 105 | 0 | 150 | 54 | 110 | 17 | 108 | 100 | 398 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 15 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 50 | 38 | 100 | 0 | 34 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 47 | 174 | 0 | 405 | 105 | 165 | 91 | 0 | 113 | 0 | 0 | 100 | 320 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6582 | 2894 | 9476 | 2064 | 477 | 1593 | 816 | 3363 | 518 | 85 | 0 | 453 | 107 | 0 | 0 | 96.82
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 130 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 98 | 61 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 20 | 32 | 51 | 0 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 100 | 78 | 25 | 21 | 10 | 0 | 0 | 80 | 140 | 295 | 163 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 44 | 25 | 21 | 11 | 16 | 9 | 101 | 50 | 0 | 20 | 0 | 43 | 0 | 53 | 0 | 110 | 0 | 40 | 78 | 0 | 126 | 18 | 0 | 10 | 290 | 20 | 8 | 150 | 293 | 302 | 100 | 189 | 100 | 149 | 0 | 90 | 34 | 135 | 0 | 115 | 105 | 105 | 0 | 135 | 54 | 110 | 17 | 109 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 50 | 38 | 100 | 0 | 50 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 189 | 0 | 377 | 105 | 172 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6644 | 3082 | 9726 | 2095 | 477 | 1567 | 924 | 3416 | 599 | 85 | 0 | 462 | 101 | 0 | 0 | 96.8
19:30 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 128 |  | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 98 | 61 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 20 | 32 | 51 | 0 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 20 | 83 | 25 | 21 | 8 | 0 | 0 | 80 | 140 | 295 | 168 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 50 | 0 | 21 | 11 | 16 | 9 | 101 | 51 | 0 | 20 | 0 | 43 | 0 | 53 | 0 | 110 | 0 | 40 | 78 | 0 | 126 | 18 | 0 | 10 | 300 | 20 | 11 | 150 | 300 | 301 | 100 | 191 | 100 | 149 | 0 | 90 | 34 | 142 | 0 | 115 | 105 | 68 | 0 | 95 | 54 | 110 | 17 | 110 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 7 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 50 | 38 | 100 | 0 | 50 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 193 | 0 | 401 | 105 | 172 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6494 | 3113 | 9607 | 2108 | 477 | 1588 | 923 | 3256 | 609 | 85 | 0 | 460 | 101 | 0 | 0 | 0
20:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 131 |  | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 98 | 61 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 20 | 30 | 51 | 0 | 46 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 83 | 25 | 21 | 10 | 0 | 0 | 80 | 140 | 290 | 174 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 0 | 21 | 11 | 16 | 9 | 101 | 50 | 0 | 20 | 0 | 43 | 0 | 53 | 0 | 110 | 0 | 40 | 78 | 0 | 126 | 18 | 0 | 10 | 280 | 20 | 11 | 150 | 296 | 305 | 100 | 191 | 100 | 149 | 0 | 90 | 34 | 138 | 0 | 115 | 105 | 68 | 0 | 30 | 54 | 110 | 0 | 109 | 80 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 50 | 38 | 100 | 0 | 50 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 193 | 0 | 370 | 105 | 172 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6344 | 3073 | 9417 | 2106 | 479 | 1542 | 927 | 3135 | 609 | 86 | 0 | 432 | 101 | 0 | 0 | 96.81
21:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 130 |  | 0 | 160 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 82 | 82 | 60 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 20 | 30 | 51 | 0 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 40 | 83 | 25 | 21 | 20 | 0 | 0 | 80 | 140 | 325 | 174 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 0 | 21 | 11 | 16 | 9 | 99 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 110 | 0 | 69 | 78 | 0 | 126 | 18 | 0 | 10 | 295 | 21 | 11 | 0 | 300 | 194 | 80 | 191 | 100 | 149 | 0 | 90 | 34 | 138 | 0 | 115 | 105 | 68 | 0 | 30 | 54 | 110 | 0 | 110 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 50 | 38 | 100 | 0 | 50 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 195 | 0 | 404 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6180 | 2857 | 9037 | 2173 | 479 | 1598 | 374 | 3184 | 629 | 85 | 0 | 416 | 99 | 0 | 0 | 96.8
22:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 130 |  | 0 | 160 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 82 | 64 | 60 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 20 | 15 | 51 | 0 | 40 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 40 | 85 | 25 | 21 | 29 | 0 | 0 | 80 | 140 | 280 | 181 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 0 | 21 | 11 | 33 | 9 | 89 | 50 | 0 | 20 | 0 | 43 | 0 | 51 | 0 | 130 | 0 | 68 | 78 | 0 | 126 | 18 | 0 | 10 | 300 | 21 | 11 | 0 | 300 | 0 | 0 | 191 | 0 | 149 | 0 | 90 | 34 | 138 | 0 | 107 | 105 | 68 | 0 | 30 | 54 | 110 | 0 | 110 | 100 | 401 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 50 | 39 | 100 | 0 | 43 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 194 | 0 | 394 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 420 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5765 | 2826 | 8591 | 2136 | 478 | 1621 | 0 | 3170 | 619 | 80 | 0 | 398 | 89 | 0 | 0 | 96.8
23:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 126 |  | 0 | 160 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 82 | 48 | 61 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 16 | 16 | 25 | 0 | 42 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 90 | 25 | 21 | 33 | 0 | 0 | 80 | 140 | 265 | 199 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 0 | 21 | 0 | 33 | 9 | 83 | 51 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 68 | 78 | 0 | 126 | 18 | 0 | 10 | 290 | 21 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 117 | 0 | 90 | 17 | 143 | 0 | 65 | 105 | 68 | 0 | 30 | 54 | 110 | 0 | 115 | 100 | 190 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 50 | 38 | 100 | 0 | 43 | 0 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 341 | 70 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 400 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5330 | 2670 | 8000 | 1900 | 479 | 1556 | 0 | 3003 | 599 | 82 | 0 | 298 | 83 | 0 | 0 | 96.79
24:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 125 |  | 0 | 160 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 64 | 16 | 61 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 16 | 12 | 0 | 0 | 42 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 89 | 25 | 21 | 26 | 0 | 0 | 80 | 140 | 265 | 209 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 0 | 21 | 11 | 33 | 9 | 82 | 52 | 0 | 20 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 68 | 79 | 0 | 118 | 18 | 0 | 10 | 280 | 21 | 11 | 0 | 300 | 0 | 0 | 191 | 0 | 75 | 0 | 90 | 0 | 142 | 0 | 16 | 105 | 68 | 0 | 30 | 54 | 110 | 0 | 85 | 100 | 181 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 50 |  | 479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 24 | 0 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 151 | 0 | 335 | 17 | 0 | 70 | 0 | 112 | 0 | 0 | 113 | 380 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5032 | 2411 | 7443 | 1852 | 479 | 1532 | 0 | 2659 | 579 | 82 | 0 | 178 | 82 | 0 | 0 | 96.79
KWH | 0 | 0 | 4986000 | 0 | 0 | 0 | 0 | 0 | 3742000 |  | 0 | 4180200 | 0 | 0 | 0 | 856404 | 0 | 0 | 0 | 0 | 1664496 | 1280640 | 893433 | 0 | 0 | 999888 | 861408 | 1233594 | 884631 | 422784 | 600000 | 201600 | 623000 | 756500 | 722880 | 0 | 962400 | 980000 | 0 | 0 | 228529 | 0 | 0 | 0 | 0 |  | 532320 | 0 | 284118 | 257640 | 2000640 | 514560 | 452880 | 408480 | 0 | 0 | 1953510 | 3586000 | 7118000 | 4107000 | 217454 | 0 | 149832 | 143520 | 0 | 1252696 | 0 | 410704 | 280411 | 499860 | 242280 | 595400 | 215560 | 2143680 | 1191360 | 0 | 431172 | 6100 | 1014000 | 0 | 1218000 | 0 | 3342109 | 0 | 1460256 | 1876800 | 0 | 3277880 | 418000 | 0 | 251460 | 7237000 | 441624 | 144768 | 444672 | 6004252 | 1148420 | 386616 | 4207200 | 444799 | 2381470 | 111780 | 2116800 | 355200 | 3263490 | 0 | 1693200 | 2233200 | 1798174 | 26041 | 1839164 | 1371799 | 2333444 | 46740 | 2204160 | 2209920 | 9158100 | 2447040 | 156760 | 3444480 | 2760000 | 0 | 437760 | 118738 | 0 | 1189800 |  | 11642909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229440 | 22784 | 0 | 2212350 | 403900 | 0 | 0 | 0 | 0 | 522896 | 420194 | 850072 | 0 | 527832 | 350800 | 678720 | 0 | 515040 | 0 | 97866 | 0 | 0 | 4856200 | 0 | 0 | 0 | 0 | 0 | 0 | 272746 | 357120 | 4466218 | 0 | 8883854 | 1629600 | 550306 | 2097504 | 141552 | 2307331 | 0 | 23485 | 2193216 | 8856000 | 4902764 | 0 | 0 | 17040 | 414000 | 47040 |  | 133090680 | 60490779 | 193581459 | 50823800 | 11642909 | 38848023 | 3331933 | 65890922 | 13712200 | 1942400 | 0 | 4371648 | 2143680 | 873944 | 0
Fuel Cost | 0 | 0 | 7279560 | 0 | 0 | 0 | 0 | 0 | 3854260 |  | 0 | 4556418 | 0 | 0 | 0 | 7245177.84 | 0 | 0 | 0 | 0 | 15180203.52 | 12601497.6 | 8237452.26 | 0 | 0 | 9088981.92 | 6288278.4 | 9535681.62 | 8722461.66 | 317088 | 450000 | 0 | 0 | 0 | 6990249.6 | 0 | 259848 | 264600 | 0 | 0 | 2123034.41 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2755944.6 | 2460462 | 17405568 | 4075315.2 | 570628.8 | 1213185.6 | 0 | 0 | 2871659.7 | 2653640 | 7118000 | 3778440 | 280515.66 | 0 | 169310.16 | 200928 | 0 | 2142110.16 | 0 | 4148110.4 | 2677925.05 | 634822.2 | 181710 | 1041950 | 161670 | 16077600 | 1262841.6 | 0 | 547588.44 | 97234 | 1662960 | 0 | 2168040 | 0 | 3810004.26 | 0 | 2876704.32 | 3584688 | 0 | 5670732.4 | 915420 | 0 | 512978.4 | 7309370 | 331218 | 110023.68 | 7563870.72 | 45392145.12 | 19500171.6 | 6464219.52 | 21877440 | 7437039.28 | 23433664.8 | 1306708.2 | 17251920 | 3853920 | 23007604.5 | 0 | 15441984 | 21103740 | 15662095.54 | 0 | 13904079.84 | 11948369.29 | 20510972.76 | 466465.2 | 18889651.2 | 14718067.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 67063155.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2406825.6 | 238776.32 | 0 | 2499955.5 | 626045 | 0 | 0 | 0 | 0 | 5145296.64 | 4269171.04 | 7523137.2 | 0 | 7136288.64 | 3399252 | 6576796.8 | 0 | 988876.8 | 0 | 74084.562 | 0 | 0 | 26320604 | 0 | 0 | 0 | 0 | 0 | 0 | 409119 | 6074611.2 | 5225475.06 | 0 | 8795015.46 | 17013024 | 9360705.06 | 19905312.96 | 1336250.88 | 17904888.56 | 0 | 259509.25 | 16207866.24 | 38877840 | 0 | 0 | 0 | 0 | 0 | 0 |  | 516208220.23 | 275637883.612 | 791846103.842 | 48405482.422 | 67063155.84 | 40451554.34 | 56400617.38 | 453573339.01 | 65198444 | 524448 | 0 | 42488011.4 | 16077600 | 1663451.45 | 0
Yesterday Day Peak | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 151 |  | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 136 | 37 | 0 | 0 | 44 | 35 | 55 | 35 | 16 | 25 | 9 | 20 | 33 | 51 | 0 | 46 | 40 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 19 | 18 | 2 | 0 | 0 | 80 | 140 | 345 | 155 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 24 | 21 | 11 | 16 | 9 | 97 | 50 | 0 | 20 | 1 | 42 | 0 | 51 | 0 | 163 | 0 | 62 | 78 | 0 | 145 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 288 | 0 | 0 | 180 | 0 | 149 | 14 | 90 | 0 | 125 | 0 | 108 | 90 | 105 | 4 | 140 | 54 | 110 | 0 | 98 | 90 | 395 | 104 | 19 | 162 | 116 | 0 | 17 | 30 | 0 | 55 |  | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 34 | 24 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 414 | 105 | 0 | 113 | 15 | 111 | 0 | 4 | 113 | 300 | 222 | 0 | 0 | 3 | 67 | 7 |  | 8457 | DayPeak
Yesterday Evening Peak | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 98 | 61 | 0 | 0 | 48 | 35 | 55 | 35 | 18 | 25 | 9 | 20 | 32 | 51 | 0 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 78 | 25 | 21 | 10 | 0 | 0 | 80 | 140 | 295 | 163 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 44 | 25 | 21 | 11 | 16 | 9 | 101 | 50 | 0 | 20 | 0 | 43 | 0 | 53 | 0 | 110 | 0 | 40 | 78 | 0 | 126 | 18 | 0 | 10 | 290 | 20 | 8 | 150 | 293 | 302 | 100 | 189 | 100 | 149 | 0 | 90 | 34 | 135 | 0 | 115 | 105 | 105 | 0 | 135 | 54 | 110 | 17 | 109 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 50 | 38 | 100 | 0 | 50 | 32 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 189 | 0 | 377 | 105 | 172 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 221 | 0 | 0 | 0 | 0 | 0 |  | 9726 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 65 | 0 | 0 | 51 | 35 | 55 | 35 | 19 | 25 | 10 | 33 | 33 | 51 | 0 | 35 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 25 | 21 | 10 | 0 | 0 | 80 | 140 | 250 | 170 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 163 | 55 | 0 | 22 | 0 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 81 | 0 | 125 | 18 | 0 | 10 | 330 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 260 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 55 |  | 490 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 35 | 40 | 0 | 91 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 0 | 50 | 32 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 65 | 0 | 0 | 51 | 35 | 55 | 35 | 19 | 25 | 10 | 33 | 33 | 51 | 0 | 35 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 25 | 21 | 6 | 0 | 0 | 100 | 0 | 0 | 216 | 0 | 0 | 29 | 50 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 9 | 138 | 55 | 0 | 22 | 1.6 | 42 | 0 | 51 | 0 | 130 | 0 | 72 | 81 | 0 | 125 | 18 | 0 | 10 | 330 | 24 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 260 | 104 | 50 | 162 | 116 | 0 | 17 | 30 |  | 55 |  | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 0 | 34 | 32 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 60 | 150 | 0 | 400 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 200 |  | 0 | 6 | 16
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 160 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 72 | 48 | 0 | 0 | 0 | 41 | 35 | 55 | 35 | 19 | 25 | 9 | 20 | 8 | 13 | 0 | 35 | 40 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 83 | 25 | 20 | 6 | 0 | 0 | 100 | 140 | 165 | 207 | 8 | 0 | 26 | 30 | 0 | 51 | 0 | 0 | 3 | 19 | 11 | 16 | 9 | 79 | 53 | 0 | 0 | 0 | 42 | 0 | 51 | 0 | 110 | 0 | 70 | 76 | 0 | 125 | 18 | 0 | 10 | 300 | 22 | 11 | 20 | 167 | 73 | 50 | 156 | 100 | 66 | 7 | 90 | 0 | 118 | 0 | 48 | 105 | 40 | 0 | 10 | 54 | 56 | 0 | 45 | 90 | 260 | 104 | 6 | 154 | 116 | 0 | 17 | 3 | 0 | 17 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 38 | 152 | 0 | 356 | 80 | 40 | 80 | 0 | 98 | 0 | 0 | 95 | 340 | 200 | 0 | 0 | 0 | 11 | 0 | 0
199
| Minimum Generation |  | 6210 | 5:00
| Highest Generation |  | 9726 | 19:00
| Day Peak Generation |  | 8457 | 12:00
| Evening Peak Generation |  | 9726 | 19:00
| HVDC Max Flow |  | 485 | 11:00
| HVDC EvPeak Flow |  | 477 | 19:00
| Load factor L.F |  | 82.93%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-01-12
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-01-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8457 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5854 | MW
Evening Peak Generation : |  | 9726 | MW Hour : | 19:00 | Available Max Generation : |  | 11250 | MW
E.P. Demand (at gen end) : |  | 9726 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9850 | MW
Maximum Generation : |  | 9726 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1400 | MW
Total Gen. (MKWH) : |  | 193.5815 | System Load Factor : | 82.93% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -12 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-01-12
Actual : | 96.73 | Ft.(MSL) , | Rule curve : | 100.9 | Ft.( MSL )
Gas Consumed : | Total = | 687.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 88857036.762
: |  | Coal : | 65198444 | Oil : | 552461967.79 | Total : | 706517448.552
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3604.1219 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1223.1082 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1095.4202 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 989.6469 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 894.4165 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 721.7562 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 406.7783 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 185.9177 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 556.6389 |  |  | 0 | 0%
Total | 0 |  | 9677.8048 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
|  |  |  | 2) Ghorasal-3,5,7 |  | 11) Chandpur CCPP 150 MW
3) Ashuganj-3,4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW
6) Raozan unit- 2
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bibiyana-Kaliakoir 400 kV Ckt-1 was under shut down from 08:33 to 18:01 for A/M.
b) Daudkandi-Comilla(N) 132 kV Ckt-1 was under shut down from 08:28 to 15:29 for A/M.
c) Dhamrai 132/33 kV T-1 transformers was under shut down from 08:24 to 22:34 for A/M.
d) Aminbazar-Agargaon 230 kV Ckt-2 was under shut down from 08:55 to 11:19 for A/M.
e) Aminbazar-Kaliakoir 230 kV Ckt-2 was under shut down from 09:08 to 17:01 for A/M.
f) Bakulia-Modern 132 kV Ckt was under shut down from 08:34 to 15:04 for A/M.
g) Hathazari-Madunaghat 132 kV Ckt-1 was under shut down from 09:30 to 13:58 for A/M.
h) Mymensingh-Bhaluka 132 kV Ckt-2 was under shut down from 09:13 to 16:18 for A/M.
i) Savar 132/33 kV T-1 transformers was under shut down from 08:55 to 16:36 for A/M.
j) Siddhirganj-Haripur 132 kV Ckt-1 was under shut down from 09:48 to 14:39 for A/M.
k) Bheramara 132/33 kV T-4 transformers was under shut down from 09:03 to 16:46 for A/M.
l) Bheramara HVDC 400 kV filter bus-2 was under shut down from 10:14 to 16:16 for A/M.
m) Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-2 was under shut down from 10:48 to 12:56 for A/M.
n) Jhenaidah(N)-Jashore 132 kV Ckt-1 was under shut down from 08:44 to 10:31 for D/W.
o) Magura-Norail 132 kV Ckt-2 was under shut down from 08:28 to 15:46 for A/M.
p) Magura-Norail 132 kV Ckt-2 was under shut down from 08:28 to 15:46 for A/M.
q) Sirajganj-Shahjadpur132 kV Ckt was under shut down from 09:16 to 13:49 for A/M.
r) Aftabnagar-Rampura 132 kV Ckt-2 was shut down at 12:25 for C/M.
s) Aminbazar-Agargaon 230 kV Ckt-2 was under shut down from 11:30 to 15:26 for A/M.
t) Pabna 132/33 kV T-3 transformer was under shut down from 12:02 to 15:03 for A/M.
u) Sherpur 132/33 kV T-1 transformer was under shut down from 13:51 to 15:06 for A/M.
v) Bogura-Naogaon 132 kV Ck-1 tripped at 22:56 showing O/C relay, AR block at Bogura end and was switched on
at 23:16.
w) Naogaon 132/33 kV T-2 transformer tripped at 22:56 showing O/C,E/F relay, R-phase, LA burst at HT side. | [5 empty] | About 6 MW power interruption occurred under
Naogaon S/S area from 22:56 to 23:55.
x) Bibiyana south ST was shut down at 23:25 due to HP drum line leakage.
y) Chattak-Sunamganj 132 kV Ckt tripped at 01:22(12/01/2022) showing 67N at Sunamganj end and was switched on | [5 empty] | About 15 MW power interruption occurred under
at 01:34. | [5 empty] | Naogaon S/S area from 01:22(12/01/2022) to 01:34.
z) Aminbazar 230/132 kV T-1 & T-3 transformer tripped at 06:41(12/01/2022) showing winding temperature high,
General trip at T-1 and General trip at T-3 transformer and T-3 was switched on at 07:57.
aa) Rampura-Ullon 132 kV Ckt-2 was shut down at 07:56(12/01/2022) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-01-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 4986000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gasshortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 130 | 3742000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 170 | 4180200 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 856404 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 61 | 893433 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 422784 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1664496
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 999888
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 861408 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 1280640 | High Voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1233594
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 884631 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 801600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 623000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 756500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 722880
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 293 | 6004252
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 302 | 1148420
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 386616
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 444799
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2381470
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2233200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2447040
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3444480
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 118738
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1189800
| Dhaka area Total |  |  |  | 5696 | 2519 | 44708273
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 228529 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 111780
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 514560 | High Voltage
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 85 | 1942400 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1798174
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 284118 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 257640
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2116800 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 452880
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 408480
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 78 | 2000640 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26041
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 135 | 1839164 | High Voltage
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1371799
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2333444
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2209920
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2760000
| Chattogram area Total |  |  |  | 2382 | 1097 | 20656369
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1953510 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 163 | 4107000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 140 | 3586000 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7118000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 149832 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 143520 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1252696
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 3263490 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 410704 | Engine problem
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 34 | 355200 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 499860
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242280
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 101 | 2143680
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 595400 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 280411 | High Voltage
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 215560 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 444672 | High Voltage
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 46740 | High Voltage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 109 | 2204160
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 437760 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 2899 | 1436 | 29667929
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 50 | 1191360 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 431172
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6100
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 189 | 4207200
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1693200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 156760
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 532320
| Mymensingh Area Total |  |  |  | 622 | 396 | 8218112
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1014000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3342109 | Frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1218000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 144768 | Engine problem
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1460256
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1876800
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 3277880 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 418000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 20 | 441624
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7237000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251460
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9158100
| Sylhet Area Total |  |  |  | 2377 | 1196 | 29839997
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 477 | 11642909
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 229440 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 15 | 22784
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 357120
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1629600
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 141552 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 414000 | On test
| Khulna Area Total |  |  |  | 2229 | 731 | 14437405
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | High Voltage
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 403900 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2212350 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 272746 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 400 | 8856000 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 4902764
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 744 | 16647760
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 522896
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 38 | 420194 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 527832
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 350800 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 189 | 4466218 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 377 | 8883854 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 515040
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 97866 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 678720 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 850072
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 172 | 550306
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2097504
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2193216
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17040
| Rajshahi Area Total |  |  |  | 2179 | 1295 | 22171558
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4856200
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2307331
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23485
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 47040 | On test
| Rangpur Area Total |  |  |  | 605 | 312 | 7234056
| Total |  |  |  | 21035 | 9726 | 193581459
| Eastern Grid Total |  |  |  | 13976 | 6644 | 133090680
| Western Grid Total |  |  |  | 7059 | 3082 | 60490779
| National Grid Total |  |  |  | 21035 | 9726 | 193581459
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-01-11
(a) ENTIRE EASTERN GRID : |  | 6639.5 | MW | (b) ENTIRE WESTERN GRID : |  | 2913 | MW
i) Dhaka area |  | 3593.5 | MW | i) Khulna area |  | 1085 | MW
ii) Chittagong area |  | 1098 | MW | ii) Rajshahi area |  | 967 | MW
iii) Comilla area |  | 795 | MW | iii) Barisal area |  | 247 | MW
iv) Mymensingh area |  | 816 | MW | iv) Rangpur area |  | 614 | MW
v) Sylhet area |  | 337 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9552.5 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 15:00 | Tangail | 147 | 18:30 | Noapara | 38 | 18:30
Munsiganj | 59 | 20:00 | Mymensing | 160 | 18:30 | Jessore | 83 | 18:00
Sonargaon | 66 | 9:00 | Kishoreganj | 102 | 19:30 | Benapol | 80 | 18:30
Shyampur | 168 | 12:00 | Netrokona | 110 | 19:00 | Jhenida(Old) | 84 | 18:30
Bhulta | 144 | 10:00 | Jamalpur | 98 | 18:30 | Bottail | 96 | 18:00
Madanganj | 39 | 18:30 | Sherpur | 116 | 18:00 | G.K Project | 39 | 18:30
Shitalakhya | 97 | 12:00 | Srimongal | 42 | 18:00 | Faridpur | 100 | 20:00
Rahim steel | 25 | 20:00 | Shahjibazar | 83 | 21:00 | Rajbari | 38 | 18:30
Matuail | 74 | 1:00 | Fenchuganj | 29 | 17:00 | Madaripur | 64 | 19:30
Ghorasal | 64 | 19:30 | Kulawara | 28 | 18:00 | Sariatpur | 42 | 20:00
Narsingdi | 127 | 20:00 | Sylhet | 99 | 18:00 | Gopalganj | 69 | 18:30
Haripur (SBU) | 104 | 14:00 | Chatak | 18 | 18:30 | Bagerhat | 70 | 19:30
Sreenagar | 27 | 21:00 | Sunamganj | 31 | 18:00 | Mongla | 36 | 9:00
Ullon | 96 | 11:00 | Biani Bazar | 42 | 18:00 | Satkhira | 77 | 19:30
Hasnabad | 60 | 18:30 | Comilla (S) | 107 | 18:00 | Gallamari | 42 | 14:00
Magbazar | 0 | 23:00 | Comilla(N) | 92 | 19:30 | Magura | 40 | 18:00
Maniknagar | 74 | 21:00 | Chandpur | 48 | 20:00 | Norail | 32 | 18:30
Bangabhaban | 9 | 15:00 | Feni | 80 | 18:00 | Chuadanga | 66 | 18:00
Motijheel | 21 | 15:00 | Chowmuhani | 134 | 21:00 | Barisal(N) | 27 | 19:00
Narinda | 32 | 18:30 | Ashuganj | 22 | 19:00 | Barisal (S) | 78 | 20:00
Kazla | 63 | 13:00 | Daudkandi | 99 | 19:00 | Patuakhali | 74 | 20:00
Dhanmondi | 42 | 8:00 | B.Baria | 100 | 18:00 | Bhandaria | 38 | 19:00
Lalbag | 96 | 18:00 | Ramganj | 52 | 18:00 | Borguna | 12 | 20:00
Madartek | 64 | 19:30 | Chaddagram | 33 | 18:00 | Borhan Uddin | 29 | 21:00
Dhaka University | 23 | 14:00 | PHP | 8 | 1:00 | Ishurdi | 49 | 18:30
Aftabnagar | 11.06 | 18:00 | Kochua | 36 | 18:30 | Ruppur Paromanobik | 3 | 20:00
Fatullah | 100 | 20:00 | Madunaghat | 36 | 18:30 | Natore | 94 | 18:30
Nawabganj | 32 | 20:00 | Hathazari | 68 | 19:00 | Bogra | 110 | 18:30
Keraniganj | 48 | 18:30 | Khulshi | 136 | 11:00 | Noagaon | 87 | 19:30
Banani | 40 | 18:00 | Halishahar | 69.5 | 14:00 | Rajshahi | 93 | 19:30
Mirpur | 83 | 18:00 | Baraulia | 160 | 10:00 | Rajshahi New | 22 | 20:00
Kalyanpur | 63 | 18:00 | Sikalbaha | 22 | 18:00 | C.Nawabganj | 43 | 19:30
Gulshan | 74 | 2:00 | Dohazari | 60 | 19:00 | Amnura | 46 | 19:30
Uttara | 38 | 21:00 | Cox'sbazar | 80 | 19:30 | Pabna | 77 | 18:30
Uttara New | 40 | 19:00 | Chandraghona | 20 | 18:00 | Shahjadpur | 71 | 19:00
Kamrangirchar | 63 | 13:00 | Kaptai | 3.2 | 18:00 | Serajganj | 78 | 20:00
Savar | 155 | 18:00 | A. Khaer Stl. | 18 | 7:00 | Niyamatpur | 73 | 20:00
Bhasantec | 84 | 13:00 | Bakulia | 88 | 18:00 | Joypurhat | 38 | 20:00
Agargaon | 49 | 13:00 | Julda | 22 | 7:00 | Sherpur(Bogura) | 48 | 18:00
Satmosjid | 69 | 19:00 | TK chemical | 22.5 | 18:00 | Mohastangor | 42 | 18:30
Old Tongi | 103 | 12:00 | Modern Steel | 0 | 1:00 | Bhangura | 23 | 18:00
Kabirpur | 200 | 18:00 | Shahmirpur | 32.5 | 18:00 | Rangpur | 95 | 18:00
Bashundara | 109 | 18:00 | Khagrachhari | 20 | 8:00 | Lalmonirhat | 26 | 18:00
Manikgong | 74 | 21:00 | Matarbari | 26 | 18:00 | Saidpur | 80 | 18:30
Joydevpur | 126 | 18:30 | Baroiar Hat | 32 | 18:00 | Purbasadipur | 88 | 19:30
New Tongi | 67 | 11:00 | Rangamati | 10 | 18:00 | Thakurgaon | 65 | 20:00
Kodda | 223 | 18:00 | Abul Khair 230 | 117 | 9:00 | Palashbari | 76 | 19:30
Dhamrai | 42 | 8:00 | BSRM | 157 | 1:00 | Barapukuria | 43 | 20:00
Rajendrapur | 92 | 13:00 | GPH Ispat | 95 | 19:30 | Panchagar | 42 | 18:30
Purbachal | 52 | 20:00 | Agrabad | 58 | 17:00 | Joldhaka | 46 | 18:00
Tongi Millgate | 53 | 10:00 | Goalpara | 26 | 13:00 | Kurigram | 45 | 19:00
Valuka | 106 | 9:00 | Central S/S | 56 | 19:00 | Mithapukur | 34 | 14:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-01-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 418 | 24:00 | 409 | 12:00 | Kaliakoir | 414 | 0.16667 | 396 | 0.5
| Bheramara | 408 | 24:00 | 398 | 7:00 | Bhulta | 411 | 24:00 | 384 | 0.5
| Ashuganj(N) | 412 | 23:00 | 386 | 12:00 | Gopalganj | 413 | 0.625 | 402 | 0.375
| Payra | 414 | 20:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 245 | 1:00 | 238 | 7:00 | Hathazari | 244 | 19:00 | 237 | 1:00
| Ishurdi | 244 | 1:00 | 233 | 9:00 | Megnaghat | 245 | 1:00 | 241 | 12:00
| Ashuganj | 251 | 1:00 | 243 | 12:00 | Fenchuganj | 248 | 1:00 | 242 | 11:00
| Serajganj | 243 | 23:00 | 237 | 8:00 | Siddhirganj | 243 | 1:00 | 233 | 11:00
| Baghabari | 242 | 2:00 | 235 | 7:00 | Maniknagar | 241 | 1:00 | 231 | 12:00
| Barapukuria | 237 | 4:00 | 230 | 18:00 | Agargaon | 244 | 3:00 | 232 | 12:00
| Bogra | 240 | 1:00 | 233 | 13:00 | Barisal | 243 | 23:00 | 235 | 21:00
| Rajshahi | 242 | 23:00 | 231 | 8:00 | Bhola 225 MW | 247 | 4:00 | 240 | 1:00
| Khulna South | 248 | 4:00 | 232 | 12:00 | AKSML | 245 | 23:00 | 237 | 9:00
| Rampura | 241 | 23:00 | 231 | 12:00 | BSRM | 244 | 23:00 | 235 | 12:00
| Haripur | 241 | 23:00 | 231 | 12:00 | Bibiyana | 244 | 2:00 | 238 | 16:00
| Hasnabad | 243 | 18:30 | 237 | 5:00 | Bhulta | 243 | 1:00 | 232 | 12:00
| Shyampur | 243 | 20:00 | 231 | 12:00 | Ashuganj (S) | 247 | 5:00 | 238 | 12:00
| Aminbazar | 245 | 1:00 | 236 | 2:00 | Kaliakoir | 243 | 21:00 | 232 | 12:00
| Tongi | 241 | 19:30 | 235 | 10:00 | GPH | 244 | 15:00 | 236 | 12:00
| Comilla (N) | 243 | 1:00 | 233 | 12:00 | Jhenaidah | 243 | 4:00 | 230 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 22:00 | 131 | 12:00 | Kachua | 144 | 0.041667 | 138 | 0.5
| Munsiganj | 142 | 23:00 | 135 | 12:00 | Madanhat | 142 | 0.58333 | 137 | 0.375
| Sonargaon | 140 | 19:30 | 133 | 7:00 | Hathazari | 143 | 0.79167 | 137 | 0.41667
| Shyampur | 136 | 21:00 | 128 | 12:00 | Khulshi | 141 | 0.625 | 135 | 0.5
| Bhulta | 133 | 1:00 | 129 | 11:00 | Halishahar | 142 | 0.625 | 135 | 0.66667
| Madanganj | 140 | 19:30 | 133 | 12:00 | Baraulia | 142 | 0.77083 | 136 | 0.41667
| Shitalakhya | 142 | 20:00 | 134 | 12:00 | Sikalbaha | 143 | 0.95833 | 137 | 0.66667
| Rahim steal | 138 | 20:00 | 132 | 12:00 | Dohazari | 140 | 0.16667 | 135 | 0.29167
| Matuail | 139 | 22:00 | 131 | 12:00 | Cox'sbazar | 128 | 0.375 | 117 | 0.75
| Ghorasal | 143 | 1:00 | 142 | 9:00 | Chandraghona | 143 | 0.79167 | 137 | 0.41667
| Narsinghdi | 138 | 23:00 | 130 | 12:00 | Kaptai | 142 | 0.041667 | 141 | 0.54167
| Haripur (SBU) | 138 | 2:00 | 132 | 12:00 | A. Khaer Stl. | 141 | 0.75 | 137 | 0.5
| Sreenagar | 139 | 20:00 | 130 | 12:00 | Bakulia | 142 | 0.79167 | 136 | 0.66667
| Ullon | 143 | 19:00 | 130 | 12:00 | Julda | 143 | 0.79167 | 138 | 0.5
| Hasnabad | 139 | 3:00 | 132 | 12:00 | TK Chemical | 143 | 0.79167 | 137 | 0.5
| Magbazar | 142 | 4:00 | 138 | 0:00 | Modern Steel | 142 | 0.16667 | 138 | 0.54167
| Maniknagar | 136 | 4:00 | 129 | 17:00 | Shahmirpur | 142 | 0.8125 | 137 | 0.66667
| Bangabhaban | 139 | 8:00 | 130 | 12:00 | Khagrachhari | 141 | 0.33333 | 138 | 0.5
| Motijheel | 137 | 7:00 | 130 | 12:00 | Matarbari | 130 | 0.083333 | 125 | 0.66667
| Narinda | 137 | 7:00 | 130 | 12:00 | Baroiar Hat | 142 | 1:00 | 137 | 12:00
| Kazla | 139 | 20:00 | 132 | 13:00 | Rangamati | 143 | 23:00 | 137 | 12:00
| Dhanmondi | 140 | 23:00 | 131 | 12:00 | Agrabad | 141 | 4:00 | 136 | 0.66667
| Lalbag | 140 | 1:00 | 132 | 9:00 | Goalpara S/S | 141 | 23:00 | 133 | 0.29167
| Madartek | 142 | 6:00 | 0 | 0:00 | Khulna Central S/S | 139 | 1:00 | 131 | 0.33333
| Dhaka University | 137 | 1:00 | 130 | 12:00 | Noapara | 140 | 2:00 | 131 | 0.29167
| Aftabnagar | 137 | 1:00 | 130 | 12:00 | Jessore | 139 | 0.95833 | 130 | 0.5
| Fatullah | 140 | 4:00 | 132 | 9:00 | Benapol | 138 | 3:00 | 129 | 0.33333
| Nawabganj | 138 | 19:30 | 131 | 12:00 | Jhenida(Old) | 139 | 0.041667 | 132 | 0.29167
| Keraniganj | 139 | 20:00 | 130 | 12:00 | Bottail | 140 | 0.041667 | 132 | 0.375
| Banani | 138 | 4:00 | 130 | 12:00 | G.K Project | 140 | 0.16667 | 135 | 0.375
| Mirpur | 137 | 4:00 | 127 | 12:00 | Faridpur | 140 | 0.16667 | 135 | 0.375
| Kalyanpur | 137 | 23:00 | 129 | 12:00 | Rajbari | 139 | 0.16667 | 130 | 0.29167
| Gulshan | 137 | 2:00 | 130 | 16:00 | Madaripur | 142 | 6:00 | 137 | 0.875
| Uttara | 138 | 1:00 | 130 | 12:00 | Shariyatpur S/S | 142 | 0.16667 | 137 | 0.5
| Uttara New | 139 | 23:00 | 132 | 12:00 | Gopalganj | 141 | 1:00 | 135 | 0.375
| Kamrangirchar | 139 | 20:00 | 132 | 13:00 | Bagerhat | 138 | 13:00 | 132 | 0.5
| Savar | 137 | 6:00 | 128 | 12:00 | Mongla | 138 | 23:00 | 131 | 8:00
| Bhasantec | 135 | 1:00 | 127 | 12:00 | Satkhira | 139 | 0.95833 | 130 | 16:00
| Agargaon | 136 | 1:00 | 130 | 13:00 | Gallamari | 140 | 1:00 | 133 | 0.375
| Satmosjid | 135 | 1:00 | 128 | 12:00 | Magura | 141 | 0.16667 | 131 | 0.5
| Old Tongi | 140 | 21:00 | 134 | 12:00 | Narail | 139 | 3:00 | 129 | 0.5
| Kabirpur | 138 | 23:00 | 131 | 17:00 | Chuadanga | 137 | 6:00 | 129 | 0.5
| Bashundara | 139 | 22:00 | 132 | 12:00 | Barisal(N) | 143 | 3:00 | 135 | 21:00
| Manikgong | 136 | 0:00 | 129 | 17:00 | Barisal (S) | 142 | 0.16667 | 136 | 0.77083
| Joydevpur | 144 | 4:00 | 139 | 12:00 | Patuakhali(S) | 141 | 0.125 | 133 | 0.875
| New Tongi | 140 | 21:00 | 133 | 12:00 | Bhandaria | 140 | 0.20833 | 134 | 0.83333
| Kodda | 138 | 0:00 | 131 | 0:00 | Borguna | 141 | 4:00 | 135 | 21:00
| Dhamrai | 140 | 23:00 | 131 | 12:00 | Jhenaidah(New) | 140 | 4:00 | 132 | 9:00
| Rajendrapur | 139 | 22:00 | 131 | 13:00 | Ishurdi | 140 | 1:00 | 134 | 12:00
| Purbachal | 138 | 1:00 | 130 | 12:00 | Ruppur Paromanobik | 138 | 1:00 | 136 | 13:00
| Tongi Millgate | 139 | 21:00 | 132 | 12:00 | Natore | 140 | 1:00 | 135 | 8:00
| Valuka | 130 | 2:00 | 119 | 9:00 | Bogra | 141 | 4:00 | 136 | 13:00
| Tangail | 136 | 23:00 | 129 | 9:00 | Noagaon | 136 | 5:00 | 130 | 8:00
| Mymensing | 132 | 23:00 | 124 | 18:00 | Rajshahi | 139 | 19:30 | 132 | 8:00
| Kishorganj | 133 | 1:00 | 127 | 18:00 | Rajshahi New | 139 | 20:00 | 131 | 8:00
| Netrokona | 131 | 23:00 | 121 | 18:00 | C.Nawabganj | 138 | 20:00 | 129 | 12:00
| Jamalpur | 140 | 14:00 | 130 | 7:00 | Amnura | 139 | 20:00 | 130 | 8:00
| Sherpur | 139 | 20:00 | 127 | 7:00 | Pabna | 141 | 4:00 | 133 | 12:00
| Srimongal | 140 | 1:00 | 136 | 12:00 | Shahjadpur | 144 | 19:30 | 140 | 12:00
| Shahjibazar | 137 | 2:00 | 134 | 12:00 | Serajganj | 141 | 1:00 | 135 | 8:00
| Fenchuganj | 138 | 1:00 | 134 | 13:00 | Niyamatpur | 135 | 19:30 | 126 | 9:00
| Khulawara | 138 | 4:00 | 135 | 11:00 | Joypurhat | 138 | 1:00 | 131 | 9:00
| Sylhet | 135 | 1:00 | 133 | 12:00 | Sherpur(Bogura) | 141 | 1:00 | 136 | 16:00
| Chatak | 136 | 1:00 | 133 | 11:00 | Mohastangor | 141 | 4:00 | 134 | 16:00
| Sunamganj | 134 | 1:00 | 131 | 12:00 | Bangura | 143 | 1:00 | 137 | 12:00
| Biani Bazar | 136 | 3:00 | 132 | 18:00 | Rangpur | 138 | 3:00 | 129 | 18:00
| Comilla(s) | 132 | 4:00 | 125 | 12:00 | Lalmonirhat | 136 | 2:00 | 130 | 18:30
| Comilla(n) | 146 | 1:00 | 141 | 12:00 | Saidpur | 136 | 6:00 | 124 | 18:00
| Chandpur | 146 | 5:00 | 141 | 12:00 | Purbasadipur | 133 | 2:00 | 123 | 18:30
| Feni | 143 | 1:00 | 138 | 12:00 | Thakurgaon | 133 | 4:00 | 119 | 18:00
| Chowmuhani | 142 | 8:00 | 137 | 12:00 | Palashbari | 138 | 3:00 | 132 | 18:00
| Ashuganj | 140 | 1:00 | 139 | 12:00 | Barapukuria | 137 | 0.16667 | 130 | 0.75
| Daudkandi | 144 | 18:30 | 133 | 12:00 | Panchagar | 134 | 0.16667 | 123 | 0.77083
| B.Baria | 136 | 1:00 | 133 | 11:00 | Joldhaka | 134 | 0.125 | 124 | 0.75
| Ramganj | 142 | 4:00 | 136 | 12:00 | Kurigram | 137 | 0.083333 | 128 | 0.75
| Chaddagram | 144 | 2:00 | 140 | 12:00 | Mithapukur | 140 | 1:00 | 133 | 18:00
| PHP | 143 | 4:00 | 139 | 10:00

## L-Curve
Date | 2022-01-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 204 | 5032 | 2411 | 7443 |  |  |  | QF-LDC-11
0:30 | 104 | 5005.5 | 2275 | 7280.5 | Date: | 2022-01-11
1:00 | 4 | 4979 | 2139 | 7118
1:30 | 19 | 4769.5 | 2115.5 | 6885
2:00 | 34 | 4560 | 2092 | 6652
2:30 | 74 | 4500.5 | 2037.5 | 6538 | [5 empty] | Gen. at Eve. Peak | 9726 | 9726 MW (19:00 )
3:00 | 114 | 4441 | 1983 | 6424 | [6 empty] | 19:00
3:30 | 111 | 4372 | 1957.5 | 6329.5 | [5 empty] | Gen. at Day Peak | 8457 | 8457 MW (12:00 )
4:00 | 108 | 4303 | 1932 | 6235 | [6 empty] | 12:00
4:30 | 114 | 4297.5 | 1925 | 6222.5 | [5 empty] | Highest Generation | 9726
5:00 | 120 | 4292 | 1918 | 6210 | [6 empty] | 19:00
5:30 | 101 | 4364.5 | 1959.5 | 6324
6:00 | 82 | 4437 | 2001 | 6438
6:30 | 47 | 4587 | 2058.5 | 6645.5
7:00 | 12 | 4737 | 2116 | 6853
7:30 | 26 | 4935 | 2242.5 | 7177.5
8:00 | 40 | 5133 | 2369 | 7502
8:30 | 78 | 5356.5 | 2441.5 | 7798
9:00 | 116 | 5580 | 2514 | 8094
9:30 | 167 | 5612 | 2514 | 8126
10:00 | 218 | 5644 | 2514 | 8158
10:30 | 214 | 5639.5 | 2501 | 8140.5
11:00 | 210 | 5635 | 2488 | 8123
11:30 | 243 | 5755 | 2535 | 8290
12:00 | 276 | 5875 | 2582 | 8457
12:30 | 258 | 5915.5 | 2618 | 8533.5
13:00 | 240 | 5956 | 2654 | 8610
13:30 | 242 | 5830 | 2603 | 8433
14:00 | 244 | 5704 | 2552 | 8256
14:30 | 289 | 5663.5 | 2493.5 | 8157
15:00 | 334 | 5623 | 2435 | 8058
15:30 | 232 | 5650.5 | 2310 | 7960.5
16:00 | 130 | 5678 | 2185 | 7863
16:30 | 156 | 5722.5 | 2281.5 | 8004
17:00 | 182 | 5767 | 2378 | 8145
17:30 | 106 | 6174.5 | 2636 | 8810.5
18:00 | 30 | 6582 | 2894 | 9476
18:30 | 28 | 6613 | 2988 | 9601
19:00 | 26 | 6644 | 3082 | 9726
19:30 | 32 | 6494 | 3113 | 9607
20:00 | 42 | 6344 | 3073 | 9417 |  |  |  | Executive Engineer
20:30 | 45 | 6262 | 2965 | 9227 |  |  |  | Network Operation Division
21:00 | 48 | 6180 | 2857 | 9037
21:30 | 114 | 5972.5 | 2841.5 | 8814
22:00 | 180 | 5765 | 2826 | 8591 |  |  |  |  | Page 6 of 7
22:30 | 218 | 5547.5 | 2748 | 8295.5
23:00 | 256 | 5330 | 2670 | 8000
23:30 | 230 | 5181 | 2540.5 | 7721.5
24:00 | 204 | 5032 | 2411 | 7443
9726 MW (19:00 )
8457 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-01-11 |  | Energy |  | 193581459
[13 empty] | 2022-01-11 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 1852 | 479 | 1532 | 0 | 2659 | 579 | 82 | 0 | 178 | 82 | 0 | 0
0:30 | 1985.5 | 479.5 | 1581.5 | 0 | 2409.5 | 554.5 | 81 | 0 | 109 | 80 | 0 | 0 | Date: | 2022-01-11
1:00 | 2119 | 480 | 1631 | 0 | 2160 | 530 | 80 | 0 | 40 | 78 | 0 | 0
1:30 | 2114 | 479.5 | 1628.5 | 0 | 1966.5 | 519.5 | 80 | 0 | 20 | 77 | 0 | 0 | [8 empty] | Total Energy | 193.5815 | Total Energy Gen 193.581 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.581 MKWHr
2:00 | 2109 | 479 | 1626 | 0 | 1773 | 509 | 80 | 0 | 0 | 76 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2114 | 479 | 1626.5 | 0 | 1661.5 | 504 | 79 | 0 | 0 | 74 | 0 | 0 | [8 empty] | Energy Requirement | 193.5815
3:00 | 2119 | 479 | 1627 | 0 | 1550 | 499 | 78 | 0 | 0 | 72 | 0 | 0
3:30 | 2122.5 | 479.5 | 1607.5 | 0 | 1478 | 494.5 | 77 | 0 | 0 | 70.5 | 0 | 0 | [6 empty] | Shortage
4:00 | 2126 | 480 | 1588 | 0 | 1406 | 490 | 76 | 0 | 0 | 69 | 0 | 0
4:30 | 2127.5 | 479.5 | 1577.5 | 0 | 1407 | 485 | 77 | 0 | 0 | 69 | 0 | 0
5:00 | 2129 | 479 | 1567 | 0 | 1408 | 480 | 78 | 0 | 0 | 69 | 0 | 0
5:30 | 2126.5 | 479.5 | 1624 | 0 | 1461 | 485 | 81 | 0 | 0 | 67 | 0 | 0
6:00 | 2124 | 480 | 1681 | 0 | 1514 | 490 | 84 | 0 | 0 | 65 | 0 | 0
6:30 | 2136 | 479.5 | 1635 | 0 | 1750 | 495 | 82 | 0 | 0 | 66.5 | 1.5 | 0 |  |  |  |  | Coal
7:00 | 2148 | 479 | 1589 | 0 | 1986 | 500 | 80 | 0 | 0 | 68 | 3 | 0
7:30 | 2138 | 479.5 | 1643 | 0 | 2235.5 | 510 | 81 | 0 | 0 | 74.5 | 16 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2128 | 480 | 1697 | 0 | 2485 | 520 | 82 | 0 | 0 | 81 | 29 | 0
8:30 | 2130.5 | 479.5 | 1687 | 0 | 2739 | 525 | 81.5 | 0 | 27.5 | 85.5 | 42.5 | 0
9:00 | 2133 | 479 | 1677 | 0 | 2993 | 530 | 81 | 0 | 55 | 90 | 56 | 0
9:30 | 2137 | 481.5 | 1638.5 | 0 | 3039.5 | 515 | 79.5 | 0 | 69 | 90.5 | 75.5 | 0
10:00 | 2141 | 484 | 1600 | 0 | 3086 | 500 | 78 | 0 | 83 | 91 | 95 | 0
10:30 | 2095 | 484.5 | 1577.5 | 0 | 3093.5 | 500 | 77 | 0 | 105 | 93 | 115 | 0
11:00 | 2049 | 485 | 1555 | 0 | 3101 | 500 | 76 | 0 | 127 | 95 | 135 | 0
11:30 | 2072.5 | 484.5 | 1619 | 0 | 3145.5 | 500 | 81 | 0 | 153 | 96 | 138.5 | 0
12:00 | 2096 | 484 | 1683 | 0 | 3190 | 500 | 86 | 0 | 179 | 97 | 142 | 0
12:30 | 2064 | 481.5 | 1677 | 74 | 3188.5 | 519.5 | 81.5 | 0 | 213.5 | 96 | 138 | 0
13:00 | 2032 | 479 | 1671 | 148 | 3187 | 539 | 77 | 0 | 248 | 95 | 134 | 0
13:30 | 2032 | 479 | 1671 | 148 | 3187 | 539 | 77 | 0 | 248 | 95 | 134 | 0
14:00 | 2032 | 479 | 1671 | 148 | 3187 | 539 | 77 | 0 | 248 | 95 | 134 | 0
14:30 | 1993.5 | 479 | 1559.5 | 74 | 3166.5 | 519.5 | 78.5 | 0 | 264.5 | 93 | 106 | 0
15:00 | 1955 | 479 | 1448 | 0 | 3146 | 500 | 80 | 0 | 281 | 91 | 78 | 0
15:30 | 1997 | 478.5 | 1450 | 0 | 3017 | 500 | 82.5 | 0 | 283.5 | 92.5 | 59.5 | 0
16:00 | 2039 | 478 | 1452 | 0 | 2888 | 500 | 85 | 0 | 286 | 94 | 41 | 0
16:30 | 2043 | 477.5 | 1533 | 0 | 2930.5 | 500 | 85 | 0 | 316.5 | 94.5 | 24 | 0
17:00 | 2047 | 477 | 1614 | 0 | 2973 | 500 | 85 | 0 | 347 | 95 | 7 | 0
17:30 | 2055.5 | 477 | 1603.5 | 408 | 3168 | 509 | 85 | 0 | 400 | 101 | 3.5 | 0
18:00 | 2064 | 477 | 1593 | 816 | 3363 | 518 | 85 | 0 | 453 | 107 | 0 | 0
18:30 | 2079.5 | 477 | 1580 | 870 | 3389.5 | 558.5 | 85 | 0 | 457.5 | 104 | 0 | 0
19:00 | 2095 | 477 | 1567 | 924 | 3416 | 599 | 85 | 0 | 462 | 101 | 0 | 0
19:30 | 2108 | 477 | 1588 | 923 | 3256 | 609 | 85 | 0 | 460 | 101 | 0 | 0
20:00 | 2106 | 479 | 1542 | 927 | 3135 | 609 | 86 | 0 | 432 | 101 | 0 | 0
20:30 | 2139.5 | 479 | 1570 | 650.5 | 3159.5 | 619 | 85.5 | 0 | 424 | 100 | 0 | 0
21:00 | 2173 | 479 | 1598 | 374 | 3184 | 629 | 85 | 0 | 416 | 99 | 0 | 0
21:30 | 2154.5 | 478.5 | 1609.5 | 187 | 3177 | 624 | 82.5 | 0 | 407 | 94 | 0 | 0
22:00 | 2136 | 478 | 1621 | 0 | 3170 | 619 | 80 | 0 | 398 | 89 | 0 | 0
22:30 | 2018 | 478.5 | 1588.5 | 0 | 3086.5 | 609 | 81 | 0 | 348 | 86 | 0 | 0
23:00 | 1900 | 479 | 1556 | 0 | 3003 | 599 | 82 | 0 | 298 | 83 | 0 | 0
23:30 | 1876 | 479 | 1544 | 0 | 2831 | 589 | 82 | 0 | 238 | 82.5 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 27.8° C
24:00 | 1852 | 479 | 1532 | 0 | 2659 | 579 | 82 | 0 | 178 | 82 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 193.581 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.581 MKWHr
Note on W13: Author:

## Generation
g | 2022-01-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 38 | 36 | 38 | 44 | 40 | 42 | 41 | 38 | 36 | 46 | 37 | 33 | 40 | 45 | 45 | 45 |  | 45 | 45 | 46 | 45 | 40 | 42 | 42 | 962400
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 980000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 2 | 8 | 8 | 15 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 228529
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 4 | 7 | 10 | 11 | 14 | 19 | 17 | 13 | 7 | 1 | [9 empty] | 111780
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 |  | 0 | 284118
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 51 | 81 | 85 | 101 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 68 | 68 | 68 | 68 | 68 | 68 | 1798174
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 120 |  | 150 | 150 | 150 |  |  |  |  | 444672
14 | Titas 50 MW Peaking PP | [12 empty] | 12 | 33 | 41 | 41 | 35 | 42 |  | 44 | 50 | 33 | 33 | 33 | 33 | 33 | 410704
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 95 | 95 | 95 | 95 | 95 | 200 | 300 | 300 | 295 | 286 | 288 | 300 | 300 | 300 | 300 | 300 | 300 |  | 293 | 300 | 296 | 300 | 300 | 300 | 300 | 6004252
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 220 | 220 | 220 | 220 | 225 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 200 | 4986000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1953510
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 149832
33 | Ashuganj 225 MW CCPP | 167 | 170 | 177 | 181 | 181 | 173 | 181 | 168 | 159 | 166 | 164 | 155 | 144 | 165 | 170 | 169 | 159 | 173 |  | 163 | 168 | 174 | 174 | 181 | 199 | 209 | 4107000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 280 | 280 | 295 | 300 | 275 | 285 | 280 | 275 | 345 | 275 | 275 | 280 | 275 | 280 | 270 |  | 295 | 295 | 290 | 325 | 280 | 265 | 265 | 7118000
| Ashuganj 450 MW CCPP(North) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3586000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143520
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 170 |  | 170 | 160 | 160 | 160 | 160 | 160 | 160 | 4180200
41 | Haripur 360MW CCPP(HPL) | 181 | 187 | 193 | 193 | 188 | 187 | 173 | 167 | 156 | 154 | 155 | 151 | 153 | 148 | 134 | 132 | 132 | 132 |  | 130 | 128 | 131 | 130 | 130 | 126 | 125 | 3742000
42 | RPCL 210MW CCPP | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 51 | 50 | 49 | 49 | 49 | 49 | 50 | 50 |  | 50 | 51 | 50 | 50 | 50 | 51 | 52 | 1191360
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 4 | 8 | 13 | 26 | 19 | 18 | 20 | 12 | 6 | 1 | [9 empty] | 156760
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 1014000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 66 | 67 | 65 | 70 | 68 | 68 | 68 | 65 | 62 | 62 | 40 | 40 | 66 | 66 | 40 |  | 40 | 40 | 40 | 69 | 68 | 68 | 68 | 1460256
48 | Shahjibazar 86MW PP (Shahjibazar) | 82 | 82 | 82 | 82 | 82 | 81 | 75 | 76 | 76 | 76 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 79 | 1876800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 126 | 126 | 126 | 126 | 126 | 126 |  | 126 | 126 | 126 | 126 | 126 | 126 | 118 | 3277880
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251460
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [7 empty] | 2 | 5 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 144768
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 53 | 53 | 53 | 51 | 51 | 51 | 51 | 1218000
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 441624
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 290 | 290 | 275 | 295 | 270 | 315 | 310 | 290 | 290 | 300 | 310 | 270 | 300 | 295 | 320 | 295 |  | 290 | 300 | 280 | 295 | 300 | 290 | 280 | 7237000
| Bibiyana South 400 MW | 400 | 400 | 400 | 401 | 400 | 399 | 400 | 400 | 400 | 400 | 400 | 395 | 400 | 360 | 340 | 400 | 394 | 398 |  | 400 | 400 | 400 | 400 | 401 | 190 | 181 | 9158100
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 884631
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 532320
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 21 | 18 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 452880
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 422784
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 431172
63 | Impoprt (Tripura) | 78 | 76 | 72 | 69 | 69 | 65 | 68 | 81 | 90 | 91 | 95 | 97 | 95 | 98 | 91 | 94 | 95 | 107 |  | 101 | 101 | 101 | 99 | 89 | 83 | 82 | 2143680
64 | Malancha, Ctg. EPZ (United) | 33 | 34 | 34 | 34 | 34 | 35 | 31 | 9 | 2 | 2 | 2 | 2 | 6 | 3 | 2 | 2 | 2 | 5 |  | 10 | 8 | 10 | 20 | 29 | 33 | 26 | 408480
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 499860
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  | 11 | 242280
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 18 | 33 | 33 | 21 | 17 | 16 | 16 | 18 | 16 | 16 | 16 | 24 | 20 |  | 16 | 16 | 16 | 16 | 33 | 33 | 33 | 595400
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 215560
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 201600
71 | Maona 33 MW PP(Summit) | 25 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 623000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 |  | 32 | 32 | 30 | 30 | 15 | 16 | 12 | 756500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [17 empty] | 17 |  | 17 | 17 |  |  |  |  | 0 | 46740
| Chowmuhani 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 63 | 98 | 98 | 98 | 98 | 98 | 103 | 110 | 108 | 112 | 108 |  | 109 | 110 | 109 | 110 | 110 | 115 | 85 | 2204160
| Manikgonj 162MW PP(MPGL) | 162 | 54 | 54 | 54 | 54 | 56 | 127 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3444480
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 2 | 26 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 25 | 0 | 722880
79 | Kodda 150MW PP | [8 empty] | 48 | 64 | 98 | 136 | 136 | 98 | 64 | 64 | 64 | 98 |  | 98 | 98 | 98 | 82 | 64 | 48 | 16 | 1280640
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | [6 empty] | 5 | 8 | 8 | 8 | 12 | 24 | 24 | 24 | 24 | 24 | 28 | 43 |  | 25 | [6 empty] | 280411
| Gazipur 100 MW PP | 105 | 50 | 50 | 50 | 50 | 90 | 92 | 90 | 90 | 90 | 90 | 90 | 90 | 102 | 100 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2233200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26041
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1371799
| Karnaphuli Power Ltd. | 110 | 51 | 51 | 51 | 51 | 51 | 51 | 76 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2333444
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 21 | 36 | 36 | 36 | 37 | 48 | 52 | 61 | 62 | 48 | 60 |  | 61 | 61 | 61 | 60 | 60 | 61 | 61 | 893433
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 60 | 54 | 54 | 55 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2447040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 50 |  | 100 | 20 | 10 | 40 | 40 | 10 | 10 | 257640
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1252696
94 | Gagnagar 102 MW PP (Digital Power) | 32 | [5 empty] | 24 | 64 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 82 | 82 | 82 | 64 | 1664496
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 14 | 20 | 24 | 20 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 514560
96 | Chattogram 108 MW PP (ECPV) | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 80 | 82 | 82 | 81 | 76 |  | 78 | 83 | 83 | 83 | 85 | 90 | 89 | 2000640
97 | katpotti 52 MW | 47 | 48 | 48 | 12 | 12 | 12 | 12 | 22 | 47 | 48 | 48 | 44 | 45 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 999888
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | [5 empty] | 6 | 25 | 40 | 48 | 55 | 55 | 55 | 55 | 55 | 42 | 40 | 40 |  | 40 | 40 | 40 | 55 | 55 | 55 | 30 | 856404
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1233594
101 | Kushiara 163 MW CCPP (KP) | 150 | 110 | 110 | 110 | 110 | 163 | 130 | 163 | 163 | 163 | 130 | 163 | 163 | 130 | 110 | 110 | 130 | 110 |  | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 3342109
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 6100
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 861408
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 83 |  |  |  |  | 304 |  | 302 | 301 | 305 | 194 |  |  | 0 | 1148420
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 80 |  | 100 | 100 | 100 | 80 |  |  | 0 | 386616
106 | Mymensingh 200 MW PP (United) | 193 | 192 | 150 | 120 | 120 | 120 | 140 | 161 | 184 | 184 | 190 | 180 | 180 | 184 | 184 | 187 | 187 | 189 |  | 189 | 191 | 191 | 191 | 191 | 190 | 191 | 4207200
112 | Aurahati 100MW PP (Aggreko) | [12 empty] | 26 |  |  |  |  | 100 |  | 100 | 100 | 100 | 100 |  |  | 0 | 444799
114 | Kodda 149 MW PP Unit-1 (Summit) | [5 empty] | 1 | 16 | 42 | 133 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 117 | 75 | 2381470
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2116800
116 | Chandpur 200MW (Desh energy) | [12 empty] | 12 | 34 | 17 | 17 | 22 | 51 |  | 34 | 34 | 34 | 34 | 34 | 17 | 0 | 355200
117 | Ashuganj 150MW PP (Midland) | 143 | 142 | 142 | 148 | 150 | 142 | 138 | 132 | 135 | 135 | 127 | 125 | 128 | 127 | 125 | 122 | 127 | 130 |  | 135 | 142 | 138 | 138 | 138 | 143 | 142 | 3263490
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 49 | 94 | 93 | 96 | 108 | 108 | 108 | 107 | 98 | 108 | 115 |  | 115 | 115 | 115 | 115 | 107 | 65 | 16 | 1693200
| Anwara 300 MW PP (United) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 65 | 65 | 120 | 140 | 155 | 100 | 100 | 100 | 100 | 150 |  | 135 | 95 | 30 | 30 | 30 | 30 | 30 | 1839164
| Juldah unit-2 (Acorn) | 100 | 100 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 80 | 100 | 100 | 100 | 100 | 2209920
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 115 | 100 | 100 | 105 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2760000
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 437760
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 4 |  | 13 | 25 | 30 | 21 | 23 | 10 | 7 | 1 | [9 empty] | 118738
Chandpur 115(Doreen)
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 1189800
120 | Eastern Zone Total | 4979 | 4560 | 4441 | 4303 | 4292 | 4437 | 4737 | 5133 | 5580 | 5644 | 5635 | 5875 | 5956 | 5704 | 5623 | 5678 | 5767 | 6582 |  | 6644 | 6494 | 6344 | 6180 | 5765 | 5330 | 5032 | 133090680
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [11 empty] | 2 | 4 | 4 | 8 | 13 | 17 | 27 |  | 34 | 34 | 30 | 30 | 29 | 29 | 29 | 229440
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 |  |  |  |  | 1 | 16 | 64 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 35 | 35 | 105 |  | 105 | 105 | 105 | 105 | 105 | 70 | 17 | 1629600
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 15 | 36 | 51 | 62 | 67 | 64 | 52 | 37 | 18 | 4 | [9 empty] | 414000
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 200 | 180 | 180 | 180 | 180 | 180 | 200 | 222 | 222 | 222 | 222 | 210 | 200 | 170 | 170 | 202 | 220 |  | 221 | 221 | 221 | 221 | 220 | 220 | 220 | 4902764
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 272746
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 92 | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2212350
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 16 | 16 | 16 | 17 | 14 | 14 | 15 | 15 | 14 | 15 | 15 | 16 | 14 | 14 | 14 | 20 |  | 21 | 22 | 22 | 22 | 22 | 20 | 19 | 403900
141 | Noapara 100 MW PP (Bangla Trac) | [12 empty] | 39 |  |  |  |  | 47 |  | 100 | 100 | 100 |  |  |  | 0 | 357120
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 15 |  | 15 | 7 | [5 empty] | 22784
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [9 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [8 empty] | 0 | 141552
146 | Bheramara HVDC | 480 | 479 | 479 | 480 | 479 | 480 | 479 | 480 | 479 | 484 | 485 | 484 | 479 | 479 | 479 | 478 | 477 | 477 |  | 477 | 477 | 479 | 479 | 478 | 479 | 479 | 11642909
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 330 | 310 | 300 | 290 | 280 | 290 | 300 | 320 | 330 | 300 | 300 | 300 | 340 | 320 | 300 | 300 | 300 | 320 |  | 400 | 410 | 410 | 430 | 420 | 400 | 380 | 8856000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 200 | 200 | 200 | 198 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4856200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 522896
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 1 | 2 | 3 | 3 | 2 | 1 | 0 | 0 | [9 empty] | 17040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 157 | 151 | 154 | 152 | 150 | 160 | 153 | 176 | 203 | 215 | 178 | 169 | 198 | 193 | 175 | 174 | 178 | 174 |  | 189 | 193 | 193 | 195 | 194 | 180 | 151 | 4466218
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 339 | 378 | 384 | 345 | 344 | 385 | 378 | 415 | 395 | 340 | 326 | 414 | 398 | 285 | 302 | 313 | 398 | 405 |  | 377 | 401 | 370 | 404 | 394 | 341 | 335 | 8883854
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [10 empty] | 5 | 17 | 31 | 36 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 39 | 38 |  | 420194
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515040
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 97866
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  |  | 8 | 34 |  | 50 | 50 | 50 | 50 | 43 | 43 | 24 | 527832
167 | Katakhali 50 MW Peaking PP | [8 empty] | 7 | 19 | 24 | 24 | 24 | 30 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 |  |  | 350800
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 678720
170 | Chapainawabganj 100 MW Peaking PP | 40 | [11 empty] | 41 | 48 | 48 | 48 | 60 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 850072
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 165 |  | 172 | 172 | 172 |  |  |  | 0 | 550306
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 35 | 35 | 35 | 37 | 70 | 80 | 112 | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 37 | 91 |  | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 2097504
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 50 | 35 | 35 | 35 | 50 | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 60 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2193216
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 56 | 54 | 54 | 56 | 111 | 112 | 112 | 112 | 112 | 111 | 62 | 93 | 103 | 39 | 90 | 113 |  | 113 | 113 | 113 | 113 | 112 | 112 | 112 | 2307331
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 2 | 3 | 4 | 4 | 4 | 2 | 2 | 2 | 0 | [9 empty] | 23485
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 8 | 10 | 7 |  |  | 10 | 13 | [9 empty] | 0 | 47040
178