## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-06-24 | Monday
|  | Date (day): | 2019-06-24 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13220 | MW |  |  | (b) At Evening Peak Hour : |  | 15144 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-06-23 | 2019-06-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Engine problem
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 219 | 229 | 229 | 229
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 200 | 200
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 240 | 240 | 0 | 0 |  | 365 | Under maint. |  | 28/06/2019
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 50 | 50 | 28 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 71 | 0 | 108 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 339 | 338 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 26 | 26 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 341 | 302 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 430 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 300 | 272 | 300 | 300
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 13 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 40 | 40 | 170 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 97 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 64 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 49 | 49 | 49
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 125 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 54 | 53 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 63 | 51 | 70 | 70 |  | 38 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 57 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 49 | 50 | 50
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 14 | 45 | 100 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
37 | Gazipur 100 MW |  | HFO | RPCL | 100 MW | 105 | 105 | 89 | 106 | 105 | 105
| Dhaka area Total |  |  |  |  | 6039 | 5803 | 2885 | 3282 | 3833 | 4533 | 628 | 475
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas Shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.6 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 46 | 46 | 46
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 71 | 69 | 70 | 70 |  | 160 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 210 | 205 | 210 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 85 | 130 | 130 | 130
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 33 | 32 | 33 |  | 18 | Engine problem
47 | Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 82 | 85 | 85
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 68 | 68
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 100 | 100
51 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
52 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 27 | 10 | 35
53 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 80 | 96 | 100 | 100
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 0 | 0 | 3 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 250 | 261 | 300 | 300
| Chattogram area Total |  |  |  |  | 1866 | 1786 | 1152.6 | 1448 | 1645 | 1663 | 140 | 218
54 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 125 | 125 | 125 | 125 | 10 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 150 | 215 | 221 | 221
56 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
57 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 235 | 220 | 360 | 360
58 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 |  | 45 | Gas Line problem.
59 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 54 | 55 | 55
60 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 0 | 5 | 5 |  |  | Contract expired
61 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 54 | 55 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 40 | 40 |  | 11 | Engine problem
63 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 140 | 0 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 90 | 100 | 100
67 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 180 | 200 | 200 | 200
68 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 146 | 168 | 143 | 187
70 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
71 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
72 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
73 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1455 | 1785 | 1794 | 2238 | 413 | 56
74 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 139 | 143 | 150 | 150 | 52 |  | GT-1 Under maint.
75 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
76 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 56 | 84 | 85 | 85 |  | 10 | Engine problem
77 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
78 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 180 | 100 | 200
79 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 96 | 100 | 100 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 217.1 | 525 | 459 | 557 | 52 | 10
80 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 54 | 54 | 54 | 54
81 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 50 | 70 | 70 | 70
82 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
83 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 310 | 305 | 300 | 330
84 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
85 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
86 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 61 | 66 | 66 |  |  | FGMO
88 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 80 | 86 | 86
89 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 44 | 46 | 46
90 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 120 | 110 | 130 | 130
91 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 19 | 19
92 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 46 | 47 | 47
93 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
94 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 320 | 341 | 341
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 250 | 292 | 285 | 285 |  |  | On test
95 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1601 | 1660 | 1748 | 1778 | 0 | 0
96 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 30 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 916 | 914 | 930 | 930
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
97 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 7 | 115 | 115 | 115
98 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 22 | 0 | 40
99 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 130 | 165 | 120 | 225
100 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 80
101 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
102 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 62 | 0 | 100
104 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 72 | 105 | 105 | 105
105 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 105 | 86 | 105 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1262 | 1599 | 1415 | 1770 | 0 | 410
106 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
107 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
108 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 36 | 33 | 33
109 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 120 | 120 | 120 | 120 |  | 74 | ST-1 & 2 Under maint.
110 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 90 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 234 | 361 | 358 | 384 | 0 | 74
111 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
112 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
113 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 0 | 35
114 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 6 | 33 | 33 | 33 |  | 17 | Engine problem
115 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 43 | 32 | 40 |  | 10 | Engine problem
116 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 40 | 40
117 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 169 | 173 | 214 | 214 |  |  | FGMO
118 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 166 | 164 | 220 | 220 |  |  | FGMO
119 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 170 | 220 | 220 |  |  | FGMO
120 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 400 | 360 | 414 | 414
121 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30
122 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
123 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
124 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
125 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 8 | 50 | 52 | 52
126 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 63 | 95 | 0 | 95
127 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
128 | Confidence Bogura-2 (CPBL) |  | HFO | IPP | 113 MW | 113 | 113 | 108 | 108 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1194 | 1452 | 1632 | 1850 | 0 | 127
129 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 65 | 63 | 63
130 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 240 | 240 | 250 | 250
131 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
132 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 18
| Confidence Rangpur |  | HFO | IPP | 113 MW | 0 | 0 | 13 | 17 | 23 | 23
| Rangpur Area Total |  |  |  |  | 564 | 484 | 320 | 339 | 336 | 371 | 0 | 85
| Total |  |  |  |  | 18539 | 17996 | 10320.7 | 12451 | 13220 | 15144 | 1233 | 1455
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9929.4567 | 11979 | 12718.8483 | 14569.9121
A. |  | 2019-06-23 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 12451 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8882.26 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12451 | MW
3 | Day peak Generation : |  |  | 10320.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11979 | MW
4 | Evening peak Generation : |  |  | 12451 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 261.3087 | MKWHr | By Solar | 0.19417 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 155.3853 | MKWHr |  | By Oil: | 70.9756 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 7.3899 | MKWHr |  | By Hydro: | 1.6007 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1233 | MW | Dhaka | 4319 | 4319 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1455 | MW | Chittagong | 1271 | 1271 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2688 | MW | Khulna | 1456 | 1456 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1396.49 | MMCFD |  |  | Rajshahi | 1279 | 1279 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 106681135.736 | ii) Oil : | Taka | 486229255.95 | Comilla | 1107 | 1107 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 31985041.04 | Total | Taka | 624895432.726 | Mymensingh | 959 | 959 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.0565 | MKWHr. | Sylhet | 521 | 521 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -310 | MW (E to W) at | 21:00 | hrs | Barisal | 334 | 334 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -340 | MW at | 20:00 | hrs | Rangpur | 733 | 733 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.1° C |  |  | Total | 11979 | 11979 |  | 0
B. |  | 2019-06-24 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 36.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15144 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
4 | Reserve(Generation end) |  |  |  | 2344 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 268.6331 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9290.5 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.9433 | MKWHr. | ii) HVDC Flow at Peak Time |  | 914 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8198 | MKWHr. | iii) Maximum HVDC Flow : |  | 933 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 77.53 |  | (b) Today: | 77.53 |  | (c) Rule Curve: |  | 82.11
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-06-23
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 159 | 200 | 0 | 200 | 108 | 0 | 330 | 325 | 13 | 0 | 400 | 270 | 7 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 130 | 27 | 66 | 0 | 6 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 50 | 0 | 40 | 30 | 100 | 120 | 25 | 205 | 0 | 85 | 0 | 0 | 16 | 24 | 34 | 50 | 82 | 47 | 21 | 31 | 125 | 0 | 0 | 15 | 360 | 217 | 110 | 90 | 0 | 56 | 5 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 21 | 180 | 146 | 85 | 22 | 0 | 54 | 57 | 50 | 50 | 100 | 306 | 58 | 83 | 46 | 110 | 0 | 47 | 8 | 300 | 24 | 0 | 0 | 14 | 0 | 0 | 189 | 0 | 113 | 0 | 100 | 196 | 135 | 279 | 87 | 106 | 0 | 0 | 270 |  | 933 | 0 | 0 | 0 | 115 | 120 | 0 | 0 | 24 | 60 | 0 | 120 | 37 | 110 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 43 | 44 | 51 | 21 | 22 | 14 | 11 | 0 | 62 | 240 | 17 | 17 | 184 | 0 | 181 | 0 | 95 | 100 | 209 | 0 | 350 | 72 | 0 | 108 | 106 | 23 |  | 7961 | 3618 | 11579 | 4303 | 933 | 2272 | 2965 | 302 | 70 | 554 | 180 | 0 | 0 | 77.53
2:00 | 35 | 159 | 200 | 0 | 200 | 108 | 25 | 327 | 331 | 0 | 0 | 400 | 270 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 64 | 0 | 66 | 0 | 6 | 54 | 35 | 35 | 22 | 25 | 31 | 33 | 33 | 24 | 0 | 38 | 30 | 100 | 120 | 25 | 203 | 0 | 85 | 0 | 0 | 16 | 0 | 34 | 10 | 82 | 41 | 21 | 32 | 125 | 0 | 0 | 20 | 360 | 217 | 110 | 90 | 0 | 56 | 5 | 35 | 0 | 0 | 52 | 0 | 8 | 25 | 21 | 176 | 148 | 85 | 22 | 0 | 54 | 57 | 50 | 50 | 163 | 305 | 62 | 83 | 46 | 111 | 0 | 47 | 8 | 300 | 24 | 2 | 0 | 0 | 0 | 0 | 192 | 0 | 58 | 0 | 100 | 196 | 78 | 296 | 87 | 106 | 0 | 0 | 270 |  | 933 | 0 | 0 | 0 | 115 | 120 | 0 | 0 | 24 | 0 | 0 | 120 | 37 | 110 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 43 | 44 | 51 | 21 | 22 | 14 | 11 | 0 | 63 | 240 | 17 | 17 | 183 | 0 | 180 | 0 | 95 | 60 | 208 | 0 | 350 | 72 | 0 | 108 | 106 | 23 |  | 7674 | 3516 | 11190 | 4303 | 933 | 2367 | 2636 | 303 | 68 | 404 | 176 | 0 | 0 | 77.53
3:00 | 35 | 159 | 200 | 0 | 200 | 108 | 30 | 327 | 330 | 0 | 0 | 400 | 260 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 64 | 0 | 66 | 0 | 6 | 54 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 24 | 0 | 38 | 30 | 100 | 120 | 25 | 203 | 0 | 85 | 0 | 0 | 16 | 0 | 17 | 10 | 82 | 47 | 21 | 41 | 125 | 0 | 0 | 40 | 360 | 217 | 110 | 90 | 0 | 56 | 5 | 35 | 0 | 0 | 52 | 0 | 8 | 25 | 21 | 170 | 148 | 85 | 22 | 0 | 54 | 57 | 50 | 50 | 163 | 306 | 63 | 83 | 46 | 110 | 0 | 47 | 8 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 15 | 0 | 100 | 197 | 50 | 297 | 87 | 106 | 0 | 0 | 270 |  | 933 | 0 | 0 | 0 | 66 | 120 | 0 | 0 | 24 | 0 | 0 | 120 | 36 | 64 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 43 | 0 | 51 | 21 | 22 | 14 | 11 | 0 | 63 | 240 | 17 | 17 | 182 | 0 | 180 | 0 | 96 | 30 | 202 | 0 | 350 | 72 | 0 | 108 | 106 | 23 |  | 7567 | 3340 | 10907 | 4327 | 933 | 2370 | 2393 | 303 | 68 | 343 | 170 | 0 | 0 | 77.53
4:00 | 35 | 159 | 200 | 0 | 200 | 108 | 30 | 327 | 331 | 0 | 0 | 400 | 270 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 66 | 0 | 6 | 54 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 24 | 0 | 38 | 30 | 100 | 120 | 25 | 203 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 82 | 47 | 21 | 41 | 125 | 0 | 0 | 100 | 360 | 217 | 110 | 90 | 0 | 55 | 5 | 35 | 0 | 0 | 52 | 0 | 8 | 25 | 21 | 164 | 148 | 85 | 22 | 0 | 54 | 57 | 50 | 50 | 163 | 305 | 64 | 83 | 46 | 108 | 0 | 47 | 8 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 100 | 198 | 50 | 260 | 87 | 106 | 0 | 0 | 268 |  | 933 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 31 | 32 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 8 | 0 | 24 | 10 | 22 | 14 | 8 | 0 | 62 | 240 | 17 | 17 | 182 | 0 | 179 | 0 | 96 | 0 | 198 | 0 | 350 | 72 | 0 | 108 | 106 | 23 |  | 7525 | 3133 | 10658 | 4340 | 933 | 2365 | 2195 | 302 | 68 | 291 | 164 | 0 | 0 | 77.53
5:00 | 35 | 159 | 201 | 0 | 200 | 104 | 40 | 329 | 331 | 0 | 0 | 400 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 6 | 54 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 38 | 30 | 100 | 120 | 25 | 205 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 22 | 46 | 21 | 37 | 125 | 0 | 0 | 160 | 360 | 217 | 110 | 90 | 0 | 56 | 5 | 35 | 0 | 0 | 8 | 0 | 8 | 25 | 21 | 160 | 148 | 85 | 22 | 0 | 54 | 57 | 50 | 50 | 163 | 303 | 54 | 83 | 46 | 109 | 0 | 47 | 8 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 100 | 198 | 50 | 260 | 87 | 70 | 0 | 0 | 258 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 31 | 32 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 3 | 8 | 0 | 63 | 240 | 0 | 0 | 183 | 0 | 180 | 0 | 96 | 0 | 199 | 0 | 300 | 53 | 0 | 108 | 105 | 23 |  | 7265 | 2963 | 10228 | 4397 | 932 | 2307 | 1862 | 303 | 68 | 199 | 160 | 0 | 0 | 77.53
6:00 | 35 | 159 | 150 | 0 | 200 | 72 | 40 | 290 | 286 | 0 | 0 | 400 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 6 | 54 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 38 | 30 | 100 | 120 | 0 | 206 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 47 | 21 | 42 | 125 | 0 | 0 | 170 | 360 | 217 | 55 | 90 | 0 | 56 | 5 | 5 | 0 | 0 | 8 | 0 | 8 | 25 | 21 | 136 | 148 | 85 | 22 | 0.2 | 54 | 57 | 5 | 5 | 100 | 306 | 56 | 50 | 5 | 109 | 0 | 7 | 8 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 1.58 | 100 | 160 | 0 | 200 | 87 | 70 | 0 | 0.189 | 116 |  | 933 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 27 | 16 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 64 | 240 | 0 | 0 | 181 | 0 | 179 | 0 | 96 | 0 | 193 | 0 | 250 | 35 | 0 | 108 | 105 | 23 |  | 6291.969 | 2873 | 9164.969 | 4251 | 933 | 1817 | 1455 | 304 | 68 | 199 | 136 | 1.969 | 0 | 77.53
7:00 | 35 | 159 | 150 | 0 | 200 | 72 | 40 | 250 | 258 | 0 | 0 | 350 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 6 | 54 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 36 | 30 | 100 | 120 | 0 | 207 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 47 | 21 | 35 | 125 | 0 | 0 | 190 | 360 | 215 | 55 | 90 | 0 | 56 | 5 | 5 | 0 | 0 | 8 | 0 | 8 | 25 | 20 | 122 | 144 | 85 | 22 | 0.7 | 54 | 57 | 5 | 5 | 100 | 308 | 61 | 10 | 5 | 78 | 0 | 7 | 8 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 5.54 | 100 | 144 | 0 | 150 | 88 | 70 | 0 | 2.02 | 116 |  | 933 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 25 | 16 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 13 | 5 | 0 | 64 | 240 | 0 | 0 | 171 | 0 | 165 | 0 | 95 | 0 | 180 | 0 | 230 | 35 | 0 | 108 | 105 | 23 |  | 6067.26 | 2815 | 8882.26 | 4114 | 933 | 1671 | 1465 | 304 | 66 | 199 | 122 | 8.26 | 0 | 77.53
8:00 | 35 | 159 | 150 | 0 | 200 | 72 | 50 | 332 | 349 | 0 | 0 | 350 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 6 | 54 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 7 | 0 | 36 | 30 | 100 | 120 | 0 | 215 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 46 | 21 | 11 | 125 | 0 | 0 | 280 | 250 | 214 | 55 | 90 | 0 | 55 | 5 | 5 | 0 | 0 | 8 | 0 | 8 | 25 | 16 | 134 | 143 | 85 | 22 | 0.5 | 54 | 57 | 5 | 5 | 100 | 308 | 60 | 10 | 5 | 76 | 0 | 7 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 11 | 60 | 105 | 0 | 200 | 87 | 70 | 0 | 3.1 | 117 |  | 933 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 0 | 64 | 240 | 0 | 0 | 166 | 0 | 157 | 0 | 92 | 0 | 168 | 0 | 250 | 35 | 0 | 108 | 71 | 17 |  | 6196.6 | 2751 | 8947.6 | 4200 | 933 | 1786 | 1311 | 304 | 66 | 199 | 134 | 14.6 | 0 | 77.53
9:00 | 35 | 159 | 152 | 0 | 200 | 72 | 50 | 344 | 346 | 0 | 0 | 350 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 48 | 0 | 36 | 0 | 6 | 54 | 54 | 5 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 38 | 30 | 100 | 120 | 2 | 206 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 22 | 46 | 21 | 2 | 125 | 0 | 0 | 230 | 246 | 214 | 54 | 0 | 0 | 55 | 5 | 5 | 0 | 0 | 8 | 0 | 8 | 25 | 16 | 146 | 143 | 84 | 20 | 1.8 | 54 | 57 | 38 | 32 | 130 | 323 | 60 | 83 | 43 | 123 | 0 | 45 | 8 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 12 | 13.9 | 100 | 115 | 0 | 250 | 87 | 90 | 0 | 3.1 | 118 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 0 | 65 | 240 | 0 | 0 | 188 | 0 | 183 | 0 | 91 | 0 | 196 | 0 | 300 | 35 | 0 | 108 | 105 | 16 |  | 6700.8 | 2904 | 9604.8 | 4242 | 932 | 2079 | 1583 | 305 | 68 | 231 | 146 | 18.8 | 0 | 77.53
10:00 | 35 | 159 | 150 | 0 | 230 | 71 | 50 | 351 | 344 | 0 | 0 | 380 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 42 | 0 | 6 | 54 | 54 | 55 | 22 | 25 | 31 | 33 | 33 | 32 | 0 | 40 | 30 | 100 | 120 | 17 | 207 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 70 | 46 | 19 | 2 | 125 | 0 | 0 | 320 | 242 | 150 | 54 | 30 | 0 | 55 | 5 | 10 | 0 | 0 | 8 | 0 | 0 | 25 | 16 | 144 | 143 | 84 | 20 | 2.3 | 54 | 50 | 44 | 50 | 130 | 309 | 61 | 49 | 44 | 113 | 0 | 41 | 6 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 122 | 0 | 62 | 18.8 | 100 | 173 | 0 | 249 | 87 | 88 | 0 | 6 | 116 |  | 921 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 0 | 65 | 240 | 0 | 0 | 195 | 0 | 193 | 0 | 92 | 0 | 203 | 0 | 350 | 54 | 0 | 108 | 105 | 13 |  | 6979.1 | 2983 | 9962.1 | 4313 | 921 | 2136 | 1815 | 305 | 70 | 231 | 144 | 27.1 | 0 | 77.53
11:00 | 35 | 159 | 150 | 0 | 210 | 71 | 50 | 331 | 303 | 26 | 0 | 420 | 270 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 48 | 0 | 58 | 0 | 6 | 54 | 53 | 55 | 22 | 25 | 28 | 25 | 33 | 33 | 0 | 40 | 30 | 100 | 120 | 26 | 205 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 77 | 47 | 19 | 6 | 125 | 0 | 0 | 285 | 239 | 150 | 54 | 30 | 0 | 53 | 5 | 35 | 0 | 0 | 8 | 21 | 8 | 25 | 20 | 138 | 141 | 84 | 20 | 2.3 | 54 | 50 | 46 | 50 | 163 | 303 | 59 | 79 | 44 | 111 | 0 | 43 | 8 | 280 | 24 | 11 | 0 | 4 | 0 | 0 | 130 | 0 | 123 | 20.3 | 100 | 200 | 0 | 249 | 87 | 89 | 0 | 6 | 201 |  | 916 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 67 | 240 | 0 | 0 | 176 | 0 | 193 | 0 | 90 | 0 | 184 | 0 | 330 | 70 | 0 | 108 | 105 | 14 |  | 7254.6 | 2939 | 10193.6 | 4208 | 916 | 2188 | 2107 | 307 | 70 | 231 | 138 | 28.6 | 0 | 77.53
12:00 | 35 | 219 | 150 | 0 | 240 | 71 | 0 | 339 | 341 | 26 | 0 | 420 | 300 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 48 | 0 | 63 | 0 | 6 | 54 | 54 | 55 | 22 | 25 | 28 | 33 | 16 | 33 | 0 | 41 | 30 | 100 | 120 | 25 | 210 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 80 | 46 | 18 | 2 | 125 | 0 | 0 | 360 | 235 | 150 | 54 | 30 | 0 | 53 | 5 | 35 | 0 | 0 | 8 | 21 | 8 | 25 | 20 | 146 | 139 | 56 | 20 | 2.1 | 54 | 50 | 47 | 50 | 163 | 310 | 59 | 78 | 44 | 120 | 0 | 43 | 8 | 290 | 24 | 11 | 0 | 14 | 0 | 0 | 0 | 0 | 149 | 19.6 | 100 | 180 | 0 | 250 | 0 | 89 | 0 | 0 | 250 |  | 916 | 0 | 0 | 0 | 7 | 130 | 0 | 0 | 0 | 0 | 32 | 120 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 0 | 67 | 240 | 0 | 0 | 169 | 0 | 166 | 0 | 90 | 0 | 170 | 0 | 400 | 72 | 0 | 108 | 105 | 13 |  | 7310.7 | 3010 | 10320.7 | 4336 | 916 | 2254 | 2028 | 307 | 71 | 241 | 146 | 21.7 | 0 | 77.53
13:00 | 35 | 250 | 150 | 0 | 240 | 71 | 0 | 336 | 337 | 55 | 0 | 420 | 245 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 84 | 98 | 0 | 41 | 0 | 6 | 54 | 53 | 55 | 22 | 25 | 28 | 33 | 33 | 33 | 0 | 41 | 30 | 100 | 120 | 26 | 206 | 0 | 85 | 0 | 0 | 16 | 0 | 6 | 10 | 83 | 46 | 18 | 10 | 125 | 0 | 0 | 360 | 184 | 183 | 54 | 30 | 0 | 53 | 5 | 35 | 0 | 0 | 34 | 21 | 8 | 25 | 20 | 154 | 143 | 55 | 20 | 2.3 | 54 | 70 | 47 | 50 | 100 | 308 | 62 | 78 | 43 | 110 | 0 | 44 | 8 | 300 | 24 | 11 | 0 | 31 | 0 | 0 | 130 | 0 | 149 | 16.3 | 100 | 185 | 0 | 291 | 72 | 72 | 0 | 5.5 | 268 |  | 784 | 0 | 0 | 0 | 32 | 155 | 0 | 0 | 0 | 0 | 32 | 120 | 24 | 32 | 0 | 0 | 55 | 0 | 0 | 63 | 6 | 8 | 0 | 24 | 0 | 20 | 14 | 5 | 0 | 68 | 240 | 0 | 0 | 191 | 0 | 185 | 0 | 92 | 0 | 197 | 0 | 370 | 72 | 0 | 108 | 104 | 13 |  | 7685.1 | 3014 | 10699.1 | 4483 | 784 | 2175 | 2378 | 308 | 71 | 322 | 154 | 24.1 | 0 | 77.53
14:00 | 35 | 230 | 150 | 0 | 240 | 0 | 0 | 347 | 339 | 55 | 0 | 380 | 262 | 51 | 0 | 5 | 0 | 0 | 0 | 0 | 30 | 101 | 125 | 0 | 56 | 0 | 6 | 35 | 53 | 55 | 20 | 25 | 26 | 33 | 33 | 33 | 0 | 41 | 30 | 100 | 120 | 21 | 206 | 0 | 85 | 0 | 0 | 16 | 0 | 17 | 30 | 81 | 45 | 18 | 4 | 125 | 0 | 0 | 275 | 30 | 184 | 54 | 30 | 0 | 50 | 5 | 35 | 0 | 0 | 52 | 21 | 8 | 25 | 20 | 160 | 140 | 66 | 20 | 2.3 | 54 | 70 | 47 | 50 | 100 | 308 | 58 | 80 | 43 | 115 | 0 | 41 | 8 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 149 | 17.5 | 100 | 200 | 0 | 241 | 84 | 72 | 0 | 4.7 | 271 |  | 915 | 0 | 0 | 0 | 55 | 135 | 0 | 0 | 0 | 0 | 40 | 120 | 26 | 32 | 0 | 0 | 55 | 50 | 0 | 63 | 6 | 8 | 0 | 45 | 0 | 20 | 14 | 5 | 0 | 66 | 240 | 0 | 0 | 174 | 0 | 162 | 0 | 92 | 0 | 163 | 0 | 370 | 90 | 0 | 108 | 87 | 13 |  | 7464.5 | 3154 | 10618.5 | 4106 | 915 | 2058 | 2588 | 306 | 71 | 390 | 160 | 24.5 | 0 | 77.53
15:00 | 35 | 230 | 150 | 0 | 240 | 0 | 0 | 346 | 336 | 110 | 0 | 420 | 270 | 93 | 20 | 15 | 0 | 0 | 0 | 0 | 40 | 101 | 125 | 0 | 58 | 0 | 6 | 35 | 53 | 55 | 22 | 25 | 28 | 33 | 33 | 32 | 0 | 42 | 30 | 95 | 120 | 16 | 216 | 0 | 135 | 0 | 0 | 11 | 0 | 16 | 30 | 83 | 46 | 18 | 2 | 125 | 0 | 0 | 275 | 45 | 202 | 55 | 90 | 0 | 50 | 5 | 35 | 0 | 0 | 52 | 20 | 8 | 25 | 20 | 170 | 139 | 72 | 20 | 0.4 | 53 | 70 | 47 | 50 | 100 | 310 | 59 | 78 | 43 | 111 | 0 | 41 | 10 | 330 | 24 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 149 | 12.8 | 100 | 200 | 0 | 239 | 85 | 89 | 0 | 3.8 | 271 |  | 914 | 0 | 0 | 0 | 94 | 50 | 0 | 0 | 0 | 0 | 40 | 120 | 27 | 32 | 0 | 0 | 55 | 50 | 0 | 63 | 6 | 8 | 0 | 49 | 0 | 21 | 13 | 5 | 0 | 66 | 240 | 0 | 0 | 170 | 0 | 161 | 0 | 87 | 0 | 172 | 0 | 370 | 90 | 0 | 108 | 87 | 13 |  | 7841 | 3111 | 10952 | 4255 | 914 | 2120 | 2794 | 306 | 72 | 304 | 170 | 17 | 0 | 77.53
16:00 | 35 | 230 | 150 | 0 | 240 | 0 | 0 | 337 | 339 | 110 | 0 | 370 | 265 | 93 | 40 | 40 | 0 | 0 | 0 | 0 | 75 | 101 | 126 | 0 | 62 | 0 | 6 | 54 | 53 | 55 | 19 | 25 | 28 | 33 | 33 | 32 | 0 | 41 | 30 | 95 | 120 | 17 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 16 | 30 | 91 | 46 | 18 | 4 | 125 | 0 | 0 | 205 | 100 | 194 | 55 | 90 | 0 | 50 | 0 | 35 | 0 | 0 | 52 | 20 | 8 | 25 | 20 | 172 | 138 | 85 | 20 | 1.4 | 53 | 70 | 50 | 46 | 100 | 308 | 61 | 78 | 43 | 116 | 0 | 45 | 10 | 315 | 24 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 148 | 7.6 | 100 | 200 | 0 | 240 | 85 | 89 | 0 | 1.1 | 274 |  | 914 | 0 | 0 | 0 | 115 | 40 | 0 | 0 | 0 | 4 | 40 | 120 | 26 | 40 | 0 | 0 | 55 | 50 | 0 | 63 | 6 | 8 | 0 | 49 | 0 | 21 | 13 | 8 | 0 | 66 | 240 | 0 | 0 | 166 | 0 | 156 | 0 | 87 | 0 | 167 | 0 | 320 | 70 | 0 | 108 | 68 | 10 |  | 7856.1 | 3030 | 10886.1 | 4199 | 914 | 2007 | 2908 | 306 | 71 | 299 | 172 | 10.1 | 0 | 77.53
17:00 | 35 | 230 | 150 | 0 | 240 | 0 | 0 | 330 | 339 | 110 | 0 | 340 | 275 | 100 | 48 | 47 | 0 | 0 | 0 | 0 | 85 | 101 | 125 | 0 | 62 | 0 | 6 | 54 | 53 | 55 | 22 | 25 | 30 | 33 | 33 | 33 | 0 | 41 | 30 | 95 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 33 | 30 | 96 | 46 | 18 | 6 | 125 | 0 | 0 | 205 | 120 | 183 | 55 | 90 | 0 | 51 | 0 | 10 | 0 | 0 | 52 | 21 | 8 | 25 | 20 | 168 | 139 | 85 | 22 | 0.6 | 53 | 70 | 14 | 10 | 100 | 306 | 61 | 10 | 10 | 110 | 0 | 13 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 149 | 4.7 | 100 | 200 | 0 | 199 | 83 | 106 | 0 | 1.1 | 274 |  | 915 | 0 | 0 | 0 | 115 | 45 | 0 | 0 | 0 | 12 | 40 | 120 | 22 | 64 | 0 | 0 | 55 | 50 | 0 | 63 | 6 | 8 | 0 | 49 | 0 | 21 | 13 | 8 | 0 | 66 | 240 | 0 | 0 | 159 | 0 | 149 | 0 | 93 | 0 | 160 | 0 | 320 | 70 | 0 | 108 | 69 | 10 |  | 7625.4 | 3050 | 10675.4 | 4139 | 915 | 1737 | 3005 | 306 | 71 | 328 | 168 | 6.4 | 0 | 77.53
18:00 | 35 | 229 | 150 | 0 | 160 | 0 | 0 | 318 | 284 | 70 | 0 | 340 | 240 | 78 | 48 | 48 | 0 | 0 | 0 | 0 | 70 | 64 | 125 | 0 | 62 | 0 | 6 | 54 | 53 | 55 | 22 | 25 | 30 | 33 | 33 | 41 | 0 | 39 | 30 | 100 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 21 | 0 | 31 | 30 | 96 | 46 | 18 | 2 | 125 | 0 | 0 | 215 | 135 | 181 | 55 | 90 | 0 | 51 | 0 | 10 | 0 | 0 | 25 | 21 | 8 | 25 | 20 | 158 | 142 | 85 | 22 | 0.6 | 53 | 70 | 14 | 10 | 100 | 307 | 57 | 10 | 10 | 108 | 0 | 13 | 10 | 305 | 24 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 115 | 0.9 | 100 | 200 | 0 | 201 | 95 | 106 | 0 | 0.1 | 221 |  | 915 | 0 | 0 | 0 | 66 | 45 | 0 | 0 | 0 | 24 | 40 | 120 | 24 | 64 | 0 | 0 | 55 | 50 | 5 | 69 | 6 | 8 | 0 | 16 | 0 | 21 | 13 | 8 | 0 | 66 | 240 | 0 | 0 | 156 | 0 | 146 | 0 | 93 | 0 | 160 | 0 | 280 | 70 | 0 | 53 | 69 | 15 |  | 7250.6 | 2897 | 10147.6 | 4068 | 915 | 1645 | 2636 | 306 | 69 | 349 | 158 | 1.6 | 0 | 77.53
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 230 | 150 | 0 | 200 | 0 | 0 | 285 | 281 | 70 | 0 | 400 | 285 | 90 | 48 | 55 | 0 | 0 | 0 | 0 | 74 | 84 | 125 | 59 | 62 | 0 | 6 | 54 | 53 | 55 | 22 | 25 | 26 | 33 | 33 | 49 | 0 | 38 | 30 | 100 | 120 | 25 | 212 | 0 | 135 | 0 | 0 | 26 | 82 | 31 | 60 | 96 | 46 | 18 | 2 | 125 | 0 | 0 | 225 | 140 | 194 | 55 | 90 | 0 | 54 | 0 | 10 | 0 | 50 | 25 | 21 | 8 | 25 | 20 | 188 | 141 | 85 | 22 | 0 | 54 | 70 | 14 | 10 | 100 | 310 | 61 | 10 | 10 | 124 | 0 | 41 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 151 | 0 | 110 | 0 | 100 | 200 | 16 | 200 | 96 | 106 | 0 | 0 | 260 |  | 915 | 14 | 0 | 0 | 78 | 120 | 0 | 0 | 25 | 50 | 40 | 120 | 29 | 110 | 0 | 0 | 55 | 50 | 28 | 90 | 33 | 8 | 36 | 34 | 28 | 22 | 13 | 11 | 0 | 65 | 240 | 0 | 18 | 156 | 0 | 147 | 0 | 56 | 0 | 158 | 0 | 310 | 70 | 30 | 102 | 86 | 13 |  | 7821 | 3360 | 11181 | 4136 | 915 | 1727 | 3095 | 305 | 68 | 747 | 188 | 0 | 0 | 77.53
19:30 | 35 | 230 | 150 | 0 | 240 | 0 | 0 | 335 | 304 | 70 | 0 | 400 | 270 | 100 | 0 | 55 | 0 | 0 | 0 | 0 | 80 | 101 | 125 | 100 | 64 | 0 | 15 | 54 | 53 | 55 | 22 | 25 | 22 | 33 | 33 | 49 | 0 | 38 | 30 | 100 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 26 | 82 | 33 | 88 | 96 | 46 | 21 | 8 | 125 | 0 | 0 | 315 | 170 | 181 | 55 | 90 | 0 | 54 | 0 | 12 | 0 | 50 | 43 | 21 | 8 | 25 | 20 | 170 | 142 | 85 | 22 | 0 | 54 | 70 | 53 | 20 | 100 | 305 | 61 | 73 | 42 | 108 | 0 | 47 | 10 | 325 | 24 | 11 | 0 | 75 | 0 | 0 | 180 | 0 | 120 | 0 | 100 | 200 | 138 | 294 | 96 | 106 | 0 | 0 | 260 |  | 914 | 30 | 0 | 0 | 115 | 165 | 0 | 0 | 22 | 76 | 40 | 120 | 35 | 110 | 0 | 0 | 60 | 50 | 27 | 95 | 33 | 24 | 44 | 50 | 29 | 22 | 14 | 11 | 0 | 64 | 240 | 0 | 18 | 167 | 0 | 156 | 0 | 95 | 45 | 167 | 0 | 320 | 105 | 0 | 108 | 87 | 15 |  | 8528 | 3673 | 12201 | 4428 | 914 | 1989 | 3482 | 304 | 68 | 846 | 170 | 0 | 0 | 0
20:00 | 35 | 229 | 150 | 0 | 240 | 0 | 0 | 329 | 302 | 70 | 0 | 400 | 250 | 97 | 0 | 55 | 0 | 0 | 0 | 0 | 90 | 101 | 125 | 100 | 41 | 0 | 40 | 54 | 53 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 38 | 30 | 100 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 33 | 82 | 33 | 100 | 96 | 46 | 21 | 21 | 125 | 0 | 0 | 335 | 220 | 216 | 55 | 90 | 0 | 54 | 0 | 25 | 0 | 0 | 40 | 21 | 8 | 25 | 20 | 168 | 143 | 84 | 22 | 0 | 53 | 70 | 53 | 43 | 100 | 306 | 57 | 83 | 44 | 109 | 0 | 47 | 10 | 320 | 24 | 11 | 0 | 150 | 0 | 0 | 180 | 0 | 141 | 0 | 100 | 200 | 138 | 296 | 96 | 106 | 0 | 0 | 261 |  | 915 | 30 | 0 | 0 | 115 | 165 | 0 | 0 | 21 | 64 | 40 | 120 | 35 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 33 | 43 | 47 | 50 | 29 | 22 | 14 | 11 | 0 | 65 | 239 | 0 | 17 | 161 | 0 | 151 | 0 | 95 | 48 | 162 | 0 | 320 | 105 | 0 | 108 | 86 | 17 |  | 8739 | 3669 | 12408 | 4520 | 915 | 2043 | 3606 | 304 | 68 | 784 | 168 | 0 | 0 | 77.53
21:00 | 35 | 229 | 150 | 0 | 240 | 0 | 0 | 338 | 302 | 26 | 0 | 430 | 272 | 100 | 13 | 55 | 0 | 0 | 0 | 0 | 97 | 64 | 125 | 50 | 51 | 0 | 49 | 54 | 53 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 39 | 30 | 100 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 33 | 82 | 33 | 100 | 96 | 46 | 21 | 27 | 125 | 0 | 0 | 360 | 220 | 215 | 55 | 90 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 21 | 5 | 25 | 20 | 168 | 143 | 84 | 22 | 0 | 54 | 70 | 53 | 50 | 130 | 305 | 61 | 80 | 44 | 110 | 0 | 46 | 10 | 320 | 24 | 11 | 0 | 45 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 140 | 292 | 96 | 106 | 0 | 0 | 261 |  | 914 | 30 | 0 | 0 | 115 | 165 | 0 | 0 | 22 | 60 | 40 | 120 | 36 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 33 | 43 | 44 | 50 | 29 | 22 | 14 | 11 | 0 | 65 | 240 | 0 | 17 | 173 | 0 | 164 | 0 | 95 | 62 | 170 | 0 | 360 | 105 | 0 | 108 | 86 | 17 |  | 8700 | 3751 | 12451 | 4584 | 914 | 2163 | 3470 | 305 | 69 | 778 | 168 | 0 | 0 | 77.53
22:00 | 35 | 229 | 150 | 0 | 240 | 0 | 0 | 328 | 350 | 26 | 0 | 390 | 282 | 100 | 15 | 55 | 0 | 0 | 0 | 0 | 100 | 64 | 126 | 10 | 64 | 0 | 48 | 54 | 53 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 40 | 30 | 100 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 33 | 82 | 33 | 88 | 97 | 46 | 21 | 36 | 125 | 0 | 0 | 320 | 260 | 214 | 55 | 90 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 166 | 143 | 84 | 22 | 0 | 54 | 70 | 53 | 50 | 163 | 304 | 61 | 82 | 44 | 115 | 0 | 47 | 9 | 315 | 24 | 11 | 0 | 45 | 0 | 0 | 180 | 0 | 150 | 0 | 100 | 196 | 0 | 293 | 96 | 106 | 0 | 0 | 261 |  | 915 | 30 | 0 | 0 | 99 | 165 | 0 | 0 | 23 | 60 | 40 | 120 | 38 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 6 | 43 | 44 | 50 | 29 | 22 | 14 | 5 | 0 | 64 | 240 | 16 | 17 | 183 | 0 | 180 | 0 | 95 | 100 | 184 | 0 | 360 | 105 | 0 | 108 | 86 | 17 |  | 8579 | 3799 | 12378 | 4616 | 915 | 2213 | 3298 | 304 | 70 | 796 | 166 | 0 | 0 | 77.53
23:00 | 35 | 229 | 150 | 0 | 240 | 0 | 0 | 341 | 350 | 26 | 0 | 390 | 285 | 100 | 16 | 55 | 0 | 0 | 0 | 0 | 100 | 64 | 125 | 10 | 64 | 0 | 24 | 54 | 53 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 40 | 30 | 100 | 120 | 25 | 205 | 0 | 131 | 0 | 0 | 16 | 82 | 33 | 88 | 97 | 46 | 20 | 39 | 125 | 0 | 0 | 320 | 300 | 214 | 55 | 90 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 160 | 144 | 84 | 22 | 0 | 54 | 70 | 53 | 50 | 163 | 308 | 61 | 81 | 44 | 110 | 0 | 47 | 10 | 330 | 24 | 11 | 0 | 45 | 0 | 0 | 163 | 0 | 150 | 0 | 100 | 195 | 0 | 293 | 96 | 106 | 0 | 0 | 261 |  | 914 | 30 | 0 | 0 | 115 | 165 | 0 | 0 | 17 | 60 | 40 | 120 | 38 | 110 | 0 | 0 | 60 | 50 | 26 | 92 | 6 | 43 | 44 | 50 | 21 | 22 | 14 | 0 | 0 | 65 | 239 | 17 | 16 | 195 | 0 | 192 | 0 | 97 | 100 | 203 | 0 | 415 | 72 | 0 | 108 | 87 | 17 |  | 8588 | 3860 | 12448 | 4707 | 914 | 2288 | 3227 | 304 | 70 | 778 | 160 | 0 | 0 | 77.53
24:00 | 35 | 229 | 150 | 0 | 100 | 52 | 0 | 330 | 351 | 26 | 0 | 390 | 240 | 100 | 30 | 55 | 0 | 0 | 0 | 0 | 100 | 64 | 125 | 10 | 64 | 0 | 6 | 54 | 53 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 40 | 30 | 100 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 32 | 82 | 33 | 88 | 97 | 46 | 19 | 39 | 125 | 0 | 0 | 320 | 300 | 217 | 55 | 90 | 0 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 25 | 20 | 166 | 146 | 84 | 22 | 0 | 54 | 70 | 53 | 50 | 130 | 307 | 49 | 81 | 44 | 118 | 0 | 45 | 10 | 285 | 24 | 11 | 0 | 45 | 0 | 0 | 165 | 0 | 149 | 0 | 100 | 196 | 0 | 295 | 95 | 106 | 0 | 0 | 261 |  | 915 | 30 | 0 | 0 | 115 | 165 | 0 | 0 | 17 | 60 | 40 | 120 | 35 | 110 | 0 | 0 | 60 | 50 | 26 | 92 | 6 | 43 | 44 | 50 | 21 | 22 | 14 | 11 | 0 | 64 | 240 | 17 | 16 | 185 | 0 | 182 | 0 | 97 | 100 | 204 | 0 | 420 | 72 | 0 | 108 | 86 | 17 |  | 8384 | 3854 | 12238 | 4548 | 915 | 2263 | 3194 | 304 | 70 | 778 | 166 | 0 | 0 | 77.53
KWH | 852000 | 4953000 | 3868000 | 0 | 5199600 | 1145818 | 481376 | 7988220 | 7693000 | 744600 | 0 | 9126375 | 6524305 | 1083840 | 396240 | 495224 | 0 | 0 | 0 | 0 | 1018560 | 1110672 | 2080320 | 326229 | 1210560 | 0 | 292656 | 1271160 | 1071574 | 960000 | 476676 | 600000 | 693540 | 784900 | 792000 | 783660 | 0 | 872700 | 728000 | 2400000 | 3000000 | 493054 | 4910983 | 0 | 2494272 | 0 | 0 | 496320 | 495200 | 392258 | 809040 | 1808640 | 1104000 | 456288 | 463680 | 3035002 | 0 | 0 | 5754200 | 5972000 | 4802000 | 1639272 | 1722480 | 0 | 1304160 | 75000 | 639916 | 0 | 62480 | 861984 | 299232 | 185400 | 608100 | 453620 | 3819840 | 3348240 | 1938240 | 465120 | 14250 | 1269000 | 1471000 | 950400 | 983736 | 3286219 | 7065000 | 1404768 | 1577280 | 837720 | 2690240 | 0 | 890640 | 216000 | 7568000 | 569472 | 246096 | 0 | 795382 | 0 | 0 | 3415200 | 0 | 2279520 | 151065 | 2388480 | 4447200 | 796218 | 6047000 | 2028000 | 2262000 | 0 | 28860 | 5497418 |  | 21943273 | 143300 | 0 | 0 | 1474560 | 2938560 | 0 | 0 | 179520 | 452352 | 488250 | 2888000 | 702257 | 1283520 | 0 | 0 | 1380000 | 538504 | 139839 | 1665372 | 230540 | 456902 | 348000 | 761760 | 323266 | 503040 | 300816 | 163188 | 0 | 1565672 | 5824200 | 114000 | 161000 | 4506773 | 0 | 4325009 | 0 | 2214132 | 633600 | 4633636 | 0 | 8012363 | 1679520 | 44933 | 2526432 | 2254176 | 397440 |  | 183110990 | 78197705 | 261308695 | 104774055 | 21943273 | 50611200 | 60941609 | 7389872 | 1600700 | 10033971 | 3819840 | 194175 | 0
Fuel Cost | 732720 | 4259580 | 3326480 | 0 | 3327744 | 928112.58 | 452493.44 | 4872814.2 | 4692730 | 7155606 | 0 | 6114671.25 | 99104192.95 | 6806515.2 | 2646883.2 | 3025818.64 | 0 | 0 | 0 | 0 | 6366000 | 7319328.48 | 20116694.4 | 2078078.73 | 7251254.4 | 0 | 1952015.52 | 9063370.8 | 6697337.5 | 6019200 | 357507 | 450000 | 0 | 0 | 0 | 7413423.6 | 0 | 0 | 0 | 2640000 | 3300000 | 4669221.38 | 3241248.78 | 0 | 2868412.8 | 0 | 0 | 4362652.8 | 5333304 | 3816670.34 | 5007957.6 | 11683814.4 | 7220160 | 387844.8 | 0 | 2761851.82 | 0 | 0 | 3567604 | 4120680 | 3361400 | 1131097.68 | 1653580.8 | 0 | 1121577.6 | 69000 | 524731.12 | 0 | 677283.2 | 6395921.28 | 230408.64 | 139050 | 468237 | 340215 | 26127705.6 | 2511180 | 17812425.6 | 358142.4 | 0 | 1319760 | 1529840 | 912384 | 885362.4 | 2563250.82 | 4945500 | 1601435.52 | 1687689.6 | 921492 | 3066873.6 | 0 | 828295.2 | 200880 | 4843520 | 427104 | 187032.96 | 0 | 5774473.32 | 0 | 0 | 24418680 | 0 | 0 | 0 | 0 | 41536848 | 7436676.12 | 5260890 | 0 | 0 | 0 | 0 | 0 |  | 111910692.3 | 4177195 | 0 | 0 | 12224102.4 | 47252044.8 | 0 | 0 | 2021395.2 | 5328706.56 | 3847410 | 1992720 | 695234.43 | 9498048 | 0 | 0 | 1449000 | 6165870.8 | 1499074.08 | 14921733.12 | 1994171 | 4066427.8 | 3706200 | 7556659.2 | 3804840.82 | 553344 | 282767.04 | 123533.316 | 0 | 9503629.04 | 22481412 | 3674220 | 4309970 | 3064605.64 | 0 | 3027506.3 | 0 | 0 | 10980288 | 0 | 0 | 0 | 0 | 39091.71 | 0 | 0 | 0 |  | 460781938.07 | 302151892.556 | 762933830.626 | 77272502.576 | 111910692.3 | 29408633.16 | 359424053.63 | 31985041.04 | 0 | 126805202.32 | 26127705.6 | 0 | 0
Yesterday Day Peak | 35 | 219 | 150 | 0 | 240 | 71 | 0 | 339 | 341 | 26 | 0 | 420 | 300 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 48 | 0 | 63 | 0 | 6 | 54 | 54 | 55 | 22 | 25 | 28 | 33 | 16 | 33 | 0 | 41 | 30 | 100 | 120 | 25 | 210 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 80 | 46 | 18 | 2 | 125 | 0 | 0 | 360 | 235 | 150 | 54 | 30 | 0 | 53 | 5 | 35 | 0 | 0 | 8 | 21 | 8 | 25 | 20 | 146 | 139 | 56 | 20 | 2.1 | 54 | 50 | 47 | 50 | 163 | 310 | 59 | 78 | 44 | 120 | 0 | 43 | 8 | 290 | 24 | 11 | 0 | 14 | 0 | 0 | 0 | 0 | 149 | 19.6 | 100 | 180 | 0 | 250 | 0 | 89 | 0 | 0 | 250 |  | 916 | 0 | 0 | 0 | 7 | 130 | 0 | 0 | 0 | 0 | 32 | 120 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 63 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 0 | 67 | 240 | 0 | 0 | 169 | 0 | 166 | 0 | 90 | 0 | 170 | 0 | 400 | 72 | 0 | 108 | 105 | 13 |  | 10320.7 | DayPeak
Yesterday Evening Peak | 35 | 229 | 150 | 0 | 240 | 0 | 0 | 338 | 302 | 26 | 0 | 430 | 272 | 100 | 13 | 55 | 0 | 0 | 0 | 0 | 97 | 64 | 125 | 50 | 51 | 0 | 49 | 54 | 53 | 55 | 22 | 25 | 32 | 33 | 33 | 49 | 0 | 39 | 30 | 100 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 33 | 82 | 33 | 100 | 96 | 46 | 21 | 27 | 125 | 0 | 0 | 360 | 220 | 215 | 55 | 90 | 0 | 54 | 0 | 35 | 0 | 0 | 52 | 21 | 5 | 25 | 20 | 168 | 143 | 84 | 22 | 0 | 54 | 70 | 53 | 50 | 130 | 305 | 61 | 80 | 44 | 110 | 0 | 46 | 10 | 320 | 24 | 11 | 0 | 45 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 140 | 292 | 96 | 106 | 0 | 0 | 261 |  | 914 | 30 | 0 | 0 | 115 | 165 | 0 | 0 | 22 | 60 | 40 | 120 | 36 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 33 | 43 | 44 | 50 | 29 | 22 | 14 | 11 | 0 | 65 | 240 | 0 | 17 | 173 | 0 | 164 | 0 | 95 | 62 | 170 | 0 | 360 | 105 | 0 | 108 | 86 | 17 |  | 12451 | EvPeak
Forecast for Evening | 35 | 229 | 200 | 0 | 0 | 108 | 50 | 412 | 360 | 110 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 40 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 30 | 100 | 120 | 25 | 225 | 0 | 130 | 0 | 0 | 33 | 85 | 68 | 100 | 100 | 46 | 21 | 35 | 125 | 0 | 0 | 360 | 360 | 221 | 55 | 100 | 0 | 55 | 5 | 40 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 187 | 150 | 85 | 22 | 0 | 54 | 70 | 51 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 19 | 47 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 100 | 105 | 105 |  | 300 |  | 930 | 30 | 0 | 0 | 115 | 225 | 0 | 0 | 40 | 80 | 40 | 120 | 33 | 110 | 26 | 0 | 60 | 50 | 35 | 95 | 33 | 40 | 40 | 52 | 30 | 22 | 14 | 11 | 0 | 63 | 250 | 17 | 18 | 214 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 105 | 23
Forecast for Day | 35 | 229 | 200 | 0 | 0 | 108 | 50 | 412 | 360 | 110 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 40 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 30 | 100 | 120 | 25 | 210 | 0 | 130 | 0 | 0 | 32 | 85 | 68 | 100 | 100 | 46 | 21 | 10 | 125 | 0 | 0 | 360 | 360 | 221 | 55 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 143 | 150 | 85 | 22 | 2 | 54 | 70 | 51 | 44 | 163 | 300 | 66 | 86 | 46 | 130 | 19 | 47 | 10 | 341 | 25 | 11 | 0 | 100 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 0 | 285 | 100 | 105 | 105 | 3 | 300 |  | 930 | 0 | 0 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 120 | 33 | 110 | 0 | 0 | 60 | 0 | 0 | 0 | 33 | 32 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 63 | 250 | 0 | 0 | 214 | 0 | 220 | 0 | 95 | 0 | 220 | 0 | 414 | 105 | 0 | 100 | 105 | 23
Generation at 08:00(Today) | 35 | 229 | 150 | 0 | 0 | 103 | 50 | 329 | 300 | 0 | 0 | 360 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 6 | 54 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 8 | 0 | 10.8 | 30 | 100 | 120 | 8 | 205 | 0 | 132 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 46 | 20 | 8 | 125 | 0 | 0 | 300 | 300 | 182 | 8 | 90 | 0 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 25 | 20 | 134 | 95 | 84 | 22 | 1 | 54 | 70 | 50 | 50 | 100 | 305 | 29 | 82 | 44 | 109 | 0 | 45 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 10.8 | 50 | 70 | 0 | 295 | 95 | 106 | 0 | 2.9 | 174 | 0 | 918 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 120 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 8 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 64 | 240 | 0 | 0 | 182 | 0 | 179 | 0 | 94 | 0 | 189 | 0 | 340 | 35 | 0 | 108 | 87 | 0 | 0
199
| Minimum Generation |  | 8882.26 | 7:00
| Highest Generation |  | 12451 | 21:00
| Day Peak Generation |  | 10320.7 | 12:00
| Evening Peak Generation |  | 12451 | 21:00
| HVDC Max Flow |  | 933 | 1:00
| HVDC EvPeak Flow |  | 914 | 21:00
| Load factor L.F |  | 87.45%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-06-24
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-06-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10320.7 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9290.5 | MW
Evening Peak Generation : |  | 12451 | MW Hour : | 21:00 | Available Max Generation : |  | 15144 | MW
E.P. Demand (at gen end) : |  | 12451 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 12451 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2344 | MW
Total Gen. (MKWH) : |  | 261.3087 | System Load Factor : | 87.45% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -340 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-06-24
Actual : | 77.53 | Ft.(MSL) , | Rule curve : | 82.11 | Ft.( MSL )
Gas Consumed : | Total = | 1396.49 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 106681135.736
|  | Coal : | 31985041.04 | Oil : | 486229255.95 | Total : | 624895432.726
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4576.0784 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1560.6739 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1399.1236 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1264.5143 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1142.5644 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 922.0205 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 509.6882 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 237.2404 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 711.136 |  |  | 0 | 0%
Total | 0 |  | 12323.0396 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1, | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-7
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal # 5
|  |  |  | 4) Bheramara 410 MW. | 10) Sikalbaha-150 MW.
|  |  |  | 5) Siddhirganj ST | 11) Bhola-225 MW CCPP ST-1 & 2
|  |  |  | 6) Ashuganj #4,5 | 12) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Mymensingh-Jamalpur 132 kV Ckt-1 tripped at 11:37 from Mymensingh end showing Dist C-phase Z1 and
was switched on at 11:47.
b) Mymensingh-Jamalpur 132 kV Ckt-2 tripped at 11:38 from Mymensingh end showing O/C and was switched on |  |  |  |  | About 144 MW power interruption occurred under Jamalpur & Sherpur S/S
at 11:47.At the same time Jamalpur 95 MW,Jamalpur 200 MW & United Jamalpur 115 MW got tripped. |  |  |  |  | areas from 11:38 to 11:47.
c) Halisahar-Khulshi 132 kV Ckt-2 was under shut down from 13:35 to 14:17 due to CB problem.
d) Aminbazar-Savar 132 kV Ckt-1 was switched on at 16:39.
e) Ashuganj (S) CCPP ST was synchronized at 16:37.
f) Khulna 225 MW CCPP ST was shut down at 15:10 due to problem with HP governing valve.
g) Chandpur CCPP ST was synchronized at 14:10.
h) Shahjibazar GT-8 was shut down at 05:31(24/06/2019) for filter cleaning and was synchronized at 09:37(24/06/19).
i) Ghorasal Unit-7 GT was shut down at 00:12(24/06/2019) for maintenance.
j) Madunaghat-TK Chemical 132 kV Ckt was under shut down from 07:16 to 08:01(24/06/2019) for C/M.
k) Sikalbaha-TK Chemical 132 kV Ckt was under shut down from 07:17 to 08:02(24/06/2019) for C/M.
l) Dohazari 132/33 kV T1 transformer was under shut down from 23:32 to 00:25(24/06/2019) for red |  |  |  |  | About 20 MW power interruption occurred under Dohazari S/S
hot maintenance. |  |  |  |  | areas from 23:32 to 00:25(24/06/2019).
m) Sreemongal 132/33 kV T1 transformer was under shut down from 06:30 to 07:33 (24/06/2019)for red |  |  |  |  | About 8 MW power interruption occurred under Sreemongal S/S
hot maintenance at 33 kV feeder isolator. |  |  |  |  | areas from 06:30 to 07:33(24/06/2019).
n) Madaripur 132/33 kV T2 transformer was shut down at 07:18 (24/06/2019) for maintenance work.
o) Faridpur 132/33 kV T2 transformer was shut down at 07:46 (24/06/2019) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-06-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 852000 | Gas shortage
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 229 | 4953000
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 150 | 3868000 | Gas shortage
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 240 | 5199600 | ST under maint.
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 481376 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 1145818 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 7988220 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 26 | 744600 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 302 | 7693000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 430 | 9126375 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1083840
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 272 | 6524305 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 13 | 396240 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 495224
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 50 | 326229 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 476676
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 97 | 1018560
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Machine problem
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 64 | 1110672 | Low demand
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 49 | 292656
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1271160
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 2080320 | Engine problem
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 53 | 1071574
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 960000
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 51 | 1210560 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1293540 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 784900
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 792000
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 49 | 783660
31 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 45 | 795382 | Low demand
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 149 | 2279520
37 | Gazipur 100 MW |  | RPCL | 100 MW | 105 | 106 | 2262000
| Dhaka area Total |  |  |  | 5803 | 3282 | 69361007
38 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2400000
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 3000000
39 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 493054
40 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 151065
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 46 | 1104000
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 69 | 1600700 | Low water level
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 205 | 4910983 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2494272
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 33 | 496320 | Engine problem
47 | Baraka Sikalbaha PL |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
48 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 82 | 495200
49 | Dohazari Peaking |  | PDB | 6*17 | 102 | 33 | 392258
50 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 809040
51 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2388480
52 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 456288
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 463680
53 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 96 | 1808640
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 28860
| Anwara United |  | United Group | 300 MW | 0 | 261 | 5497418 | on test
| Chattogram area Total |  |  |  | 1786 | 1448 | 28990258
54 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 125 | 3035002
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 215 | 4802000 | FGMO
56 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 5754200
57 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 220 | 5972000
58 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas Line maint.
59 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 54 | 1304160
60 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 0 | 75000 | Contract Expired
61 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 55 | 1639272 | Gas shortage
62 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 35 | 639916 | Machine problem
63 | Midland 150MW |  | IPP | 23*7.015 | 150 | 140 | 796218
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 62480 | Reserve
66 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1722480
67 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 4447200
68 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 21 | 299232
69 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 185400 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 168 | 3819840
70 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 608100 | Engine problem
71 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 861984
72 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 453620 | Engine problem
73 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1785 | 36478104
74 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 143 | 3348240 | Machine problem
75 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 465120
76 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 84 | 1938240 | Engine problem
77 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 14250
78 | United Mymensingh PPL |  | IPP | 200 | 200 | 180 | 3415200 | Engine problem
79 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 96 | 2028000 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 525 | 11209050
80 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 54 | 1269000
81 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 70 | 1471000
82 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3286219 | Frequency control
83 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 305 | 7065000 | FGMO
84 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 950400
85 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 983736
86 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 246096
87 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 61 | 1404768 | FGMO
88 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 80 | 1577280
89 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 44 | 837720
90 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 110 | 2690240 | FGMO
91 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
92 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 890640
93 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 569472
94 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 320 | 7568000 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 292 | 6047000 | On test
95 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 216000
| Sylhet Area Total |  |  |  | 1549 | 1660 | 37072571
96 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 30 | 143300
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 914 | 21943273
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
97 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1474560
98 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 22 | 179520
99 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 165 | 2938560 | Low demand
100 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 452352
101 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
102 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 488250
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
103 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 62 | 633600 | Engine problem
104 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1679520
105 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 86 | 2254176 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1599 | 32187111
106 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1283520
107 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
108 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 36 | 702257
109 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 120 | 2888000 | FGMO
110 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 2214132
| Barisal Area Total |  |  |  | 462 | 361 | 7087909
111 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 1380000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
112 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 538504
113 | Bera Peaking |  | PDB | 9*8.29 | 71 | 26 | 139839
114 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 33 | 230540 | Engine problem
115 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 456902 | Engine problem
116 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 348000
117 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 173 | 4506773 | FGMO
118 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 164 | 4325009 | FGMO
119 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 170 | 4633636 | FGMO
120 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 360 | 8012363 | Frequency control
121 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 29 | 323266
122 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 503040
123 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 14 | 300816
124 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 163188
125 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 761760
126 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 95 | 1665372
127 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 44933 | Reserve
128 | Confidence Bogura-2 (CPBL) |  | IPP | 113 MW | 113 | 108 | 2526432
| Rajshahi Area Total |  |  |  | 2070 | 1452 | 30860373
129 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 65 | 1565672
130 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 240 | 5824200
131 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 114000
132 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 161000
| Confidence Rangpur |  | IPP | 113 MW | 0 | 17 | 397440
| Rangpur Area Total |  |  |  | 484 | 339 | 8062312
| Total |  |  |  | 17996 | 12451 | 261308695
| Eastern Grid Total |  |  |  | 12666 | 8700 | 183110990
| Western Grid Total |  |  |  | 5330 | 3751 | 78197705
| National Grid Total |  |  |  | 17996 | 12451 | 261308695
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-06-23
| (a) ENTIRE EASTERN GRID : |  | 8177 | MW | (b) ENTIRE WESTERN GRID : |  | 3802 | MW
| i) Dhaka area |  | 4319 | MW | i) Khulna area |  | 1456 | MW
| ii) Chittagong area |  | 1271 | MW | ii) Rajshahi area |  | 1279 | MW
| iii) Comilla area |  | 1107 | MW | iii) Barisal area |  | 334 | MW
| iv) Mymensingh area |  | 959 | MW | iv) Rangpur area |  | 733 | MW
| v) Sylhet area |  | 521 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11979 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 134 | 1500 | Jamalpur | 137 | 2100 | Jessore | 117 | 2000
2 | Munsiganj | 118 | 2000 | Sherpur | 102 | 100 | Jhenida | 112 | 2000
3 | Sonargaon | 65 | 2100 | Srimongal | 38 | 2300 | Bottail | 130 | 2100
4 | Shyampur | 180 | 700 | Shahjibazar | 127 | 2100 | G.K Project | 58 | 2100
5 | Bhulta | 189 | 1600 | Fenchuganj | 54 | 1930 | Faridpur | 168 | 1930
6 | Madanganj | 65 | 100 | Kulawara | 45 | 2300 | Madaripur | 112 | 2300
7 | Shitalakhya | 87 | 1700 | Sylhet | 149 | 2100 | Gopalganj | 93 | 1930
8 | Rahim steel | 20 | 1100 | Chatak | 35 | 1930 | Bagerhat | 85 | 1930
9 | Matuail | 95 | 1000 | Sunamganj | 39 | 2100 | Mongla | 40 | 100
10 | Ghorasal | 85 | 1900 | Biani Bazar | 49 | 2200 | Satkhira | 110 | 2000
11 | Narsingdi | 143 | 2000 | Comilla (S) | 188 | 1900 | Gallamari | 53 | 1300
12 | Haripur (SBU) | 96 | 1500 | Comilla(N) | 145 | 1930 | Magura | 56 | 2000
13 | Ullon | 95 | 1600 | Chandpur | 105 | 2300 | Chuadanga | 87 | 2100
14 | Hasnabad | 217 | 2100 | Feni | 128 | 2200 | Barisal | 114 | 1930
15 | Magbazar | 151 | 1700 | Chowmuhani | 180 | 1900 | Patuakhali | 102 | 2100
16 | Maniknagar | 116 | 1200 | Ashuganj | 62 | 2300 | Bhandaria | 60 | 2200
17 | Bangabhaban | 40 | 1500 | Daudkandi | 140 | 2200 | Barisal (N) | 44 | 2200
18 | Narinda | 94 | 1300 | B.Baria | 140 | 1930 | Sariatpur | 32 | 400
19 | Dhanmondi | 189 | 1300 | Ramganj | 94 | 2300 | Benapol | 43 | 2000
20 | Lalbag | 99 | 1100 | Madunaghat | 63 | 2000 | Borhan Uddin | 37 | 1930
21 | Madartek | 62 | 2100 | Hathazari | 107 | 2000 | Ishurdi | 64 | 1930
22 | Mirpur | 116 | 1930 | Khulshi | 202 | 1700 | Ruppur Paromanobik | 2 | 100
23 | Kalyanpur | 129 | 1930 | Halishahar | 157 | 1500 | Natore | 135 | 2000
24 | Gulshan | 172 | 1600 | Baraulia | 182 | 300 | Bogra | 255 | 2000
25 | Uttara | 90 | 1930 | Sikalbaha | 38 | 2000 | Noagaon | 123 | 2000
26 | Uttara New | 19 | 1000 | Dohazari | 94 | 2100 | Rajshahi | 160 | 2000
27 | Kamrangirchar | 75 | 1930 | Cox'sbazar | 94 | 2400 | C.Nawabganj | 77 | 1930
28 | Savar | 149 | 1500 | Chandraghona | 28 | 1900 | Amnura | 36 | 2000
29 | Bhasantec | 173 | 1600 | Kaptai | 5 | 1930 | Pabna | 121 | 2000
30 | Agargaon | 68 | 1300 | A. Khaer Stl. | 0 | 100 | Shahjadpur | 108 | 1930
31 | Satmosjid | 113 | 1930 | Bakulia | 116 | 1900 | Serajganj | 111 | 2000
32 | Tongi | 162 | 2100 | Julda | 20 | 1900 | Niyamatpur | 61 | 100
33 | Kabirpur | 221 | 1200 | TK chemical | 4 | 1600 | Joypurhat | 50 | 1930
34 | Basundhara | 138 | 1900 | Modern Steel | 12 | 500 | Mohastangor | 17 | 1930
35 | Manikganj | 92 | 2100 | Shahmirpur | 35 | 2400 | Rangpur | 145 | 1930
36 | Joydevpur | 230 | 2000 | Khagrachhari | 21 | 1930 | Lalmonirhat | 94 | 2000
37 | New Tongi | 105 | 1500 | Matarbari | 31 | 2100 | Saidpur | 109 | 2000
38 | Korda | 260 | 1930 | Baroiar Hat | 38 | 2100 | Purbasadipur | 103 | 2000
39 | Dhamrai | 60 | 1930 | Rangamati | 12 | 1900 | Thakurgaon | 74 | 2000
40 | Valuka | 120 | 1930 | Abul Khair 230 | 128 | 100 | Palashbari | 111 | 2000
41 | Tangail | 187 | 2200 | BSRM | 142 | 800 | Barapukuria | 51 | 2000
42 | Mymensing | 231 | 2100 | Goalpara | 28 | 1900 | Panchagar | 41 | 1930
43 | Kishorganj | 130 | 2200 | Central (S) | 96 | 1930 | Joldhaka | 19 | 2000
44 | Netrokona | 98 | 2200 | Noapara | 102 | 1930
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-06-23
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 386 | 8:00 | 381 | 12:00 | Kaliakoir | 367 | 6:00 | 352
2 | Bheramara | 401 | 4:00 | 385 | 22:00 | Bhulta | 381 | 5:00 | 366
3 | Ashuganj(N) | 385 | 6:00 | 372 | 16:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 16:00
1 | Ghorasal | 230 | 1:00 | 222 | 11:00 | Hathazari | 222 | 3:00 | 217
2 | Ishurdi | 237 | 6:00 | 225 | 12:00 | Megnaghat | 220 | 1:00 | 215
3 | Ashuganj | 235 | 1:00 | 225 | 15:00 | Fenchuganj | 235 | 5:00 | 229
4 | Serajganj | 232 | 18:00 | 226 | 23:00 | Siddhirganj | 222 | 4:00 | 212
5 | Baghabari | 230 | 7:00 | 225 | 15:00 | Maniknagar | 218 | 3:00 | 208
6 | Barapukuria | 234 | 6:00 | 221 | 21:00 | Old Airport | 217 | 4:00 | 207
7 | Bogra | 227 | 6:00 | 211 | 21:00 | Barisal | 236 | 6:00 | 223
8 | Khulna South | 233 | 18:00 | 224 | 12:00 | AKSML | 219 | 4:00 | 214
9 | Rampura | 221 | 3:00 | 211 | 12:00 | BSRM | 220 | 7:00 | 214
10 | Haripur | 220 | 4:00 | 211 | 12:00 | Bibiyana | 232 | 5:00 | 226
11 | Hasnabad | 220 | 3:00 | 210 | 11:00 | Bhulta | 222 | 5:00 | 212
12 | Aminbazar | 219 | 5:00 | 209 | 12:00 | Ashuganj (S) | 233 | 4:00 | 224
13 | Tongi | 221 | 4:00 | 210 | 11:00 | Kaliakoir | 221 | 5:00 | 213
14 | Comilla (N) | 229 | 7:00 | 222 | 9:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 128 | 1830 | 121 | 1000 | Hathazari | 132 | 400 | 128
2 | Munsiganj | 129 | 1830 | 121 | 1200 | Khulshi | 130 | 600 | 125
3 | Megnaghat | 129 | 1930 | 122 | 1000 | Halishahar | 134 | 2000 | 129
4 | Shyampur | 128 | 1830 | 122 | 1000 | Baraulia | 130 | 700 | 127
5 | Bhulta | 121 | 1830 | 112 | 1000 | Sikalbaha | 134 | 1700 | 129
6 | Madanganj | 126 | 100 | 120 | 1300 | Dohazari | 132 | 1700 | 127
7 | Shitalakhya | 135 | 2000 | 124 | 1200 | Cox'sbazar | 126 | 1700 | 118
8 | Rahim steal | 129 | 1900 | 122 | 1000 | Chandraghona | 132 | 600 | 129
9 | Matuail | 127 | 2000 | 120 | 1200 | Kaptai | 132 | 100 | 129
10 | Ghorasal | 135 | 100 | 132 | 1200 | A. Khaer Stl. | 130 | 100 | 127
11 | Narsinghdi | 123 | 1830 | 114 | 1200 | Bakulia | 132 | 600 | 128
12 | Haripur (SBU) | 128 | 1800 | 124 | 1000 | Julda | 134 | 1800 | 129
13 | Ullon | 133 | 600 | 123 | 1500 | TK Chemical | 136 | 2400 | 131
14 | Hasnabad | 130 | 1800 | 124 | 1200 | Modern Steel | 133 | 100 | 128
15 | Magbazar | 135 | 600 | 123 | 1300 | Shahmirpur | 133 | 1800 | 129
16 | Maniknagar | 133 | 600 | 125 | 1200 | Khagrachhari | 131 | 1830 | 127
17 | Bangabhaban | 133 | 600 | 125 | 1200 | Matarbari | 129 | 1800 | 120
18 | Narinda | 133 | 600 | 125 | 1200 | Baroiar Hat | 127 | 1700 | 123
19 | Dhanmondi | 133 | 600 | 123 | 1500 | Rangamati | 131 | 100 | 128
20 | Lalbag | 127 | 400 | 118 | 1200 | Goalpara | 139 | 1800 | 133
21 | Madartek | 133 | 400 | 127 | 1500 | Central s/s | 138 | 1800 | 131
22 | Mirpur | 132 | 500 | 126 | 1500 | Noapara | 135 | 1700 | 127
23 | Kalyanpur | 134 | 300 | 127 | 1200 | Jessore | 130 | 600 | 118
24 | Gulshan | 133 | 600 | 122 | 1200 | Jhenida | 129 | 600 | 114
25 | Uttara | 129 | 100 | 123 | 1200 | Bottail | 135 | 600 | 122
26 | Uttara New | 132 | 100 | 126 | 1200 | G.K.Project | 137 | 600 | 132
27 | Kamrangirchar | 129 | 600 | 120 | 1200 | Faridpur | 132 | 700 | 120
28 | Savar | 132 | 400 | 124 | 1300 | Madaripur | 134 | 600 | 123
29 | Bhasantec | 135 | 500 | 128 | 1000 | Gopalganj | 140 | 600 | 130
30 | Agargaon | 136 | 400 | 127 | 1200 | Bagerhat | 138 | 1800 | 129
31 | Satmosjid | 136 | 400 | 127 | 1200 | Mongla | 134 | 1700 | 127
32 | Tongi | 136 | 400 | 128 | 1500 | Satkhira | 136 | 600 | 128
33 | Kabirpur | 133 | 500 | 123 | 1200 | Gallamari | 138 | 1800 | 133
34 | Basundhara | 131 | 1830 | 126 | 1500 | Magura | 129 | 600 | 111
35 | Manikganj | 137 | 1300 | 128 | 900 | Chuadanga | 124 | 600 | 104
36 | Joydevpur | 137 | 1800 | 131 | 1200 | Barisal | 137 | 600 | 130
37 | New Tongi | 132 | 2000 | 126 | 1500 | Patuakhali | 135 | 1700 | 125
38 | Kodda | 134 | 2000 | 124 | 700 | Bhandaria | 136 | 1800 | 126
39 | Dhamrai | 132 | 600 | 123 | 1200 | Barisal (N) | 140 | 600 | 130
40 | Valuka | 125 | 1800 | 107 | 1200 | Sariatpur | 136 | 600 | 121
41 | Tangail | 132 | 600 | 119 | 2100 | Benapol | 132 | 1800 | 118
42 | Mymensing | 129 | 800 | 114 | 2100 | Ishurdi | 139 | 600 | 130
43 | Kishorganj | 130 | 700 | 117 | 2400 | Ruppur Paromanobik | 138 | 1800 | 131
44 | Netrokona | 130 | 600 | 112 | 2300 | Natore | 134 | 1800 | 125
45 | Jamalpur | 137 | 800 | 128 | 2300 | Bogra | 134 | 600 | 122
46 | Sherpur | 136 | 900 | 125 | 2300 | Noagaon | 129 | 600 | 114
47 | Srimongal | 135 | 500 | 130 | 1900 | Rajshahi | 132 | 1830 | 122
48 | Shahjibazar | 135 | 1100 | 128 | 2100 | C.Nawabganj | 128 | 1800 | 120
49 | Fenchuganj | 134 | 100 | 131 | 1930 | Amnura | 130 | 700 | 122
50 | Khulawara | 133 | 500 | 130 | 2300 | Pabna | 136 | 1800 | 127
51 | Sylhet | 134 | 400 | 130 | 1900 | Shahjadpur | 140 | 1800 | 133
52 | Chatak | 134 | 500 | 129 | 1700 | Serajganj | 134 | 500 | 126
53 | Sunamganj | 132 | 600 | 126 | 2200 | Niyamatpur | 127 | 600 | 110
54 | Biani Bazar | 133 | 600 | 128 | 2100 | Joypurhat | 129 | 600 | 113
55 | Comilla(s) | 124 | 1830 | 119 | 1900 | Mohastangor | 132 | 600 | 118
56 | Comilla(n) | 134 | 1830 | 131 | 1000 | Rangpur | 127 | 600 | 110
57 | Chandpur | 135 | 1830 | 130 | 2000 | Lalmonirhat | 121 | 600 | 102
58 | Feni | 128 | 1830 | 123 | 2200 | Saidpur | 129 | 500 | 110
59 | Chowmuhani | 125 | 700 | 119 | 2000 | Purbasadipur | 128 | 600 | 107
60 | Ashuganj | 135 | 700 | 130 | 2100 | Thakurgaon | 125 | 700 | 100
61 | Daudkandi | 129 | 1830 | 123 | 900 | Palashbari | 128 | 600 | 113
62 | B.Baria | 132 | 600 | 124 | 800 | Barapukuria | 134 | 600 | 121

## L-Curve
Date | 2019-06-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 140 | 8384 | 3854 | 12238 |  |  |  | QF-LDC-12
0:30 | 135 | 8172.5 | 3736 | 11908.5 | Date: | 2019-06-23
1:00 | 130 | 7961 | 3618 | 11579
1:30 | 140 | 7817.5 | 3567 | 11384.5
2:00 | 150 | 7674 | 3516 | 11190
2:30 | 170 | 7620.5 | 3428 | 11048.5 | [5 empty] | Gen. at Eve. Peak | 12451 | 12451 MW (21:00 )
3:00 | 190 | 7567 | 3340 | 10907 | [6 empty] | 21:00
3:30 | 220 | 7546 | 3236.5 | 10782.5 | [5 empty] | Gen. at Day Peak | 10320.7 | 10320.7 MW (12:00 )
4:00 | 250 | 7525 | 3133 | 10658 | [6 empty] | 12:00
4:30 | 245 | 7395 | 3048 | 10443 | [5 empty] | Highest Generation | 12451
5:00 | 240 | 7265 | 2963 | 10228 | [6 empty] | 21:00
5:30 | 185 | 6778.4845 | 2918 | 9696.4845
6:00 | 130 | 6291.969 | 2873 | 9164.969
6:30 | 125 | 6179.6145 | 2844 | 9023.6145
7:00 | 120 | 6067.26 | 2815 | 8882.26
7:30 | 210 | 6131.93 | 2783 | 8914.93
8:00 | 300 | 6196.6 | 2751 | 8947.6
8:30 | 305 | 6448.7 | 2827.5 | 9276.2
9:00 | 310 | 6700.8 | 2904 | 9604.8
9:30 | 305 | 6839.95 | 2943.5 | 9783.45
10:00 | 300 | 6979.1 | 2983 | 9962.1
10:30 | 230 | 7116.85 | 2961 | 10077.85
11:00 | 160 | 7254.6 | 2939 | 10193.6
11:30 | 195 | 7282.65 | 2974.5 | 10257.15
12:00 | 230 | 7310.7 | 3010 | 10320.7
12:30 | 132 | 7497.9 | 3012 | 10509.9
13:00 | 34 | 7685.1 | 3014 | 10699.1
13:30 | 19 | 7574.8 | 3084 | 10658.8
14:00 | 4 | 7464.5 | 3154 | 10618.5
14:30 | 7 | 7652.75 | 3132.5 | 10785.25
15:00 | 10 | 7841 | 3111 | 10952
15:30 | 40 | 7848.55 | 3070.5 | 10919.05
16:00 | 70 | 7856.1 | 3030 | 10886.1
16:30 | 95 | 7740.75 | 3040 | 10780.75
17:00 | 120 | 7625.4 | 3050 | 10675.4
17:30 | 140 | 7438 | 2973.5 | 10411.5
18:00 | 160 | 7250.6 | 2897 | 10147.6
18:30 | 205 | 7535.8 | 3128.5 | 10664.3
19:00 | 250 | 7821 | 3360 | 11181
19:30 | 320 | 8528 | 3673 | 12201
20:00 | 340 | 8739 | 3669 | 12408 |  |  |  | Executive Engineer
20:30 | 325 | 8719.5 | 3710 | 12429.5 |  |  |  | Network Operation Division
21:00 | 310 | 8700 | 3751 | 12451
21:30 | 285 | 8639.5 | 3775 | 12414.5
22:00 | 260 | 8579 | 3799 | 12378 |  |  |  |  | Page 6 of 7
22:30 | 215 | 8583.5 | 3829.5 | 12413
23:00 | 170 | 8588 | 3860 | 12448
23:30 | 155 | 8486 | 3857 | 12343
24:00 | 140 | 8384 | 3854 | 12238
12451 MW (21:00 )
10320.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-06-23 |  | Energy | 261308695
[10 empty] | 2019-06-23 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4548 | 915 | 2263 | 3194 | 304 | 70 | 778 | 0 | 166
0:30 | 4425.5 | 924 | 2267.5 | 3079.5 | 303 | 70 | 666 | 0 | 173 | Date: | 2019-06-23
1:00 | 4303 | 933 | 2272 | 2965 | 302 | 70 | 554 | 0 | 180
1:30 | 4303 | 933 | 2319.5 | 2800.5 | 302.5 | 69 | 479 | 0 | 178 | [7 empty] | Total Energy | 261.3087 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 4303 | 933 | 2367 | 2636 | 303 | 68 | 404 | 0 | 176 | [7 empty] | Energy not Served | 0
2:30 | 4315 | 933 | 2368.5 | 2514.5 | 303 | 68 | 373.5 | 0 | 173 | [7 empty] | Energy Requirement | 261.3087
3:00 | 4327 | 933 | 2370 | 2393 | 303 | 68 | 343 | 0 | 170
3:30 | 4333.5 | 933 | 2367.5 | 2294 | 302.5 | 68 | 317 | 0 | 167 | [6 empty] | Shortage
4:00 | 4340 | 933 | 2365 | 2195 | 302 | 68 | 291 | 0 | 164
4:30 | 4368.5 | 932.5 | 2336 | 2028.5 | 302.5 | 68 | 245 | 0 | 162
5:00 | 4397 | 932 | 2307 | 1862 | 303 | 68 | 199 | 0 | 160
5:30 | 4324 | 932.5 | 2062 | 1658.5 | 303.5 | 68 | 199 | 0 | 148
6:00 | 4251 | 933 | 1817 | 1455 | 304 | 68 | 199 | 0 | 136
6:30 | 4182.5 | 933 | 1744 | 1460 | 304 | 67 | 199 | 0 | 129 |  |  |  |  | Coal
7:00 | 4114 | 933 | 1671 | 1465 | 304 | 66 | 199 | 0 | 122
7:30 | 4157 | 933 | 1728.5 | 1388 | 304 | 66 | 199 | 0 | 128 |  |  |  | Oil |  |  |  | ,
8:00 | 4200 | 933 | 1786 | 1311 | 304 | 66 | 199 | 0 | 134
8:30 | 4221 | 932.5 | 1932.5 | 1447 | 304.5 | 67 | 215 | 0 | 140
9:00 | 4242 | 932 | 2079 | 1583 | 305 | 68 | 231 | 0 | 146
9:30 | 4277.5 | 926.5 | 2107.5 | 1699 | 305 | 69 | 231 | 0 | 145
10:00 | 4313 | 921 | 2136 | 1815 | 305 | 70 | 231 | 0 | 144
10:30 | 4260.5 | 918.5 | 2162 | 1961 | 306 | 70 | 231 | 0 | 141
11:00 | 4208 | 916 | 2188 | 2107 | 307 | 70 | 231 | 0 | 138
11:30 | 4272 | 916 | 2221 | 2067.5 | 307 | 70.5 | 236 | 0 | 142
12:00 | 4336 | 916 | 2254 | 2028 | 307 | 71 | 241 | 0 | 146
12:30 | 4409.5 | 850 | 2214.5 | 2203 | 307.5 | 71 | 281.5 | 0 | 150
13:00 | 4483 | 784 | 2175 | 2378 | 308 | 71 | 322 | 0 | 154
13:30 | 4483 | 784 | 2175 | 2378 | 308 | 71 | 322 | 0 | 154
14:00 | 4483 | 784 | 2175 | 2378 | 308 | 71 | 322 | 0 | 154
14:30 | 4369 | 849 | 2147.5 | 2586 | 307 | 71.5 | 313 | 0 | 162
15:00 | 4255 | 914 | 2120 | 2794 | 306 | 72 | 304 | 0 | 170
15:30 | 4227 | 914 | 2063.5 | 2851 | 306 | 71.5 | 301.5 | 0 | 171
16:00 | 4199 | 914 | 2007 | 2908 | 306 | 71 | 299 | 0 | 172
16:30 | 4169 | 914.5 | 1872 | 2956.5 | 306 | 71 | 313.5 | 0 | 170
17:00 | 4139 | 915 | 1737 | 3005 | 306 | 71 | 328 | 0 | 168
17:30 | 4103.5 | 915 | 1691 | 2820.5 | 306 | 70 | 338.5 | 0 | 163
18:00 | 4068 | 915 | 1645 | 2636 | 306 | 69 | 349 | 0 | 158
18:30 | 4102 | 915 | 1686 | 2865.5 | 305.5 | 68.5 | 548 | 0 | 173
19:00 | 4136 | 915 | 1727 | 3095 | 305 | 68 | 747 | 0 | 188
19:30 | 4428 | 914 | 1989 | 3482 | 304 | 68 | 846 | 0 | 170
20:00 | 4520 | 915 | 2043 | 3606 | 304 | 68 | 784 | 0 | 168
20:30 | 4552 | 914.5 | 2103 | 3538 | 304.5 | 68.5 | 781 | 0 | 168
21:00 | 4584 | 914 | 2163 | 3470 | 305 | 69 | 778 | 0 | 168
21:30 | 4600 | 914.5 | 2188 | 3384 | 304.5 | 69.5 | 787 | 0 | 167
22:00 | 4616 | 915 | 2213 | 3298 | 304 | 70 | 796 | 0 | 166
22:30 | 4661.5 | 914.5 | 2250.5 | 3262.5 | 304 | 70 | 787 | 0 | 163
23:00 | 4707 | 914 | 2288 | 3227 | 304 | 70 | 778 | 0 | 160
23:30 | 4627.5 | 914.5 | 2275.5 | 3210.5 | 304 | 70 | 778 | 0 | 163 | Max Temp. in Dhaka |  | 36.1° C
24:00 | 4548 | 915 | 2263 | 3194 | 304 | 70 | 778 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-06-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 40 | 38 | 38 | 38 | 38 | 38 | 36 | 36 | 38 | 40 | 40 | 41 | 41 | 41 | 42 | 41 | 41 | 39 |  | 38 | 38 | 38 | 39 | 40 | 40 | 40 | 872700
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 25 | 25 | 0 |  |  | 2 | 17 | 26 | 25 | 26 | 21 | 16 | 17 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 493054
| Teknaf Solartech 20MW |  |  |  |  | 0 | 1.58 | 5.54 | 11 | 13.9 | 18.8 | 20.3 | 19.6 | 16.3 | 17.5 | 12.8 | 7.6 | 4.7 | 0.9 |  | 0 | [6 empty] | 151065
6 | Sikalbaha 225MW (Gas) | 205 | 203 | 203 | 203 | 205 | 206 | 207 | 215 | 206 | 207 | 205 | 210 | 206 | 206 | 216 | 206 | 205 | 205 |  | 212 | 205 | 205 | 205 | 205 | 205 | 205 | 4910983
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 135 | 130 | 130 | 130 |  | 135 | 130 | 130 | 130 | 130 | 131 | 130 | 2494272
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 34 | 34 | 17 | 0 | [8 empty] | 6 | 17 | 16 | 16 | 33 | 31 |  | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 392258
12 | Hathazari peaking | 24 | 0 | [17 empty] | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 495200
Baraka Sikalbaha PL
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [19 empty] | 50 | 50 | 0 |  |  |  |  | 62480
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | 14 | 0 | [8 empty] | 4 | 14 | 31 | 45 | 45 | 45 | 45 | 45 |  | 45 | 75 | 150 | 45 | 45 | 45 | 45 | 795382
19 | Ashuganj 195MW Modular | 110 | 110 | 110 | 110 | 110 | 55 | 55 | 55 | 54 | 54 | 54 | 54 | 54 | 54 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1639272
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 852000
21 | Ghorasal GT: Unit-3 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 219 | 250 | 230 | 230 | 230 | 230 | 229 |  | 230 | 230 | 229 | 229 | 229 | 229 | 229 | 4953000
22 | Ghorasal GT: Unit-4 | 200 | 200 | 200 | 200 | 201 | 150 | 150 | 150 | 152 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3868000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 230 | 210 | 240 | 240 | 240 | 240 | 240 | 240 | 160 |  | 200 | 240 | 240 | 240 | 240 | 240 | 100 | 5199600
26
28 | Ashuganj ST: Unit- 3 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 3035002
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK
33 | Ashuganj CCPP 225 MW | 217 | 217 | 217 | 217 | 217 | 217 | 215 | 214 | 214 | 150 | 150 | 150 | 183 | 184 | 202 | 194 | 183 | 181 |  | 194 | 181 | 216 | 215 | 214 | 214 | 217 | 4802000
34 | Ashuganj CCPP(South) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 250 | 246 | 242 | 239 | 235 | 184 | 30 | 45 | 100 | 120 | 135 |  | 140 | 170 | 220 | 220 | 260 | 300 | 300 | 5972000
| Ashuganj CCPP(North) | 15 | 20 | 40 | 100 | 160 | 170 | 190 | 280 | 230 | 320 | 285 | 360 | 360 | 275 | 275 | 205 | 205 | 215 |  | 225 | 315 | 335 | 360 | 320 | 320 | 320 | 5754200
35 | Ashuganj (Precision) 55MW | 56 | 56 | 56 | 55 | 56 | 56 | 56 | 55 | 55 | 55 | 53 | 53 | 53 | 50 | 50 | 50 | 51 | 51 |  | 54 | 54 | 54 | 54 | 55 | 55 | 55 | 1304160
36 | Chandpur CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 30 | 30 | 30 | 30 | 30 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1722480
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 330 | 327 | 327 | 327 | 329 | 290 | 250 | 332 | 344 | 351 | 331 | 339 | 336 | 347 | 346 | 337 | 330 | 318 |  | 285 | 335 | 329 | 338 | 328 | 341 | 330 | 7988220
40 | Meghnaghat CCPP 450MW | 400 | 400 | 400 | 400 | 400 | 400 | 350 | 350 | 350 | 380 | 420 | 420 | 420 | 380 | 420 | 370 | 340 | 340 |  | 400 | 400 | 400 | 430 | 390 | 390 | 390 | 9126375
41 | Haripur Power CCPP 360MW | 325 | 331 | 330 | 331 | 331 | 286 | 258 | 349 | 346 | 344 | 303 | 341 | 337 | 339 | 336 | 339 | 339 | 284 |  | 281 | 304 | 302 | 302 | 350 | 350 | 351 | 7693000
42 | Mymensingh RPCL 210MW | 146 | 148 | 148 | 148 | 148 | 148 | 144 | 143 | 143 | 143 | 141 | 139 | 143 | 140 | 139 | 138 | 139 | 142 |  | 141 | 142 | 143 | 143 | 143 | 144 | 146 | 3348240
43 | Haripur NEPC 110MW | 13 | 0 | [8 empty] | 26 | 26 | 55 | 55 | 110 | 110 | 110 | 70 |  | 70 | 70 | 70 | 26 | 26 | 26 | 26 | 744600
44 | Fenchugonj CCPP-1 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 53 | 53 | 53 |  | 54 | 54 | 53 | 54 | 54 | 54 | 54 | 1269000
45 | Fenchugonj CCPP-2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 50 | 50 | 50 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1471000
46 | Shajibazar 330 MW | 306 | 305 | 306 | 305 | 303 | 306 | 308 | 308 | 323 | 309 | 303 | 310 | 308 | 308 | 310 | 308 | 306 | 307 |  | 310 | 305 | 306 | 305 | 304 | 308 | 307 | 7065000
47 | Shahjibazar GT: Unit- 8, 9 | 58 | 62 | 63 | 64 | 54 | 56 | 61 | 60 | 60 | 61 | 59 | 59 | 62 | 58 | 59 | 61 | 61 | 57 |  | 61 | 61 | 57 | 61 | 61 | 61 | 49 | 1404768
48 | Shahjibazar 86MW | 83 | 83 | 83 | 83 | 83 | 50 | 10 | 10 | 83 | 49 | 79 | 78 | 78 | 80 | 78 | 78 | 10 | 10 |  | 10 | 73 | 83 | 80 | 82 | 81 | 81 | 1577280
49 | Shahjibazar (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 5 | 5 | 5 | 43 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 10 | 10 |  | 10 | 42 | 44 | 44 | 44 | 44 | 44 | 837720
50 | Sylhet GT 150 MW | 110 | 111 | 110 | 108 | 109 | 109 | 78 | 76 | 123 | 113 | 111 | 120 | 110 | 115 | 111 | 116 | 110 | 108 |  | 124 | 108 | 109 | 110 | 115 | 110 | 118 | 2690240
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 7 | 7 | 7 | 45 | 41 | 43 | 43 | 44 | 41 | 41 | 45 | 13 | 13 |  | 41 | 47 | 47 | 46 | 47 | 47 | 45 | 890640
53 | Sylhet (Desh) 10MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 8 | 6 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 216000
54 | Hobiganj 11MW | 0 | 2 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246096
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 38 | 44 | 46 | 47 | 47 | 47 | 47 | 50 | 14 | 14 |  | 14 | 53 | 53 | 53 | 53 | 53 | 53 | 950400
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 569472
57 | Summit Bibiana- 2 | 300 | 300 | 290 | 290 | 290 | 270 | 270 | 290 | 310 | 300 | 280 | 290 | 300 | 300 | 330 | 315 | 300 | 305 |  | 300 | 325 | 320 | 320 | 315 | 330 | 285 | 7568000
58 | Southern 55MW | 55 | 35 | 17 | 17 | 0 |  |  |  | 5 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 960000
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | 16 | 16 | 21 |  | 26 | 26 | 33 | 33 | 33 | 16 | 32 | 496320
60 | Barabkunda (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 21 | 21 | 21 | 21 | 20 | 19 | 456288
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 476676
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465120
63 | Tripura | 180 | 176 | 170 | 164 | 160 | 136 | 122 | 134 | 146 | 144 | 138 | 146 | 154 | 160 | 170 | 172 | 168 | 158 |  | 188 | 170 | 168 | 168 | 166 | 160 | 166 | 3819840
64 | Malancha, Ctg. EPZ (United) | 31 | 32 | 41 | 41 | 37 | 42 | 35 | 11 | 2 | 2 | 6 | 2 | 10 | 4 | 2 | 4 | 6 | 2 |  | 2 | 8 | 21 | 27 | 36 | 39 | 39 | 463680
65 | Feni (Doreen) 22MW | 22 | 0 | [8 empty] | 21 | 21 | 21 | 21 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 299232
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 185400
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 608100
68 | Summit Cumilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 453620
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 28 | 28 | 28 | 26 | 28 | 28 | 30 | 30 |  | 26 | 22 | 32 | 32 | 32 | 32 | 32 | 693540
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 784900
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792000
73 | Ghorashal (Regent) | 108 | 108 | 108 | 108 | 104 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 0 | 0 | 0 | [8 empty] | 0 | 52 | 1145818
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | 24 | 24 | 16 | 0 |  |  |  | 0 |  |  |  |  | 9 | 30 | 40 | 75 | 85 | 70 |  | 74 | 80 | 90 | 97 | 100 | 100 | 100 | 1018560
78 | Gazipur (RPCL) | 50 | 24 | 24 | 24 | 0 | 0 |  | 7 | 25 | 32 | 33 | 33 | 33 | 33 | 32 | 32 | 33 | 41 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 783660
79 | Kodda 149MW | 130 | 64 | 64 | 64 | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 98 | 125 | 125 | 126 | 125 | 125 |  | 125 | 125 | 125 | 125 | 126 | 125 | 125 | 2080320
80 | Jamalpur 95MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 84 | 56 | 55 | 66 | 72 | 85 | 85 | 85 |  | 85 | 85 | 84 | 84 | 84 | 84 | 84 | 1938240
81 | Lakdhanvi 52 MW | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 | 52 | 52 | 52 | 52 | 25 |  | 25 | 43 | 40 | 52 | 52 | 52 | 52 | 861984
| Gazipur 100 MW | 106 | 106 | 106 | 106 | 70 | 70 | 70 | 70 | 90 | 88 | 89 | 89 | 72 | 72 | 89 | 89 | 106 | 106 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 2262000
| Kaptai Solar |  |  |  |  | 0 | 0.189 | 2.02 | 3.1 | 3.1 | 6 | 6 | 0 | 5.5 | 4.7 | 3.8 | 1.1 | 1.1 | 0.1 |  | 0 | [6 empty] | 28860
82 | Madanganj 102MW | 30 | 30 | 30 | 15 | 0 | [9 empty] | 20 | 40 | 48 | 48 |  | 48 | 0 |  | 13 | 15 | 16 | 30 | 396240
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | 27 | 0 | [14 empty] | 0 | 0 |  | 59 | 100 | 100 | 50 | 10 | 10 | 10 | 326229
86 | Meghnaghat CCPP(Summit) | 270 | 270 | 260 | 270 | 270 | 250 | 275 | 290 | 300 | 255 | 270 | 300 | 245 | 262 | 270 | 265 | 275 | 240 |  | 285 | 270 | 250 | 272 | 282 | 285 | 240 | 6524305
87 | Meghnaghat (IEL) | 7 | 0 | [8 empty] | 1 | 7 | 35 | 51 | 93 | 93 | 100 | 78 |  | 90 | 100 | 97 | 100 | 100 | 100 | 100 | 1083840
88 | Ghorashal 78MW (MAX) | 0 | 25 | 30 | 30 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | [11 empty] | 481376
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | [8 empty] | 75000
91 | Juldah (Acorn) | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 30 |  | 60 | 88 | 100 | 100 | 88 | 88 | 88 | 809040
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 32 | 50 | 50 | 50 | 50 | 50 | 50 | 46 | 10 | 10 |  | 10 | 20 | 43 | 50 | 50 | 50 | 50 | 983736
93 | Ashuganj (Midland) 51MW | 35 | 35 | 35 | 35 | 35 | 5 | 5 | 5 | 5 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 |  | 10 | 12 | 25 | 35 | 35 | 35 | 35 | 639916
94 | Gagnagar (Orion) | 7 | 0 | [6 empty] | 7 | 16 | 30 | 48 | 84 | 101 | 101 | 101 | 101 | 64 |  | 84 | 101 | 101 | 64 | 64 | 64 | 64 | 1110672
95 | Patenga 50MW | 47 | 41 | 47 | 47 | 46 | 47 | 47 | 46 | 46 | 46 | 47 | 46 | 46 | 45 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1104000
96 | Chattogram ECPV 108 MW | 82 | 82 | 82 | 82 | 22 | 12 | 12 | 12 | 22 | 70 | 77 | 80 | 83 | 81 | 83 | 91 | 96 | 96 |  | 96 | 96 | 96 | 96 | 97 | 97 | 97 | 1808640
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 15 | 40 | 49 | 48 | 24 | 6 | 292656
98 | Bosila 108MW | 66 | 66 | 66 | 66 | 8 | 8 | 8 | 8 | 36 | 42 | 58 | 63 | 41 | 56 | 58 | 62 | 62 | 62 |  | 62 | 64 | 41 | 51 | 64 | 64 | 64 | 1210560
99 | Madanganj-55 MW | [13 empty] | 5 | 15 | 40 | 47 | 48 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 495224
100 | Northern 55 MW | 55 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 53 | 54 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1071574
101 | Kushiara 163 MW CCPP GT | 100 | 163 | 163 | 163 | 163 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 130 | 163 | 163 | 130 | 3286219
102 | Sarishabari (Solar) |  |  |  |  | 0 | 0.2 | 0.7 | 0.5 | 1.8 | 2.3 | 2.3 | 2.1 | 2.3 | 2.3 | 0.4 | 1.4 | 0.6 | 0.6 |  | 0 | [6 empty] | 14250
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1271160
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 189 | 192 | 192 | 189 | 189 | 100 | 100 | 60 | 100 | 122 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 |  | 151 | 180 | 180 | 180 | 180 | 163 | 165 | 3415200
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 113 | 58 | 15 | 0 |  |  |  | 0 | 12 | 62 | 123 | 149 | 149 | 149 | 149 | 148 | 149 | 115 |  | 110 | 120 | 141 | 149 | 150 | 150 | 149 | 2279520
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2388480
116 | Chandpur Desh 200MW | 196 | 196 | 197 | 198 | 198 | 160 | 144 | 105 | 115 | 173 | 200 | 180 | 185 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 196 | 195 | 196 | 4447200
117 | Midland 150MW | 135 | 78 | 50 | 50 | 50 | 0 | [11 empty] | 0 |  | 16 | 138 | 138 | 140 | 0 | 0 |  | 796218
118 | Bibiyana-3 285 MW | 279 | 296 | 297 | 260 | 260 | 200 | 150 | 200 | 250 | 249 | 249 | 250 | 291 | 241 | 239 | 240 | 199 | 201 |  | 200 | 294 | 296 | 292 | 293 | 293 | 295 | 6047000
| United Jamalpur PPL | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 87 | 87 | 87 | 87 | 0 | 72 | 84 | 85 | 85 | 83 | 95 |  | 96 | 96 | 96 | 96 | 96 | 96 | 95 | 2028000
| Anwara United | 270 | 270 | 270 | 268 | 258 | 116 | 116 | 117 | 118 | 116 | 201 | 250 | 268 | 271 | 271 | 274 | 274 | 221 |  | 260 | 260 | 261 | 261 | 261 | 261 | 261 | 5497418
120 | Eastern Zone Total | 7961 | 7674 | 7567 | 7525 | 7265 | 6291.969 | 6067.26 | 6196.6 | 6700.8 | 6979.1 | 7254.6 | 7310.7 | 7685.1 | 7464.5 | 7841 | 7856.1 | 7625.4 | 7250.6 |  | 7821 | 8528 | 8739 | 8700 | 8579 | 8588 | 8384 | 183110990
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 115 | 115 | 66 | 32 | 0 | [6 empty] | 7 | 32 | 55 | 94 | 115 | 115 | 66 |  | 78 | 115 | 115 | 115 | 99 | 115 | 115 | 1474560
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 24 | 24 | 24 | 0 | [15 empty] | 25 | 22 | 21 | 22 | 23 | 17 | 17 | 179520
| Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 155 | 135 | 50 | 40 | 45 | 45 |  | 120 | 165 | 165 | 165 | 165 | 165 | 165 | 2938560
129 | Labon Chora 105 MW | 72 | 72 | 72 | 72 | 53 | 35 | 35 | 35 | 35 | 54 | 70 | 72 | 72 | 90 | 90 | 70 | 70 | 70 |  | 70 | 105 | 105 | 105 | 105 | 72 | 72 | 1679520
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 64 | 32 | 32 | 16 | 16 | 0 |  |  |  |  | 32 | 32 | 32 | 40 | 64 | 64 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1283520
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 95 | 95 | 96 | 96 | 96 | 96 | 95 | 92 | 91 | 92 | 90 | 90 | 92 | 92 | 87 | 87 | 93 | 93 |  | 56 | 95 | 95 | 95 | 95 | 97 | 97 | 2214132
| Bhola CCPP 194MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2888000
140 | Bhola (Venture) 33MW | 37 | 37 | 36 | 31 | 31 | 27 | 25 | 24 | 24 | 23 | 22 | 24 | 24 | 26 | 27 | 26 | 22 | 24 |  | 29 | 35 | 35 | 36 | 38 | 38 | 35 | 702257
141 | Bangla Trak Noapara | 100 | 60 | 30 | 0 | [15 empty] | 0 | 45 | 48 | 62 | 100 | 100 | 100 | 633600
142 | Noapara (KZA) 40MW | [11 empty] | 32 | 32 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 488250
143 | Gopalganj Peaking | 60 | 0 | [13 empty] | 4 | 12 | 24 |  | 50 | 76 | 64 | 60 | 60 | 60 | 60 | 452352
144 | Bheramara GT-1,2,3 | [19 empty] | 14 | 30 | 30 | 30 | 30 | 30 | 30 | 143300
145 | Madhumati Power Plant | 106 | 106 | 106 | 106 | 105 | 105 | 105 | 71 | 105 | 105 | 105 | 105 | 104 | 87 | 87 | 68 | 69 | 69 |  | 86 | 87 | 86 | 86 | 86 | 87 | 86 | 2254176
146 | Bheramara HVDC | 933 | 933 | 933 | 933 | 932 | 933 | 933 | 933 | 932 | 921 | 916 | 916 | 784 | 915 | 914 | 914 | 915 | 915 |  | 915 | 914 | 915 | 914 | 915 | 914 | 915 | 21943273
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 62 | 63 | 63 | 62 | 63 | 64 | 64 | 64 | 65 | 65 | 67 | 67 | 68 | 66 | 66 | 66 | 66 | 66 |  | 65 | 64 | 65 | 65 | 64 | 65 | 64 | 1565672
152 | Barapukuria Unit-3 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 239 | 240 | 240 | 239 | 240 | 5824200
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 60 | 60 | 60 | 60 | 60 | 60 | 1380000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [13 empty] | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 538504
157 | Sirajgonj Unit-1 225MW (Gas) | 184 | 183 | 182 | 182 | 183 | 181 | 171 | 166 | 188 | 195 | 176 | 169 | 191 | 174 | 170 | 166 | 159 | 156 |  | 156 | 167 | 161 | 173 | 183 | 195 | 185 | 4506773
158 | Sirajgonj Unit-1 225MW (Oil) | [7 empty] | 0
| Sirajgonj Unit-2 225MW (Gas) | 181 | 180 | 180 | 179 | 180 | 179 | 165 | 157 | 183 | 193 | 193 | 166 | 185 | 162 | 161 | 156 | 149 | 146 |  | 147 | 156 | 151 | 164 | 180 | 192 | 182 | 4325009
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 209 | 208 | 202 | 198 | 199 | 193 | 180 | 168 | 196 | 203 | 184 | 170 | 197 | 163 | 172 | 167 | 160 | 160 |  | 158 | 167 | 162 | 170 | 184 | 203 | 204 | 4633636
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 350 | 350 | 350 | 350 | 300 | 250 | 230 | 250 | 300 | 350 | 330 | 400 | 370 | 370 | 370 | 320 | 320 | 280 |  | 310 | 320 | 320 | 360 | 360 | 415 | 420 | 8012363
161 | Bera Peaking | [16 empty] | 0 | 5 |  | 28 | 27 | 26 | 26 | 26 | 26 | 26 | 139839
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 503040
163 | Bogra (EPL) | 14 | 14 | 14 | 14 | 3 | 11 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 13 |  | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 300816
164 | Ullapara (Summit) | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 5 | 0 | 11 | 163188
165 | Amnura 50MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 33 | 33 | 33 | 33 | 6 | 6 | 6 | 230540
166 | Katakhali (Northern) | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 24 | 43 | 43 | 43 | 43 | 43 | 456902
167 | Katakhali Peaking | 44 | 44 | 0 | [14 empty] | 0 |  | 36 | 44 | 47 | 44 | 44 | 44 | 44 | 348000
168 | Santahar Peaking | 21 | 21 | 21 | 10 | 0 | [12 empty] | 0 |  | 28 | 29 | 29 | 29 | 29 | 21 | 21 | 323266
169 | Rajlanka 52 MW | 51 | 51 | 51 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 45 | 49 | 49 | 49 | 16 |  | 34 | 50 | 50 | 50 | 50 | 50 | 50 | 761760
170 | Chapainawabganj-100 MW | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 69 |  | 90 | 95 | 95 | 95 | 95 | 92 | 92 | 1665372
171 | Paramount Baghabari | [19 empty] | 30 | 0 | 0 |  |  |  |  | 44933
172 | Confidence Bogura-2 (CPBL) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 53 |  | 102 | 108 | 108 | 108 | 108 | 108 | 108 | 2526432
173 | Rangpur GT | 17 | 17 | 17 | 17 | 0 | [12 empty] | 0 |  | 0 |  |  |  | 16 | 17 | 17 | 114000
175 | Saidpur GT | 17 | 17 | 17 | 17 | 0 | [12 empty] | 0 |  | 18 | 18 | 17 | 17 | 17 | 16 | 16 | 161000
176 | Confidence Rangpur | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 17 | 16 | 13 | 14 | 13 | 13 | 13 | 13 | 10 | 10 | 15 |  | 13 | 15 | 17 | 17 | 17 | 17 | 17 | 397440
177
178
178 | Western Zone Total | 3618 | 3516 | 3340 | 3133 | 2963 | 2873 | 2815 | 2751 | 2904 | 2983 | 2939 | 3010 | 3014 | 3154 | 3111 | 3030 | 3050 | 2897 | 0 | 3360 | 3673 | 3669 | 3751 | 3799 | 3860 | 3854 | 78197705