## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-02-01 | Tuesday
|  |  | Date (day): | 2022-02-01 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11234.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12010 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-01-31 | 2022-02-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 220 | 200 | 200 | 200
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 164 | 167 | 180 | 200 | 160 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 170 | 160 | 170 | 170 | 280 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 36 | 60 | 50 | 60 |  | 40 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 46 | 48 | 51 | 51
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 34 | 35 | 35 |  | 45 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 20 | 20 |  | 13 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 250 | 270 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 132 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 80 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 1959 | 2386 | 2536 | 2636 | 1840 | 1205
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 39 | 40 | 40 |  | 10 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 84 | 83 | 84 | 84 |  | 146 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 96 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 19 | 20 |  | 2 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 18 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 85 | 89 | 90 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 282 | 300 | 260 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 2 | 17 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 23 | 34 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 40 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 115 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 887 | 1027 | 1266 | 1297 | 180 | 898
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 196 | 180 | 200 | 21 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 200 | 150 | 200 | 200 | 160 |  | ST under maint, Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 265 | 270 | 300 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 25 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 135 | 147 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 50 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 86 | 86 | 88 |  | 75 | ST under maint
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 85 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 18 | 18 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 116 | 138 | 160
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 8 | 25 | 25 |  | 8 | Engine problem
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 6 | 9 | 9 | 9 |  | 16 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 106 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 12 | 0 | 0 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1385 | 1540 | 1822 | 2003 | 697 | 136
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 85 | 105 | 100 | 110 | 92 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 194 | 200 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 89 | 98 | 98 | 100
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 455 | 447 | 493.6 | 454 | 92 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 135 | 136 | 150 | 150 |  | 180 | GT-2 under S/D due to gas
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 53 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 67 | 69 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 76 | 75 | 80
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 177 | 177 | 180 | 180 |  | 51 | Machine problem
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 285 | 330 | 330
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 | 10 |  | Gas shortage
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1383 | 1393 | 1467 | 1472 | 63 | 840
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 736 | 769 | 744 | 744
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 28 | 0 | 35 |  | 19 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 19 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 10 | 80 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 100 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 924 | 931 | 1024 | 1344 | 410 | 88
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 24 | 20 | 24 |  | 9 | Engine problem
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 92 | 90 | 92 | 102 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 310 | 380 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 221 | 220 | 220
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 651 | 728 | 1071 | 1227 | 186 | 9
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 34 | 34 |  | 18 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 34 | 47 | 50 | 50 |  | 21 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 135 | 134 | 130 | 140 | 80 |  | Gas shortage
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 345 | 295 | 300 | 300 | 114 |  | Gas shortage
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 30 | 31 |  | 19 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 50 | 100 | 90 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 50 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 914 | 1042 | 1234 | 1249 | 794 | 75
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 107 | 107 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 311 | 307 | 321 | 328 | 74 | 195
|  | Total |  |  |  |  | 22066 | 21035 | 8869 | 9801 | 11234.6 | 12010 | 4336 | 3454
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8738.6933 | 9657 | 11069.537 | 11833.5445
| A. |  | 2022-01-31 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 9801 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6119 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9801 | MW
| 3 | Day peak Generation : |  |  | 8869 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9657 | MW
| 4 | Evening peak Generation : |  |  | 9801 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 197.3276 | MKWHr | By Solar | 1.1322 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 92.4249 | MKWHr |  | By Oil: | 68.3804 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.5281 | MKWHr |  | By Hydro: | 1.9687 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4336 | MW | Dhaka | 3540 | 3540 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3454 | MW | Chittagong | 1058 | 1058 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7790 | MW | Khulna | 1127 | 1127 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 729.16 | MMCFD |  |  | Rajshahi | 1007 | 1007 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 91133446.73 | ii) Oil : | Taka | 498367361.73 | Comilla | 778 | 778 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 64385095 | Total | Taka | 653885903.46 | Mymensingh | 857 | 857 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.258 | MKWHr. | Sylhet | 335 | 335 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -247 | MW (E to W) at | 19:00 | hrs | Barisal | 245 | 245 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -247 | MW at | 19:00 | hrs | Rangpur | 710 | 710 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 24° C |  |  | Total | 9657 | 9657 |  | 0
| B. |  | 2022-02-01 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 26° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12010 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 2010 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 201.3341 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6140 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.6604 | MKWHr. | ii) HVDC Flow at Peak Time |  | 769 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.233 | MKWHr. | iii) Maximum HVDC Flow : |  | 769 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.81 |  | (b) Today: | 93.69 |  | (c) Rule Curve: |  | 97
.

## YesterdayGen
2022-01-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 225 | 0 | 0 | 7 | 0 | 0 | 163 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 48 | 35 | 35 | 17 | 22 | 25 | 9 | 16 | 13 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 41 | 40 | 17 | 35 | 0 | 0 | 0 | 140 | 275 | 226 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 25 | 9 | 79 | 112 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 138 | 40 | 81 | 0 | 177 | 0 | 0 | 0 | 270 | 16 | 11 | 0 | 95 | 0 | 0 | 120 | 0 | 22 | 0 | 0 | 0 | 135 | 0 | 8 | 90 | 17 | 0 | 260 | 0 | 0 | 0 | 8 | 0 | 340 | 104 | 0 | 162 | 106 | 0 | 17 | 0 | 0 | 55 |  | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 114 | 0 | 255 | 0 | 0 | 50 | 0 | 105 | 0 | 0 | 35 | 310 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4648 | 2209 | 6857 | 2274 | 737 | 1437 | 0 | 1738 | 510 | 82 | 0 | 0 | 79 | 0 | 0 | 93.83
2:00 | 0 | 0 | 220 | 0 | 0 | 7 | 0 | 0 | 177 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 17 | 17 | 22 | 25 | 9 | 16 | 13 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 22 | 40 | 17 | 35 | 0 | 0 | 0 | 140 | 270 | 190 | 8 | 87 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 25 | 9 | 77 | 112 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 135 | 72 | 81 | 0 | 177 | 0 | 0 | 0 | 295 | 16 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 8 | 90 | 17 | 0 | 230 | 0 | 0 | 0 | 8 | 0 | 340 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 116 | 0 | 284 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 310 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4502 | 2097 | 6599 | 2260 | 685 | 1505 | 0 | 1481 | 510 | 81 | 0 | 0 | 77 | 0 | 0 | 93.83
3:00 | 0 | 0 | 220 | 0 | 0 | 7 | 0 | 0 | 180 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 17 | 17 | 22 | 25 | 9 | 16 | 13 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 12 | 40 | 17 | 35 | 0 | 0 | 0 | 140 | 270 | 184 | 8 | 87 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 25 | 9 | 75 | 112 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 135 | 72 | 81 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 8 | 90 | 17 | 0 | 190 | 0 | 0 | 0 | 8 | 0 | 340 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 17 |  | 685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 116 | 0 | 299 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 280 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4381 | 2051 | 6432 | 2254 | 685 | 1516 | 0 | 1341 | 480 | 81 | 0 | 0 | 75 | 0 | 0 | 93.82
4:00 | 0 | 0 | 220 | 0 | 0 | 7 | 0 | 0 | 193 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 17 | 17 | 22 | 25 | 9 | 16 | 13 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 12 | 40 | 17 | 35 | 0 | 0 | 0 | 140 | 270 | 182 | 8 | 85 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 25 | 9 | 73 | 113 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 134 | 72 | 81 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 8 | 35 | 17 | 0 | 135 | 0 | 0 | 0 | 8 | 0 | 340 | 55 | 0 | 162 | 51 | 0 | 17 | 0 | 0 | 17 |  | 685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 116 | 0 | 304 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 280 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4123 | 2052 | 6175 | 2249 | 685 | 1531 | 0 | 1075 | 480 | 82 | 0 | 0 | 73 | 0 | 0 | 93.82
5:00 | 0 | 0 | 220 | 0 | 0 | 7 | 0 | 0 | 202 |  | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 17 | 17 | 22 | 25 | 9 | 16 | 13 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 12 | 40 | 17 | 36 | 0 | 0 | 0 | 140 | 270 | 184 | 8 | 87 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 25 | 9 | 72 | 114 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 135 | 40 | 81 | 0 | 177 | 0 | 0 | 0 | 285 | 16 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 8 | 35 | 17 | 0 | 135 | 0 | 0 | 0 | 8 | 0 | 340 | 55 | 0 | 90 | 51 | 0 | 17 | 0 | 0 | 17 |  | 685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 116 | 0 | 322 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 280 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4049 | 2070 | 6119 | 2223 | 685 | 1574 | 0 | 1003 | 480 | 82 | 0 | 0 | 72 | 0 | 0 | 93.81
6:00 | 0 | 0 | 220 | 0 | 0 | 7 | 0 | 0 | 205 |  | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 47 | 35 | 35 | 17 | 22 | 25 | 9 | 16 | 15 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 29 | 40 | 17 | 32 | 0 | 0 | 0 | 140 | 270 | 184 | 8 | 85 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 25 | 9 | 70 | 114 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 135 | 40 | 76 | 0 | 177 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 30 | 0 | 0 | 90 | 0 | 0 | 0 | 6 | 0 | 123 | 0 | 12 | 64 | 18 | 0 | 135 | 0 | 0 | 0 | 8 | 0 | 340 | 57 | 0 | 90 | 75 | 0 | 17 | 0 | 0 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 116 | 0 | 326 | 0 | 0 | 35 | 0 | 60 | 0 | 0 | 20 | 280 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4229 | 2166 | 6395 | 2217 | 731 | 1588 | 0 | 1226 | 480 | 83 | 0 | 0 | 70 | 0 | 0 | 93.81
7:00 | 0 | 0 | 225 | 0 | 0 | 7 | 0 | 0 | 191 |  | 0 | 170 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 48 | 35 | 35 | 40 | 22 | 25 | 9 | 16 | 15 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 86 | 39 | 17 | 33 | 0 | 0 | 0 | 140 | 310 | 196 | 8 | 85 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 25 | 9 | 72 | 112 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 134 | 40 | 76 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 118 | 0 | 0 | 144 | 0 | 8 | 1 | 30 | 0 | 135 | 0 | 32 | 90 | 34 | 0 | 135 | 0 | 14 | 0 | 8 | 0 | 335 | 93 | 1 | 90 | 100 | 0 | 17 | 1 | 0 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 115 | 0 | 359 | 2 | 0 | 70 | 0 | 78 | 0 | 0 | 35 | 280 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4682 | 2270 | 6952 | 2268 | 731 | 1597 | 0 | 1718 | 480 | 83 | 0 | 0 | 72 | 3 | 0 | 93.81
8:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 169 |  | 0 | 170 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 64 | 32 | 21 | 0 | 0 | 47 | 35 | 35 | 55 | 22 | 25 | 9 | 16 | 14 | 12 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 40 | 17 | 7 | 0 | 0 | 0 | 220 | 280 | 190 | 8 | 85 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 25 | 9 | 88 | 112 | 0 | 22 | 0 | 30 | 30 | 47 | 0 | 110 | 135 | 72 | 76 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 233 | 0 | 0 | 200 | 0 | 67 | 6 | 70 | 1 | 130 | 0 | 70 | 90 | 50 | 1 | 190 | 0 | 17 | 34 | 8 | 0 | 300 | 93 | 9 | 90 | 100 | 0 | 17 | 4 | 0 | 55 |  | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 113 | 0 | 372 | 77 | 0 | 92 | 0 | 99 | 0 | 1 | 100 | 310 | 214 | 0 | 0 | 0 | 17 | 0 |  | 5255 | 2571 | 7826 | 2301 | 734 | 1567 | 0 | 2473 | 510 | 83 | 0 | 32 | 88 | 38 | 0 | 93.8
9:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 170 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 100 | 35 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 16 | 14 | 45 | 0 | 83 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 86 | 40 | 17 | 3 | 0 | 0 | 0 | 275 | 305 | 181 | 8 | 84 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 16 | 9 | 90 | 113 | 0 | 22 | 1 | 30 | 30 | 48 | 0 | 110 | 135 | 71 | 76 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 245 | 0 | 0 | 200 | 0 | 144 | 11 | 90 | 38 | 132 | 0 | 89 | 90 | 81 | 2 | 275 | 0 | 17 | 51 | 8 | 10 | 339 | 92 | 21 | 90 | 100 | 0 | 17 | 13 | 0 | 55 |  | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 43 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 113 | 0 | 350 | 105 | 0 | 113 | 0 | 107 | 0 | 2 | 113 | 350 | 220 | 0 | 0 | 2 | 39 | 8 |  | 5883 | 2753 | 8636 | 2402 | 734 | 1549 | 0 | 2982 | 550 | 83 | 0 | 155 | 90 | 91 | 0 | 93.79
10:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 171 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 100 | 36 | 0 | 0 | 46 | 35 | 55 | 35 | 22 | 25 | 9 | 20 | 17 | 51 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 39 | 18 | 3 | 0 | 0 | 0 | 220 | 270 | 182 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 5 | 8 | 9 | 94 | 98 | 0 | 22 | 1 | 30 | 30 | 45 | 0 | 110 | 136 | 40 | 76 | 0 | 164 | 0 | 0 | 0 | 280 | 16 | 8 | 0 | 233 | 0 | 0 | 200 | 0 | 149 | 15 | 90 | 68 | 128 | 0 | 89 | 70 | 85 | 3 | 282 | 0 | 17 | 51 | 12 | 10 | 360 | 93 | 31 | 90 | 100 | 0 | 17 | 21 | 0 | 55 |  | 736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 43 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 125 | 0 | 350 | 105 | 0 | 113 | 0 | 107 | 0 | 4 | 113 | 300 | 220 | 0 | 0 | 3 | 59 | 34 |  | 5830 | 2762 | 8592 | 2287 | 736 | 1534 | 0 | 3017 | 499 | 83 | 0 | 205 | 94 | 137 | 0 | 93.79
11:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 165 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 100 | 36 | 0 | 0 | 43 | 35 | 55 | 35 | 0 | 25 | 9 | 20 | 25 | 51 | 0 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 85 | 39 | 18 | 2 | 0 | 0 | 0 | 220 | 270 | 183 | 45 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 5 | 8 | 9 | 94 | 85 | 0 | 22 | 2 | 30 | 30 | 48 | 0 | 110 | 138 | 40 | 76 | 0 | 164 | 0 | 0 | 0 | 280 | 16 | 8 | 0 | 250 | 0 | 0 | 194 | 0 | 149 | 18 | 90 | 68 | 130 | 0 | 89 | 70 | 68 | 4 | 284 | 0 | 17 | 51 | 10 | 10 | 360 | 93 | 37 | 102 | 100 | 0 | 17 | 25 | 7 | 55 |  | 736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 43 | 0 | 52 | 0 | 17 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 130 | 0 | 350 | 105 | 0 | 113 | 0 | 107 | 0 | 5 | 113 | 300 | 220 | 0 | 0 | 3 | 72 | 20 |  | 5871 | 2764 | 8635 | 2265 | 736 | 1566 | 0 | 3019 | 500 | 84 | 0 | 205 | 94 | 166 | 0 | 93.78
12:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 164 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 133 | 36 | 0 | 0 | 46 | 35 | 55 | 55 | 0 | 25 | 9 | 20 | 25 | 51 | 0 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 85 | 39 | 18 | 4 | 0 | 0 | 0 | 200 | 270 | 180 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 5 | 8 | 6 | 106 | 85 | 0 | 22 | 2 | 30 | 30 | 49 | 0 | 110 | 135 | 67 | 76 | 0 | 177 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 250 | 0 | 0 | 194 | 0 | 149 | 20 | 90 | 68 | 135 | 0 | 89 | 80 | 96 | 2 | 282 | 2 | 23 | 70 | 8 | 10 | 400 | 104 | 41 | 108 | 115 | 0 | 17 | 27 | 12 | 55 |  | 736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 34 | 50 | 0 | 43 | 0 | 52 | 0 | 17 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 135 | 0 | 345 | 105 | 0 | 113 | 0 | 107 | 0 | 5 | 113 | 310 | 220 | 0 | 0 | 4 | 79 | 0 |  | 6069 | 2800 | 8869 | 2324 | 736 | 1534 | 0 | 3125 | 509 | 84 | 0 | 271 | 106 | 180 | 0 | 93.78
13:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 168 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 133 | 38 | 0 | 0 | 41 | 35 | 55 | 55 | 19 | 25 | 9 | 20 | 25 | 51 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 39 | 18 | 10 | 0 | 0 | 0 | 220 | 300 | 142 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 8 | 6 | 109 | 84 | 0 | 22 | 2 | 30 | 30 | 51 | 0 | 110 | 137 | 68 | 76 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 231 | 51 | 0 | 193 | 0 | 149 | 18 | 90 | 75 | 140 | 0 | 98 | 90 | 105 | 3 | 282 | 27 | 55 | 114 | 8 | 50 | 400 | 104 | 39 | 108 | 116 | 0 | 17 | 23 | 0 | 55 |  | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 43 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 137 | 0 | 338 | 105 | 0 | 113 | 0 | 107 | 0 | 5 | 113 | 370 | 220 | 0 | 0 | 3 | 75 | 20 |  | 6320 | 2902 | 9222 | 2362 | 735 | 1545 | 66 | 3297 | 569 | 83 | 0 | 288 | 109 | 168 | 0 | 93.77
14:00 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 160 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 55 | 0 | 0 | 46 | 35 | 55 | 55 | 19 | 25 | 9 | 20 | 25 | 51 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 90 | 39 | 18 | 2 | 0 | 0 | 0 | 150 | 270 | 171 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 8 | 9 | 111 | 84 | 0 | 22 | 1 | 30 | 30 | 51 | 0 | 110 | 138 | 53 | 76 | 0 | 177 | 0 | 0 | 0 | 280 | 16 | 8 | 0 | 243 | 36 | 0 | 184 | 0 | 149 | 17 | 90 | 94 | 147 | 0 | 99 | 90 | 105 | 3 | 0 | 21 | 68 | 114 | 8 | 60 | 400 | 104 | 31 | 114 | 116 | 0 | 17 | 23 | 0 | 55 |  | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 47 | 66 | 0 | 43 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 137 | 0 | 306 | 105 | 0 | 113 | 0 | 107 | 0 | 4 | 113 | 350 | 220 | 0 | 0 | 3 | 69 | 0 |  | 5889 | 2826 | 8715 | 2160 | 737 | 1486 | 36 | 3080 | 550 | 83 | 0 | 321 | 111 | 151 | 0 | 93.77
15:00 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 161 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 64 | 20 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 25 | 25 | 0 | 80 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 39 | 18 | 2 | 0 | 0 | 0 | 150 | 265 | 188 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 8 | 9 | 100 | 85 | 0 | 22 | 1 | 30 | 30 | 51 | 0 | 110 | 137 | 40 | 75 | 0 | 177 | 0 | 0 | 0 | 260 | 16 | 11 | 0 | 243 | 0 | 0 | 193 | 0 | 137 | 12 | 70 | 51 | 137 | 0 | 99 | 90 | 64 | 2 | 130 | 17 | 17 | 88 | 8 | 10 | 350 | 104 | 20 | 129 | 116 | 0 | 17 | 18 | 0 | 55 |  | 738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 3 | 0 | 92 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 66 | 0 | 43 | 0 | 52 | 0 | 15 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 137 | 0 | 289 | 105 | 0 | 113 | 0 | 107 | 0 | 3 | 70 | 310 | 220 | 0 | 0 | 2 | 53 | 20 |  | 5494 | 2728 | 8222 | 2116 | 738 | 1445 | 0 | 2885 | 510 | 80 | 0 | 237 | 100 | 111 | 0 | 93.76
16:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 164 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 64 | 10 | 0 | 0 | 48 | 35 | 55 | 55 | 0 | 25 | 9 | 20 | 25 | 25 | 0 | 82 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 86 | 39 | 18 | 3 | 0 | 0 | 0 | 150 | 265 | 188 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 8 | 9 | 100 | 96 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 137 | 40 | 75 | 0 | 176 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 257 | 0 | 0 | 193 | 0 | 102 | 7 | 40 | 51 | 130 | 0 | 88 | 105 | 17 | 1 | 277 | 17 | 17 | 88 | 8 | 10 | 350 | 104 | 10 | 126 | 116 | 0 | 17 | 10 | 10 | 55 |  | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 0 | 92 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 66 | 0 | 8 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 135 | 0 | 285 | 105 | 0 | 70 | 0 | 107 | 0 | 2 | 70 | 280 | 201 | 0 | 0 | 1 | 29 | 0 |  | 5572 | 2560 | 8132 | 2142 | 737 | 1457 | 0 | 2826 | 480 | 82 | 0 | 248 | 100 | 60 | 0 | 93.76
17:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 167 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 100 | 10 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 6 | 20 | 25 | 25 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 89 | 39 | 18 | 10 | 0 | 0 | 0 | 150 | 295 | 189 | 8 | 89 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 10 | 9 | 106 | 102 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 134 | 40 | 75 | 0 | 162 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 263 | 0 | 0 | 193 | 0 | 92 | 2 | 20 | 51 | 138 | 0 | 89 | 105 | 17 | 0 | 300 | 17 | 17 | 52 | 85 | 10 | 330 | 104 | 3 | 128 | 116 | 0 | 17 | 3 | 0 | 55 |  | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 15 | 0 | 92 | 18 | 0 | 0 | 0 | 0 | 0 | 40 | 66 | 0 | 8 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 134 | 0 | 286 | 105 | 0 | 76 | 0 | 107 | 0 | 1 | 35 | 280 | 180 | 0 | 0 | 0 | 8 | 20 |  | 5714 | 2522 | 8236 | 2204 | 737 | 1454 | 0 | 2861 | 480 | 83 | 0 | 294 | 106 | 17 | 0 | 93.75
18:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 169 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 145 | 30 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 6 | 20 | 25 | 40 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 87 | 39 | 18 | 12 | 0 | 0 | 0 | 150 | 290 | 194 | 8 | 88 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 8 | 9 | 122 | 104 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 138 | 69 | 75 | 0 | 176 | 0 | 0 | 0 | 290 | 16 | 11 | 20 | 268 | 113 | 25 | 200 | 25 | 144 | 0 | 76 | 69 | 145 | 0 | 89 | 105 | 50 | 0 | 290 | 17 | 18 | 103 | 104 | 30 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 0 | 92 | 23 | 0 | 0 | 0 | 0 | 34 | 44 | 100 | 0 | 34 | 0 | 52 | 28 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 134 | 0 | 288 | 105 | 50 | 113 | 0 | 107 | 0 | 0 | 100 | 280 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6459 | 2830 | 9289 | 2340 | 737 | 1505 | 239 | 3287 | 480 | 83 | 0 | 496 | 122 | 0 | 0 | 93.75
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 167 |  | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 28 | 51 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 89 | 39 | 18 | 18 | 0 | 0 | 0 | 150 | 265 | 196 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 8 | 9 | 116 | 105 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 69 | 76 | 0 | 177 | 0 | 0 | 0 | 285 | 16 | 11 | 20 | 270 | 132 | 100 | 200 | 100 | 149 | 0 | 90 | 85 | 147 | 0 | 98 | 105 | 105 | 0 | 300 | 17 | 34 | 114 | 106 | 40 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 19 | 0 | 92 | 24 | 0 | 0 | 0 | 0 | 34 | 47 | 100 | 0 | 43 | 0 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 134 | 0 | 295 | 105 | 50 | 113 | 0 | 107 | 0 | 0 | 113 | 380 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6793 | 3008 | 9801 | 2321 | 769 | 1506 | 412 | 3504 | 580 | 83 | 0 | 510 | 116 | 0 | 0 | 93.73
19:30 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 164 |  | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 28 | 51 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 90 | 39 | 18 | 14 | 0 | 0 | 0 | 150 | 265 | 201 | 8 | 88 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 8 | 9 | 120 | 105 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 137 | 69 | 76 | 0 | 177 | 0 | 0 | 0 | 305 | 16 | 11 | 20 | 270 | 62 | 80 | 200 | 80 | 149 | 0 | 70 | 85 | 148 | 0 | 98 | 105 | 105 | 0 | 300 | 17 | 17 | 114 | 108 | 10 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 0 | 92 | 24 | 0 | 0 | 0 | 0 | 34 | 47 | 100 | 0 | 43 | 0 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 134 | 0 | 300 | 105 | 30 | 113 | 0 | 107 | 0 | 0 | 113 | 410 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6645 | 3020 | 9665 | 2329 | 769 | 1524 | 282 | 3441 | 610 | 83 | 0 | 507 | 120 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 155 |  | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 28 | 51 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 90 | 39 | 18 | 24 | 0 | 0 | 0 | 150 | 265 | 205 | 8 | 88 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 8 | 9 | 119 | 105 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 137 | 70 | 76 | 0 | 177 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 268 | 62 | 80 | 193 | 80 | 149 | 0 | 70 | 85 | 147 | 0 | 99 | 105 | 105 | 0 | 300 | 17 | 17 | 114 | 108 | 10 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 0 | 92 | 25 | 0 | 0 | 0 | 0 | 34 | 47 | 100 | 0 | 43 | 0 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 134 | 0 | 298 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 410 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6616 | 2970 | 9586 | 2334 | 761 | 1519 | 222 | 3432 | 610 | 83 | 0 | 506 | 119 | 0 | 0 | 93.74
21:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 165 |  | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 59 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 28 | 51 | 0 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 49 | 0 | 90 | 40 | 18 | 32 | 0 | 0 | 0 | 150 | 265 | 205 | 8 | 85 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 15 | 9 | 117 | 111 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 70 | 76 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 200 | 0 | 149 | 0 | 70 | 85 | 145 | 0 | 99 | 105 | 68 | 0 | 300 | 17 | 17 | 114 | 108 | 10 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 0 | 92 | 25 | 0 | 0 | 0 | 0 | 34 | 40 | 100 | 0 | 43 | 0 | 52 | 23 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 134 | 0 | 314 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 221 | 0 | 0 | 0 | 0 | 0 |  | 6378 | 2974 | 9352 | 2343 | 761 | 1543 | 0 | 3408 | 610 | 84 | 0 | 486 | 117 | 0 | 0 | 93.73
22:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 155 |  | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 82 | 20 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 33 | 25 | 0 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 40 | 18 | 40 | 0 | 0 | 0 | 150 | 270 | 205 | 8 | 85 | 27 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 13 | 9 | 110 | 110 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 40 | 76 | 0 | 177 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 200 | 0 | 140 | 0 | 70 | 51 | 148 | 0 | 80 | 105 | 17 | 0 | 300 | 17 | 17 | 52 | 108 | 0 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 92 | 24 | 0 | 0 | 0 | 0 | 34 | 0 | 100 | 0 | 43 | 0 | 52 | 21 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 135 | 0 | 323 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 400 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5931 | 2894 | 8825 | 2319 | 761 | 1549 | 0 | 3156 | 600 | 84 | 0 | 246 | 110 | 0 | 0 | 93.73
23:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 149 |  | 0 | 160 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 16 | 33 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 40 | 18 | 40 | 0 | 0 | 0 | 150 | 265 | 212 | 8 | 85 | 27 | 5 | 0 | 43 | 0 | 0 | 47 | 19 | 8 | 16 | 9 | 99 | 110 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 40 | 75 | 0 | 177 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 283 | 0 | 0 | 200 | 0 | 118 | 0 | 10 | 51 | 148 | 0 | 45 | 105 | 17 | 0 | 300 | 17 | 17 | 17 | 50 | 0 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 137 | 0 | 321 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 380 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5494 | 2739 | 8233 | 2323 | 727 | 1522 | 0 | 2799 | 580 | 83 | 0 | 100 | 99 | 0 | 0 | 93.72
24:00 | 0 | 0 | 205 | 0 | 0 | 7 | 0 | 0 | 157 |  | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 16 | 33 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 40 | 18 | 35 | 0 | 0 | 0 | 150 | 265 | 214 | 8 | 85 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 25 | 9 | 87 | 112 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 137 | 40 | 75 | 0 | 177 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 17 | 148 | 0 | 8 | 105 | 17 | 0 | 300 | 0 | 0 | 17 | 8 | 0 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 137 | 0 | 338 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 330 | 216 | 0 | 0 | 0 | 0 | 0 |  | 5137 | 2470 | 7607 | 2343 | 728 | 1541 | 0 | 2296 | 530 | 82 | 0 | 0 | 87 | 0 | 0 | 93.72
KWH | 0 | 0 | 4793000 | 0 | 0 | 176681 | 0 | 0 | 4108000 |  | 0 | 3809750 | 0 | 0 | 0 | 653725 | 0 | 0 | 0 | 0 | 1602864 | 1639200 | 588730 | 0 | 0 | 1142976 | 865080 | 1085942 | 1082832 | 424296 | 600000 | 206460 | 549600 | 541200 | 631680 | 0 | 1968682 | 0 | 0 | 0 | 242424 | 0 | 0 | 0 | 0 |  | 531840 | 0 | 215261 | 42840 | 1727040 | 960960 | 424416 | 484800 | 0 | 0 | 0 | 4225000 | 6797000 | 4593000 | 250909 | 2075720 | 667728 | 143520 | 0 | 1191752 | 0 | 581008 | 1244966 | 452448 | 195840 | 370000 | 238400 | 2232960 | 2438400 | 0 | 526716 | 9900 | 716000 | 623640 | 1200000 | 0 | 2922463 | 3238000 | 1299168 | 1834560 | 0 | 4237110 | 0 | 0 | 0 | 7116000 | 496560 | 230160 | 42816 | 4787344 | 376544 | 205942 | 4207200 | 196947 | 2256336 | 127305 | 1143360 | 1079040 | 3250109 | 0 | 1528800 | 2195676 | 1338181 | 22559 | 5823600 | 232818 | 487599 | 1246020 | 833280 | 254400 | 8716000 | 2384640 | 241440 | 3088800 | 2560527 | 0 | 446040 | 171117 | 28800 | 1244160 |  | 17660363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167520 | 96384 | 0 | 2217376 | 455000 | 0 | 0 | 0 | 0 | 154326 | 426875 | 1127056 | 0 | 608625 | 0 | 1249666 | 135904 | 465840 | 0 | 179190 | 0 | 0 | 4851200 | 0 | 0 | 0 | 0 | 0 | 0 | 265445 | 72960 | 3283573 | 0 | 7580800 | 1775040 | 102204 | 2223168 | 0 | 2222457 | 0 | 30484 | 1826400 | 8676900 | 5063345 | 0 | 0 | 24660 | 504720 | 113472 |  | 133766607 | 63560953 | 197327560 | 55356001 | 17660363 | 37068865 | 997413 | 62839457 | 13528100 | 1968682 | 0 | 4543534 | 2232960 | 1132185 | 0
Fuel Cost | 0 | 0 | 6997780 | 0 | 0 | 233218.92 | 0 | 0 | 4231240 |  | 0 | 4152627.5 | 0 | 0 | 0 | 5530513.5 | 0 | 0 | 0 | 0 | 14618119.68 | 16129728 | 5428090.6 | 0 | 0 | 10389651.84 | 6315084 | 8394331.66 | 10676723.52 | 318222 | 450000 | 0 | 0 | 0 | 6108345.6 | 0 | 531544.14 | 0 | 0 | 0 | 2252118.96 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2088031.7 | 409122 | 15025248 | 7610803.2 | 534764.16 | 1439856 | 0 | 0 | 0 | 3126500 | 6797000 | 4225560 | 323672.61 | 2387078 | 754532.64 | 200928 | 0 | 2037895.92 | 0 | 5868180.8 | 11889425.3 | 574608.96 | 146880 | 647500 | 178800 | 16747200 | 2584704 | 0 | 668929.32 | 157806 | 1174240 | 997824 | 2136000 | 0 | 3331607.82 | 3367520 | 2559360.96 | 3504009.6 | 0 | 7330200.3 | 0 | 0 | 0 | 7187160 | 372420 | 174921.6 | 728300.16 | 36192320.64 | 6393717.12 | 3443350.24 | 21877440 | 3292953.84 | 22202346.24 | 1488195.45 | 9318384 | 11707584 | 22913268.45 | 0 | 13942656 | 20749138.2 | 11655556.51 | 0 | 44026416 | 2027844.78 | 4285995.21 | 12435279.6 | 7141209.6 | 1694304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101723690.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1757284.8 | 1010104.32 | 0 | 2505634.88 | 705250 | 0 | 0 | 0 | 0 | 1518567.84 | 4337050 | 9974445.6 | 0 | 8228610 | 0 | 12109263.54 | 1318268.8 | 894412.8 | 0 | 135646.83 | 0 | 0 | 26293504 | 0 | 0 | 0 | 0 | 0 | 0 | 398167.5 | 1241049.6 | 3841780.41 | 0 | 7504992 | 18531417.6 | 1738490.04 | 21097864.32 | 0 | 17246266.32 | 0 | 336848.2 | 13497096 | 38091591 | 0 | 0 | 0 | 0 | 0 | 0 |  | 478833890.85 | 296037297.28 | 774871188.13 | 52852408.06 | 101723690.88 | 38281038.67 | 16837861 | 437527838.87 | 64385095 | 531544.14 | 0 | 44001661.86 | 16747200 | 1982849.65 | 0
Yesterday Day Peak | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 164 |  | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 133 | 36 | 0 | 0 | 46 | 35 | 55 | 55 | 0 | 25 | 9 | 20 | 25 | 51 | 0 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 85 | 39 | 18 | 4 | 0 | 0 | 0 | 200 | 270 | 180 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 5 | 8 | 6 | 106 | 85 | 0 | 22 | 2 | 30 | 30 | 49 | 0 | 110 | 135 | 67 | 76 | 0 | 177 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 250 | 0 | 0 | 194 | 0 | 149 | 20 | 90 | 68 | 135 | 0 | 89 | 80 | 96 | 2 | 282 | 2 | 23 | 70 | 8 | 10 | 400 | 104 | 41 | 108 | 115 | 0 | 17 | 27 | 12 | 55 |  | 736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 34 | 50 | 0 | 43 | 0 | 52 | 0 | 17 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 135 | 0 | 345 | 105 | 0 | 113 | 0 | 107 | 0 | 5 | 113 | 310 | 220 | 0 | 0 | 4 | 79 | 0 |  | 8869 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 160 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 28 | 51 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 10 | 89 | 39 | 18 | 18 | 0 | 0 | 0 | 150 | 265 | 196 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 8 | 9 | 116 | 105 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 69 | 76 | 0 | 177 | 0 | 0 | 0 | 285 | 16 | 11 | 20 | 270 | 132 | 100 | 200 | 100 | 149 | 0 | 90 | 85 | 147 | 0 | 98 | 105 | 105 | 0 | 300 | 17 | 34 | 114 | 106 | 40 | 400 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 19 | 0 | 92 | 24 | 0 | 0 | 0 | 0 | 34 | 47 | 100 | 0 | 43 | 0 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 134 | 0 | 295 | 105 | 50 | 113 | 0 | 107 | 0 | 0 | 113 | 380 | 221 | 0 | 0 | 0 | 0 | 0 |  | 9801 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 170 |  | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 51 | 35 | 55 | 55 | 22 | 25 | 10 | 20 | 33 | 51 | 0 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 40 | 20 | 20 | 0 | 0 | 0 | 200 | 300 | 200 | 8 | 88 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 25 | 9 | 160 | 110 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 150 | 66 | 80 | 0 | 180 | 18 | 0 | 0 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 100 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 17 |  |  | 55 |  | 744 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 35 | 40 | 0 | 92 | 24 | 110 | 0 | 0 | 0 | 34 | 50 | 100 | 0 | 43 | 40 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 140 | 0 | 300 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 51 | 35 | 55 | 55 | 22 | 25 | 10 | 20 | 33 | 51 | 0 | 84 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 40 | 19 | 5 | 0 | 0 | 0 | 200 | 270 | 180 | 8 | 86 | 25 | 5 | 0 | 51 | 0 | 50 | 52 | 18 | 11 | 25 | 9 | 138 | 100 | 0 | 22 | 1.6 | 30 | 30 | 51 | 0 | 110 | 150 | 66 | 75 | 0 | 180 | 18 | 0 | 0 | 330 | 16 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 0 | 98 | 105 | 105 | 5 | 260 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 | 17 | 30 |  | 55 |  | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 110 | 0 | 0 | 0 | 34 | 50 | 90 | 0 | 43 | 40 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 80 | 130 | 0 | 300 | 100 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 220 |  | 0 | 6 | 50
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 190 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 64 | 16 | 24 | 0 | 0 | 47 | 35 | 55 | 55 | 19 | 25 | 0 | 16 | 33 | 33 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 90 | 40 | 18 | 13 | 0 | 0 | 0 | 215 | 330 | 195 | 8 | 86 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 16 | 8 | 90 | 112 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 135 | 40 | 75 | 0 | 177 | 0 | 0 | 0 | 300 | 5 | 11 | 0 | 153 | 0 | 0 | 180 | 0 | 53 | 6 | 20 | 38 | 130 | 0 | 70 | 105 | 17 | 1 | 185 | 17 | 17 | 34 | 8 | 10 | 340 | 104 | 7 | 144 | 99 | 0 | 17 | 6 | 0 | 55 | 0 | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 25 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 122 | 0 | 321 | 68 | 0 | 67 | 0 | 107 | 0 | 0 | 100 | 330 | 220 | 0 | 0 | 0 | 17 | 0 | 0
199
| Minimum Generation |  | 6119 | 5:00
| Highest Generation |  | 9801 | 19:00
| Day Peak Generation |  | 8869 | 12:00
| Evening Peak Generation |  | 9801 | 19:00
| HVDC Max Flow |  | 769 | 19:00
| HVDC EvPeak Flow |  | 769 | 19:00
| Load factor L.F |  | 83.89%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-02-01
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-01-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8869 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6140 | MW
Evening Peak Generation : |  | 9801 | MW Hour : | 19:00 | Available Max Generation : |  | 12010 | MW
E.P. Demand (at gen end) : |  | 9801 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 9801 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2010 | MW
Total Gen. (MKWH) : |  | 197.3276 | System Load Factor : | 83.89% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -247 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-02-01
Actual : | 93.69 | Ft.(MSL) , | Rule curve : | 97 | Ft.( MSL )
Gas Consumed : | Total = | 729.16 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 91133446.73
: |  | Coal : | 64385095 | Oil : | 498367361.73 | Total : | 653885903.46
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3669.5197 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1245.8212 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1115.8548 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1008.1413 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 911.1131 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 735.2309 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 413.7025 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 189.3709 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 567.0342 |  |  | 0 | 0%
Total | 0 |  | 9855.7886 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
2) Ghorasal-3,5,7
3) Ashuganj-4,
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW GT-2
6) Raozan unit- 1,2
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Cantonment 132/33 kV T-1 transformer was under shut down from 08:16 to 16:18 for D/W.
b) Chandraghona-Kaptai 132 kV Ckt-2 was under shut down from 08:50 to 17:04 for C/M.
c) Ashuganj-B.Baria 132 kV Ckt-2 was under shut down from 09:09 to 16:13 for C/M.
d) Fenchuganj 230/132 kV T-2 transformer was under shut down from 09:19 to 10:08 for C/M.
e) Keraniganj-Aminbazar 230 kV Ckt-2 was under shut down from 09:34 to 15:53 for A/M.
f) Madaripur-Gopalganj 132 kV Ckt-2 was under shut down from 09:28 to 10:18 for C/M.
g) Savar 132/33 kV T-2 transformer was under shut down at 09:52 for A/M.
h) Fenchuganj-Srimongal 132 kV Ckt-1 was under shut down from 10:10 to 10:49 for C/M.
i) Fenchuganj-Srimongal 132 kV Ckt-2 was under shut down from 10:51 to 16:16 for C/M.
j) Tongi 230/132 kV ATR-1 transformer was under shut down from 11:03 to 15:38 for C/M.
k) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 11:10 to 16:55 for A/M.
l) Mymensing 132 kV Bus-2 was under shut down from 11:08 to 17:01 for A/M.
m) New Tongi 132/33 kV T-2 transformer was under shut down from 11:29 to 15:30 for A/M.
n) Mymensing-Kishorganj 132 kV Ckt-2 was under shut down from 11:30 to 16:56 for A/M.
o) Kazla 132/33 kV GT-2 transformer was under shut down from 09:12 to 11:51 for A/M.
p) Khagrachari 132 kV main bus-2 was under shut down from 10:35 to 15:40 for A/M.
q) Madaripur-Gopalganj(N) 132 kV Ckt-4 was under shut down from 10:29 to 11:49 for C/M.
r) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 11:45 to 20:07 for C/M.
s) Fenchuganj-Kulaura 132 kV Ckt-2 was under shut down from 11:48 to 12:22 for A/M.
t) Kamrangirchar 132/33 kV GT-1 transformer was under shut down from 09:38 to 19:47 for A/M.
u) Fenchuganj-Kulaura 132 kV Ckt-1 was under shut down from 12:23 to 13:02 for A/M.
v) Madaripur 132/33 kV T-3 transformer was under shut down from 12:09 to 13:49 for C/M.
w) Barishal(S) 132/33 kV T-2 transformer was under shut down from 12:20 to 12:43 for red hot maint.
x) Keraniganj 132/33 kV T-1 transformer was under shut down from 13:16 to 18:29 for D/W.
y) Fenchuganj-Fenchuganj P/S 132 kV Ckt-3 was under shut down from 13:29 to 13:53 for A/M.
z) Anwera-300 MW tripped at 13:30 showing E/F relay and was synchronized at 14:01.
aa) Hathazari 132 kV Bus-1 is under shut down since 06:29(1/2/22) for D/W.
ab) Gopalganj-Modhumoti P/S 132 kV Bus is under shut down since 07:19(1/2/22) for A/M.
ac) Ghorasal #4 tripped at 07:44(1/2/22) GBC problem.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-01-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4793000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 176681 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 167 | 4108000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 160 | 3809750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 653725 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 60 | 588730 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 424296
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1602864
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 1142976
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 865080 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1639200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1085942
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1082832
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 806460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 549600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 541200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 631680
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 4787344 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 132 | 376544
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 205942
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 196947
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2256336
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2195676
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2384640
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3088800 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 171117
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1244160
| Dhaka area Total |  |  |  | 5696 | 2386 | 41409522
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 242424 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 127305
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 960960 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 83 | 1968682 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1338181
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 215261 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 42840 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1143360 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 424416 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 484800
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 89 | 1727040 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22559
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 5823600
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 232818 | High Voltage
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 34 | 487599 | High Voltage
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 40 | 254400 | High Voltage
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2560527
| Chattogram area Total |  |  |  | 2382 | 1027 | 18056772
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4593000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 150 | 4225000 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6797000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 667728 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 143520 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 250909 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1191752
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 3250109
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 581008
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2075720 | ST Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 85 | 1079040 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 452448
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 195840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2232960
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 8 | 370000 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1244966
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 238400 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 42816
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1246020
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 106 | 833280 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 446040 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 28800 | On test
| Cumilla Area Total |  |  |  | 2899 | 1540 | 32186356
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 2438400 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 526716
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9900
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4207200
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 98 | 1528800 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 241440
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 531840
| Mymensingh Area Total |  |  |  | 622 | 447 | 9484296
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 623640 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2922463 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 136 | 3238000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1200000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 230160
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1299168
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1834560
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine problem
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 177 | 4237110 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 496560 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7116000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8716000
| Sylhet Area Total |  |  |  | 2377 | 1393 | 32629661
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 769 | 17660363
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 167520 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 19 | 96384
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 10 | 72960
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1775040
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 504720 | On test
| Khulna Area Total |  |  |  | 2229 | 931 | 20276987
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 24 | 455000 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 92 | 2217376 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 265445 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 380 | 8676900 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 5063345
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 728 | 16678066
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 154326 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 47 | 426875 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 608625 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Under maint.
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 134 | 3283573 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 295 | 7580800 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 135904 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 465840
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 179190 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1249666
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1127056
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 102204
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2223168
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1826400
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24660
| Rajshahi Area Total |  |  |  | 2179 | 1042 | 19388287
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4851200 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 2222457 | Engine problem
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30484
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 113472 | On test
| Rangpur Area Total |  |  |  | 605 | 307 | 7217613
| Total |  |  |  | 21035 | 9801 | 197327560
| Eastern Grid Total |  |  |  | 13976 | 6793 | 133766607
| Western Grid Total |  |  |  | 7059 | 3008 | 63560953
| National Grid Total |  |  |  | 21035 | 9801 | 197327560
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-01-31
(a) ENTIRE EASTERN GRID : |  | 6568 | MW | (b) ENTIRE WESTERN GRID : |  | 3089 | MW
i) Dhaka area |  | 3540 | MW | i) Khulna area |  | 1127 | MW
ii) Chittagong area |  | 1058 | MW | ii) Rajshahi area |  | 1007 | MW
iii) Comilla area |  | 778 | MW | iii) Barisal area |  | 245 | MW
iv) Mymensingh area |  | 857 | MW | iv) Rangpur area |  | 710 | MW
v) Sylhet area |  | 335 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9657 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 88 | 12:00 | Tangail | 150 | 19:30 | Noapara | 30 | 21:00
Munsiganj | 60 | 19:30 | Mymensing | 176 | 13:00 | Jessore | 94 | 13:00
Sonargaon | 73 | 15:00 | Kishoreganj | 104 | 19:00 | Benapol | 44 | 9:00
Shyampur | 168 | 10:00 | Netrokona | 115 | 18:30 | Jhenida(Old) | 66 | 18:00
Bhulta | 186 | 18:30 | Jamalpur | 124 | 9:00 | Bottail | 104 | 13:00
Madanganj | 24 | 18:00 | Sherpur | 128 | 18:30 | G.K Project | 41 | 18:30
Shitalakhya | 94 | 12:00 | Srimongal | 33 | 18:00 | Faridpur | 104 | 20:00
Rahim steel | 21 | 14:00 | Shahjibazar | 80 | 21:00 | Rajbari | 40 | 18:30
Matuail | 48 | 9:00 | Fenchuganj | 28 | 17:00 | Madaripur | 68 | 19:30
Ghorasal | 58 | 18:30 | Kulawara | 26 | 18:00 | Sariatpur | 42 | 19:30
Narsingdi | 129 | 19:00 | Sylhet | 87 | 18:00 | Gopalganj | 71 | 18:30
Haripur (SBU) | 114 | 9:00 | Chatak | 19 | 20:00 | Bagerhat | 73 | 19:00
Sreenagar | 27 | 19:30 | Sunamganj | 33 | 18:30 | Mongla | 42 | 19:30
Ullon | 21 | 22:00 | Biani Bazar | 40 | 19:00 | Satkhira | 78 | 19:00
Hasnabad | 59 | 12:00 | Comilla (S) | 122 | 18:00 | Gallamari | 39 | 13:00
Magbazar | 76 | 19:30 | Comilla(N) | 86 | 20:00 | Magura | 42 | 18:30
Maniknagar | 52 | 13:00 | Chandpur | 44 | 20:00 | Norail | 36 | 18:30
Bangabhaban | 5 | 10:00 | Feni | 83 | 18:00 | Chuadanga | 69 | 18:30
Motijheel | 21 | 13:00 | Chowmuhani | 132 | 20:00 | Barisal(N) | 27 | 20:00
Narinda | 34 | 18:30 | Ashuganj | 22 | 13:00 | Barisal (S) | 76 | 20:00
Kazla | 67 | 13:00 | Daudkandi | 98 | 18:30 | Patuakhali | 73 | 20:00
Dhanmondi | 107 | 18:00 | B.Baria | 101 | 19:30 | Bhandaria | 38 | 19:00
Lalbag | 72 | 13:00 | Ramganj | 56 | 20:00 | Borguna | 12 | 18:30
Madartek | 47 | 21:00 | Chaddagram | 26 | 14:00 | Borhan Uddin | 29 | 21:00
Dhaka University | 20 | 14:00 | PHP | 7 | 19:00 | Ishurdi | 46 | 18:30
Aftabnagar | 18 | 21:00 | Kochua | 36 | 18:30 | Ruppur Paromanobik | 3 | 20:00
Fatullah | 49 | 10:00 | Madunaghat | 38 | 18:00 | Natore | 93 | 20:00
Nawabganj | 30 | 21:00 | Hathazari | 61 | 13:00 | Bogra | 113 | 18:30
Keraniganj | 50 | 13:00 | Khulshi | 143 | 10:00 | Noagaon | 95 | 9:00
Banani | 38 | 18:00 | Halishahar | 63.5 | 13:00 | Rajshahi | 87 | 18:30
Mirpur | 79 | 14:00 | Baraulia | 151 | 12:00 | Rajshahi New | 30 | 19:30
Kalyanpur | 57 | 14:00 | Sikalbaha | 27 | 18:30 | C.Nawabganj | 55 | 12:00
Gulshan | 62 | 13:00 | Dohazari | 60 | 18:00 | Amnura | 44 | 18:30
Uttara | 46 | 13:00 | Cox'sbazar | 79 | 19:30 | Pabna | 70 | 18:30
Uttara New | 20 | 21:00 | Chandraghona | 22 | 18:30 | Shahjadpur | 74 | 18:30
Kamrangirchar | 51 | 18:30 | Kaptai | 3.5 | 18:00 | Serajganj | 83 | 19:00
Savar | 137 | 12:00 | A. Khaer Stl. | 8 | 1:00 | Niyamatpur | 79 | 8:00
Bhasantec | 83 | 13:00 | Bakulia | 84 | 12:00 | Joypurhat | 52 | 9:00
Agargaon | 50 | 13:00 | Julda | 22 | 16:00 | Sherpur(Bogura) | 48 | 18:30
Satmosjid | 66 | 13:00 | TK chemical | 21 | 18:30 | Mohastangor | 42 | 18:30
Old Tongi | 97 | 15:00 | Modern Steel | 0 | 1:00 | Bhangura | 20 | 20:00
Kabirpur | 164 | 15:00 | Shahmirpur | 32 | 6:00 | Rangpur | 116 | 18:30
Manikgong | 55 | 19:30 | Khagrachhari | 22 | 22:00 | Lalmonirhat | 40 | 18:30
Joydevpur | 120 | 18:00 | Matarbari | 26 | 18:30 | Saidpur | 92 | 9:00
New Tongi | 61 | 12:00 | Baroiar Hat | 32 | 18:00 | Purbasadipur | 89 | 19:00
Kodda | 215 | 12:00 | Rangamati | 10 | 18:30 | Thakurgaon | 68 | 19:00
Dhamrai | 82 | 9:00 | Abul Khair 230 | 137 | 2:00 | Palashbari | 94 | 18:30
Rajendrapur | 88 | 13:00 | BSRM | 158 | 4:00 | Barapukuria | 53 | 13:00
Bashundara | 92 | 18:00 | GPH Ispat | 97 | 16:00 | Panchagar | 48 | 18:30
Purbachal | 13 | 18:00 | Agrabad | 52 | 18:30 | Joldhaka | 57 | 18:30
Tongi Millgate | 36 | 12:00 | Goalpara | 22 | 13:00 | Kurigram | 56 | 18:30
Valuka | 88 | 9:00 | Central S/S | 66 | 18:30 | Mithapukur | 30 | 8:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-01-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 421 | 23:00 | 412 | 12:00 | Kaliakoir | 416 | 0.125 | 402 | 0.5
| Bheramara | 405 | 6:00 | 393 | 12:00 | Bhulta | 422 | 0.95833 | 404 | 0.5
| Ashuganj(N) | 421 | 6:00 | 407 | 12:00 | Gopalganj | 417 | 0.625 | 406 | 0.54167
| Payra | 418 | 6:00 | 411 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 248 | 1:00 | 242 | 15:00 | Hathazari | 244 | 20:00 | 237 | 17:00
| Ishurdi | 247 | 3:00 | 231 | 12:00 | Megnaghat | 247 | 3:00 | 240 | 11:00
| Ashuganj | 251 | 19:00 | 245 | 12:00 | Fenchuganj | 246 | 2:00 | 243 | 12:00
| Serajganj | 243 | 10:00 | 235 | 12:00 | Siddhirganj | 243 | 3:00 | 233 | 12:00
| Baghabari | 240 | 2:00 | 230 | 11:00 | Maniknagar | 242 | 3:00 | 234 | 11:00
| Barapukuria | 236 | 24:00 | 227 | 8:00 | Agargaon | 245 | 3:00 | 236 | 12:00
| Bogra | 239 | 1:00 | 229 | 9:00 | Barisal | 247 | 13:00 | 242 | 13:00
| Rajshahi | 243 | 3:00 | 229 | 12:00 | Bhola 225 MW | 250 | 3:00 | 245 | 14:00
| Khulna South | 249 | 3:00 | 229 | 19:00 | AKSML | 243 | 13:00 | 233 | 5:00
| Rampura | 240 | 1:00 | 232 | 11:00 | BSRM | 245 | 14:00 | 235 | 4:00
| Haripur | 240 | 1:00 | 233 | 12:00 | Bibiyana | 247 | 8:00 | 242 | 3:00
| Hasnabad | 242 | 1:00 | 234 | 12:00 | Bhulta | 243 | 3:00 | 233 | 12:00
| Shyampur | 244 | 6:00 | 234 | 12:00 | Ashuganj (S) | 250 | 6:00 | 241 | 16:00
| Aminbazar | 245 | 1:00 | 236 | 2:00 | Kaliakoir | 243 | 6:00 | 241 | 19:30
| Tongi | 241 | 1:00 | 235 | 11:00 | GPH | 244 | 14:00 | 232 | 4:00
| Comilla (N) | 243 | 2:00 | 236 | 12:00 | Jhenaidah | 240 | 1:00 | 226 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 5:00 | 132 | 12:00 | Kachua | 142 | 0.083333 | 139 | 0.5
| Munsiganj | 141 | 8:00 | 135 | 12:00 | Madanhat | 143 | 0.8125 | 138 | 0.125
| Sonargaon | 138 | 6:00 | 133 | 12:00 | Hathazari | 143 | 0.8125 | 138 | 0.5
| Shyampur | 136 | 19:00 | 129 | 12:00 | Khulshi | 140 | 0.20833 | 135 | 0.45833
| Bhulta | 134 | 18:00 | 128 | 12:00 | Halishahar | 143 | 0.875 | 136 | 0.29167
| Madanganj | 139 | 3:00 | 134 | 12:00 | Baraulia | 143 | 0.83333 | 135 | 0.5
| Shitalakhya | 141 | 20:00 | 135 | 12:00 | Sikalbaha | 143 | 0.29167 | 132 | 0.25
| Rahim steal | 138 | 18:00 | 133 | 11:00 | Dohazari | 140 | 0.58333 | 134 | 0.45833
| Matuail | 139 | 5:00 | 132 | 12:00 | Cox'sbazar | 128 | 0.625 | 120 | 0.75
| Ghorasal | 145 | 1:00 | 141 | 15:00 | Chandraghona | 144 | 0.875 | 139 | 0.16667
| Narsinghdi | 136 | 4:00 | 131 | 11:00 | Kaptai | 142 | 0.29167 | 140 | 0.041667
| Haripur (SBU) | 138 | 1:00 | 133 | 13:00 | A. Khaer Stl. | 143 | 0.875 | 136 | 0.5
| Sreenagar | 139 | 1:00 | 132 | 13:00 | Bakulia | 143 | 0.58333 | 139 | 0.041667
| Ullon | 140 | 01:00 | 133 | 12:00 | Julda | 140 | 0.041667 | 138 | 0.66667
| Hasnabad | 142 | 18:00 | 137 | 12:00 | TK Chemical | 143 | 0.77083 | 137 | 0.33333
| Magbazar | 137 | 02:00 | 0 | 00:00 | Modern Steel | 142 | 0.58333 | 139 | 0.45833
| Maniknagar | 138 | 17:00 | 132 | 19:00 | Shahmirpur | 142 | 0.25 | 137 | 0.083333
| Bangabhaban | 138 | 6:00 | 132 | 11:00 | Khagrachhari | 143 | 0.91667 | 138 | 0.16667
| Motijheel | 138 | 6:00 | 132 | 11:00 | Matarbari | 131 | 0.25 | 125 | 0.083333
| Narinda | 136 | 00:00 | 129 | 12:00 | Baroiar Hat | 143 | 19:00 | 136 | 5:00
| Kazla | 143 | 22:00 | 0 | 11:00 | Rangamati | 143 | 14:00 | 138 | 4:00
| Dhanmondi | 141 | 18:00 | 137 | 12:00 | Agrabad | 142 | 14:00 | 136 | 0.16667
| Lalbag | 133 | 03:00 | 122 | 12:00 | Goalpara S/S | 141 | 1:00 | 131 | 0.8125
| Madartek | 143 | 20:00 | 138 | 04:00 | Khulna Central S/S | 138 | 2:00 | 131 | 0.5
| Dhaka University | 137 | 00:00 | 132 | 12:00 | Noapara | 140 | 1:00 | 130 | 0.5
| Aftabnagar | 135 | 00:00 | 128 | 12:00 | Jessore | 139 | 0.95833 | 127 | 0.5
| Fatullah | 143 | 18:30 | 0 | 00:00 | Benapol | 140 | 4:00 | 126 | 0.54167
| Nawabganj | 138 | 3:00 | 132 | 12:00 | Jhenida(Old) | 140 | 0.20833 | 130 | 0.45833
| Keraniganj | 139 | 6:00 | 132 | 12:00 | Bottail | 140 | 0.041667 | 130 | 0.5
| Banani | 135 | 03:00 | 129 | 16:00 | G.K Project | 142 | 0.083333 | 133 | 0.5
| Mirpur | 137 | 1:00 | 132 | 12:00 | Faridpur | 140 | 0.25 | 131 | 0.5
| Kalyanpur | 134 | 5:00 | 132 | 12:00 | Rajbari | 141 | 0.125 | 131 | 0.54167
| Gulshan | 134 | 5:00 | 127 | 12:00 | Madaripur | 143 | 1:00 | 139 | 0.45833
| Uttara | 139 | 00:00 | 132 | 12:00 | Shariyatpur S/S | 144 | 0.20833 | 138 | 0.5
| Uttara New | 138 | 19:30 | 132 | 13:00 | Gopalganj | 142 | 6:00 | 136 | 0.5
| Kamrangirchar | 137 | 03:00 | 130 | 13:00 | Bagerhat | 140 | 23:00 | 128 | 0.77083
| Savar | 138 | 6:00 | 132 | 12:00 | Mongla | 137 | 2:00 | 126 | 13:30
| Bhasantec | 136 | 1:00 | 130 | 12:00 | Satkhira | 139 | 0.041667 | 128 | 19:00
| Agargaon | 137 | 3:00 | 131 | 12:00 | Gallamari | 140 | 3:00 | 135 | 0.45833
| Satmosjid | 136 | 3:00 | 131 | 12:00 | Magura | 140 | 0.041667 | 130 | 0.5
| Old Tongi | 141 | 4:00 | 135 | 11:00 | Narail | 141 | 3:00 | 127 | 0.5
| Kabirpur | 147 | 5:00 | 130 | 12:00 | Chuadanga | 138 | 4:00 | 124 | 0.79167
| Manikgong | 134 | 1:00 | 130 | 12:00 | Barisal(N) | 145 | 4:00 | 141 | 13:00
| Joydevpur | 144 | 1:00 | 140 | 15:00 | Barisal (S) | 143 | 0.083333 | 138 | 0.5
| New Tongi | 141 | 3:00 | 132 | 12:00 | Patuakhali(S) | 137 | 0.20833 | 135 | 0.29167
| Kodda | 140 | 13:00 | 135 | 9:00 | Bhandaria | 144 | 0.125 | 139 | 0.77083
| Dhamrai | 138 | 3:00 | 132 | 12:00 | Borguna | 145 | 5:00 | 140 | 18:00
| Rajendrapur | 139 | 14:00 | 133 | 16:00 | Jhenaidah(New) | 139 | 24:00 | 130 | 8:00
| Bashundara | 140 | 08:00 | 133 | 12:00 | Ishurdi | 143 | 3:00 | 133 | 12:00
| Purbachal | 134 | 23:00 | 120 | 08:00 | Ruppur Paromanobik | 140 | 1:00 | 132 | 12:00
| Tongi Millgate | 137 | 00:00 | 132 | 12:00 | Natore | 141 | 2:00 | 132 | 12:00
| Valuka | 132 | 1:00 | 120 | 12:00 | Bogra | 142 | 1:00 | 133 | 12:00
| Tangail | 136 | 1:00 | 128 | 12:00 | Noagaon | 137 | 3:00 | 127 | 12:00
| Mymensing | 134 | 1:00 | 121 | 12:00 | Rajshahi | 139 | 2:00 | 131 | 12:00
| Kishorganj | 136 | 3:00 | 128 | 12:00 | Rajshahi New | 139 | 2:00 | 131 | 12:00
| Netrokona | 132 | 4:00 | 120 | 12:00 | C.Nawabganj | 137 | 4:00 | 129 | 12:00
| Jamalpur | 140 | 21:00 | 133 | 9:00 | Amnura | 136 | 2:00 | 129 | 9:00
| Sherpur | 139 | 16:00 | 131 | 12:00 | Pabna | 142 | 3:00 | 132 | 13:00
| Srimongal | 141 | 1:00 | 137 | 11:00 | Shahjadpur | 145 | 1:00 | 138 | 7:00
| Shahjibazar | 139 | 5:00 | 134 | 12:00 | Serajganj | 141 | 3:00 | 132 | 12:00
| Fenchuganj | 140 | 1:00 | 136 | 10:00 | Niyamatpur | 134 | 3:00 | 124 | 12:00
| Khulawara | 140 | 1:00 | 136 | 10:00 | Joypurhat | 137 | 1:00 | 125 | 9:00
| Sylhet | 137 | 1:00 | 134 | 9:00 | Sherpur(Bogura) | 140 | 1:00 | 133 | 9:00
| Chatak | 139 | 6:00 | 136 | 10:00 | Mohastangor | 140 | 1:00 | 132 | 12:00
| Sunamganj | 136 | 1:00 | 133 | 10:00 | Bangura | 140 | 18:00 | 135 | 8:00
| Biani Bazar | 138 | 5:00 | 134 | 10:00 | Rangpur | 137 | 1:00 | 125 | 18:30
| Comilla(s) | 130 | 22:00 | 125 | 18:00 | Lalmonirhat | 133 | 3:00 | 120 | 9:00
| Comilla(n) | 143 | 7:00 | 140 | 5:00 | Saidpur | 134 | 4:00 | 122 | 8:00
| Chandpur | 141 | 1:00 | 139 | 12:00 | Purbasadipur | 133 | 3:00 | 120 | 8:00
| Feni | 143 | 18:30 | 136 | 4:00 | Thakurgaon | 133 | 3:00 | 119 | 9:00
| Chowmuhani | 142 | 18:30 | 135 | 1:00 | Palashbari | 138 | 1:00 | 127 | 12:00
| Ashuganj | 142 | 1:00 | 138 | 12:00 | Barapukuria | 134 | 0.041667 | 127 | 0.33333
| Daudkandi | 141 | 18:00 | 137 | 12:00 | Panchagar | 134 | 0.125 | 119 | 0.375
| B.Baria | 138 | 1:00 | 131 | 12:00 | Joldhaka | 133 | 0.16667 | 120 | 0.375
| Ramganj | 141 | 18:00 | 133 | 5:00 | Kurigram | 136 | 0.041667 | 121 | 0.5
| Chaddagram | 144 | 20:00 | 138 | 12:00 | Mithapukur | 137 | 4:00 | 128 | 9:00
| PHP | 141 | 8:00 | 136 | 1:00

## L-Curve
Date | 2022-01-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 176 | 5137 | 2470 | 7607 |  |  |  | QF-LDC-11
0:30 | 124.5 | 4892.5 | 2339.5 | 7232 | Date: | 2022-01-31
1:00 | 73 | 4648 | 2209 | 6857
1:30 | 94 | 4575 | 2153 | 6728
2:00 | 115 | 4502 | 2097 | 6599
2:30 | 123.5 | 4441.5 | 2074 | 6515.5 | [5 empty] | Gen. at Eve. Peak | 9801 | 9801 MW (19:00 )
3:00 | 132 | 4381 | 2051 | 6432 | [6 empty] | 19:00
3:30 | 159 | 4252 | 2051.5 | 6303.5 | [5 empty] | Gen. at Day Peak | 8869 | 8869 MW (12:00 )
4:00 | 186 | 4123 | 2052 | 6175 | [6 empty] | 12:00
4:30 | 184.5 | 4086 | 2061 | 6147 | [5 empty] | Highest Generation | 9801
5:00 | 183 | 4049 | 2070 | 6119 | [6 empty] | 19:00
5:30 | 141.5 | 4139 | 2118 | 6257
6:00 | 100 | 4229 | 2166 | 6395
6:30 | 60.5 | 4455.5 | 2218 | 6673.5
7:00 | 21 | 4682 | 2270 | 6952
7:30 | 84 | 4968.5 | 2420.5 | 7389
8:00 | 147 | 5255 | 2571 | 7826
8:30 | 90.5 | 5569 | 2662 | 8231
9:00 | 34 | 5883 | 2753 | 8636
9:30 | 99 | 5856.5 | 2757.5 | 8614
10:00 | 164 | 5830 | 2762 | 8592
10:30 | 156 | 5850.5 | 2763 | 8613.5
11:00 | 148 | 5871 | 2764 | 8635
11:30 | 129 | 5970 | 2782 | 8752
12:00 | 110 | 6069 | 2800 | 8869
12:30 | 55 | 6194.5 | 2851 | 9045.5
13:00 | 0 | 6320 | 2902 | 9222
13:30 | 67 | 6104.5 | 2864 | 8968.5
14:00 | 134 | 5889 | 2826 | 8715
14:30 | 254 | 5691.5 | 2777 | 8468.5
15:00 | 374 | 5494 | 2728 | 8222
15:30 | 354 | 5533 | 2644 | 8177
16:00 | 334 | 5572 | 2560 | 8132
16:30 | 289.5 | 5643 | 2541 | 8184
17:00 | 245 | 5714 | 2522 | 8236
17:30 | 145 | 6086.5 | 2676 | 8762.5
18:00 | 45 | 6459 | 2830 | 9289
18:30 | 146 | 6626 | 2919 | 9545
19:00 | 247 | 6793 | 3008 | 9801
19:30 | 164 | 6645 | 3020 | 9665
20:00 | 223 | 6616 | 2970 | 9586 |  |  |  | Executive Engineer
20:30 | 153.5 | 6497 | 2972 | 9469 |  |  |  | Network Operation Division
21:00 | 84 | 6378 | 2974 | 9352
21:30 | 95 | 6154.5 | 2934 | 9088.5
22:00 | 106 | 5931 | 2894 | 8825 |  |  |  |  | Page 6 of 7
22:30 | 178.5 | 5712.5 | 2816.5 | 8529
23:00 | 251 | 5494 | 2739 | 8233
23:30 | 213.5 | 5315.5 | 2604.5 | 7920
24:00 | 176 | 5137 | 2470 | 7607
9801 MW (19:00 )
8869 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-01-31 |  | Energy |  | 197327560
[13 empty] | 2022-01-31 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2343 | 728 | 1541 | 0 | 2296 | 530 | 82 | 0 | 0 | 87 | 0 | 0
0:30 | 2308.5 | 732.5 | 1489 | 0 | 2017 | 520 | 82 | 0 | 0 | 83 | 0 | 0 | Date: | 2022-01-31
1:00 | 2274 | 737 | 1437 | 0 | 1738 | 510 | 82 | 0 | 0 | 79 | 0 | 0
1:30 | 2267 | 711 | 1471 | 0 | 1609.5 | 510 | 81.5 | 0 | 0 | 78 | 0 | 0 | [8 empty] | Total Energy | 197.3276 | Total Energy Gen 197.328 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 197.328 MKWHr
2:00 | 2260 | 685 | 1505 | 0 | 1481 | 510 | 81 | 0 | 0 | 77 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2257 | 685 | 1510.5 | 0 | 1411 | 495 | 81 | 0 | 0 | 76 | 0 | 0 | [8 empty] | Energy Requirement | 197.3276
3:00 | 2254 | 685 | 1516 | 0 | 1341 | 480 | 81 | 0 | 0 | 75 | 0 | 0
3:30 | 2251.5 | 685 | 1523.5 | 0 | 1208 | 480 | 81.5 | 0 | 0 | 74 | 0 | 0 | [6 empty] | Shortage
4:00 | 2249 | 685 | 1531 | 0 | 1075 | 480 | 82 | 0 | 0 | 73 | 0 | 0
4:30 | 2236 | 685 | 1552.5 | 0 | 1039 | 480 | 82 | 0 | 0 | 72.5 | 0 | 0
5:00 | 2223 | 685 | 1574 | 0 | 1003 | 480 | 82 | 0 | 0 | 72 | 0 | 0
5:30 | 2220 | 708 | 1581 | 0 | 1114.5 | 480 | 82.5 | 0 | 0 | 71 | 0 | 0
6:00 | 2217 | 731 | 1588 | 0 | 1226 | 480 | 83 | 0 | 0 | 70 | 0 | 0
6:30 | 2242.5 | 731 | 1592.5 | 0 | 1472 | 480 | 83 | 0 | 0 | 71 | 1.5 | 0 |  |  |  |  | Coal
7:00 | 2268 | 731 | 1597 | 0 | 1718 | 480 | 83 | 0 | 0 | 72 | 3 | 0
7:30 | 2284.5 | 732.5 | 1582 | 0 | 2095.5 | 495 | 83 | 0 | 16 | 80 | 20.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2301 | 734 | 1567 | 0 | 2473 | 510 | 83 | 0 | 32 | 88 | 38 | 0
8:30 | 2351.5 | 734 | 1558 | 0 | 2727.5 | 530 | 83 | 0 | 93.5 | 89 | 64.5 | 0
9:00 | 2402 | 734 | 1549 | 0 | 2982 | 550 | 83 | 0 | 155 | 90 | 91 | 0
9:30 | 2344.5 | 735 | 1541.5 | 0 | 2999.5 | 524.5 | 83 | 0 | 180 | 92 | 114 | 0
10:00 | 2287 | 736 | 1534 | 0 | 3017 | 499 | 83 | 0 | 205 | 94 | 137 | 0
10:30 | 2276 | 736 | 1550 | 0 | 3018 | 499.5 | 83.5 | 0 | 205 | 94 | 151.5 | 0
11:00 | 2265 | 736 | 1566 | 0 | 3019 | 500 | 84 | 0 | 205 | 94 | 166 | 0
11:30 | 2294.5 | 736 | 1550 | 0 | 3072 | 504.5 | 84 | 0 | 238 | 100 | 173 | 0
12:00 | 2324 | 736 | 1534 | 0 | 3125 | 509 | 84 | 0 | 271 | 106 | 180 | 0
12:30 | 2343 | 735.5 | 1539.5 | 33 | 3211 | 539 | 83.5 | 0 | 279.5 | 107.5 | 174 | 0
13:00 | 2362 | 735 | 1545 | 66 | 3297 | 569 | 83 | 0 | 288 | 109 | 168 | 0
13:30 | 2362 | 735 | 1545 | 66 | 3297 | 569 | 83 | 0 | 288 | 109 | 168 | 0
14:00 | 2362 | 735 | 1545 | 66 | 3297 | 569 | 83 | 0 | 288 | 109 | 168 | 0
14:30 | 2239 | 736.5 | 1495 | 33 | 3091 | 539.5 | 81.5 | 0 | 262.5 | 104.5 | 139.5 | 0
15:00 | 2116 | 738 | 1445 | 0 | 2885 | 510 | 80 | 0 | 237 | 100 | 111 | 0
15:30 | 2129 | 737.5 | 1451 | 0 | 2855.5 | 495 | 81 | 0 | 242.5 | 100 | 85.5 | 0
16:00 | 2142 | 737 | 1457 | 0 | 2826 | 480 | 82 | 0 | 248 | 100 | 60 | 0
16:30 | 2204 | 737 | 1455.5 | 0 | 2843.5 | 480 | 82.5 | 0 | 271 | 103 | 38.5 | 0
17:00 | 2204 | 737 | 1454 | 0 | 2861 | 480 | 83 | 0 | 294 | 106 | 17 | 0
17:30 | 2272 | 737 | 1479.5 | 119.5 | 3074 | 480 | 83 | 0 | 395 | 114 | 8.5 | 0
18:00 | 2340 | 737 | 1505 | 239 | 3287 | 480 | 83 | 0 | 496 | 122 | 0 | 0
18:30 | 2330.5 | 753 | 1505.5 | 325.5 | 3395.5 | 530 | 83 | 0 | 503 | 119 | 0 | 0
19:00 | 2321 | 769 | 1506 | 412 | 3504 | 580 | 83 | 0 | 510 | 116 | 0 | 0
19:30 | 2329 | 769 | 1524 | 282 | 3441 | 610 | 83 | 0 | 507 | 120 | 0 | 0
20:00 | 2334 | 761 | 1519 | 222 | 3432 | 610 | 83 | 0 | 506 | 119 | 0 | 0
20:30 | 2338.5 | 761 | 1531 | 111 | 3420 | 610 | 83.5 | 0 | 496 | 118 | 0 | 0
21:00 | 2343 | 761 | 1543 | 0 | 3408 | 610 | 84 | 0 | 486 | 117 | 0 | 0
21:30 | 2331 | 761 | 1546 | 0 | 3282 | 605 | 84 | 0 | 366 | 113.5 | 0 | 0
22:00 | 2319 | 761 | 1549 | 0 | 3156 | 600 | 84 | 0 | 246 | 110 | 0 | 0
22:30 | 2321 | 744 | 1535.5 | 0 | 2977.5 | 590 | 83.5 | 0 | 173 | 104.5 | 0 | 0
23:00 | 2323 | 727 | 1522 | 0 | 2799 | 580 | 83 | 0 | 100 | 99 | 0 | 0
23:30 | 2333 | 727.5 | 1531.5 | 0 | 2547.5 | 555 | 82.5 | 0 | 50 | 93 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 24° C
24:00 | 2343 | 728 | 1541 | 0 | 2296 | 530 | 82 | 0 | 0 | 87 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 197.328 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 197.328 MKWHr
Note on W13: Author:

## Generation
g | 2022-01-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 82 | 81 | 81 | 82 | 82 | 83 | 83 | 83 | 83 | 83 | 84 | 84 | 83 | 83 | 80 | 82 | 83 | 83 |  | 83 | 83 | 83 | 84 | 84 | 83 | 82 | 1968682
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 242424
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 11 | 15 | 18 | 20 | 18 | 17 | 12 | 7 | 2 | [9 empty] | 127305
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 49 |  |  | 0 | 215261
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 18 | 34 | 50 | 81 | 85 | 68 | 96 | 105 | 105 | 64 | 17 | 17 | 50 |  | 105 | 105 | 105 | 68 | 17 | 17 | 17 | 1338181
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 20 |  | 20 | 20 | [5 empty] | 42816
14 | Titas 50 MW Peaking PP | [9 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 |  |  | 0 | 581008
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 15 | 15 | 15 | 15 | 30 | 118 | 233 | 245 | 233 | 250 | 250 | 231 | 243 | 243 | 257 | 263 | 268 |  | 270 | 270 | 268 | 280 | 280 | 283 | 270 | 4787344
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 250909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 225 | 220 | 220 | 220 | 220 | 220 | 225 | 220 | 220 | 220 | 220 | 220 | 220 | 100 | 100 | 140 | 180 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 205 | 4793000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 27 | 27 | 29 | 667728
33 | Ashuganj 225 MW CCPP | 226 | 190 | 184 | 182 | 184 | 184 | 196 | 190 | 181 | 182 | 183 | 180 | 142 | 171 | 188 | 188 | 189 | 194 |  | 196 | 201 | 205 | 205 | 205 | 212 | 214 | 4593000
34 | Ashuganj 450 MW CCPP(South) | 275 | 270 | 270 | 270 | 270 | 270 | 310 | 280 | 305 | 270 | 270 | 270 | 300 | 270 | 265 | 265 | 295 | 290 |  | 265 | 265 | 265 | 265 | 270 | 265 | 265 | 6797000
| Ashuganj 450 MW CCPP(North) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 220 | 275 | 220 | 220 | 200 | 220 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4225000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143520
36 | Chandpur 150 MW CCPP | 86 | 87 | 87 | 85 | 87 | 85 | 85 | 85 | 84 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 89 | 88 |  | 86 | 88 | 88 | 85 | 85 | 85 | 85 | 2075720
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 150 | 150 | 150 | 150 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3809750
41 | Haripur 360MW CCPP(HPL) | 163 | 177 | 180 | 193 | 202 | 205 | 191 | 169 | 170 | 171 | 165 | 164 | 168 | 160 | 161 | 164 | 167 | 169 |  | 167 | 164 | 155 | 165 | 155 | 149 | 157 | 4108000
42 | RPCL 210MW CCPP | 112 | 112 | 112 | 113 | 114 | 114 | 112 | 112 | 113 | 98 | 85 | 85 | 84 | 84 | 85 | 96 | 102 | 104 |  | 105 | 105 | 105 | 111 | 110 | 110 | 112 | 2438400
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 9 | 21 | 31 | 37 | 41 | 39 | 31 | 20 | 10 | 3 | [9 empty] | 241440
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 623640
46 | Shajibazar 330 MW CCPP | 138 | 135 | 135 | 134 | 135 | 135 | 134 | 135 | 135 | 136 | 138 | 135 | 137 | 138 | 137 | 137 | 134 | 138 |  | 136 | 137 | 137 | 136 | 135 | 136 | 137 | 3238000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 72 | 72 | 72 | 40 | 40 | 40 | 72 | 71 | 40 | 40 | 67 | 68 | 53 | 40 | 40 | 40 | 69 |  | 69 | 69 | 70 | 70 | 40 | 40 | 40 | 1299168
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 75 | 75 | 75 |  | 76 | 76 | 76 | 76 | 76 | 75 | 75 | 1834560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 164 | 164 | 177 | 177 | 177 | 177 | 176 | 162 | 176 |  | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 4237110
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 230160
55 | Fenchugonj 51 MW PP (Barakatullah) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 48 | 45 | 48 | 49 | 51 | 51 | 51 | 51 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 1200000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 496560
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 295 | 290 | 290 | 285 | 300 | 290 | 290 | 290 | 280 | 280 | 285 | 290 | 280 | 260 | 290 | 290 | 290 |  | 285 | 305 | 300 | 290 | 290 | 280 | 280 | 7116000
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 340 | 340 | 335 | 300 | 339 | 360 | 360 | 400 | 400 | 400 | 350 | 350 | 330 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8716000
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1082832
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531840
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 424416
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 19 | 19 | 22 |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 424296
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 526716
63 | Impoprt (Tripura) | 79 | 77 | 75 | 73 | 72 | 70 | 72 | 88 | 90 | 94 | 94 | 106 | 109 | 111 | 100 | 100 | 106 | 122 |  | 116 | 120 | 119 | 117 | 110 | 99 | 87 | 2232960
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 35 | 35 | 36 | 32 | 33 | 7 | 3 | 3 | 2 | 4 | 10 | 2 | 2 | 3 | 10 | 12 |  | 18 | 14 | 24 | 32 | 40 | 40 | 35 | 484800
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 |  | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 452448
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 195840
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 8 |  | 8 | 8 | 8 | 15 | 13 | 16 | 25 | 370000
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 238400
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 6 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 206460
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 549600
72 | Rupganj 33 MW PP(Summit) | 13 | 13 | 13 | 13 | 13 | 15 | 15 | 14 | 14 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 541200
73 | Ghorashal 108MW PP (Regent) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [18 empty] | 7 | 176681
| Feni Lanka Power | [7 empty] | 34 | 51 | 51 | 51 | 70 | 114 | 114 | 88 | 88 | 52 | 103 |  | 114 | 114 | 114 | 114 | 52 | 17 | 17 | 1246020
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 10 | 8 | 8 | 8 | 8 | 8 | 85 | 104 |  | 106 | 108 | 108 | 108 | 108 | 50 | 8 | 833280
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 90 | 90 | 90 | 90 | 90 | 90 | 102 | 108 | 108 | 114 | 129 | 126 | 128 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3088800
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 12 | 45 | 51 | 51 | 51 | 51 | 51 | 25 | 25 | 25 | 40 |  | 51 | 51 | 51 | 51 | 25 |  | 0 | 631680
79 | Kodda 150MW PP | [7 empty] | 32 | 100 | 100 | 100 | 133 | 133 | 150 | 64 | 64 | 100 | 145 |  | 150 | 150 | 150 | 150 | 82 |  | 0 | 1639200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 47 | 52 | 1244966
| Gazipur 100 MW PP | 90 | 90 | 90 | 35 | 35 | 64 | 90 | 90 | 90 | 70 | 70 | 80 | 90 | 90 | 90 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2195676
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 2 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 22559
| Jodiac Power | [11 empty] | 2 | 27 | 21 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 232818
| Karnaphuli Power Ltd. | [6 empty] | 14 | 17 | 17 | 17 | 17 | 23 | 55 | 68 | 17 | 17 | 17 | 18 |  | 34 | 17 | 17 | 17 | 17 | 17 | 0 | 487599
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 21 | 35 | 36 | 36 | 36 | 38 | 55 | 20 | 10 | 10 | 30 |  | 60 | 60 | 60 | 59 | 20 |  | 0 | 588730
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 55 | 55 | 57 | 93 | 93 | 92 | 93 | 93 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2384640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [13 empty] | 10 |  |  |  | 10 |  | 10 | 10 | 10 |  |  |  |  | 42840
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 1191752
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 0 |  |  | 0 | 2 | 16 | 64 | 93 | 93 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 72 | 7 | 1602864
95 | Patenga 50MW PP (Baraka) | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 40 | 40 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 40 | 40 | 40 | 40 | 960960
96 | Chattogram 108 MW PP (ECPV) | 41 | 22 | 12 | 12 | 12 | 29 | 86 | 90 | 86 | 90 | 85 | 85 | 90 | 90 | 90 | 86 | 89 | 87 |  | 89 | 90 | 90 | 90 | 91 | 90 | 90 | 1727040
97 | katpotti 52 MW | 48 | 48 | 48 | 48 | 48 | 47 | 48 | 47 | 48 | 46 | 43 | 46 | 41 | 46 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1142976
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 5 | 22 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 25 | 0 | 653725
100 | Manikganj 55 MW PP (Northern) | 35 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1085942
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2922463
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [9 empty] | 9900
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 865080
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 51 | 36 |  |  |  | 113 |  | 132 | 62 | 62 |  |  |  | 0 | 376544
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 25 |  | 100 | 80 | 80 |  |  |  | 0 | 205942
106 | Mymensingh 200 MW PP (United) | 120 | 120 | 120 | 80 | 80 | 90 | 144 | 200 | 200 | 200 | 194 | 194 | 193 | 184 | 193 | 193 | 193 | 200 |  | 200 | 200 | 193 | 200 | 200 | 200 | 200 | 4207200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 25 |  | 100 | 80 | 80 |  |  |  | 0 | 196947
114 | Kodda 149 MW PP Unit-1 (Summit) | 22 | 0 |  |  |  |  | 8 | 67 | 144 | 149 | 149 | 149 | 149 | 149 | 137 | 102 | 92 | 144 |  | 149 | 149 | 149 | 149 | 140 | 118 | 0 | 2256336
115 | Juldah 100 MW PP Unit-3 (Acorn) |  |  |  |  | 0 | 6 | 30 | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 40 | 20 | 76 |  | 90 | 70 | 70 | 70 | 70 | 10 | 0 | 1143360
116 | Chandpur 200MW (Desh energy) | [7 empty] | 1 | 38 | 68 | 68 | 68 | 75 | 94 | 51 | 51 | 51 | 69 |  | 85 | 85 | 85 | 85 | 51 | 51 | 17 | 1079040
117 | Ashuganj 150MW PP (Midland) | 135 | 135 | 112 | 110 | 110 | 123 | 135 | 130 | 132 | 128 | 130 | 135 | 140 | 147 | 137 | 130 | 138 | 145 |  | 147 | 148 | 147 | 145 | 148 | 148 | 148 | 3250109
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 12 | 32 | 70 | 89 | 89 | 89 | 89 | 98 | 99 | 99 | 88 | 89 | 89 |  | 98 | 98 | 99 | 99 | 80 | 45 | 8 | 1528800
| Anwara 300 MW PP (United) | 260 | 230 | 190 | 135 | 135 | 135 | 135 | 190 | 275 | 282 | 284 | 282 | 282 | 0 | 130 | 277 | 300 | 290 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5823600
| Juldah unit-2 (Acorn) | [8 empty] | 10 | 10 | 10 | 10 | 50 | 60 | 10 | 10 | 10 | 30 |  | 40 | 10 | 10 | 10 |  |  | 0 | 254400
| Anlima Energy Ltd. | 106 | 116 | 116 | 51 | 51 | 75 | 100 | 100 | 100 | 100 | 100 | 115 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2560527
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 446040
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 4 | 13 | 21 | 25 | 27 | 23 | 23 | 18 | 10 | 3 | [9 empty] | 171117
| Chandpur 115(Doreen) | [10 empty] | 7 | 12 |  |  |  | 10 | 0 | [8 empty] | 0 | 28800
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1244160
120 | Eastern Zone Total | 4648 | 4502 | 4381 | 4123 | 4049 | 4229 | 4682 | 5255 | 5883 | 5830 | 5871 | 6069 | 6320 | 5889 | 5494 | 5572 | 5714 | 6459 |  | 6793 | 6645 | 6616 | 6378 | 5931 | 5494 | 5137 | 133766607
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [11 empty] | 4 | 4 | 8 | 14 | 18 | 23 | 25 |  | 28 | 25 | 25 | 25 | 9 |  |  | 167520
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 2 | 77 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 53 | 1775040
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 17 | 39 | 59 | 72 | 79 | 75 | 69 | 53 | 29 | 8 | [9 empty] | 504720
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 214 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 201 | 180 | 220 |  | 221 | 221 | 221 | 221 | 221 | 221 | 216 | 5063345
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 265445
| Bhola 225 MW CCPP | 92 | 92 | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 92 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 2217376
140 | Bhola 33 MW PP (Venture) | 21 | 21 | 19 | 16 | 16 | 17 | 16 | 17 | 17 | 16 | 16 | 19 | 21 | 20 | 17 | 17 | 18 | 23 |  | 24 | 24 | 25 | 25 | 24 | 24 | 23 | 455000
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 |  |  | 15 |  |  |  |  | 6 |  | 10 | 10 |  |  |  |  | 0 | 72960
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [14 empty] | 3 | 10 | 15 | 19 |  | 19 | 19 | 19 | 15 |  |  |  | 96384
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 737 | 685 | 685 | 685 | 685 | 731 | 731 | 734 | 734 | 736 | 736 | 736 | 735 | 737 | 738 | 737 | 737 | 737 |  | 769 | 769 | 761 | 761 | 761 | 727 | 728 | 17660363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 310 | 310 | 280 | 280 | 280 | 280 | 280 | 310 | 350 | 300 | 300 | 310 | 370 | 350 | 310 | 280 | 280 | 280 |  | 380 | 410 | 410 | 410 | 400 | 380 | 330 | 8676900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 199 | 199 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4851200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 34 |  | 34 | 34 | 34 | 34 | 34 |  |  | 154326
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 3 | 3 | 4 | 3 | 3 | 2 | 1 | [10 empty] | 24660
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 114 | 116 | 116 | 116 | 116 | 116 | 115 | 113 | 113 | 125 | 130 | 135 | 137 | 137 | 137 | 135 | 134 | 134 |  | 134 | 134 | 134 | 134 | 135 | 137 | 137 | 3283573
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 255 | 284 | 299 | 304 | 322 | 326 | 359 | 372 | 350 | 350 | 350 | 345 | 338 | 306 | 289 | 285 | 286 | 288 |  | 295 | 300 | 298 | 314 | 323 | 321 | 338 | 7580800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [8 empty] | 5 | 5 | 5 | 34 | 51 | 47 | 40 | 40 | 40 | 44 |  | 47 | 47 | 47 | 40 |  |  |  | 426875
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 18 | 17 | 17 | 16 | 16 | 15 | 16 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 179190
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 34 |  | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 608625
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 28 |  | 31 | 31 | 30 | 23 | 21 |  |  | 135904
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1249666
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 50 | 50 | 50 | 50 | 50 | 66 | 66 | 66 | 66 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 1127056
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 50 |  | 50 | 30 |  |  |  |  | 0 | 102204
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 35 | 35 | 35 | 35 | 70 | 92 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 76 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2223168
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 0 |  |  | 0 | 20 | 35 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 35 | 100 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 1826400
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 105 | 49 | 35 | 35 | 35 | 60 | 78 | 99 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 113 | 107 | 113 | 113 | 2222457
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 30484
178 | Energypac Power Venture Thakurgaon Ltd. | [8 empty] | 8 | 34 | 20 |  | 20 |  | 20 |  | 20 | [8 empty] | 0 | 113472
178