## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-02-03 | Thursday
|  |  | Date (day): | 2022-02-03 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11510.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12204 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-02-02 | 2022-02-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 220 | 220 | 220 | 220
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 243 | 252 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 210 | 220 | 220 | 220 | 230 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 59 | 60 | 60 |  | 40 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 42 | 47 | 51 | 51
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 54 | 54 |  | 0 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 34 | 35 | 35 |  | 45 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 25 | 20 | 20 |  | 13 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 13 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 265 | 275 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 221 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 162 | 160 | 160 |  | 2 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 37 | 43 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2189 | 2639 | 2771 | 2841 | 1690 | 1170
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 40 | 40 | 40 |  | 10 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 |  | 184 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 68 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 70 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 19 | 20 |  | 2 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 13 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 89 | 89 | 97 | 97 |  | 11 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 300 | 300 | 260 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 51 | 51 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 40 | 50 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 887 | 1003 | 1240 | 1266 | 180 | 929
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 202 | 220 | 220 | 1
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 150 | 150 | 235 | 260 | 100 |  | ST under maint
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 275 | 360 | 360 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 142 | 140 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 45 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 122 | 135 | 135 |  | 28 | ST under maint
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 34 | 100 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 108 | 138 | 134
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 25 | 25 | 25 |  | 8 | Engine problem
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 9 | 9 | 9 | 9 |  | 16 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 51 | 52 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 108 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 104 | 0 | 0 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1445 | 1530 | 2019 | 2140 | 641 | 89
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 83 | 101 | 110 | 110 | 92 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 194 | 193 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 109 | 110 | 110
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 465 | 447 | 515.6 | 464 | 92 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 138 | 136 | 135 | 135 |  | 195 | GT-2 under S/D due to gas
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 69 | 70 | 70
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 75 | 80
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 177 | 177 | 180 | 180 |  | 51 | Machine problem
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1376 | 1430 | 1466 | 1471 | 53 | 855
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 731 | 731 | 751 | 751
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 0 | 35 |  | 19 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 85 | 80 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 899 | 910 | 1036 | 1351 | 410 | 88
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 21 | 20 | 24 |  | 9 | Engine problem
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 90 | 90 | 92 | 102 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 83 | 87 | 76 | 76 | 19
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 430 | 560 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 619 | 758 | 916 | 1072 | 121 | 229
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 34 | 34 |  | 18 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 48 | 50 | 50 |  | 21 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 40 |  | 10 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 126 | 126 | 130 | 130 | 90 |  | Gas shortage
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 268 | 226 | 325 | 325 | 89 |  | Gas shortage
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 31 |  | 19 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 49 | 100 | 90 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 100 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 91 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 736 | 982 | 1226 | 1271 | 779 | 68
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 113 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 14 | 0 | 0 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 318 | 312 | 321 | 328 | 74 | 195
|  | Total |  |  |  |  | 22066 | 21035 | 8934 | 10011 | 11510.6 | 12204 | 4040 | 3631
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8772.4723 | 9830 | 11302.4871 | 11983.3503
| A. |  | 2022-02-02 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 10011 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6103 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10011 | MW
| 3 | Day peak Generation : |  |  | 8934 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9830 | MW
| 4 | Evening peak Generation : |  |  | 10011 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 199.8261 | MKWHr | By Solar | 1.0413 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 93.9767 | MKWHr |  | By Oil: | 67.4208 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.3523 | MKWHr |  | By Hydro: | 1.1047 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4040 | MW | Dhaka | 3590 | 3590 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3631 | MW | Chittagong | 1098 | 1098 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7671 | MW | Khulna | 1139 | 1139 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 738.7 | MMCFD |  |  | Rajshahi | 1027 | 1027 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 97714056.736 | ii) Oil : | Taka | 482376632.12 | Comilla | 785 | 785 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 76809186 | Total | Taka | 656899874.856 | Mymensingh | 884 | 884 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.873 | MKWHr. | Sylhet | 336 | 336 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -325 | MW (E to W) at | 19:00 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -337 | MW at | 8:00 | hrs | Rangpur | 734 | 734 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.7° C |  |  | Total | 9830 | 9830 |  | 0
| B. |  | 2022-02-03 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 26.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12204 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 2004 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 203.5987 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6186 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.4785 | MKWHr. | ii) HVDC Flow at Peak Time |  | 731 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4518 | MKWHr. | iii) Maximum HVDC Flow : |  | 736 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.57 |  | (b) Today: | 93.45 |  | (c) Rule Curve: |  | 96.72
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-02-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 220 | 0 | 0 | 6 | 0 | 0 | 216 |  | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 22 | 25 | 9 | 16 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 40 | 18 | 32 | 0 | 0 | 0 | 150 | 335 | 209 | 8 | 85 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 25 | 9 | 77 | 82 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 69 | 75 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 45 | 0 | 0 | 180 | 0 | 0 | 0 | 50 | 0 | 140 | 0 | 8 | 105 | 51 | 0 | 260 | 0 | 0 | 0 | 8 | 0 | 381 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 120 | 0 | 295 | 17 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 310 | 213 | 0 | 0 | 0 | 0 | 0 |  | 4870 | 2100 | 6970 | 2351 | 727 | 1605 | 0 | 1655 | 509 | 46 | 0 | 0 | 77 | 0 | 0 | 93.59
2:00 | 0 | 0 | 222 | 0 | 0 | 6 | 0 | 0 | 230 |  | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 0 | 0 | 22 | 25 | 9 | 16 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 97 | 40 | 18 | 32 | 0 | 0 | 0 | 150 | 330 | 211 | 8 | 86 | 5 | 5 | 0 | 51 | 0 | 0 | 34 | 21 | 8 | 25 | 9 | 73 | 105 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 69 | 75 | 0 | 177 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 0 | 0 | 20 | 0 | 50 | 0 | 8 | 105 | 0 | 0 | 260 | 0 | 0 | 0 | 8 | 0 | 350 | 104 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 120 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 184 | 0 | 0 | 0 | 0 | 0 |  | 4575 | 2005 | 6580 | 2344 | 682 | 1596 | 0 | 1330 | 509 | 46 | 0 | 0 | 73 | 0 | 0 | 93.59
3:00 | 0 | 0 | 220 | 0 | 0 | 6 | 0 | 0 | 238 |  | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 17 | 0 | 0 | 22 | 25 | 9 | 16 | 13 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 97 | 38 | 18 | 32 | 0 | 0 | 0 | 150 | 315 | 209 | 8 | 85 | 5 | 5 | 0 | 51 | 0 | 0 | 34 | 21 | 8 | 25 | 9 | 74 | 103 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 40 | 75 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 30 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 8 | 70 | 0 | 0 | 260 | 0 | 0 | 0 | 8 | 0 | 350 | 72 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 55 |  | 683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 120 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 135 | 0 | 0 | 0 | 0 | 0 |  | 4329 | 1997 | 6326 | 2277 | 683 | 1585 | 0 | 1122 | 539 | 46 | 0 | 0 | 74 | 0 | 0 | 93.58
4:00 | 0 | 0 | 220 | 0 | 0 | 6 | 0 | 0 | 283 |  | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 17 | 0 | 0 | 22 | 25 | 9 | 16 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 40 | 18 | 40 | 0 | 0 | 0 | 150 | 320 | 214 | 8 | 85 | 5 | 5 | 0 | 51 | 0 | 0 | 34 | 21 | 8 | 25 | 9 | 68 | 105 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 134 | 40 | 75 | 0 | 177 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 15 | 0 | 0 | 30 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 8 | 52 | 0 | 0 | 230 | 0 | 0 | 0 | 8 | 0 | 320 | 17 | 0 | 144 | 116 | 0 | 17 | 0 | 0 | 17 |  | 684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 120 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 121 | 0 | 0 | 0 | 0 | 0 |  | 4226 | 1988 | 6214 | 2262 | 684 | 1649 | 0 | 955 | 550 | 46 | 0 | 0 | 68 | 0 | 0 | 93.58
5:00 | 0 | 0 | 221 | 0 | 0 | 6 | 0 | 0 | 285 |  | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 17 | 0 | 0 | 22 | 25 | 9 | 16 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 97 | 40 | 18 | 40 | 0 | 0 | 0 | 150 | 315 | 213 | 8 | 86 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 25 | 9 | 69 | 106 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 40 | 75 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 41 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 8 | 52 | 0 | 0 | 230 | 0 | 0 | 0 | 8 | 0 | 300 | 17 | 0 | 90 | 116 | 0 | 17 | 0 | 0 | 17 |  | 685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 120 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 62 | 0 | 0 | 0 | 0 | 0 |  | 4166 | 1937 | 6103 | 2240 | 685 | 1585 | 0 | 928 | 550 | 46 | 0 | 0 | 69 | 0 | 0 | 93.57
6:00 | 0 | 0 | 221 | 0 | 0 | 6 | 0 | 0 | 303 |  | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 35 | 0 | 0 | 22 | 25 | 9 | 16 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 97 | 40 | 18 | 40 | 0 | 0 | 0 | 150 | 340 | 208 | 8 | 84 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 20 | 9 | 69 | 105 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 40 | 75 | 0 | 177 | 0 | 0 | 10 | 315 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 0 | 0 | 50 | 0 | 13 | 0 | 11 | 70 | 0 | 0 | 230 | 0 | 0 | 0 | 8 | 0 | 300 | 45 | 0 | 90 | 116 | 0 | 17 | 0 | 0 | 34 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 120 | 0 | 344 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 350 | 62 | 0 | 0 | 0 | 0 | 0 |  | 4373 | 2085 | 6458 | 2252 | 731 | 1692 | 0 | 1118 | 550 | 46 | 0 | 0 | 69 | 0 | 0 | 93.57
7:00 | 0 | 0 | 220 | 0 | 0 | 6 | 0 | 0 | 291 |  | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 35 | 12 | 22 | 25 | 9 | 16 | 17 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 96 | 40 | 18 | 38 | 0 | 0 | 0 | 150 | 315 | 220 | 8 | 85 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 25 | 9 | 69 | 110 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 137 | 40 | 76 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 88 | 0 | 0 | 127 | 0 | 13 | 1 | 50 | 7 | 95 | 0 | 45 | 105 | 1 | 0 | 300 | 0 | 1 | 0 | 8 | 0 | 300 | 70 | 1 | 90 | 116 | 0 | 17 | 1 | 0 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 120 | 0 | 300 | 10 | 0 | 26 | 0 | 100 | 0 | 0 | 10 | 350 | 62 | 0 | 0 | 0 | 0 | 0 |  | 4805 | 2167 | 6972 | 2251 | 731 | 1610 | 0 | 1712 | 550 | 46 | 0 | 0 | 69 | 3 | 0 | 93.56
8:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 270 |  | 0 | 200 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 64 | 100 | 26 | 0 | 0 | 47 | 35 | 35 | 48 | 22 | 25 | 9 | 16 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 96 | 40 | 18 | 10 | 0 | 0 | 0 | 150 | 275 | 220 | 8 | 85 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 25 | 9 | 78 | 111 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 70 | 76 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 105 | 0 | 0 | 190 | 0 | 48 | 5 | 88 | 34 | 133 | 0 | 77 | 105 | 21 | 1 | 300 | 0 | 19 | 51 | 8 | 20 | 310 | 93 | 8 | 90 | 116 | 0 | 17 | 7 | 0 | 6 |  | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 120 | 0 | 316 | 70 | 0 | 57 | 0 | 107 | 0 | 0 | 100 | 390 | 0 | 0 | 0 | 0 | 8 | 0 |  | 5353 | 2379 | 7732 | 2266 | 732 | 1488 | 0 | 2381 | 590 | 46 | 0 | 122 | 78 | 29 | 0 | 93.56
9:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 250 |  | 0 | 200 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 50 | 0 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 9 | 16 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 96 | 40 | 18 | 4 | 0 | 0 | 0 | 120 | 275 | 221 | 26 | 85 | 5 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 25 | 9 | 84 | 110 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 135 | 70 | 76 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 215 | 57 | 25 | 193 | 0 | 134 | 11 | 90 | 34 | 135 | 0 | 109 | 105 | 68 | 2 | 300 | 0 | 51 | 51 | 8 | 40 | 340 | 104 | 7 | 90 | 116 | 0 | 17 | 16 | 0 | 37 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 50 | 0 | 20 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 121 | 0 | 310 | 88 | 0 | 92 | 0 | 113 | 0 | 1 | 113 | 480 | 0 | 0 | 0 | 2 | 20 | 0 |  | 6059 | 2578 | 8637 | 2265 | 731 | 1513 | 82 | 2976 | 680 | 46 | 0 | 201 | 84 | 59 | 0 | 93.55
10:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 250 |  | 0 | 210 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 60 | 0 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 9 | 16 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 91 | 40 | 18 | 3 | 0 | 0 | 0 | 110 | 275 | 228 | 26 | 84 | 5 | 10 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 21 | 9 | 90 | 96 | 0 | 22 | 1 | 30 | 30 | 51 | 0 | 110 | 138 | 69 | 76 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 250 | 29 | 25 | 194 | 0 | 141 | 16 | 76 | 34 | 137 | 0 | 109 | 105 | 68 | 3 | 300 | 0 | 51 | 51 | 8 | 40 | 360 | 104 | 7 | 90 | 116 | 0 | 17 | 23 | 54 | 37 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 51 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 122 | 0 | 297 | 90 | 0 | 94 | 0 | 113 | 0 | 2 | 113 | 480 | 0 | 0 | 0 | 3 | 35 | 0 |  | 6115 | 2586 | 8701 | 2266 | 731 | 1476 | 54 | 3063 | 680 | 46 | 0 | 205 | 90 | 90 | 0 | 93.55
11:00 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 243 |  | 0 | 210 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 9 | 16 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 89 | 39 | 18 | 3 | 0 | 0 | 0 | 100 | 275 | 184 | 26 | 84 | 5 | 10 | 0 | 51 | 0 | 7 | 43 | 17 | 8 | 16 | 9 | 92 | 83 | 0 | 22 | 2 | 30 | 30 | 51 | 0 | 110 | 135 | 40 | 76 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 264 | 0 | 0 | 194 | 0 | 149 | 19 | 76 | 34 | 143 | 0 | 109 | 105 | 68 | 4 | 300 | 0 | 51 | 51 | 8 | 40 | 390 | 104 | 9 | 108 | 116 | 0 | 17 | 28 | 87 | 38 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 51 | 0 | 0 | 0 | 43 | 0 | 16 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 125 | 0 | 283 | 90 | 0 | 94 | 0 | 107 | 0 | 4 | 113 | 440 | 0 | 0 | 0 | 4 | 74 | 4 |  | 6094 | 2579 | 8673 | 2202 | 731 | 1459 | 0 | 3147 | 640 | 46 | 0 | 212 | 92 | 144 | 0 | 93.54
12:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 243 |  | 0 | 210 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 42 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 89 | 39 | 18 | 6 | 0 | 0 | 0 | 150 | 345 | 184 | 26 | 85 | 5 | 10 | 0 | 51 | 0 | 45 | 43 | 18 | 8 | 16 | 9 | 94 | 83 | 0 | 22 | 2 | 30 | 30 | 51 | 0 | 110 | 138 | 40 | 76 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 265 | 0 | 0 | 194 | 0 | 149 | 20 | 90 | 34 | 142 | 0 | 109 | 105 | 68 | 4 | 300 | 0 | 51 | 51 | 8 | 40 | 400 | 104 | 37 | 126 | 116 | 0 | 17 | 31 | 104 | 37 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 5 | 49 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 126 | 0 | 268 | 90 | 0 | 94 | 0 | 100 | 0 | 4 | 113 | 430 | 0 | 0 | 0 | 5 | 78 | 14 |  | 6362 | 2572 | 8934 | 2336 | 731 | 1465 | 0 | 3202 | 630 | 46 | 0 | 249 | 94 | 181 | 0 | 93.54
13:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 241 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 42 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 10 | 86 | 39 | 18 | 10 | 0 | 0 | 0 | 150 | 275 | 193 | 26 | 86 | 5 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 16 | 9 | 98 | 85 | 0 | 22 | 2 | 30 | 30 | 51 | 0 | 110 | 136 | 67 | 76 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 268 | 56 | 25 | 193 | 0 | 149 | 20 | 90 | 55 | 137 | 0 | 109 | 105 | 90 | 1 | 300 | 0 | 64 | 70 | 8 | 70 | 400 | 104 | 41 | 126 | 116 | 0 | 17 | 9 | 102 | 42 |  | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 49 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 126 | 0 | 258 | 90 | 0 | 94 | 0 | 107 | 0 | 4 | 113 | 460 | 0 | 0 | 0 | 5 | 78 | 20 |  | 6532 | 2611 | 9143 | 2303 | 730 | 1480 | 81 | 3327 | 659 | 46 | 0 | 259 | 98 | 160 | 0 | 93.53
14:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 243 |  | 0 | 220 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 64 | 10 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 0 | 20 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 94 | 39 | 18 | 7 | 0 | 0 | 0 | 150 | 295 | 193 | 26 | 88 | 5 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 8 | 16 | 9 | 100 | 85 | 0 | 22 | 2 | 30 | 30 | 51 | 0 | 110 | 137 | 40 | 76 | 0 | 177 | 0 | 0 | 10 | 275 | 16 | 8 | 0 | 270 | 0 | 0 | 193 | 0 | 149 | 17 | 90 | 100 | 135 | 0 | 109 | 105 | 105 | 4 | 300 | 0 | 68 | 34 | 8 | 20 | 340 | 104 | 34 | 126 | 116 | 0 | 17 | 25 | 94 | 55 |  | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 14 | 49 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 127 | 0 | 247 | 90 | 0 | 94 | 0 | 110 | 0 | 4 | 70 | 430 | 0 | 0 | 0 | 4 | 68 | 20 |  | 6108 | 2520 | 8628 | 2230 | 730 | 1440 | 0 | 3118 | 629 | 46 | 0 | 177 | 100 | 158 | 0 | 93.53
15:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 250 |  | 0 | 220 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 64 | 48 | 10 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 95 | 40 | 18 | 2 | 0 | 0 | 0 | 150 | 275 | 198 | 26 | 85 | 5 | 10 | 0 | 51 | 0 | 50 | 52 | 18 | 8 | 16 | 9 | 94 | 84 | 0 | 22 | 1 | 30 | 30 | 51 | 0 | 110 | 136 | 65 | 75 | 0 | 178 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 278 | 0 | 0 | 192 | 0 | 122 | 13 | 76 | 100 | 135 | 0 | 109 | 105 | 105 | 1 | 300 | 0 | 68 | 34 | 8 | 20 | 340 | 104 | 24 | 126 | 116 | 0 | 17 | 11 | 94 | 55 |  | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 49 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 127 | 0 | 253 | 90 | 0 | 94 | 0 | 113 | 0 | 3 | 70 | 450 | 0 | 0 | 0 | 3 | 46 | 41 |  | 6062 | 2556 | 8618 | 2245 | 730 | 1453 | 0 | 3129 | 649 | 46 | 0 | 170 | 94 | 102 | 0 | 93.52
16:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 250 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 48 | 48 | 10 | 0 | 0 | 44 | 35 | 55 | 35 | 22 | 25 | 9 | 20 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 6 | 89 | 39 | 18 | 2 | 0 | 0 | 0 | 150 | 275 | 203 | 26 | 124 | 5 | 10 | 0 | 51 | 0 | 50 | 43 | 0 | 8 | 25 | 9 | 95 | 83 | 0 | 22 | 1 | 30 | 30 | 51 | 0 | 110 | 135 | 67 | 75 | 0 | 178 | 0 | 0 | 10 | 280 | 16 | 0 | 0 | 250 | 0 | 0 | 192 | 0 | 100 | 8 | 30 | 68 | 135 | 0 | 75 | 90 | 68 | 2 | 300 | 0 | 51 | 17 | 8 | 20 | 340 | 104 | 13 | 126 | 108 | 0 | 17 | 8 | 108 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 14 | 40 | 49 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 127 | 0 | 233 | 90 | 0 | 70 | 0 | 70 | 0 | 2 | 50 | 430 | 0 | 0 | 0 | 1 | 28 | 49 |  | 5797 | 2455 | 8252 | 2272 | 731 | 1436 | 0 | 2775 | 629 | 46 | 0 | 205 | 95 | 63 | 0 | 93.52
17:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 250 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 48 | 82 | 17 | 0 | 0 | 43 | 35 | 35 | 35 | 22 | 25 | 9 | 20 | 33 | 30 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 89 | 40 | 18 | 9 | 0 | 0 | 0 | 150 | 275 | 200 | 26 | 123 | 5 | 10 | 0 | 51 | 0 | 50 | 46 | 19 | 5 | 25 | 9 | 95 | 96 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 137 | 67 | 75 | 0 | 178 | 0 | 0 | 10 | 290 | 16 | 0 | 0 | 273 | 0 | 0 | 170 | 0 | 82 | 2 | 46 | 51 | 135 | 0 | 65 | 70 | 68 | 0 | 300 | 3 | 51 | 17 | 56 | 30 | 340 | 72 | 3 | 126 | 107 | 0 | 17 | 3 | 123 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 34 | 51 | 49 | 0 | 0 | 3 | 52 | 12 | 20 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 127 | 0 | 230 | 53 | 0 | 35 | 0 | 50 | 0 | 1 | 35 | 430 | 0 | 0 | 0 | 0 | 10 | 41 |  | 5884 | 2366 | 8250 | 2299 | 731 | 1455 | 0 | 2691 | 629 | 46 | 0 | 285 | 95 | 19 | 0 | 93.51
18:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 254 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 85 | 133 | 48 | 0 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 33 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 20 | 89 | 40 | 18 | 6 | 0 | 0 | 0 | 150 | 280 | 204 | 26 | 123 | 5 | 10 | 0 | 51 | 0 | 50 | 52 | 20 | 8 | 25 | 9 | 108 | 100 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 68 | 75 | 0 | 178 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 270 | 38 | 25 | 175 | 25 | 98 | 0 | 50 | 55 | 140 | 0 | 82 | 105 | 76 | 0 | 300 | 17 | 51 | 52 | 99 | 50 | 400 | 79 | 0 | 144 | 116 | 0 | 17 | 0 | 50 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 34 | 49 | 98 | 0 | 0 | 30 | 52 | 31 | 20 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 10 | 126 | 0 | 233 | 68 | 0 | 48 | 0 | 106 | 0 | 0 | 90 | 450 | 0 | 0 | 0 | 0 | 0 | 41 |  | 6464 | 2626 | 9090 | 2379 | 731 | 1466 | 98 | 3133 | 649 | 46 | 0 | 480 | 108 | 0 | 0 | 93.51
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 252 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 59 | 0 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 9 | 25 | 13 | 51 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 20 | 89 | 40 | 18 | 13 | 0 | 0 | 0 | 150 | 275 | 202 | 26 | 122 | 5 | 10 | 0 | 51 | 0 | 50 | 52 | 20 | 8 | 25 | 9 | 108 | 101 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 69 | 78 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 275 | 221 | 100 | 193 | 100 | 149 | 0 | 70 | 100 | 140 | 0 | 109 | 105 | 105 | 0 | 300 | 17 | 51 | 52 | 108 | 50 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 43 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 34 | 48 | 100 | 0 | 0 | 32 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 85 | 126 | 0 | 226 | 90 | 100 | 91 | 0 | 113 | 0 | 0 | 113 | 560 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7049 | 2962 | 10011 | 2364 | 731 | 1489 | 606 | 3409 | 759 | 46 | 0 | 499 | 108 | 0 | 0 | 93.49
19:30 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 250 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 115 | 60 | 0 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 9 | 25 | 13 | 51 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 17 | 0 | 89 | 40 | 18 | 11 | 0 | 0 | 0 | 150 | 275 | 205 | 26 | 121 | 5 | 10 | 0 | 51 | 0 | 50 | 52 | 21 | 8 | 25 | 9 | 106 | 101 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 135 | 69 | 78 | 0 | 177 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 275 | 151 | 100 | 200 | 100 | 149 | 0 | 70 | 100 | 142 | 0 | 109 | 105 | 105 | 0 | 300 | 17 | 51 | 52 | 118 | 50 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 34 | 47 | 100 | 0 | 0 | 32 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 97 | 126 | 0 | 220 | 90 | 100 | 94 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6888 | 2993 | 9881 | 2367 | 731 | 1449 | 548 | 3424 | 780 | 46 | 0 | 430 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 250 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 115 | 59 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 25 | 13 | 51 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 89 | 40 | 18 | 15 | 0 | 0 | 0 | 150 | 270 | 205 | 26 | 124 | 5 | 10 | 0 | 51 | 0 | 50 | 52 | 21 | 8 | 25 | 9 | 104 | 100 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 68 | 78 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 293 | 71 | 100 | 200 | 100 | 149 | 0 | 70 | 100 | 140 | 0 | 109 | 105 | 105 | 0 | 300 | 17 | 51 | 34 | 115 | 50 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 34 | 48 | 100 | 0 | 0 | 32 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 60 | 126 | 0 | 244 | 90 | 45 | 94 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6775 | 2939 | 9714 | 2364 | 731 | 1468 | 376 | 3419 | 780 | 46 | 0 | 426 | 104 | 0 | 0 | 93.5
21:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 249 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 115 | 59 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 25 | 13 | 51 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 89 | 40 | 18 | 22 | 0 | 0 | 0 | 150 | 275 | 197 | 26 | 124 | 5 | 10 | 0 | 51 | 0 | 50 | 52 | 21 | 8 | 25 | 9 | 98 | 100 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 137 | 68 | 78 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 288 | 53 | 100 | 200 | 60 | 149 | 0 | 50 | 100 | 142 | 0 | 109 | 105 | 85 | 0 | 283 | 17 | 51 | 17 | 119 | 20 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 34 | 41 | 100 | 0 | 0 | 32 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 10 | 126 | 0 | 252 | 90 | 5 | 94 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6642 | 2867 | 9509 | 2362 | 731 | 1512 | 228 | 3316 | 780 | 46 | 0 | 436 | 98 | 0 | 0 | 93.49
22:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 244 |  | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 64 | 50 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 25 | 13 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 89 | 40 | 18 | 40 | 0 | 0 | 0 | 150 | 270 | 201 | 26 | 124 | 5 | 10 | 0 | 51 | 0 | 18 | 52 | 21 | 8 | 25 | 9 | 92 | 94 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 69 | 78 | 0 | 178 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 298 | 0 | 0 | 200 | 0 | 149 | 0 | 10 | 68 | 133 | 0 | 109 | 105 | 51 | 0 | 283 | 17 | 17 | 0 | 117 | 0 | 390 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 34 | 25 | 100 | 0 | 0 | 32 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 126 | 0 | 260 | 90 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 580 | 8 | 0 | 0 | 0 | 0 | 0 |  | 6103 | 2829 | 8932 | 2346 | 731 | 1511 | 0 | 3112 | 780 | 46 | 0 | 314 | 92 | 0 | 0 | 93.49
23:00 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 242 |  | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 9 | 25 | 13 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 40 | 18 | 35 | 0 | 0 | 0 | 150 | 275 | 211 | 8 | 125 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 9 | 88 | 89 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 69 | 78 | 0 | 178 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 193 | 0 | 112 | 0 | 10 | 68 | 133 | 0 | 32 | 105 | 51 | 0 | 283 | 0 | 17 | 0 | 50 | 0 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 126 | 0 | 254 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 50 | 530 | 33 | 0 | 0 | 0 | 0 | 0 |  | 5605 | 2605 | 8210 | 2367 | 735 | 1506 | 0 | 2638 | 730 | 46 | 0 | 100 | 88 | 0 | 0 | 93.48
24:00 | 0 | 0 | 220 | 0 | 0 | 6 | 0 | 0 | 239 |  | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 55 | 35 | 22 | 25 | 9 | 22 | 13 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 40 | 18 | 35 | 0 | 0 | 0 | 150 | 275 | 227 | 8 | 124 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 9 | 82 | 89 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 134 | 69 | 78 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 95 | 0 | 0 | 200 | 0 | 0 | 0 | 10 | 34 | 135 | 0 | 8 | 105 | 17 | 0 | 283 | 0 | 17 | 0 | 27 | 0 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 55 |  | 736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 125 | 0 | 263 | 70 | 0 | 50 | 0 | 113 | 0 | 0 | 35 | 450 | 50 | 0 | 0 | 0 | 0 | 0 |  | 5146 | 2371 | 7517 | 2375 | 736 | 1546 | 0 | 2082 | 650 | 46 | 0 | 0 | 82 | 0 | 0 | 93.48
KWH | 0 | 0 | 5284000 | 0 | 0 | 71090 | 0 | 0 | 6014000 |  | 0 | 4900500 | 0 | 0 | 0 | 576060 | 0 | 0 | 0 | 0 | 1382400 | 1615680 | 683692 | 0 | 0 | 1126800 | 823320 | 937741 | 887358 | 495432 | 600000 | 203220 | 504500 | 587100 | 585600 | 0 | 1104660 | 0 | 0 | 0 | 91879 | 0 | 0 | 0 | 0 |  | 496080 | 0 | 105442 | 76680 | 2217600 | 955680 | 418752 | 476160 | 0 | 0 | 0 | 3694000 | 7139000 | 4989000 | 468363 | 2368100 | 167184 | 215520 | 0 | 1209600 | 0 | 529784 | 1113125 | 447444 | 181440 | 560100 | 241270 | 2451840 | 2254 | 0 | 512712 | 11450 | 716000 | 694320 | 1263000 | 0 | 2905527 | 3203000 | 1433472 | 1825920 | 0 | 4340300 | 0 | 0 | 250020 | 7170500 | 3874810 | 204192 | 0 | 4704544 | 530602 | 402129 | 3900000 | 278701 | 2113200 | 132705 | 1273920 | 1168800 | 2766690 | 0 | 1626000 | 2400000 | 1401745 | 25680 | 6852327 | 95545 | 868141 | 623580 | 845880 | 519360 | 8640100 | 2279040 | 183770 | 3130560 | 2788855 | 0 | 444960 | 178082 | 831360 | 1121040 |  | 17478545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72000 | 0 | 0 | 2216358 | 415100 | 0 | 0 | 0 | 0 | 218200 | 346868 | 1018536 | 0 | 0 | 133863 | 1184160 | 141056 | 467040 | 0 | 168948 | 0 | 0 | 4876300 | 0 | 0 | 0 | 0 | 0 | 0 | 1576629 | 221200 | 3213445 | 0 | 6697600 | 1519680 | 161711 | 1505472 | 0 | 1871443 | 0 | 25199 | 1629312 | 11476000 | 949691 | 0 | 0 | 31500 | 452880 | 225408 |  | 139531989 | 60294144 | 199826133 | 57100453 | 17478545 | 36876260 | 1594343 | 61645037 | 16352300 | 1104660 | 0 | 4181429 | 2451840 | 1041266 | 0
Fuel Cost | 0 | 0 | 7714640 | 0 | 0 | 93838.8 | 0 | 0 | 6194420 |  | 0 | 5341545 | 0 | 0 | 0 | 4873467.6 | 0 | 0 | 0 | 0 | 12607488 | 15898291.2 | 6303640.24 | 0 | 0 | 10242612 | 6010236 | 7248737.93 | 8749349.88 | 371574 | 450000 | 0 | 0 | 0 | 5662752 | 0 | 298258.2 | 0 | 0 | 0 | 853555.91 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1022787.4 | 732294 | 19293120 | 7568985.6 | 527627.52 | 1414195.2 | 0 | 0 | 0 | 2733560 | 7139000 | 4589880 | 604188.27 | 2723315 | 188917.92 | 301728 | 0 | 2068416 | 0 | 5350818.4 | 10630343.75 | 568253.88 | 136080 | 980175 | 180952.5 | 18388800 | 2389.24 | 0 | 651144.24 | 182513 | 1174240 | 1110912 | 2248140 | 0 | 3312300.78 | 3331120 | 2823939.84 | 3487507.2 | 0 | 7508719 | 0 | 0 | 510040.8 | 7242205 | 2906107.5 | 155185.92 | 0 | 35566352.64 | 9009621.96 | 6723596.88 | 20280000 | 4659880.72 | 20793888 | 1551321.45 | 10382448 | 12681480 | 19505164.5 | 0 | 14829120 | 22680000 | 12209198.95 | 0 | 51803592.12 | 832196.95 | 7630959.39 | 6223328.4 | 7249191.6 | 3458937.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100676419.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755280 | 0 | 0 | 2504484.54 | 643405 | 0 | 0 | 0 | 0 | 2147088 | 3524178.88 | 9014043.6 | 0 | 0 | 1297132.47 | 11474510.4 | 1368243.2 | 896716.8 | 0 | 127893.636 | 0 | 0 | 26429546 | 0 | 0 | 0 | 0 | 0 | 0 | 2364943.5 | 3762612 | 3759730.65 | 0 | 6630624 | 15865459.2 | 2750704.11 | 14286929.28 | 0 | 14522397.68 | 0 | 278448.95 | 12040615.68 | 50379640 | 0 | 0 | 0 | 0 | 0 | 0 |  | 490774588.88 | 287501046.776 | 778275635.656 | 54359842.386 | 100676419.2 | 43354214.35 | 26906415.67 | 415092353.3 | 76809186 | 298258.2 | 0 | 40377863.15 | 18388800 | 2012283.4 | 0
Yesterday Day Peak | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 243 |  | 0 | 210 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 42 | 35 | 55 | 55 | 22 | 25 | 9 | 20 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 89 | 39 | 18 | 6 | 0 | 0 | 0 | 150 | 345 | 184 | 26 | 85 | 5 | 10 | 0 | 51 | 0 | 45 | 43 | 18 | 8 | 16 | 9 | 94 | 83 | 0 | 22 | 2 | 30 | 30 | 51 | 0 | 110 | 138 | 40 | 76 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 265 | 0 | 0 | 194 | 0 | 149 | 20 | 90 | 34 | 142 | 0 | 109 | 105 | 68 | 4 | 300 | 0 | 51 | 51 | 8 | 40 | 400 | 104 | 37 | 126 | 116 | 0 | 17 | 31 | 104 | 37 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 5 | 49 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 126 | 0 | 268 | 90 | 0 | 94 | 0 | 100 | 0 | 4 | 113 | 430 | 0 | 0 | 0 | 5 | 78 | 14 |  | 8934 | DayPeak
Yesterday Evening Peak | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 59 | 0 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 9 | 25 | 13 | 51 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 20 | 89 | 40 | 18 | 13 | 0 | 0 | 0 | 150 | 275 | 202 | 26 | 122 | 5 | 10 | 0 | 51 | 0 | 50 | 52 | 20 | 8 | 25 | 9 | 108 | 101 | 0 | 22 | 0 | 30 | 30 | 53 | 0 | 110 | 136 | 69 | 78 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 275 | 221 | 100 | 193 | 100 | 149 | 0 | 70 | 100 | 140 | 0 | 109 | 105 | 105 | 0 | 300 | 17 | 51 | 52 | 108 | 50 | 400 | 104 | 0 | 162 | 116 | 0 | 17 | 0 | 0 | 43 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 34 | 48 | 100 | 0 | 0 | 32 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 85 | 126 | 0 | 226 | 90 | 100 | 91 | 0 | 113 | 0 | 0 | 113 | 560 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10011 | EvPeak
Forecast for Evening | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 220 |  | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 51 | 54 | 55 | 55 | 22 | 25 | 10 | 20 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 97 | 40 | 20 | 20 | 0 | 0 | 0 | 260 | 360 | 220 | 8 | 135 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 25 | 9 | 134 | 110 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 135 | 70 | 80 | 0 | 180 | 18 | 0 | 10 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 110 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 160 | 116 | 0 | 17 |  |  | 55 |  | 751 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 35 | 40 | 0 | 92 | 24 | 110 | 0 | 0 | 0 | 34 | 50 | 100 | 0 | 50 | 40 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 200 | 15 | 0 | 0 | 0 | 0 | 0 | 76 | 100 | 130 | 0 | 325 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 0 |  | 150
Forecast for Day | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 220 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 102 | 150 | 60 | 0 | 0 | 51 | 54 | 55 | 55 | 22 | 25 | 10 | 20 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 97 | 40 | 19 | 10 | 0 | 0 | 0 | 235 | 360 | 220 | 8 | 135 | 5 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 25 | 9 | 138 | 110 | 0 | 22 | 1.6 | 30 | 30 | 51 | 0 | 110 | 135 | 70 | 75 | 0 | 180 | 18 | 0 | 10 | 330 | 16 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 0 | 110 | 105 | 105 | 5 | 260 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 160 | 116 | 0 | 17 | 30 |  | 55 |  | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 110 | 0 | 0 | 0 | 34 | 50 | 90 | 0 | 50 | 0 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 80 | 130 | 0 | 325 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 0 |  | 0 | 6 | 50
Generation at 08:00(Today) | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 220 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 0 | 5 | 0 | 0 | 48 | 35 | 55 | 35 | 22 | 25 | 9 | 20 | 15 | 11 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 74 | 40 | 18 | 5 | 0 | 0 | 0 | 235 | 315 | 195 | 8 | 133 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 7 | 20 | 9 | 90 | 109 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 135 | 68 | 76 | 0 | 177 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 185 | 0 | 0 | 170 | 0 | 40 | 4 | 30 | 58 | 142 | 0 | 64 | 105 | 34 | 1 | 245 | 0 | 17 | 34 | 8 | 0 | 400 | 104 | 5 | 90 | 116 | 0 | 17 | 6 | 0 | 55 | 0 | 737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 121 | 0 | 325 | 80 | 0 | 70 | 0 | 113 | 0 | 1 | 100 | 370 | 0 | 0 | 0 | 0 | 10 | 0 | 0
199
| Minimum Generation |  | 6103 | 5:00
| Highest Generation |  | 10011 | 19:00
| Day Peak Generation |  | 8934 | 12:00
| Evening Peak Generation |  | 10011 | 19:00
| HVDC Max Flow |  | 736 | 24:00
| HVDC EvPeak Flow |  | 731 | 19:00
| Load factor L.F |  | 83.17%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-02-03
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-02-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8934 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6186 | MW
Evening Peak Generation : |  | 10011 | MW Hour : | 19:00 | Available Max Generation : |  | 12204 | MW
E.P. Demand (at gen end) : |  | 10011 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10200 | MW
Maximum Generation : |  | 10011 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2004 | MW
Total Gen. (MKWH) : |  | 199.8261 | System Load Factor : | 83.17% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -337 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-02-03
Actual : | 93.45 | Ft.(MSL) , | Rule curve : | 96.72 | Ft.( MSL )
Gas Consumed : | Total = | 738.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 97714056.736
: |  | Coal : | 76809186 | Oil : | 482376632.12 | Total : | 656899874.856
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3729.5358 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1266.6651 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1134.6078 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1025.1137 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 926.4357 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 747.5968 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 420.057 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 192.54 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 576.574 |  |  | 0 | 0%
Total | 0 |  | 10019.1259 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
|  |  |  | 2) Ghorasal-3,5,7 |  | 11) Bhola 225 MW GT-1
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 MW GT-2
6) Raozan unit- 1,2
7) Sirajganj Unit 1 & 2
8) Summit Bibiyana-3
9) Haripur 412 MW EGCB
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bibiyana-Shahjibazar 230 kV Ckt-1 was under shut down from 09:09 to 17:31 for A/M.
b) Madartek 132/33 kV T-1 transformer was under shut down from 08:55 to 15:30 for A/M.
c) Aminbazar-Manikganj PP 132 kV Ckt-2 was under shut down from 09:22 to 17:03 for A/M.
d) Hathazari-Baroaulia 132 kV Ckt-1 was under shut down from 08:20 to 19:42 for A/M.
e) Khulshi-Madunaghat 132 kV Ckt-1 was under shut down from 08:57 to 16:06 for A/M.
f) Tongi-Kabirpur 132 kV Ckt-2 was under shut down from 09:39 to 17:53 for A/M.
g) Rangamati-Khagrachari 132 kV Ckt-2 was under shut down from 09:07 to 16:32 for A/M.
h) Sreemangal 132/33 kV T2 & T3 transformer were under shut down from 09:45 to 17:44 for A/M.
i) Kamrangirchar 132/33 kV T-3 transformer was under shut down from 09:50 to 14:11 for A/M.
j) Savar 132/33 kV T-2 transformer was under shut down from 10:04 to 12:25 for A/M.
k) Madaripur-Barishal(N) 132 kV Ckt-2 was under shut down from 08:29 to 17:03 for A/M.
l) Gopalganj-Madhumati PP 132 kV Ckt was under shut down from 09:26 to 16:24 for A/M.
m) Gopalganj(old) 132/33 kV T-2 transformer was under shut down from 10:19 to 11:00 for C/M.
n) Cumilla(S)-Tripura 132 kV Ckt-2 was under shut down from 09:57 to 17:53 for D/W.
o) Meghnaghat-Haripur 230 kV Ckt-2 was under shut down from 10:53 to 16:23 for D/W.
p) Dhamrai 132/33 kV T-1 transformer tripped at 12:15 showing PRD relay and was switched on at 14:42.
q) Savar 132/33 kV T-3 transformer was under shut down from 12:28 to 14:39 for A/M.
r) Rampur-Agrabad 132 kV Ckt-2 was under shut down from 12:59 to 13:57 for A/M.
s) Bhulta 400/132 kV T-2 transformer was under shut down from 07:32 to 18:11 for A/M.
t) Bhola Nutun Biddut GT-1 & ST were synchronized at 21:03,00:32 respectively and shut down at 03:39
due to DP high.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-02-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 5284000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 71090 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 252 | 6014000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 220 | 4900500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 576060 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 59 | 683692 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 495432
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1382400
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 1126800
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 823320 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1615680
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 937741
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 887358
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 803220 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 504500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 13 | 587100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 585600
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Machine problem
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 4704544
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 221 | 530602 | Low Demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 402129
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 278701
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2113200
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2400000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2279040
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3130560
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178082
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 43 | 1121040
| Dhaka area Total |  |  |  | 5696 | 2639 | 44416391
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 91879 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 132705
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 955680 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1104660 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1401745
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 105442 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 76680 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 1273920 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 418752 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 476160
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 89 | 2217600 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25680
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 6852327
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 95545 | High Voltage
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 51 | 868141 | High Voltage
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 519360 | High Voltage
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2788855
| Chattogram area Total |  |  |  | 2382 | 1003 | 19405131
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 202 | 4989000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 150 | 3694000 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7139000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 167184 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 215520 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 468363 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1209600
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 2766690
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 529784
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 122 | 2368100 | ST Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 1168800 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 447444
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 181440 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2451840
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 560100 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1113125
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 9 | 241270 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | High Voltage
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 623580 | High Voltage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 108 | 845880
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444960 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 831360 | On test
| Cumilla Area Total |  |  |  | 2899 | 1530 | 32457040
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 101 | 2254 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 512712
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11450
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 193 | 3900000
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 109 | 1626000
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 183770
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 496080
| Mymensingh Area Total |  |  |  | 622 | 447 | 6732266
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 694320 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2905527 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 136 | 3203000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1263000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 204192
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1433472
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1825920
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine problem
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 177 | 4340300 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 3874810 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7170500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250020
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8640100
| Sylhet Area Total |  |  |  | 2377 | 1430 | 36521161
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 731 | 17478545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 72000 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 85 | 221200 | Low Demand
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1519680 | Engine problem
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 452880 | On test
| Khulna Area Total |  |  |  | 2229 | 910 | 19744305
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 415100 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 2216358 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 87 | 1576629 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 560 | 11476000 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 949691 | Gas shortage
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 758 | 16633778
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 218200 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 48 | 346868 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 133863 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 126 | 3213445 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 226 | 6697600 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 141056 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 467040
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 168948 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1184160
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1018536 | Machine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 100 | 161711 | Low Demand
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 91 | 1505472 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1629312
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31500
| Rajshahi Area Total |  |  |  | 2179 | 982 | 16917711
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4876300 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1871443
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25199
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 225408 | On test
| Rangpur Area Total |  |  |  | 605 | 312 | 6998350
| Total |  |  |  | 21035 | 10011 | 199826133
| Eastern Grid Total |  |  |  | 13976 | 7049 | 139531989
| Western Grid Total |  |  |  | 7059 | 2962 | 60294144
| National Grid Total |  |  |  | 21035 | 10011 | 199826133
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-02-02
(a) ENTIRE EASTERN GRID : |  | 6693 | MW | (b) ENTIRE WESTERN GRID : |  | 3137 | MW
i) Dhaka area |  | 3590 | MW | i) Khulna area |  | 1139 | MW
ii) Chittagong area |  | 1098 | MW | ii) Rajshahi area |  | 1027 | MW
iii) Comilla area |  | 785 | MW | iii) Barisal area |  | 237 | MW
iv) Mymensingh area |  | 884 | MW | iv) Rangpur area |  | 734 | MW
v) Sylhet area |  | 336 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9830 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 94 | 18:00 | Tangail | 163 | 18:30 | Noapara | 41 | 12:00
Munsiganj | 63 | 21:00 | Mymensing | 168 | 19:00 | Jessore | 82 | 13:00
Sonargaon | 71 | 13:00 | Kishoreganj | 102 | 19:30 | Benapol | 44 | 8:00
Shyampur | 168 | 11:00 | Netrokona | 115 | 9:00 | Jhenida(Old) | 86 | 18:30
Bhulta | 185 | 11:00 | Jamalpur | 124 | 18:30 | Bottail | 94 | 18:30
Madanganj | 20 | 18:30 | Sherpur | 130 | 8:00 | G.K Project | 40 | 18:30
Shitalakhya | 86 | 12:00 | Srimongal | 32 | 18:30 | Faridpur | 96 | 18:30
Rahim steel | 10 | 16:00 | Shahjibazar | 78 | 20:00 | Rajbari | 46 | 18:30
Matuail | 51 | 9:00 | Fenchuganj | 26 | 18:00 | Madaripur | 67 | 20:00
Ghorasal | 64 | 19:30 | Kulawara | 26 | 18:30 | Sariatpur | 42 | 19:30
Narsingdi | 133 | 20:00 | Sylhet | 93 | 18:00 | Gopalganj | 70 | 19:00
Haripur (SBU) | 116 | 13:00 | Chatak | 19 | 18:00 | Bagerhat | 71 | 19:00
Sreenagar | 28 | 21:00 | Sunamganj | 33 | 20:00 | Mongla | 42 | 18:00
Ullon | 24 | 6:00 | Biani Bazar | 40 | 19:30 | Satkhira | 79 | 19:00
Hasnabad | 51 | 12:00 | Comilla (S) | 110 | 18:30 | Gallamari | 40 | 13:00
Magbazar | 79 | 19:30 | Comilla(N) | 97 | 19:30 | Magura | 42 | 19:00
Maniknagar | 44 | 13:00 | Chandpur | 46 | 19:30 | Norail | 36 | 18:30
Bangabhaban | 6 | 13:00 | Feni | 81 | 18:00 | Chuadanga | 66 | 18:30
Motijheel | 20 | 13:00 | Chowmuhani | 134 | 1:00 | Barisal(N) | 27 | 20:00
Narinda | 34 | 18:00 | Ashuganj | 22 | 13:00 | Barisal (S) | 78 | 13:00
Kazla | 65 | 11:00 | Daudkandi | 94 | 21:00 | Patuakhali | 74 | 21:00
Dhanmondi | 124 | 13:00 | B.Baria | 100 | 18:30 | Bhandaria | 38 | 19:30
Lalbag | 73 | 13:00 | Ramganj | 54 | 20:00 | Borguna | 12 | 19:00
Madartek | 46 | 21:00 | Chaddagram | 33 | 18:00 | Borhan Uddin | 29 | 21:00
Dhaka University | 22 | 13:00 | PHP | 8 | 2:00 | Ishurdi | 46 | 18:30
Aftabnagar | 18 | 21:00 | Kochua | 36 | 18:30 | Ruppur Paromanobik | 3 | 8:00
Fatullah | 47 | 18:30 | Madunaghat | 40 | 18:30 | Natore | 95 | 18:30
Nawabganj | 32 | 21:00 | Hathazari | 63 | 18:00 | Bogra | 117 | 18:30
Keraniganj | 56 | 18:30 | Khulshi | 146 | 12:00 | Noagaon | 94 | 12:00
Banani | 38 | 18:00 | Halishahar | 61 | 18:30 | Rajshahi | 86 | 18:30
Mirpur | 81 | 18:30 | Baraulia | 137 | 15:00 | Rajshahi New | 30 | 18:30
Kalyanpur | 60 | 13:00 | Sikalbaha | 21 | 19:00 | C.Nawabganj | 55 | 13:00
Gulshan | 66 | 15:00 | Dohazari | 58 | 18:30 | Amnura | 46 | 19:00
Uttara | 38 | 18:30 | Cox'sbazar | 96 | 18:00 | Pabna | 69 | 19:30
Uttara New | 21 | 18:00 | Chandraghona | 20 | 18:00 | Shahjadpur | 74 | 18:00
Kamrangirchar | 56 | 13:00 | Kaptai | 3.5 | 18:30 | Serajganj | 85 | 19:30
Savar | 130 | 17:00 | A. Khaer Stl. | 7 | 19:00 | Niyamatpur | 87 | 9:00
Bhasantec | 83 | 18:30 | Bakulia | 88 | 18:30 | Joypurhat | 52 | 10:00
Agargaon | 51 | 13:00 | Julda | 20 | 7:00 | Sherpur(Bogura) | 50 | 8:00
Satmosjid | 69 | 13:00 | TK chemical | 21.5 | 18:30 | Mohastangor | 44 | 18:30
Old Tongi | 103 | 11:00 | Modern Steel | 0 | 1:00 | Bhangura | 22 | 19:00
Kabirpur | 189 | 12:00 | Shahmirpur | 39.5 | 18:00 | Rangpur | 114 | 19:00
Manikgong | 57 | 19:00 | Khagrachhari | 22 | 19:00 | Lalmonirhat | 38 | 18:30
Joydevpur | 138 | 19:00 | Matarbari | 26 | 18:30 | Saidpur | 95 | 9:00
New Tongi | 63 | 12:00 | Baroiar Hat | 36 | 19:00 | Purbasadipur | 99 | 18:30
Kodda | 205 | 18:30 | Rangamati | 10 | 18:30 | Thakurgaon | 70 | 19:0
Dhamrai | 94 | 19:00 | Abul Khair 230 | 148 | 5:00 | Palashbari | 98 | 18:30
Rajendrapur | 94 | 19:00 | BSRM | 155 | 23:00 | Barapukuria | 53 | 10:00
Bashundara | 89 | 13:00 | GPH Ispat | 102 | 17:00 | Panchagar | 49 | 18:30
Purbachal | 12 | 21:00 | Agrabad | 56 | 19:00 | Joldhaka | 55 | 18:30
Tongi Millgate | 36 | 12:00 | Goalpara | 20 | 13:00 | Kurigram | 56 | 18:30
Valuka | 102 | 19:00 | Central S/S | 66 | 18:30 | Mithapukur | 32 | 18:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-02-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 419 | 22:00 | 411 | 12:00 | Kaliakoir | 413 | 0.20833 | 401 | 0.5
| Bheramara | 404 | 18:30 | 395 | 14:00 | Bhulta | 418 | 0.91667 | 404 | 0.5
| Ashuganj(N) | 418 | 20:00 | 407 | 12:00 | Gopalganj | 415 | 0.625 | 401 | 0.77083
| Payra | 417 | 20:00 | 407 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 248 | 1:00 | 246 | 7:00 | Hathazari | 243 | 6:00 | 237 | 14:00
| Ishurdi | 245 | 5:00 | 229 | 12:00 | Megnaghat | 246 | 5:00 | 243 | 15:00
| Ashuganj | 250 | 1:00 | 246 | 12:00 | Fenchuganj | 245 | 1:00 | 241 | 16:00
| Serajganj | 244 | 4:00 | 235 | 11:00 | Siddhirganj | 242 | 20:00 | 233 | 16:00
| Baghabari | 243 | 1:00 | 230 | 11:00 | Maniknagar | 241 | 20:00 | 234 | 12:00
| Barapukuria | 237 | 1:00 | 226 | 9:00 | Agargaon | 244 | 6:00 | 235 | 12:00
| Bogra | 238 | 22:00 | 226 | 12:00 | Barisal | 248 | 22:00 | 240 | 19:30
| Rajshahi | 243 | 3:00 | 228 | 12:00 | Bhola 225 MW | 251 | 15:00 | 245 | 18:30
| Khulna South | 247 | 5:00 | 227 | 12:00 | AKSML | 245 | 22:00 | 232 | 12:00
| Rampura | 240 | 1:00 | 231 | 11:00 | BSRM | 245 | 20:00 | 237 | 1:00
| Haripur | 241 | 22:00 | 234 | 11:00 | Bibiyana | 246 | 2:00 | 239 | 7:00
| Hasnabad | 243 | 22:00 | 236 | 15:00 | Bhulta | 244 | 22:00 | 233 | 12:00
| Shyampur | 244 | 20:00 | 234 | 17:00 | Ashuganj (S) | 248 | 21:00 | 242 | 12:00
| Aminbazar | 245 | 1:00 | 237 | 2:00 | Kaliakoir | 242 | 1:00 | 234 | 12:00
| Tongi | 240 | 1:00 | 235 | 11:00 | GPH | 245 | 20:00 | 234 | 1:00
| Comilla (N) | 244 | 20:00 | 236 | 12:00 | Jhenaidah | 243 | 3:00 | 223 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 19:30 | 133 | 12:00 | Kachua | 142 | 0.625 | 139 | 0.5
| Munsiganj | 142 | 22:00 | 136 | 17:00 | Madanhat | 144 | 0.83333 | 138 | 0.375
| Sonargaon | 139 | 20:00 | 134 | 12:00 | Hathazari | 143 | 0.16667 | 138 | 0.5
| Shyampur | 136 | 21:00 | 130 | 12:00 | Khulshi | 140 | 0.79167 | 134 | 0.5
| Bhulta | 133 | 5:00 | 127 | 16:00 | Halishahar | 141 | 0.041667 | 136 | 0.41667
| Madanganj | 141 | 22:00 | 135 | 12:00 | Baraulia | 142 | 0.041667 | 135 | 0.5
| Shitalakhya | 141 | 20:00 | 136 | 12:00 | Sikalbaha | 144 | 0.83333 | 137 | 0.625
| Rahim steal | 138 | 10:00 | 133 | 13:00 | Dohazari | 139 | 0.625 | 133 | 0.5
| Matuail | 138 | 19:30 | 133 | 12:00 | Cox'sbazar | 128 | 0.375 | 116 | 0.75
| Ghorasal | 144 | 1:00 | 143 | 7:00 | Chandraghona | 143 | 0.91667 | 139 | 0.25
| Narsinghdi | 136 | 7:00 | 132 | 11:00 | Kaptai | 142 | 0.54167 | 140 | 0.041667
| Haripur (SBU) | 138 | 19:30 | 132 | 13:00 | A. Khaer Stl. | 142 | 0.8125 | 136 | 0.5
| Sreenagar | 139 | 19:00 | 133 | 17:00 | Bakulia | 141 | 0.29167 | 136 | 0.5
| Ullon | 134 | 5:00 | 128 | 12:00 | Julda | 141 | 0.70833 | 136 | 0.5
| Hasnabad | 141 | 19:30 | 136 | 12:00 | TK Chemical | 143 | 0.29167 | 138 | 0.5
| Magbazar | 135 | 0:00 | 130 | 11:00 | Modern Steel | 142 | 0.29167 | 138 | 0.58333
| Maniknagar | 137 | 2:00 | 131 | 16:00 | Shahmirpur | 142 | 0.83333 | 136 | 0.5
| Bangabhaban | 137 | 2:00 | 131 | 12:00 | Khagrachhari | 141 | 0.79167 | 136 | 0.5
| Motijheel | 137 | 2:00 | 131 | 12:00 | Matarbari | 132 | 0.45833 | 126 | 0.75
| Narinda | 137 | 2:00 | 131 | 16:00 | Baroiar Hat | 142 | 1:00 | 135 | 12:00
| Kazla | 137 | 5:00 | 131 | 12:00 | Rangamati | 143 | 20:00 | 136 | 12:00
| Dhanmondi | 138 | 0:00 | 133 | 12:00 | Agrabad | 142 | 18:00 | 136 | 0.5
| Lalbag | 139 | 20:00 | 132 | 12:00 | Goalpara S/S | 141 | 2:00 | 128 | 0.33333
| Madartek | 133 | 0:00 | 128 | 12:00 | Khulna Central S/S | 140 | 1:00 | 128 | 0.5
| Dhaka University | 138 | 21:00 | 132 | 12:00 | Noapara | 140 | 1:00 | 129 | 0.33333
| Aftabnagar | 134 | 0:00 | 128 | 12:00 | Jessore | 138 | 0.041667 | 127 | 0.5
| Fatullah | 137 | 20:00 | 130 | 12:00 | Benapol | 139 | 2:00 | 125 | 0.5
| Nawabganj | 139 | 21:00 | 133 | 12:00 | Jhenida(Old) | 138 | 0.041667 | 128 | 0.5
| Keraniganj | 139 | 19:00 | 133 | 16:00 | Bottail | 140 | 0.20833 | 128 | 0.5
| Banani | 133 | 0:00 | 129 | 12:00 | G.K Project | 142 | 0.20833 | 130 | 0.5
| Mirpur | 136 | 2:00 | 131 | 12:00 | Faridpur | 139 | 0.125 | 131 | 0.77083
| Kalyanpur | 137 | 1:00 | 132 | 12:00 | Rajbari | 140 | 0.20833 | 130 | 0.33333
| Gulshan | 133 | 1:00 | 128 | 12:00 | Madaripur | 143 | 4:00 | 137 | 0.77083
| Uttara | 138 | 0:00 | 133 | 12:00 | Shariyatpur S/S | 144 | 0.125 | 137 | 0.77083
| Uttara New | 139 | 0:00 | 133 | 12:00 | Gopalganj | 142 | 1:00 | 136 | 0.77083
| Kamrangirchar | 138 | 19:00 | 132 | 16:00 | Bagerhat | 140 | 2:00 | 130 | 0.5
| Savar | 137 | 20:00 | 133 | 17:00 | Mongla | 138 | 3:00 | 128 | 12:00
| Bhasantec | 135 | 20:00 | 130 | 17:00 | Satkhira | 139 | 0.16667 | 128 | 9:00
| Agargaon | 135 | 8:00 | 131 | 12:00 | Gallamari | 140 | 1:00 | 134 | 0.77083
| Satmosjid | 135 | 20:00 | 130 | 17:00 | Magura | 140 | 0.041667 | 128 | 0.5
| Old Tongi | 140 | 1:00 | 136 | 11:00 | Narail | 140 | 4:00 | 127 | 0.5
| Kabirpur | 137 | 1:00 | 130 | 12:00 | Chuadanga | 138 | 3:00 | 123 | 0.5
| Manikgong | 134 | 1:00 | 129 | 18:00 | Barisal(N) | 146 | 6:00 | 139 | 18:30
| Joydevpur | 143 | 1:00 | 139 | 12:00 | Barisal (S) | 144 | 0.16667 | 139 | 0.77083
| New Tongi | 140 | 4:00 | 133 | 16:00 | Patuakhali(S) | 137 | 0.083333 | 133 | 0.45833
| Kodda | 140 | 18:00 | 135 | 4:00 | Bhandaria | 145 | 0.25 | 138 | 0.8125
| Dhamrai | 136 | 1:00 | 131 | 12:00 | Borguna | 145 | 16:00 | 139 | 18:30
| Rajendrapur | 139 | 20:00 | 132 | 17:00 | Jhenaidah(New) | 140 | 2:00 | 128 | 12:00
| Bashundara | 139 | 21:00 | 134 | 12:00 | Ishurdi | 141 | 2:00 | 132 | 12:00
| Purbachal | 134 | 3:00 | 130 | 0:00 | Ruppur Paromanobik | 141 | 2:00 | 132 | 8:00
| Tongi Millgate | 139 | 2:00 | 134 | 14:00 | Natore | 140 | 4:00 | 131 | 12:00
| Valuka | 133 | 3:00 | 120 | 9:00 | Bogra | 141 | 3:00 | 131 | 12:00
| Tangail | 135 | 1:00 | 126 | 13:00 | Noagaon | 136 | 3:00 | 123 | 9:00
| Mymensing | 134 | 1:00 | 123 | 13:00 | Rajshahi | 138 | 1:00 | 128 | 8:00
| Kishorganj | 136 | 5:00 | 127 | 13:00 | Rajshahi New | 139 | 3:00 | 129 | 12:00
| Netrokona | 132 | 1:00 | 112 | 13:00 | C.Nawabganj | 137 | 1:00 | 126 | 12:00
| Jamalpur | 141 | 19:30 | 131 | 8:00 | Amnura | 139 | 3:00 | 127 | 12:00
| Sherpur | 138 | 21:00 | 127 | 3:00 | Pabna | 140 | 2:00 | 131 | 12:00
| Srimongal | 140 | 1:00 | 138 | 12:00 | Shahjadpur | 145 | 1:00 | 134 | 12:00
| Shahjibazar | 138 | 1:00 | 135 | 17:00 | Serajganj | 140 | 2:00 | 129 | 12:00
| Fenchuganj | 139 | 1:00 | 137 | 12:00 | Niyamatpur | 135 | 3:00 | 119 | 9:00
| Khulawara | 140 | 1:00 | 138 | 10:00 | Joypurhat | 136 | 2:00 | 120 | 9:00
| Sylhet | 137 | 1:00 | 135 | 12:00 | Sherpur(Bogura) | 140 | 2:00 | 131 | 9:00
| Chatak | 137 | 1:00 | 135 | 11:00 | Mohastangor | 139 | 6:00 | 129 | 9:00
| Sunamganj | 136 | 4:00 | 134 | 18:00 | Bangura | 142 | 2:00 | 132 | 11:00
| Biani Bazar | 138 | 3:00 | 135 | 18:00 | Rangpur | 136 | 4:00 | 121 | 9:00
| Comilla(s) | 131 | 18:00 | 125 | 11:00 | Lalmonirhat | 134 | 1:00 | 120 | 9:00
| Comilla(n) | 143 | 4:00 | 140 | 11:00 | Saidpur | 133 | 1:00 | 120 | 9:00
| Chandpur | 143 | 13:00 | 140 | 1:00 | Purbasadipur | 133 | 1:00 | 118 | 9:00
| Feni | 142 | 18:30 | 136 | 16:00 | Thakurgaon | 133 | 4:00 | 117 | 18:30
| Chowmuhani | 139 | 18:30 | 132 | 6:00 | Palashbari | 136 | 6:00 | 125 | 12:00
| Ashuganj | 141 | 5:00 | 139 | 13:00 | Barapukuria | 137 | 0.041667 | 126 | 0.375
| Daudkandi | 141 | 20:00 | 136 | 12:00 | Panchagar | 134 | 0.20833 | 116 | 0.375
| B.Baria | 138 | 5:00 | 133 | 11:00 | Joldhaka | 134 | 0.16667 | 117 | 0.375
| Ramganj | 142 | 20:00 | 135 | 3:00 | Kurigram | 134 | 0.083333 | 117 | 0.375
| Chaddagram | 142 | 18:30 | 137 | 12:00 | Mithapukur | 138 | 7:00 | 126 | 11:00
| PHP | 141 | 20:00 | 136 | 2:00

## L-Curve
Date | 2022-02-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 53 | 5146 | 2371 | 7517 |  |  |  | QF-LDC-11
0:30 | 46.5 | 5008 | 2235.5 | 7243.5 | Date: | 2022-02-02
1:00 | 40 | 4870 | 2100 | 6970
1:30 | 23 | 4722.5 | 2052.5 | 6775
2:00 | 6 | 4575 | 2005 | 6580
2:30 | 16 | 4452 | 2001 | 6453 | [5 empty] | Gen. at Eve. Peak | 10011 | 10011 MW (19:00 )
3:00 | 26 | 4329 | 1997 | 6326 | [6 empty] | 19:00
3:30 | 34 | 4277.5 | 1992.5 | 6270 | [5 empty] | Gen. at Day Peak | 8934 | 8934 MW (12:00 )
4:00 | 42 | 4226 | 1988 | 6214 | [6 empty] | 12:00
4:30 | 40 | 4196 | 1962.5 | 6158.5 | [5 empty] | Highest Generation | 10011
5:00 | 38 | 4166 | 1937 | 6103 | [6 empty] | 19:00
5:30 | 29 | 4269.5 | 2011 | 6280.5
6:00 | 20 | 4373 | 2085 | 6458
6:30 | 67 | 4589 | 2126 | 6715
7:00 | 114 | 4805 | 2167 | 6972
7:30 | 225.5 | 5079 | 2273 | 7352
8:00 | 337 | 5353 | 2379 | 7732
8:30 | 300.5 | 5706 | 2478.5 | 8184.5
9:00 | 264 | 6059 | 2578 | 8637
9:30 | 208 | 6087 | 2582 | 8669
10:00 | 152 | 6115 | 2586 | 8701
10:30 | 131 | 6104.5 | 2582.5 | 8687
11:00 | 110 | 6094 | 2579 | 8673
11:30 | 149.5 | 6228 | 2575.5 | 8803.5
12:00 | 189 | 6362 | 2572 | 8934
12:30 | 262.5 | 6447 | 2591.5 | 9038.5
13:00 | 336 | 6532 | 2611 | 9143
13:30 | 223.5 | 6320 | 2565.5 | 8885.5
14:00 | 111 | 6108 | 2520 | 8628
14:30 | 119 | 6085 | 2538 | 8623
15:00 | 127 | 6062 | 2556 | 8618
15:30 | 129 | 5929.5 | 2505.5 | 8435
16:00 | 131 | 5797 | 2455 | 8252
16:30 | 77.5 | 5840.5 | 2410.5 | 8251
17:00 | 24 | 5884 | 2366 | 8250
17:30 | 86 | 6174 | 2496 | 8670
18:00 | 148 | 6464 | 2626 | 9090
18:30 | 236.5 | 6756.5 | 2794 | 9550.5
19:00 | 325 | 7049 | 2962 | 10011
19:30 | 292 | 6888 | 2993 | 9881
20:00 | 312 | 6775 | 2939 | 9714 |  |  |  | Executive Engineer
20:30 | 277 | 6708.5 | 2903 | 9611.5 |  |  |  | Network Operation Division
21:00 | 242 | 6642 | 2867 | 9509
21:30 | 138.5 | 6372.5 | 2848 | 9220.5
22:00 | 35 | 6103 | 2829 | 8932 |  |  |  |  | Page 6 of 7
22:30 | 32 | 5854 | 2717 | 8571
23:00 | 29 | 5605 | 2605 | 8210
23:30 | 41 | 5375.5 | 2488 | 7863.5
24:00 | 53 | 5146 | 2371 | 7517
10011 MW (19:00 )
8934 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-02-02 |  | Energy |  | 199826133
[13 empty] | 2022-02-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2375 | 736 | 1546 | 0 | 2082 | 650 | 46 | 0 | 0 | 82 | 0 | 0
0:30 | 2363 | 731.5 | 1575.5 | 0 | 1868.5 | 579.5 | 46 | 0 | 0 | 79.5 | 0 | 0 | Date: | 2022-02-02
1:00 | 2351 | 727 | 1605 | 0 | 1655 | 509 | 46 | 0 | 0 | 77 | 0 | 0
1:30 | 2347.5 | 704.5 | 1600.5 | 0 | 1492.5 | 509 | 46 | 0 | 0 | 75 | 0 | 0 | [8 empty] | Total Energy | 199.8261 | Total Energy Gen 199.826 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 199.826 MKWHr
2:00 | 2344 | 682 | 1596 | 0 | 1330 | 509 | 46 | 0 | 0 | 73 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2310.5 | 682.5 | 1590.5 | 0 | 1226 | 524 | 46 | 0 | 0 | 73.5 | 0 | 0 | [8 empty] | Energy Requirement | 199.8261
3:00 | 2277 | 683 | 1585 | 0 | 1122 | 539 | 46 | 0 | 0 | 74 | 0 | 0
3:30 | 2269.5 | 683.5 | 1617 | 0 | 1038.5 | 544.5 | 46 | 0 | 0 | 71 | 0 | 0 | [6 empty] | Shortage
4:00 | 2262 | 684 | 1649 | 0 | 955 | 550 | 46 | 0 | 0 | 68 | 0 | 0
4:30 | 2251 | 684.5 | 1617 | 0 | 941.5 | 550 | 46 | 0 | 0 | 68.5 | 0 | 0
5:00 | 2240 | 685 | 1585 | 0 | 928 | 550 | 46 | 0 | 0 | 69 | 0 | 0
5:30 | 2246 | 708 | 1638.5 | 0 | 1023 | 550 | 46 | 0 | 0 | 69 | 0 | 0
6:00 | 2252 | 731 | 1692 | 0 | 1118 | 550 | 46 | 0 | 0 | 69 | 0 | 0
6:30 | 2251.5 | 731 | 1651 | 0 | 1415 | 550 | 46 | 0 | 0 | 69 | 1.5 | 0 |  |  |  |  | Coal
7:00 | 2251 | 731 | 1610 | 0 | 1712 | 550 | 46 | 0 | 0 | 69 | 3 | 0
7:30 | 2258.5 | 731.5 | 1549 | 0 | 2046.5 | 570 | 46 | 0 | 61 | 73.5 | 16 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2266 | 732 | 1488 | 0 | 2381 | 590 | 46 | 0 | 122 | 78 | 29 | 0
8:30 | 2265.5 | 731.5 | 1500.5 | 41 | 2678.5 | 635 | 46 | 0 | 161.5 | 81 | 44 | 0
9:00 | 2265 | 731 | 1513 | 82 | 2976 | 680 | 46 | 0 | 201 | 84 | 59 | 0
9:30 | 2265.5 | 731 | 1494.5 | 68 | 3019.5 | 680 | 46 | 0 | 203 | 87 | 74.5 | 0
10:00 | 2266 | 731 | 1476 | 54 | 3063 | 680 | 46 | 0 | 205 | 90 | 90 | 0
10:30 | 2234 | 731 | 1467.5 | 27 | 3105 | 660 | 46 | 0 | 208.5 | 91 | 117 | 0
11:00 | 2202 | 731 | 1459 | 0 | 3147 | 640 | 46 | 0 | 212 | 92 | 144 | 0
11:30 | 2269 | 731 | 1462 | 0 | 3174.5 | 635 | 46 | 0 | 230.5 | 93 | 162.5 | 0
12:00 | 2336 | 731 | 1465 | 0 | 3202 | 630 | 46 | 0 | 249 | 94 | 181 | 0
12:30 | 2319.5 | 730.5 | 1472.5 | 40.5 | 3264.5 | 644.5 | 46 | 0 | 254 | 96 | 170.5 | 0
13:00 | 2303 | 730 | 1480 | 81 | 3327 | 659 | 46 | 0 | 259 | 98 | 160 | 0
13:30 | 2303 | 730 | 1480 | 81 | 3327 | 659 | 46 | 0 | 259 | 98 | 160 | 0
14:00 | 2303 | 730 | 1480 | 81 | 3327 | 659 | 46 | 0 | 259 | 98 | 160 | 0
14:30 | 2274 | 730 | 1466.5 | 40.5 | 3228 | 654 | 46 | 0 | 214.5 | 96 | 131 | 0
15:00 | 2245 | 730 | 1453 | 0 | 3129 | 649 | 46 | 0 | 170 | 94 | 102 | 0
15:30 | 2258.5 | 730.5 | 1444.5 | 0 | 2952 | 639 | 46 | 0 | 187.5 | 94.5 | 82.5 | 0
16:00 | 2272 | 731 | 1436 | 0 | 2775 | 629 | 46 | 0 | 205 | 95 | 63 | 0
16:30 | 2299 | 731 | 1445.5 | 0 | 2733 | 629 | 46 | 0 | 245 | 95 | 41 | 0
17:00 | 2299 | 731 | 1455 | 0 | 2691 | 629 | 46 | 0 | 285 | 95 | 19 | 0
17:30 | 2339 | 731 | 1460.5 | 49 | 2912 | 639 | 46 | 0 | 382.5 | 101.5 | 9.5 | 0
18:00 | 2379 | 731 | 1466 | 98 | 3133 | 649 | 46 | 0 | 480 | 108 | 0 | 0
18:30 | 2371.5 | 731 | 1477.5 | 352 | 3271 | 704 | 46 | 0 | 489.5 | 108 | 0 | 0
19:00 | 2364 | 731 | 1489 | 606 | 3409 | 759 | 46 | 0 | 499 | 108 | 0 | 0
19:30 | 2367 | 731 | 1449 | 548 | 3424 | 780 | 46 | 0 | 430 | 106 | 0 | 0
20:00 | 2364 | 731 | 1468 | 376 | 3419 | 780 | 46 | 0 | 426 | 104 | 0 | 0
20:30 | 2363 | 731 | 1490 | 302 | 3367.5 | 780 | 46 | 0 | 431 | 101 | 0 | 0
21:00 | 2362 | 731 | 1512 | 228 | 3316 | 780 | 46 | 0 | 436 | 98 | 0 | 0
21:30 | 2354 | 731 | 1511.5 | 114 | 3214 | 780 | 46 | 0 | 375 | 95 | 0 | 0
22:00 | 2346 | 731 | 1511 | 0 | 3112 | 780 | 46 | 0 | 314 | 92 | 0 | 0
22:30 | 2356.5 | 733 | 1508.5 | 0 | 2875 | 755 | 46 | 0 | 207 | 90 | 0 | 0
23:00 | 2367 | 735 | 1506 | 0 | 2638 | 730 | 46 | 0 | 100 | 88 | 0 | 0
23:30 | 2371 | 735.5 | 1526 | 0 | 2360 | 690 | 46 | 0 | 50 | 85 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 27.7° C
24:00 | 2375 | 736 | 1546 | 0 | 2082 | 650 | 46 | 0 | 0 | 82 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 199.826 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 199.826 MKWHr
Note on W13: Author:

## Generation
g | 2022-02-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1104660
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 8 | 17 |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 91879
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 11 | 16 | 19 | 20 | 20 | 17 | 13 | 8 | 2 | [9 empty] | 132705
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 17 | [5 empty] | 105442
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | [5 empty] | 1 | 21 | 68 | 68 | 68 | 68 | 90 | 105 | 105 | 68 | 68 | 76 |  | 105 | 105 | 105 | 85 | 51 | 51 | 17 | 1401745
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [10 empty] | 7 | 45 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 18 | 0 | 0 | 529784
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | 15 | 15 | 15 | 15 | 15 | 88 | 105 | 215 | 250 | 264 | 265 | 268 | 270 | 278 | 250 | 273 | 270 |  | 275 | 275 | 293 | 288 | 298 | 300 | 95 | 4704544
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 468363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 220 | 222 | 220 | 220 | 221 | 221 | 220 | 220 | 220 | 220 | 229 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5284000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 167184
33 | Ashuganj 225 MW CCPP | 209 | 211 | 209 | 214 | 213 | 208 | 220 | 220 | 221 | 228 | 184 | 184 | 193 | 193 | 198 | 203 | 200 | 204 |  | 202 | 205 | 205 | 197 | 201 | 211 | 227 | 4989000
34 | Ashuganj 450 MW CCPP(South) | 335 | 330 | 315 | 320 | 315 | 340 | 315 | 275 | 275 | 275 | 275 | 345 | 275 | 295 | 275 | 275 | 275 | 280 |  | 275 | 275 | 270 | 275 | 270 | 275 | 275 | 7139000
| Ashuganj 450 MW CCPP(North) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 110 | 100 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3694000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 215520
36 | Chandpur 150 MW CCPP | 85 | 86 | 85 | 85 | 86 | 84 | 85 | 85 | 85 | 84 | 84 | 85 | 86 | 88 | 85 | 124 | 123 | 123 |  | 122 | 121 | 124 | 124 | 124 | 125 | 124 | 2368100
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 190 | 190 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 210 | 210 | 210 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4900500
41 | Haripur 360MW CCPP(HPL) | 216 | 230 | 238 | 283 | 285 | 303 | 291 | 270 | 250 | 250 | 243 | 243 | 241 | 243 | 250 | 250 | 250 | 254 |  | 252 | 250 | 250 | 249 | 244 | 242 | 239 | 6014000
42 | RPCL 210MW CCPP | 82 | 105 | 103 | 105 | 106 | 105 | 110 | 111 | 110 | 96 | 83 | 83 | 85 | 85 | 84 | 83 | 96 | 100 |  | 101 | 101 | 100 | 100 | 94 | 89 | 89 | 2254
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 7 | 7 | 9 | 37 | 41 | 34 | 24 | 13 | 3 | [9 empty] | 183770
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 694320
46 | Shajibazar 330 MW CCPP | 135 | 136 | 135 | 134 | 135 | 135 | 137 | 135 | 135 | 138 | 135 | 138 | 136 | 137 | 136 | 135 | 137 | 135 |  | 136 | 135 | 136 | 137 | 136 | 136 | 134 | 3203000
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 69 | 40 | 40 | 40 | 40 | 40 | 70 | 70 | 69 | 40 | 40 | 67 | 40 | 65 | 67 | 67 | 68 |  | 69 | 69 | 68 | 68 | 69 | 69 | 69 | 1433472
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 75 | 75 | 75 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1825920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 178 | 178 | 178 | 178 |  | 177 | 177 | 177 | 177 | 178 | 178 | 177 | 4340300
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250020
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 204192
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1263000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 3874810
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 290 | 295 | 290 | 315 | 290 | 270 | 310 | 270 | 270 | 290 | 300 | 275 | 280 | 280 | 290 | 290 |  | 310 | 280 | 270 | 300 | 270 | 280 | 290 | 7170500
| Bibiyana South 400 MW | 381 | 350 | 350 | 320 | 300 | 300 | 300 | 310 | 340 | 360 | 390 | 400 | 400 | 340 | 340 | 340 | 340 | 400 |  | 400 | 400 | 400 | 400 | 390 | 400 | 400 | 8640100
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 12 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 887358
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496080
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418752
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495432
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512712
63 | Impoprt (Tripura) | 77 | 73 | 74 | 68 | 69 | 69 | 69 | 78 | 84 | 90 | 92 | 94 | 98 | 100 | 94 | 95 | 95 | 108 |  | 108 | 106 | 104 | 98 | 92 | 88 | 82 | 2451840
64 | Malancha, Ctg. EPZ (United) | 32 | 32 | 32 | 40 | 40 | 40 | 38 | 10 | 4 | 3 | 3 | 6 | 10 | 7 | 2 | 2 | 9 | 6 |  | 13 | 11 | 15 | 22 | 40 | 35 | 35 | 476160
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 17 | 18 | 18 | 18 | 18 |  | 19 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 447444
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 181440
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 25 | 25 | 21 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 560100
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 241270
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 203220
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 504500
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 13 | 17 | 17 | 17 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 587100
73 | Ghorashal 108MW PP (Regent) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [18 empty] | 6 | 71090
| Feni Lanka Power | [7 empty] | 51 | 51 | 51 | 51 | 51 | 70 | 34 | 34 | 17 | 17 | 52 |  | 52 | 52 | 34 | 17 |  |  | 0 | 623580
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 56 | 99 |  | 108 | 118 | 115 | 119 | 117 | 50 | 27 | 845880
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 90 | 90 | 90 | 90 | 90 | 90 | 108 | 126 | 126 | 126 | 126 | 126 | 126 | 144 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3130560
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 16 | 51 | 51 | 51 | 51 | 51 | 8 | 8 | 8 | 30 | 42 |  | 51 | 51 | 51 | 51 | 51 | 0 | 0 | 585600
79 | Kodda 150MW PP | [7 empty] | 100 | 150 | 150 | 150 | 150 | 150 | 64 | 48 | 48 | 82 | 133 |  | 150 | 115 | 115 | 115 | 64 | 0 | 0 | 1615680
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 34 | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 52 | 43 | 46 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1113125
| Gazipur 100 MW PP | 105 | 105 | 70 | 52 | 52 | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 70 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2400000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 1 | 4 | 1 | 2 | 0 | [9 empty] | 25680
| Jodiac Power | [16 empty] | 3 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 95545
| Karnaphuli Power Ltd. | [6 empty] | 1 | 19 | 51 | 51 | 51 | 51 | 64 | 68 | 68 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 17 | 17 | 17 | 868141
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 26 | 50 | 60 | 60 | 60 | 60 | 10 | 10 | 10 | 17 | 48 |  | 59 | 60 | 59 | 59 | 50 | 0 | 0 | 683692
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 72 | 17 | 17 | 45 | 70 | 93 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 72 | 79 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2279040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 10 |  |  | 6 | 20 | 20 |  | 20 | [5 empty] | 0 | 76680
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1209600
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 64 | 93 | 93 | 102 | 102 | 102 | 64 | 64 | 48 | 48 | 85 |  | 102 | 102 | 102 | 102 | 102 | 32 | 0 | 1382400
95 | Patenga 50MW PP (Baraka) | 40 | 40 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 40 | 39 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 955680
96 | Chattogram 108 MW PP (ECPV) | 96 | 97 | 97 | 96 | 97 | 97 | 96 | 96 | 96 | 91 | 89 | 89 | 86 | 94 | 95 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 90 | 90 | 2217600
97 | katpotti 52 MW | 47 | 48 | 47 | 47 | 47 | 46 | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 48 | 48 | 44 | 43 | 47 |  | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 1126800
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 6 | 40 | 40 | 40 | 40 | 40 | 15 | 25 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 576060
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 937741
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2905527
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 11450
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 823320
104 | Keranigonj 300 MW PP (APR) | [8 empty] | 57 | 29 |  |  | 56 |  |  |  |  | 38 |  | 221 | 151 | 71 | 53 |  |  | 0 | 530602
105 | Bramhangoan 100 MW PP (Aggreko) | [8 empty] | 25 | 25 |  |  | 25 |  |  |  |  | 25 |  | 100 | 100 | 100 | 100 |  |  |  | 402129
106 | Mymensingh 200 MW PP (United) | 180 | 100 | 30 | 30 | 41 | 68 | 127 | 190 | 193 | 194 | 194 | 194 | 193 | 193 | 192 | 192 | 170 | 175 |  | 193 | 200 | 200 | 200 | 200 | 193 | 200 | 3900000
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 25 |  | 100 | 100 | 100 | 60 |  |  | 0 | 278701
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 13 | 48 | 134 | 141 | 149 | 149 | 149 | 149 | 122 | 100 | 82 | 98 |  | 149 | 149 | 149 | 149 | 149 | 112 |  | 2113200
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 20 | 10 | 10 | 10 | 50 | 50 | 88 | 90 | 76 | 76 | 90 | 90 | 90 | 76 | 30 | 46 | 50 |  | 70 | 70 | 70 | 50 | 10 | 10 | 10 | 1273920
116 | Chandpur 200MW (Desh energy) | [6 empty] | 7 | 34 | 34 | 34 | 34 | 34 | 55 | 100 | 100 | 68 | 51 | 55 |  | 100 | 100 | 100 | 100 | 68 | 68 | 34 | 1168800
117 | Ashuganj 150MW PP (Midland) | 140 | 50 | 10 | 10 | 10 | 13 | 95 | 133 | 135 | 137 | 143 | 142 | 137 | 135 | 135 | 135 | 135 | 140 |  | 140 | 142 | 140 | 142 | 133 | 133 | 135 | 2766690
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 11 | 45 | 77 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 75 | 65 | 82 |  | 109 | 109 | 109 | 109 | 109 | 32 | 8 | 1626000
| Anwara 300 MW PP (United) | 260 | 260 | 260 | 230 | 230 | 230 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 283 | 283 | 283 | 283 | 6852327
| Juldah unit-2 (Acorn) | [7 empty] | 20 | 40 | 40 | 40 | 40 | 70 | 20 | 20 | 20 | 30 | 50 |  | 50 | 50 | 50 | 20 |  |  | 0 | 519360
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 108 | 107 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2788855
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444960
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 16 | 23 | 28 | 31 | 9 | 25 | 11 | 8 | 3 | [9 empty] | 178082
| Chandpur 115(Doreen) | [9 empty] | 54 | 87 | 104 | 102 | 94 | 94 | 108 | 123 | 50 | [8 empty] | 831360
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 17 | 17 | 34 | 55 | 6 | 37 | 37 | 38 | 37 | 42 | 55 | 55 | 55 | 55 | 55 |  | 43 | 55 | 55 | 55 | 55 | 55 | 55 | 1121040
120 | Eastern Zone Total | 4870 | 4575 | 4329 | 4226 | 4166 | 4373 | 4805 | 5353 | 6059 | 6115 | 6094 | 6362 | 6532 | 6108 | 6062 | 5797 | 5884 | 6464 |  | 7049 | 6888 | 6775 | 6642 | 6103 | 5605 | 5146 | 139531989
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 4 | 4 |  | 4 | 5 | 17 | 34 | 11 | 0 |  | 72000
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [5 empty] | 10 | 70 | 88 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 53 | 68 |  | 90 | 90 | 90 | 90 | 90 | 92 | 70 | 1519680
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 8 | 20 | 35 | 74 | 78 | 78 | 68 | 46 | 28 | 10 | [9 empty] | 452880
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 213 | 184 | 135 | 121 | 62 | 62 | 62 | [16 empty] | 8 | 33 | 50 | 949691
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 13 | 71 | 72 | 72 | 76 | 80 | 83 | 83 | 85 | 83 | 83 | 83 | 84 | 87 |  | 87 | 86 | 86 | 86 | 86 | 85 | 86 | 1576629
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 90 | 90 | 90 | 90 |  | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 2216358
140 | Bhola 33 MW PP (Venture) | 18 | 18 | 16 | 15 | 15 | 17 | 16 | 15 | 14 | 14 | 17 | 15 | 16 | 15 | 16 | 17 | 17 | 21 |  | 21 | 22 | 23 | 23 | 23 | 20 | 20 | 415100
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 10 |  | 85 | 97 | 60 | 10 |  |  | 0 | 221200
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 727 | 682 | 683 | 684 | 685 | 731 | 731 | 732 | 731 | 731 | 731 | 731 | 730 | 730 | 730 | 731 | 731 | 731 |  | 731 | 731 | 731 | 731 | 731 | 735 | 736 | 17478545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 310 | 310 | 340 | 350 | 350 | 350 | 350 | 390 | 480 | 480 | 440 | 430 | 460 | 430 | 450 | 430 | 430 | 450 |  | 560 | 580 | 580 | 580 | 580 | 530 | 450 | 11476000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 4876300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 14 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 |  | 0 | 218200
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 31500
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 122 | 125 | 126 | 126 | 127 | 127 | 127 | 127 | 126 |  | 126 | 126 | 126 | 126 | 126 | 126 | 125 | 3213445
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 295 | 311 | 323 | 344 | 340 | 344 | 300 | 316 | 310 | 297 | 283 | 268 | 258 | 247 | 253 | 233 | 230 | 233 |  | 226 | 220 | 244 | 252 | 260 | 254 | 263 | 6697600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [9 empty] | 4 | 4 | 5 | 10 | 14 | 23 | 40 | 51 | 49 |  | 48 | 47 | 48 | 41 | 25 |  |  | 346868
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 18 | 16 | 16 | 16 | 16 | 16 | 18 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 467040
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 168948
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [16 empty] | 3 | 30 |  | 32 | 32 | 32 | 32 | 32 |  | 0 | 133863
168 | Santahar 50 MW Peaking PP | [16 empty] | 12 | 31 |  | 30 | 30 | 30 | 30 | 30 |  |  | 141056
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 25 | 34 | 52 | 52 | 52 | 50 | 43 | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1184160
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 22 | 51 | 51 | 51 | 49 | 49 | 49 | 49 | 49 | 49 | 98 |  | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 1018536
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 100 | 100 | 45 | 5 |  |  | 0 | 161711
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 26 | 57 | 92 | 94 | 94 | 94 | 94 | 94 | 94 | 70 | 35 | 48 |  | 91 | 94 | 94 | 94 | 94 | 94 | 50 | 1505472
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 10 | 100 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 50 | 35 | 90 |  | 113 | 113 | 113 | 113 | 113 | 50 | 35 | 1629312
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 20 |  |  |  |  | 20 | 100 | 107 | 113 | 113 | 107 | 100 | 107 | 110 | 113 | 70 | 50 | 106 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1871443
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 25199
178 | Energypac Power Venture Thakurgaon Ltd. | [10 empty] | 4 | 14 | 20 | 20 | 41 | 49 | 41 | 41 | [7 empty] | 0 | 225408
178