## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-06-22 | Saturday
|  | Date (day): | 2019-06-22 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13390 | MW |  |  | (b) At Evening Peak Hour : |  | 15290 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-06-21 | 2019-06-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Engine problem
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 114 | 220 | 210 | 220
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 190 | 200 | 200 | 200
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 240 | 210 | 255 | 255 |  | 110 | ST under maint.
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 25 | 30 | 40 | 40 | 38 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 54 | 50 | 54 | 54 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 348 | 280 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 273 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 276 | 335 | 335
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 40 | 40 | 40 | 170 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 40 | 186 | 150 | 217
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 24 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 49 | 49 | 49
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 125 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 54 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 24 | 70 | 70 |  | 38 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 44 | 45 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 110 | 100 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
37 | Gazipur 100 MW |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 107 | 105 | 105
| Dhaka area Total |  |  |  |  | 6039 | 5803 | 2314 | 2981 | 4186 | 4967 | 692 | 220
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas Shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 6.4 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 42 | 46 | 46
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 40 | 40 | 40 |  | 190 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 219 | 210 | 210 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 100 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 33 | 32 | 33 |  | 18 | Engine problem
47 | Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 84 | 85 | 85
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 15 | 68 | 68 | 68
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
51 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
52 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 23 | 15 | 10 | 20
53 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 100 | 100
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 4.8 | 0 | 3 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 52 | 206 | 300 | 300
| Chattogram area Total |  |  |  |  | 1866 | 1786 | 793.2 | 1186 | 1485 | 1488 | 140 | 398
54 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 201 | 221 | 221
56 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 260 | 360 | 360
57 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 330 | 360 | 360
58 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 |  | 45 | Gas Line problem.
59 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 56 | 55 | 55
60 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 6 | 47 |  | Gas Shortage
61 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 16 | 16 | 16 | 179 |  | Gas shortage
62 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 40 | 40 | 40 |  | 11 | Engine problem
63 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 18 | 0 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 90 | 100 | 100
67 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 17 | 105 | 200 | 200
68 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 116 | 176 | 140 | 187
70 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 25 | 25
71 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
72 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
73 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1177 | 1493 | 1727 | 2175 | 524 | 56
74 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 96 | 95 | 100 | 100 | 102 |  | GT-1 Under maint.
75 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 21 | 22
76 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 77 | 85 | 85 |  | 10 | Engine problem
77 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 2 | 0
78 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 32 | 183 | 100 | 200
79 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 70 | 97 | 100 | 100 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 260 | 474 | 408 | 507 | 102 | 10
80 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 53 | 54 | 54 | 54
81 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 57 | 57 | 57 | 57
82 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
83 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 310 | 309 | 300 | 330
84 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 53 | 51 | 51
85 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 46 | 44 | 44
86 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 62 | 66 | 66 |  |  | FGMO
88 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 83 | 86 | 86
89 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 44 | 46 | 46
90 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 68 | 120 | 130 | 130
91 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 19 | 19
92 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 10 | 47 | 47 | 47
93 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
94 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 341 | 341
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 200 | 250 | 285 | 285 |  |  | On test
95 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1276 | 1570 | 1735 | 1765 | 0 | 0
96 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 30 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 931 | 931 | 943 | 943
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
97 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 100 | 115 | 115
98 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 0 | 40
99 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 120 | 225
100 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 62 | 0 | 80
101 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
102 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
104 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
105 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 17 | 89 | 105 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1068 | 1561 | 1428 | 1783 | 0 | 410
106 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
107 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
108 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 35 | 33 | 33
109 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 172 | 143 | 120 | 120 |  | 74 | ST-1 & 2 Under maint.
110 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 41 | 88 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 237 | 376 | 358 | 384 | 0 | 74
111 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
112 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
113 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 0 | 35
114 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 6 | 33 | 33 | 33 |  | 17 | Engine problem
115 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 32 | 40 |  | 10 | Engine problem
116 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40
117 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 175 | 194 | 214 | 214 |  |  | FGMO
118 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 191 | 220 | 220 |  |  | FGMO
119 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 182 | 207 | 220 | 220 |  |  | FGMO
120 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 330 | 414 | 414
121 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30
122 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
123 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 14 | 14 | 14
124 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
125 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
126 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 30 | 95 | 95 | 95
127 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
128 | Confidence Bogura-2 (CPBL) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 53 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 974 | 1368 | 1727 | 1850 | 0 | 127
129 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 63 | 63 | 63
130 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 239 | 240 | 250 | 250
131 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
132 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 18
| Confidence Rangpur |  | HFO | IPP | 113 MW | 0 | 0 | 15 | 23 | 23 | 23
| Rangpur Area Total |  |  |  |  | 564 | 484 | 317 | 360 | 336 | 371 | 0 | 85
| Total |  |  |  |  | 18539 | 17996 | 8416.2 | 11369 | 13390 | 15290 | 1458 | 1380
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8051.9841 | 10877 | 12810.5401 | 14628.3165
A. |  | 2019-06-21 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11722 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8231.7 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11369 | MW
3 | Day peak Generation : |  |  | 8416.2 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10877 | MW
4 | Evening peak Generation : |  |  | 11369 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 231.7827 | MKWHr | By Solar | 0.1033 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 148.7555 | MKWHr |  | By Oil: | 48.9956 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 7.3581 | MKWHr |  | By Hydro: | 0.8052 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1458 | MW | Dhaka | 3759 | 3759 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1380 | MW | Chittagong | 1104 | 1104 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2838 | MW | Khulna | 1405 | 1405 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1383.25 | MMCFD |  |  | Rajshahi | 1185 | 1185 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 100795903.466 | ii) Oil : | Taka | 385278118.57 | Comilla | 1031 | 1031 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 31795723.48 | Total | Taka | 517869745.516 | Mymensingh | 905 | 905 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.431 | MKWHr. | Sylhet | 470 | 470 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -230 | MW (E to W) at | 21:00 | hrs | Barisal | 324 | 324 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -230 | MW at | 21:00 | hrs | Rangpur | 694 | 694 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.4° C |  |  | Total | 10877 | 10877 |  | 0
B. |  | 2019-06-22 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15290 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 3790 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 227.393 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8196.2 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3484 | MKWHr. | ii) HVDC Flow at Peak Time |  | 931 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4166 | MKWHr. | iii) Maximum HVDC Flow : |  | 935 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.61 |  | (b) Today: | 77.18 |  | (c) Rule Curve: |  | 81.57
.

## YesterdayGen
2019-06-21
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 114 | 190 | 0 | 240 | 52 | 30 | 329 | 351 | 55 | 0 | 400 | 273 | 75 | 15 | 30 | 13 | 0 | 0 | 0 | 15 | 66 | 125 | 0 | 74 | 0 | 6 | 54 | 53 | 55 | 22 | 25 | 29 | 33 | 33 | 49 | 0 | 32 | 0 | 100 | 120 | 25 | 206 | 0 | 145 | 0 | 0 | 16 | 32 | 34 | 10 | 97 | 47 | 21 | 38 | 100 | 0 | 0 | 320 | 320 | 213 | 16 | 50 | 0 | 56 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 0 | 20 | 174 | 55 | 84 | 22 | 0 | 53 | 57 | 53 | 50 | 130 | 306 | 61 | 82 | 45 | 0 | 0 | 47 | 10 | 290 | 16 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 94 | 106 | 17 | 0 | 281 |  | 935 | 28 | 0 | 0 | 115 | 238 | 0 | 0 | 23 | 50 | 40 | 171 | 37 | 110 | 0 | 0 | 60 | 42 | 26 | 90 | 6 | 43 | 44 | 50 | 28 | 22 | 11 | 11 | 0 | 64 | 240 | 17 | 16 | 186 | 0 | 182 | 0 | 96 | 100 | 199 | 0 | 380 | 72 | 0 | 108 | 104 | 12 |  | 7766 | 3956 | 11722 | 4098 | 935 | 2241 | 3145 | 304 | 32 | 793 | 174 | 0 | 0 | 76.36
2:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 341 | 351 | 0 | 0 | 400 | 264 | 0 | 15 | 0 | 13 | 0 | 0 | 0 | 0 | 66 | 125 | 0 | 51 | 0 | 6 | 54 | 54 | 55 | 22 | 25 | 22 | 33 | 33 | 49 | 0 | 32 | 0 | 100 | 120 | 26 | 205 | 0 | 142 | 0 | 0 | 16 | 20 | 17 | 10 | 97 | 47 | 21 | 39 | 100 | 0 | 0 | 320 | 320 | 215 | 16 | 50 | 0 | 56 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 0 | 20 | 168 | 86 | 84 | 22 | 0 | 53 | 57 | 53 | 50 | 130 | 301 | 62 | 82 | 45 | 0 | 0 | 47 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 94 | 106 | 0 | 0 | 281 |  | 931 | 28 | 0 | 0 | 115 | 234 | 0 | 0 | 23 | 50 | 40 | 172 | 36 | 110 | 0 | 0 | 60 | 42 | 26 | 90 | 6 | 16 | 44 | 50 | 28 | 22 | 11 | 11 | 0 | 64 | 240 | 0 | 16 | 194 | 0 | 190 | 0 | 96 | 100 | 207 | 0 | 380 | 72 | 0 | 108 | 104 | 12 |  | 7455 | 3928 | 11383 | 4153 | 931 | 2251 | 2801 | 304 | 32 | 743 | 168 | 0 | 0 | 76.41
3:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 330 | 351 | 0 | 0 | 400 | 277 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 24 | 62 | 0 | 51 | 0 | 6 | 54 | 53 | 35 | 22 | 25 | 22 | 33 | 33 | 50 | 0 | 31 | 0 | 100 | 120 | 26 | 206 | 0 | 140 | 0 | 0 | 16 | 0 | 17 | 10 | 97 | 47 | 21 | 38 | 100 | 0 | 0 | 320 | 320 | 205 | 16 | 50 | 0 | 55 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 0 | 20 | 166 | 96 | 84 | 22 | 0 | 53 | 57 | 50 | 50 | 130 | 306 | 62 | 79 | 45 | 53 | 0 | 47 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 92 | 0 | 100 | 200 | 0 | 0 | 94 | 106 | 0 | 0 | 255 |  | 931 | 0 | 0 | 0 | 115 | 234 | 0 | 0 | 23 | 50 | 40 | 172 | 37 | 110 | 0 | 0 | 60 | 42 | 26 | 90 | 6 | 16 | 44 | 50 | 28 | 22 | 11 | 11 | 0 | 64 | 240 | 0 | 0 | 191 | 0 | 187 | 0 | 96 | 80 | 209 | 0 | 380 | 72 | 0 | 108 | 104 | 12 |  | 7265 | 3861 | 11126 | 4195 | 931 | 2249 | 2634 | 304 | 31 | 616 | 166 | 0 | 0 | 76.46
4:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 330 | 351 | 0 | 0 | 400 | 278 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 74 | 0 | 6 | 54 | 36 | 17 | 22 | 25 | 22 | 33 | 33 | 50 | 0 | 30 | 0 | 100 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 77 | 47 | 21 | 39 | 100 | 0 | 0 | 280 | 320 | 213 | 16 | 50 | 0 | 56 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 0 | 20 | 156 | 96 | 84 | 22 | 0 | 53 | 57 | 50 | 50 | 130 | 304 | 63 | 79 | 45 | 68 | 0 | 47 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 100 | 200 | 0 | 28 | 94 | 107 | 0 | 0 | 265 |  | 931 | 0 | 0 | 0 | 115 | 210 | 0 | 0 | 23 | 0 | 40 | 172 | 36 | 96 | 0 | 0 | 60 | 42 | 26 | 90 | 6 | 43 | 0 | 50 | 0 | 22 | 11 | 8 | 0 | 63 | 240 | 0 | 0 | 191 | 0 | 187 | 0 | 96 | 0 | 209 | 0 | 380 | 72 | 0 | 108 | 104 | 13 |  | 7058 | 3644 | 10702 | 4190 | 931 | 2230 | 2406 | 303 | 30 | 456 | 156 | 0 | 0 | 76.51
5:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 329 | 354 | 0 | 0 | 400 | 227 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 74 | 0 | 6 | 54 | 18 | 17 | 22 | 25 | 22 | 25 | 33 | 0 | 0 | 30 | 0 | 100 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 12 | 46 | 21 | 40 | 100 | 0 | 0 | 280 | 320 | 214 | 16 | 50 | 0 | 56 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 0 | 20 | 130 | 97 | 84 | 22 | 0 | 53 | 57 | 47 | 50 | 130 | 306 | 64 | 79 | 45 | 69 | 0 | 47 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 100 | 195 | 0 | 139 | 94 | 106 | 0 | 0 | 263 |  | 931 | 0 | 0 | 0 | 115 | 173 | 0 | 0 | 14 | 0 | 40 | 172 | 33 | 96 | 0 | 0 | 60 | 42 | 0 | 90 | 6 | 24 | 0 | 50 | 0 | 22 | 11 | 8 | 0 | 63 | 239 | 0 | 0 | 187 | 0 | 183 | 0 | 96 | 0 | 206 | 0 | 380 | 72 | 0 | 108 | 104 | 0 |  | 6921 | 3525 | 10446 | 4287 | 931 | 2233 | 2149 | 302 | 30 | 384 | 130 | 0 | 0 | 76.56
6:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 328 | 323 | 0 | 0 | 370 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 13 | 0 | 6 | 35 | 55 | 0 | 22 | 25 | 22 | 25 | 33 | 0 | 0 | 30 | 0 | 100 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 0 | 37 | 21 | 5 | 100 | 0 | 0 | 280 | 290 | 181 | 16 | 30 | 0 | 55 | 5 | 40 | 0 | 0 | 8 | 22 | 8 | 0 | 20 | 128 | 98 | 84 | 22 | 0 | 53 | 57 | 50 | 50 | 130 | 305 | 40 | 79 | 46 | 67 | 0 | 47 | 10 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 1.2 | 50 | 144 | 0 | 139 | 94 | 52 | 0 | 0.1 | 228 |  | 931 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 29 | 0 | 0 | 0 | 60 | 0 | 0 | 60 | 6 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 63 | 239 | 0 | 0 | 181 | 0 | 178 | 0 | 95 | 0 | 195 | 0 | 300 | 72 | 0 | 53 | 104 | 12 |  | 6225.3 | 2943 | 9168.3 | 4142 | 931 | 2025 | 1396 | 302 | 30 | 213 | 128 | 1.3 | 0 | 76.61
7:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 328 | 303 | 0 | 0 | 370 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 55 | 0 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 35 | 0 | 75 | 60 | 0 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 0 | 18 | 21 | 26 | 100 | 0 | 0 | 280 | 330 | 182 | 16 | 30 | 0 | 56 | 5 | 10 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 122 | 98 | 64 | 22 | 0.2 | 53 | 57 | 11 | 50 | 100 | 300 | 63 | 10 | 46 | 68 | 0 | 47 | 0 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 2.6 | 10 | 17 | 0 | 140 | 95 | 52 | 0 | 0.9 | 67 |  | 931 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 171 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 62 | 239 | 0 | 0 | 186 | 0 | 181 | 0 | 94 | 0 | 195 | 0 | 300 | 17 | 0 | 17 | 24 | 12 |  | 5690.7 | 2726 | 8416.7 | 4125 | 931 | 1873 | 859 | 301 | 35 | 167 | 122 | 3.7 | 0 | 76.66
8:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 328 | 303 | 0 | 0 | 370 | 240 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 55 | 0 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 36 | 0 | 100 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 0 | 18 | 21 | 30 | 100 | 0 | 0 | 270 | 340 | 182 | 16 | 30 | 0 | 55 | 5 | 10 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 106 | 97 | 64 | 22 | 0.8 | 53 | 57 | 11 | 10 | 100 | 305 | 63 | 10 | 46 | 67 | 0 | 10 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 5 | 10 | 17 | 0 | 140 | 95 | 52 | 0 | 1.7 | 52 |  | 931 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 171 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 66 | 239 | 0 | 0 | 185 | 0 | 179 | 0 | 63 | 0 | 196 | 0 | 270 | 17 | 0 | 17 | 17 | 11 |  | 5688.5 | 2643 | 8331.5 | 4250 | 931 | 1733 | 796 | 305 | 36 | 167 | 106 | 7.5 | 0 | 0
9:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 327 | 300 | 0 | 0 | 370 | 266 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 55 | 0 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 36 | 0 | 100 | 120 | 0 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 0 | 18 | 21 | 28 | 100 | 0 | 0 | 250 | 300 | 182 | 16 | 30 | 0 | 51 | 5 | 10 | 0 | 0 | 0 | 22 | 8 | 0 | 20 | 108 | 95 | 64 | 22 | 1.2 | 55 | 57 | 11 | 10 | 100 | 305 | 61 | 10 | 45 | 67 | 0 | 10 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 5.3 | 10 | 17 | 0 | 165 | 95 | 70 | 0 | 5.2 | 52 |  | 931 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 64 | 239 | 0 | 0 | 167 | 0 | 161 | 0 | 62 | 0 | 174 | 0 | 270 | 17 | 0 | 0 | 17 | 11 |  | 5673.7 | 2558 | 8231.7 | 4150 | 931 | 1710 | 815 | 303 | 36 | 167 | 108 | 11.7 | 0 | 0
10:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 327 | 300 | 0 | 0 | 370 | 270 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 30 | 35 | 0 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 36 | 0 | 100 | 120 | 0 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 16 | 10 | 0 | 18 | 21 | 26 | 100 | 0 | 0 | 250 | 300 | 188 | 16 | 30 | 0 | 51 | 5 | 10 | 0 | 0 | 0 | 21 | 8 | 0 | 20 | 110 | 96 | 40 | 22 | 1.9 | 53 | 57 | 11 | 10 | 100 | 304 | 61 | 10 | 42 | 68 | 0 | 10 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 7.8 | 10 | 17 | 0 | 200 | 95 | 70 | 0 | 5.4 | 52 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 171 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 63 | 239 | 0 | 0 | 155 | 0 | 146 | 0 | 42 | 0 | 163 | 0 | 270 | 17 | 0 | 0 | 17 | 11 |  | 5641.1 | 2487 | 8128.1 | 4151 | 932 | 1672 | 744 | 302 | 36 | 166 | 110 | 15.1 | 0 | 0
11:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 339 | 300 | 0 | 0 | 370 | 282 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 18 | 0 | 22 | 25 | 19 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 120 | 0 | 204 | 0 | 130 | 0 | 0 | 16 | 0 | 16 | 10 | 0 | 18 | 21 | 26 | 100 | 0 | 0 | 250 | 300 | 190 | 16 | 30 | 0 | 50 | 5 | 10 | 0 | 0 | 0 | 21 | 8 | 0 | 20 | 112 | 98 | 40 | 22 | 0.2 | 53 | 57 | 11 | 10 | 100 | 305 | 61 | 10 | 42 | 66 | 0 | 10 | 0 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 4 | 10 | 17 | 0 | 197 | 94 | 70 | 0 | 6.5 | 52 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 64 | 239 | 0 | 0 | 182 | 0 | 175 | 0 | 41 | 0 | 186 | 0 | 270 | 0 | 0 | 0 | 17 | 10 |  | 5675.7 | 2561 | 8236.7 | 4239 | 932 | 1703 | 733 | 303 | 38 | 166 | 112 | 10.7 | 0 | 0
12:00 | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 348 | 330 | 0 | 0 | 400 | 290 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 18 | 0 | 19 | 25 | 19 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 120 | 0 | 219 | 0 | 140 | 0 | 0 | 16 | 0 | 15 | 10 | 0 | 18 | 21 | 23 | 100 | 0 | 0 | 280 | 300 | 212 | 16 | 30 | 0 | 50 | 5 | 10 | 0 | 0 | 0 | 21 | 0 | 0 | 20 | 116 | 96 | 40 | 22 | 0 | 53 | 57 | 11 | 10 | 130 | 310 | 57 | 10 | 43 | 68 | 0 | 10 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 6.4 | 10 | 17 | 0 | 200 | 70 | 70 | 0 | 4.8 | 52 |  | 931 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 63 | 239 | 0 | 0 | 175 | 0 | 181 | 0 | 41 | 0 | 182 | 0 | 300 | 0 | 0 | 0 | 17 | 15 |  | 5820.2 | 2596 | 8416.2 | 4319 | 931 | 1812 | 722 | 302 | 38 | 165 | 116 | 11.2 | 0 | 0
13:00 | 35 | 114 | 190 | 0 | 240 | 51 | 25 | 360 | 330 | 0 | 0 | 400 | 270 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18 | 0 | 6 | 35 | 18 | 0 | 19 | 25 | 19 | 25 | 33 | 0 | 0 | 39 | 0 | 100 | 120 | 0 | 206 | 0 | 130 | 0 | 0 | 16 | 0 | 15 | 10 | 0 | 18 | 21 | 26 | 100 | 0 | 0 | 280 | 300 | 186 | 16 | 30 | 0 | 51 | 5 | 10 | 0 | 0 | 2 | 19 | 8 | 24 | 20 | 130 | 94 | 40 | 22 | 2.2 | 53 | 57 | 11 | 10 | 163 | 307 | 62 | 10 | 43 | 110 | 0 | 46 | 0 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 24 | 0 | 250 | 78 | 70 | 0 | 5.8 | 52 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 8 | 0 | 142 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 65 | 239 | 0 | 0 | 194 | 0 | 186 | 0 | 50 | 0 | 206 | 0 | 350 | 0 | 0 | 0 | 17 | 17 |  | 6159 | 2684 | 8843 | 4539 | 932 | 1954 | 764 | 304 | 39 | 173 | 130 | 8 | 0 | 0
14:00 | 35 | 114 | 190 | 0 | 180 | 54 | 25 | 327 | 270 | 0 | 0 | 340 | 273 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 35 | 18 | 17 | 19 | 25 | 14 | 25 | 33 | 0 | 0 | 39 | 0 | 100 | 120 | 7 | 205 | 0 | 130 | 0 | 0 | 16 | 0 | 15 | 10 | 0 | 18 | 21 | 28 | 100 | 0 | 0 | 260 | 300 | 183 | 16 | 30 | 0 | 51 | 5 | 10 | 0 | 0 | 23 | 19 | 8 | 25 | 20 | 130 | 95 | 40 | 22 | 1 | 53 | 57 | 11 | 10 | 130 | 308 | 62 | 10 | 20 | 119 | 0 | 46 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 50 | 52 | 0 | 249 | 70 | 70 | 0 | 4.56 | 52 |  | 931 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 8 | 0 | 143 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 65 | 239 | 0 | 0 | 181 | 0 | 177 | 0 | 71 | 0 | 185 | 0 | 270 | 0 | 0 | 0 | 53 | 7 |  | 5903.56 | 2603 | 8506.56 | 4341 | 931 | 1704 | 879 | 304 | 39 | 173 | 130 | 5.56 | 0 | 76.09
15:00 | 35 | 114 | 190 | 0 | 220 | 54 | 25 | 361 | 300 | 0 | 0 | 360 | 270 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 35 | 18 | 17 | 22 | 25 | 14 | 25 | 33 | 8 | 0 | 38 | 0 | 100 | 120 | 8 | 217 | 0 | 0 | 0 | 0 | 16 | 0 | 15 | 10 | 0 | 5 | 21 | 28 | 100 | 0 | 0 | 280 | 295 | 202 | 16 | 87 | 0 | 52 | 5 | 10 | 0 | 0 | 25 | 19 | 8 | 0 | 9 | 140 | 95 | 41 | 22 | 1.7 | 52 | 57 | 11 | 10 | 130 | 313 | 59 | 10 | 20 | 119 | 0 | 45 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 50 | 50 | 0 | 250 | 70 | 70 | 0 | 3.62 | 52 |  | 931 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 8 | 0 | 143 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 65 | 239 | 0 | 0 | 200 | 0 | 199 | 0 | 71 | 0 | 195 | 0 | 350 | 0 | 0 | 17 | 53 | 16 |  | 6034.32 | 2758 | 8792.32 | 4416 | 931 | 1882 | 903 | 304 | 38 | 173 | 140 | 5.32 | 0 | 76.11
16:00 | 35 | 114 | 190 | 0 | 220 | 54 | 30 | 337 | 300 | 0 | 0 | 360 | 285 | 0 | 0 | 0 | 120 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 35 | 18 | 17 | 22 | 25 | 14 | 25 | 33 | 8 | 0 | 38 | 0 | 100 | 120 | 8 | 204 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 10 | 0 | 16 | 21 | 27 | 100 | 0 | 0 | 270 | 224 | 183 | 16 | 89 | 0 | 53 | 5 | 10 | 0 | 0 | 25 | 19 | 8 | 0 | 20 | 140 | 95 | 40 | 22 | 0.5 | 53 | 57 | 11 | 10 | 163 | 306 | 61 | 10 | 20 | 110 | 0 | 45 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 6.75 | 50 | 50 | 0 | 249 | 70 | 70 | 0 | 1.6 | 120 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 12 | 0 | 143 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 65 | 239 | 0 | 0 | 191 | 0 | 188 | 0 | 72 | 0 | 205 | 0 | 320 | 0 | 0 | 17 | 53 | 16 |  | 6064.85 | 2723 | 8787.85 | 4330 | 932 | 1860 | 996 | 304 | 38 | 179 | 140 | 8.85 | 0 | 76.13
17:00 | 35 | 114 | 190 | 0 | 200 | 54 | 30 | 280 | 270 | 0 | 0 | 330 | 273 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 18 | 17 | 0 | 25 | 14 | 25 | 33 | 8 | 0 | 38 | 0 | 100 | 120 | 8 | 204 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 10 | 0 | 18 | 21 | 32 | 100 | 0 | 0 | 200 | 260 | 182 | 16 | 90 | 0 | 52 | 5 | 10 | 0 | 0 | 25 | 21 | 5 | 0 | 20 | 136 | 93 | 40 | 22 | 0 | 53 | 57 | 14 | 10 | 130 | 304 | 62 | 10 | 20 | 113 | 0 | 47 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1.55 | 50 | 50 | 0 | 249 | 70 | 42 | 0 | 0.12 | 135 |  | 931 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 20 | 0 | 143 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 65 | 240 | 0 | 0 | 178 | 0 | 175 | 0 | 72 | 0 | 202 | 0 | 320 | 0 | 0 | 17 | 16 | 2 |  | 5744.67 | 2653 | 8397.67 | 4145 | 931 | 1748 | 906 | 305 | 38 | 187 | 136 | 1.67 | 0 | 76.15
18:00 | 35 | 114 | 150 | 0 | 180 | 54 | 30 | 280 | 246 | 0 | 0 | 310 | 273 | 0 | 0 | 0 | 120 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 18 | 17 | 22 | 25 | 14 | 25 | 33 | 8 | 0 | 38 | 0 | 100 | 120 | 8 | 203 | 0 | 15 | 0 | 0 | 20 | 0 | 17 | 10 | 0 | 18 | 21 | 31 | 100 | 0 | 0 | 170 | 335 | 182 | 16 | 90 | 0 | 55 | 5 | 10 | 0 | 0 | 25 | 21 | 5 | 0 | 20 | 122 | 96 | 40 | 22 | 0 | 53 | 57 | 14 | 10 | 100 | 308 | 53 | 10 | 10 | 110 | 0 | 10 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0.16 | 50 | 50 | 0 | 150 | 70 | 42 | 0 | 0 | 138 |  | 931 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 6 | 35 | 0 | 143 | 24 | 16 | 0 | 0 | 55 | 0 | 0 | 39 | 12 | 0 | 0 | 0 | 0 | 18 | 10 | 5 | 0 | 63 | 240 | 0 | 0 | 156 | 0 | 146 | 0 | 73 | 0 | 177 | 0 | 280 | 0 | 0 | 17 | 16 | 16 |  | 5539.16 | 2614 | 8153.16 | 3981 | 931 | 1596 | 965 | 303 | 38 | 217 | 122 | 0.16 | 0 | 76.17
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 200 | 200 | 0 | 210 | 54 | 30 | 280 | 270 | 26 | 0 | 330 | 300 | 5 | 8 | 9 | 120 | 0 | 40 | 0 | 2 | 7 | 98 | 5 | 16 | 0 | 6 | 35 | 18 | 17 | 22 | 25 | 14 | 25 | 33 | 10 | 0 | 39 | 0 | 100 | 120 | 8 | 223 | 0 | 31 | 0 | 0 | 33 | 80 | 68 | 10 | 1 | 18 | 21 | 11 | 100 | 0 | 0 | 230 | 330 | 211 | 16 | 90 | 0 | 55 | 5 | 10 | 0 | 8 | 25 | 21 | 8 | 18 | 20 | 168 | 95 | 40 | 22 | 0 | 55 | 57 | 24 | 28 | 100 | 326 | 61 | 10 | 10 | 105 | 0 | 46 | 10 | 280 | 24 | 11 | 0 | 15 | 0 | 0 | 36 | 0 | 6 | 0 | 100 | 50 | 6 | 250 | 95 | 107 | 0 | 0 | 138 |  | 932 | 14 | 0 | 0 | 27 | 120 | 0 | 0 | 24 | 60 | 0 | 143 | 32 | 24 | 0 | 0 | 60 | 20 | 18 | 95 | 33 | 0 | 0 | 8 | 30 | 22 | 14 | 8 | 0 | 64 | 240 | 17 | 17 | 160 | 0 | 152 | 0 | 83 | 6 | 177 | 0 | 320 | 70 | 0 | 17 | 16 | 22 |  | 6635 | 3045 | 9680 | 4433 | 932 | 1760 | 1375 | 304 | 39 | 669 | 168 | 0 | 0 | 76.19
19:30 | 35 | 220 | 200 | 0 | 220 | 54 | 30 | 326 | 300 | 26 | 0 | 400 | 225 | 7 | 8 | 15 | 180 | 0 | 35 | 0 | 7 | 24 | 116 | 10 | 58 | 0 | 6 | 54 | 54 | 55 | 22 | 25 | 14 | 25 | 33 | 42 | 0 | 39 | 0 | 100 | 120 | 10 | 203 | 0 | 80 | 0 | 0 | 33 | 84 | 68 | 10 | 22 | 18 | 21 | 26 | 100 | 0 | 0 | 260 | 330 | 182 | 16 | 90 | 0 | 56 | 5 | 20 | 0 | 8 | 25 | 21 | 8 | 25 | 20 | 170 | 97 | 64 | 22 | 0 | 55 | 57 | 53 | 46 | 100 | 308 | 40 | 80 | 42 | 108 | 0 | 46 | 10 | 260 | 24 | 11 | 0 | 105 | 0 | 0 | 165 | 0 | 16 | 0 | 100 | 105 | 15 | 302 | 96 | 107 | 0 | 0 | 200 |  | 932 | 30 | 0 | 0 | 70 | 120 | 0 | 0 | 24 | 77 | 0 | 143 | 36 | 64 | 0 | 0 | 60 | 50 | 27 | 95 | 33 | 8 | 13 | 8 | 30 | 22 | 14 | 11 | 0 | 63 | 240 | 16 | 17 | 178 | 0 | 170 | 0 | 89 | 90 | 200 | 0 | 300 | 105 | 0 | 53 | 89 | 18 |  | 7630 | 3495 | 11125 | 4681 | 932 | 2005 | 2220 | 303 | 39 | 775 | 170 | 0 | 0 | 76.19
20:00 | 35 | 210 | 200 | 0 | 210 | 54 | 30 | 280 | 270 | 26 | 0 | 400 | 242 | 7 | 0 | 15 | 180 | 0 | 37 | 0 | 0 | 24 | 125 | 0 | 24 | 0 | 18 | 54 | 54 | 55 | 22 | 25 | 12 | 25 | 33 | 44 | 0 | 39 | 0 | 100 | 120 | 19 | 203 | 0 | 80 | 0 | 0 | 33 | 84 | 68 | 10 | 12 | 24 | 21 | 30 | 100 | 0 | 0 | 260 | 330 | 183 | 16 | 90 | 0 | 55 | 5 | 20 | 0 | 0 | 25 | 21 | 8 | 25 | 20 | 174 | 97 | 70 | 22 | 0 | 54 | 57 | 53 | 46 | 100 | 305 | 54 | 82 | 43 | 108 | 0 | 46 | 10 | 255 | 24 | 11 | 0 | 106 | 0 | 0 | 185 | 0 | 16 | 0 | 100 | 80 | 15 | 250 | 96 | 107 | 0 | 0 | 206 |  | 931 | 30 | 0 | 0 | 99 | 120 | 0 | 0 | 24 | 70 | 0 | 143 | 32 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 33 | 8 | 39 | 8 | 29 | 22 | 12 | 11 | 0 | 63 | 240 | 16 | 18 | 179 | 0 | 174 | 0 | 87 | 95 | 194 | 0 | 280 | 105 | 0 | 53 | 89 | 27 |  | 7484 | 3572 | 11056 | 4573 | 931 | 1948 | 2294 | 303 | 39 | 794 | 174 | 0 | 0 | 76.21
21:00 | 35 | 220 | 200 | 0 | 210 | 54 | 30 | 280 | 273 | 0 | 0 | 400 | 276 | 0 | 0 | 0 | 186 | 0 | 40 | 0 | 0 | 24 | 125 | 0 | 24 | 0 | 49 | 54 | 54 | 55 | 22 | 25 | 20 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 120 | 25 | 210 | 0 | 100 | 0 | 0 | 33 | 84 | 68 | 10 | 12 | 42 | 21 | 15 | 100 | 0 | 0 | 260 | 330 | 201 | 16 | 90 | 0 | 56 | 5 | 40 | 0 | 0 | 25 | 21 | 5 | 25 | 20 | 176 | 95 | 77 | 22 | 0 | 54 | 57 | 53 | 46 | 100 | 309 | 62 | 83 | 44 | 120 | 0 | 47 | 10 | 300 | 24 | 11 | 0 | 110 | 0 | 0 | 183 | 0 | 0 | 0 | 100 | 105 | 18 | 250 | 97 | 107 | 0 | 0 | 206 |  | 931 | 30 | 0 | 0 | 100 | 120 | 0 | 0 | 24 | 62 | 0 | 143 | 35 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 33 | 8 | 37 | 8 | 29 | 22 | 14 | 11 | 0 | 63 | 240 | 17 | 17 | 194 | 0 | 191 | 0 | 88 | 100 | 207 | 0 | 330 | 105 | 0 | 53 | 89 | 23 |  | 7704 | 3665 | 11369 | 4709 | 931 | 2061 | 2365 | 303 | 40 | 784 | 176 | 0 | 0 | 76.23
22:00 | 35 | 210 | 200 | 0 | 210 | 54 | 30 | 333 | 274 | 0 | 0 | 400 | 260 | 0 | 0 | 0 | 180 | 0 | 40 | 0 | 0 | 24 | 125 | 0 | 24 | 0 | 48 | 41 | 54 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 120 | 25 | 210 | 0 | 100 | 0 | 0 | 33 | 84 | 68 | 10 | 0 | 46 | 21 | 28 | 100 | 0 | 0 | 260 | 330 | 183 | 16 | 90 | 0 | 56 | 5 | 40 | 0 | 0 | 25 | 21 | 5 | 25 | 20 | 168 | 96 | 77 | 20 | 0 | 54 | 57 | 53 | 46 | 100 | 308 | 63 | 82 | 44 | 113 | 0 | 47 | 10 | 300 | 24 | 11 | 0 | 110 | 0 | 0 | 190 | 0 | 0 | 0 | 100 | 100 | 18 | 251 | 97 | 107 | 0 | 0 | 206 |  | 929 | 29 | 0 | 0 | 115 | 120 | 0 | 0 | 24 | 62 | 0 | 120 | 33 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 6 | 8 | 37 | 8 | 28 | 22 | 14 | 11 | 0 | 63 | 239 | 17 | 17 | 191 | 0 | 188 | 0 | 91 | 100 | 209 | 0 | 330 | 105 | 0 | 53 | 89 | 20 |  | 7701 | 3619 | 11320 | 4710 | 929 | 2075 | 2314 | 302 | 40 | 782 | 168 | 0 | 0 | 76.88
23:00 | 35 | 210 | 201 | 0 | 210 | 52 | 30 | 340 | 271 | 0 | 0 | 400 | 277 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 0 | 24 | 125 | 0 | 24 | 0 | 19 | 54 | 54 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 41 | 0 | 100 | 120 | 25 | 214 | 0 | 100 | 0 | 0 | 33 | 84 | 68 | 10 | 0 | 47 | 21 | 30 | 100 | 0 | 0 | 260 | 330 | 200 | 16 | 90 | 0 | 55 | 5 | 40 | 0 | 0 | 25 | 21 | 5 | 25 | 20 | 174 | 96 | 77 | 20 | 0 | 54 | 57 | 53 | 46 | 100 | 309 | 62 | 82 | 44 | 125 | 0 | 48 | 10 | 310 | 24 | 11 | 0 | 112 | 0 | 0 | 187 | 0 | 0 | 0 | 100 | 100 | 18 | 250 | 87 | 107 | 0 | 0 | 206 |  | 930 | 29 | 0 | 0 | 115 | 120 | 0 | 0 | 24 | 45 | 0 | 120 | 34 | 110 | 0 | 0 | 60 | 50 | 17 | 90 | 6 | 8 | 37 | 8 | 28 | 22 | 13 | 11 | 0 | 61 | 240 | 17 | 17 | 194 | 0 | 191 | 0 | 93 | 100 | 208 | 0 | 330 | 105 | 0 | 53 | 91 | 23 |  | 7801 | 3600 | 11401 | 4810 | 930 | 2084 | 2310 | 301 | 41 | 751 | 174 | 0 | 0 | 76.84
24:00 | 35 | 210 | 200 | 0 | 210 | 52 | 30 | 338 | 273 | 0 | 0 | 400 | 268 | 0 | 10 | 0 | 180 | 0 | 95 | 0 | 0 | 24 | 130 | 0 | 24 | 0 | 6 | 54 | 54 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 41 | 0 | 100 | 120 | 25 | 203 | 0 | 100 | 0 | 0 | 33 | 84 | 68 | 10 | 0 | 47 | 21 | 31 | 100 | 0 | 0 | 260 | 330 | 190 | 16 | 90 | 0 | 56 | 5 | 40 | 0 | 0 | 25 | 22 | 5 | 25 | 20 | 180 | 96 | 77 | 19 | 0 | 54 | 57 | 53 | 46 | 130 | 305 | 63 | 82 | 46 | 110 | 0 | 48 | 10 | 310 | 23 | 11 | 0 | 110 | 0 | 0 | 187 | 0 | 0 | 0 | 100 | 100 | 18 | 250 | 88 | 107 | 0 | 0 | 206 |  | 930 | 29 | 0 | 0 | 115 | 120 | 0 | 0 | 24 | 40 | 0 | 120 | 38 | 110 | 0 | 0 | 60 | 34 | 0 | 90 | 6 | 8 | 37 | 8 | 28 | 22 | 13 | 11 | 0 | 63 | 239 | 16 | 17 | 195 | 0 | 190 | 0 | 96 | 100 | 203 | 0 | 360 | 70 | 0 | 53 | 106 | 23 |  | 7792 | 3574 | 11366 | 4762 | 930 | 2157 | 2277 | 302 | 41 | 717 | 180 | 0 | 0 | 76.96
KWH | 824000 | 3386400 | 4554000 | 0 | 5286900 | 1256636 | 766752 | 8001530 | 7290000 | 135700 | 0 | 8970250 | 6504233 | 119040 | 72552 | 82199 | 2101783 | 0 | 488000 | 0 | 27840 | 338400 | 1160160 | 42384 | 604800 | 0 | 266928 | 1017360 | 888519 | 577000 | 444780 | 600000 | 467640 | 629400 | 803900 | 521040 | 0 | 805200 | 0 | 2300000 | 2900000 | 265383 | 4940967 | 0 | 2399598 | 0 | 0 | 513600 | 513464 | 700832 | 309312 | 463680 | 702720 | 506640 | 693120 | 2461614 | 0 | 0 | 6665500 | 7708000 | 4731000 | 418182 | 1351860 | 0 | 1302240 | 120000 | 642312 | 0 | 7696 | 570302 | 499680 | 162900 | 165600 | 454820 | 3416640 | 2172800 | 1534080 | 483012 | 10000 | 1267000 | 1370160 | 748800 | 751032 | 463680 | 6952000 | 1374240 | 1076160 | 896760 | 2059700 | 0 | 879460 | 181620 | 7313700 | 458184 | 264000 | 0 | 762760 | 0 | 0 | 2472000 | 0 | 444960 | 57780 | 1513920 | 2125440 | 100363 | 4147000 | 2115600 | 1962000 | 0 | 35520 | 3582982 |  | 22348364 | 202600 | 0 | 0 | 1193280 | 3532337 | 0 | 0 | 246240 | 571648 | 222000 | 2883000 | 673452 | 1123488 | 11330 | 0 | 1375000 | 473920 | 215279 | 1799750 | 231670 | 192470 | 305700 | 324480 | 255025 | 504480 | 258336 | 203688 | 0 | 1535564 | 5822500 | 115000 | 133000 | 4663309 | 0 | 4502591 | 0 | 1880673 | 843840 | 4904636 | 0 | 7751000 | 1051200 | 0 | 1003488 | 1463616 | 465000 |  | 156499701 | 75282954 | 231782655 | 103916832 | 22348364 | 44838645 | 38751629 | 7358064 | 805200 | 10243981 | 3416640 | 103300 | 0
Fuel Cost | 708640 | 2912304 | 3916440 | 0 | 3383616 | 1017875.16 | 720746.88 | 4880933.3 | 4446900 | 1304077 | 0 | 6010067.5 | 98799299.27 | 747571.2 | 484647.36 | 502235.89 | 1366158.95 | 0 | 541680 | 0 | 174000 | 2230056 | 11218747.2 | 269986.08 | 3622752 | 0 | 1780409.76 | 7253776.8 | 5553243.75 | 3617790 | 333585 | 450000 | 0 | 0 | 0 | 4929038.4 | 0 | 0 | 0 | 2530000 | 3190000 | 2513177.01 | 3261038.22 | 0 | 2759537.7 | 0 | 0 | 4514544 | 5530007.28 | 6819095.36 | 1914641.28 | 2995372.8 | 4595788.8 | 430644 | 0 | 2240068.74 | 0 | 0 | 4132610 | 5318520 | 3311700 | 288545.58 | 1297785.6 | 0 | 1119926.4 | 110400 | 526695.84 | 0 | 83424.64 | 4231640.84 | 384753.6 | 122175 | 127512 | 341115 | 23369817.6 | 1629600 | 14098195.2 | 371919.24 | 0 | 1317680 | 1424966.4 | 718848 | 675928.8 | 361670.4 | 4866400 | 1566633.6 | 1151491.2 | 986436 | 2348058 | 0 | 817897.8 | 168906.6 | 4680768 | 343638 | 200640 | 0 | 5537637.6 | 0 | 0 | 17674800 | 0 | 0 | 0 | 0 | 19851609.6 | 937390.42 | 3607890 | 0 | 0 | 0 | 0 | 0 |  | 113976656.4 | 5905790 | 0 | 0 | 9892291.2 | 56799978.96 | 0 | 0 | 2772662.4 | 6734013.44 | 1749360 | 1989270 | 666717.48 | 8313811.2 | 381594.4 | 0 | 1443750 | 5426384 | 2307790.88 | 16125760 | 2003945.5 | 1712983 | 3255705 | 3218841.6 | 3001644.25 | 554928 | 242835.84 | 154191.816 | 0 | 9320873.48 | 22474850 | 3706450 | 3560410 | 3171050.12 | 0 | 3151813.7 | 0 | 0 | 14623747.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 346576119.65 | 308640099.866 | 655216219.516 | 75528317.986 | 113976656.4 | 25267585.48 | 251648660.76 | 31795723.48 | 0 | 133629457.81 | 23369817.6 | 0 | 0
Yesterday Day Peak | 35 | 114 | 190 | 0 | 240 | 52 | 25 | 348 | 330 | 0 | 0 | 400 | 290 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 18 | 0 | 19 | 25 | 19 | 25 | 33 | 0 | 0 | 38 | 0 | 100 | 120 | 0 | 219 | 0 | 140 | 0 | 0 | 16 | 0 | 15 | 10 | 0 | 18 | 21 | 23 | 100 | 0 | 0 | 280 | 300 | 212 | 16 | 30 | 0 | 50 | 5 | 10 | 0 | 0 | 0 | 21 | 0 | 0 | 20 | 116 | 96 | 40 | 22 | 0 | 53 | 57 | 11 | 10 | 130 | 310 | 57 | 10 | 43 | 68 | 0 | 10 | 0 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 6.4 | 10 | 17 | 0 | 200 | 70 | 70 | 0 | 4.8 | 52 |  | 931 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 24 | 0 | 0 | 0 | 60 | 0 | 0 | 30 | 6 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 63 | 239 | 0 | 0 | 175 | 0 | 181 | 0 | 41 | 0 | 182 | 0 | 300 | 0 | 0 | 0 | 17 | 15 |  | 8416.2 | DayPeak
Yesterday Evening Peak | 35 | 220 | 200 | 0 | 210 | 54 | 30 | 280 | 273 | 0 | 0 | 400 | 276 | 0 | 0 | 0 | 186 | 0 | 40 | 0 | 0 | 24 | 125 | 0 | 24 | 0 | 49 | 54 | 54 | 55 | 22 | 25 | 20 | 25 | 33 | 50 | 0 | 40 | 0 | 100 | 120 | 25 | 210 | 0 | 100 | 0 | 0 | 33 | 84 | 68 | 10 | 12 | 42 | 21 | 15 | 100 | 0 | 0 | 260 | 330 | 201 | 16 | 90 | 0 | 56 | 5 | 40 | 0 | 0 | 25 | 21 | 5 | 25 | 20 | 176 | 95 | 77 | 22 | 0 | 54 | 57 | 53 | 46 | 100 | 309 | 62 | 83 | 44 | 120 | 0 | 47 | 10 | 300 | 24 | 11 | 0 | 110 | 0 | 0 | 183 | 0 | 0 | 0 | 100 | 105 | 18 | 250 | 97 | 107 | 0 | 0 | 206 |  | 931 | 30 | 0 | 0 | 100 | 120 | 0 | 0 | 24 | 62 | 0 | 143 | 35 | 110 | 0 | 0 | 60 | 50 | 26 | 95 | 33 | 8 | 37 | 8 | 29 | 22 | 14 | 11 | 0 | 63 | 240 | 17 | 17 | 194 | 0 | 191 | 0 | 88 | 100 | 207 | 0 | 330 | 105 | 0 | 53 | 89 | 23 |  | 11369 | EvPeak
Forecast for Evening | 35 | 220 | 200 | 0 | 255 | 54 | 40 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 217 | 0 | 40 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 120 | 25 | 225 | 0 | 0 | 0 | 0 | 33 | 85 | 68 | 100 | 100 | 46 | 21 | 20 | 100 | 0 | 0 | 360 | 360 | 221 | 16 | 100 | 0 | 55 | 6 | 40 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 187 | 100 | 85 | 22 | 0 | 54 | 57 | 51 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 19 | 47 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 100 | 105 | 105 |  | 300 |  | 943 | 30 | 0 | 0 | 115 | 225 | 0 | 0 | 40 | 80 | 40 | 120 | 33 | 110 | 26 | 0 | 60 | 50 | 35 | 95 | 33 | 40 | 40 | 52 | 30 | 22 | 14 | 11 | 0 | 63 | 250 | 17 | 18 | 214 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 105 | 23
Forecast for Day | 35 | 210 | 200 | 0 | 255 | 50 | 40 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 150 | 0 | 40 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 120 | 25 | 210 | 0 | 0 | 0 | 0 | 32 | 85 | 68 | 100 | 100 | 46 | 21 | 10 | 100 | 0 | 0 | 360 | 360 | 221 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 140 | 100 | 85 | 21 | 2 | 54 | 57 | 51 | 44 | 163 | 300 | 66 | 86 | 46 | 130 | 19 | 47 | 10 | 341 | 25 | 11 | 0 | 100 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 0 | 285 | 100 | 105 | 105 | 3 | 300 |  | 943 | 0 | 0 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 120 | 33 | 110 | 0 | 0 | 60 | 0 | 0 | 95 | 33 | 32 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 63 | 250 | 0 | 0 | 214 | 0 | 220 | 0 | 95 | 0 | 220 | 0 | 414 | 105 | 0 | 100 | 105 | 23
Generation at 08:00(Today) | 35 | 209 | 200 | 0 | 200 | 12 | 40 | 327 | 276 | 0 | 0 | 300 | 263 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 0 | 28 | 33 | 33 | 0 | 0 | 38 | 0 | 100 | 120 | 0 | 204 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 10 | 0 | 46 | 21 | 11 | 100 | 0 | 0 | 260 | 250 | 182 | 16 | 90 | 0 | 55 | 5 | 10 | 0 | 0 | 0 | 22 | 0 | 25 | 16 | 106 | 97 | 8 | 19 | 0.6 | 54 | 57 | 11 | 10 | 100 | 304 | 62 | 60 | 46 | 110 | 0 | 5 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 10.6 | 70 | 17 | 0 | 200 | 8 | 70 | 0 | 3 | 140 | 0 | 937 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 120 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 63 | 240 | 0 | 0 | 147 | 0 | 171 | 0 | 95 | 0 | 136 | 0 | 240 | 17 | 0 | 0 | 17 | 23 | 0
199
| Minimum Generation |  | 8231.7 | 9:00
| Highest Generation |  | 11722 | 1:00
| Day Peak Generation |  | 8416.2 | 12:00
| Evening Peak Generation |  | 11369 | 21:00
| HVDC Max Flow |  | 935 | 1:00
| HVDC EvPeak Flow |  | 931 | 21:00
| Load factor L.F |  | 82.39%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-06-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-06-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8416.2 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8196.2 | MW
Evening Peak Generation : |  | 11369 | MW Hour : | 21:00 | Available Max Generation : |  | 15290 | MW
E.P. Demand (at gen end) : |  | 11369 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11722 | MW Hour : | 1:00 | Reserve(Generation end) |  | 3790 | MW
Total Gen. (MKWH) : |  | 231.7827 | System Load Factor : | 82.39% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -230 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-06-22
Actual : | 77.18 | Ft.(MSL) , | Rule curve : | 81.57 | Ft.( MSL )
Gas Consumed : | Total = | 1383.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 100795903.466
|  | Coal : | 31795723.48 | Oil : | 385278118.57 | Total : | 517869745.516
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4094.3812 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1393.3779 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1248.6096 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1128.2913 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1019.5835 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 822.7704 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 458.6865 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 211.8051 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 634.5679 |  |  | 0 | 0%
Total | 0 |  | 11012.0735 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1, | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-7 ST
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal # 5
|  |  |  | 4) Bheramara 410 MW. | 10) Sikalbaha-150 MW.
|  |  |  | 5) Siddhirganj ST | 11) Bhola-225 MW CCPP ST-1 & 2
6) Ashuganj #4,5
)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Bashundhara-Tongi 132 kV Ckt-1 was under shut down from 08:23 to 09:20 for line isolator B-phase temperature
high at Bashundhara end.
b) Hathazari 132/33 kV T-2 transformer was under shut down from 08:18 to 11:54 for C/M.
c) Bhola-225 MW CCPP ST-2 was shut down at 12:17 for maintenance.
d) Sikalbaha-150 MW tripped at 14:40 showing general protection and was synchronized at 17:56.
e) After maintenance Chandpur-150 MW CCPP ST was synchronized at 14:50.
f) Noapara 132/33 kV T-4 transformer tripped at 14:12 due to 33 kV feeder fault and was switched on at 14:17. |  |  |  |  | About 40 MW power interruption occurred under Noapara S/S
area from 14:12 to 14:17.
g) Cumilla (S) 33 kV Bus under T-1 transformer was shut down at 21:06 for red hot maintenance at 33 kV Bus loop |  |  |  |  | About 35 MW power interruption occurred under Cumilla(S) S/S
and was switched on at 21:45. |  |  |  |  | area from 21:06 to 21:45.
h) Cumilla(S) 132/33 kV T-2 transformer & its associated 33 kV Bus was shut down at 22:10 for red hot maintenance |  |  |  |  | About 10 MW power interruption occurred under Cumilla(S) S/S
at 33 kV Bus loop and was switched on at 22:45. |  |  |  |  | area from 22:10 to 22:45.
i) Sikalbaha-150 MW CCPP GT tripped at 04:12(22/6/19) due to problem with emergency shut off valve.
j) Mymensing 33 kV Bus of 132/33 kV T-1 & T-2 transformers were shut down from 06:04to 09:35(22/6/19) for |  |  |  |  | About 100 MW power interruption occurred under Mymensing S/S
replacing sectionalizer. |  |  |  |  | area from 06:04 to 09:35(22/6/19).
k) Sonargaon 132/33 kV T-2 transformer was under shut down from 07:09 to 08:47(22/6/19) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-06-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 824000 | Gas shortage
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 220 | 3386400
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 200 | 4554000
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 210 | 5286900 | ST under maint.
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 30 | 766752 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 54 | 1256636 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 280 | 8001530 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 135700 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 273 | 7290000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 8970250 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 119040 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 276 | 6504233 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 72552 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 82199 | Reserve
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 42384 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 444780
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 40 | 488000 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 27840 | Reserve
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 186 | 2101783 | Machine problem
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 24 | 338400 | Low demand
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 49 | 266928
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1017360
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 1160160 | Engine problem
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 54 | 888519
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 577000
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 24 | 604800 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1067640 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 629400 | Machine problem
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 803900
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 521040
31 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 110 | 762760 | Low demand
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 0 | 444960 | Reserve
37 | Gazipur 100 MW |  | RPCL | 100 MW | 105 | 107 | 1962000
| Dhaka area Total |  |  |  | 5803 | 2981 | 61399846
38 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
39 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 265383
40 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 57780
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 42 | 702720 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 805200 | Low water level
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 210 | 4940967 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2399598
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 33 | 513600 | Engine problem
47 | Baraka Sikalbaha PL |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
48 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 84 | 513464
49 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 700832
50 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 309312 | Low demand
51 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 1513920
52 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 506640
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 693120
53 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 12 | 463680 | Low demand
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 35520
| Anwara United |  | United Group | 300 MW | 0 | 206 | 3582982 | on test
| Chattogram area Total |  |  |  | 1786 | 1186 | 23204718
54 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2461614
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 201 | 4731000 | FGMO
56 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6665500 | Frequency control
57 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7708000 | Frequency control
58 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas Line maint.
59 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 56 | 1302240
60 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
61 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 16 | 418182 | Gas shortage
62 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 40 | 642312 | Machine problem
63 | Midland 150MW |  | IPP | 23*7.015 | 150 | 18 | 100363 | Low demand
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 7696 | Reserve
66 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1351860
67 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 105 | 2125440 | Low demand
68 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 21 | 499680
69 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 162900
** | Tripura |  | Imported power | 0 | 160 | 176 | 3416640
70 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 165600
71 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 25 | 570302 | Low demand
72 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 454820
73 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1493 | 32904149
74 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 95 | 2172800 | Machine problem
75 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 483012
76 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 77 | 1534080 | Engine problem
77 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 10000
78 | United Mymensingh PPL |  | IPP | 200 | 200 | 183 | 2472000 | Engine problem
79 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 97 | 2115600 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 474 | 8787492
80 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 54 | 1267000
81 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1370160
82 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 463680 | Frequency control
83 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 309 | 6952000 | FGMO
84 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 748800
85 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 46 | 751032
86 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
87 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 62 | 1374240 | FGMO
88 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 83 | 1076160
89 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 44 | 896760
90 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 120 | 2059700 | FGMO
91 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0
92 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 879460
93 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 458184
94 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 300 | 7313700 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 250 | 4147000 | On test
95 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 181620
| Sylhet Area Total |  |  |  | 1549 | 1570 | 30203496
96 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 30 | 202600
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 931 | 22348364
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
97 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 100 | 1193280
98 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 24 | 246240
99 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3532337 | Low demand
100 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 62 | 571648
101 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
102 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 0 | 222000 | 33 kV line problem
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
103 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 100 | 843840
104 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1051200
105 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 89 | 1463616
| Khulna Area Total |  |  |  | 2314 | 1561 | 31675125
106 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1123488
107 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 11330 | Reserve
108 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 35 | 673452
109 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 143 | 2883000 | FGMO
110 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 88 | 1880673
| Barisal Area Total |  |  |  | 462 | 376 | 6571943
111 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 1375000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
112 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 473920
113 | Bera Peaking |  | PDB | 9*8.29 | 71 | 26 | 215279
114 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 33 | 231670 | Engine problem
115 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 192470
116 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 37 | 305700
117 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 194 | 4663309 | FGMO
118 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4502591 | FGMO
119 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 207 | 4904636 | FGMO
120 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 330 | 7751000 | Frequency control
121 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 29 | 255025
122 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 504480
123 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 14 | 258336
124 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 203688
125 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 8 | 324480 | Low demand
126 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 95 | 1799750
127 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
128 | Confidence Bogura-2 (CPBL) |  | IPP | 113 MW | 113 | 53 | 1003488
| Rajshahi Area Total |  |  |  | 2070 | 1368 | 28964822
129 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 63 | 1535564
130 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 240 | 5822500
131 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 115000
132 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 133000
| Confidence Rangpur |  | IPP | 113 MW | 0 | 23 | 465000
| Rangpur Area Total |  |  |  | 484 | 360 | 8071064
| Total |  |  |  | 17996 | 11369 | 231782655
| Eastern Grid Total |  |  |  | 12666 | 7704 | 156499701
| Western Grid Total |  |  |  | 5330 | 3665 | 75282954
| National Grid Total |  |  |  | 17996 | 11369 | 231782655
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-06-21
| (a) ENTIRE EASTERN GRID : |  | 7269 | MW | (b) ENTIRE WESTERN GRID : |  | 3608 | MW
| i) Dhaka area |  | 3759 | MW | i) Khulna area |  | 1405 | MW
| ii) Chittagong area |  | 1104 | MW | ii) Rajshahi area |  | 1185 | MW
| iii) Comilla area |  | 1031 | MW | iii) Barisal area |  | 324 | MW
| iv) Mymensingh area |  | 905 | MW | iv) Rangpur area |  | 694 | MW
| v) Sylhet area |  | 470 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10877 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 108 | 100 | Jamalpur | 128 | 2100 | Jessore | 116 | 2200
2 | Munsiganj | 120 | 2200 | Sherpur | 102 | 2300 | Jhenida | 103 | 1930
3 | Sonargaon | 64 | 100 | Srimongal | 38 | 2100 | Bottail | 120 | 100
4 | Shyampur | 184 | 100 | Shahjibazar | 117 | 2200 | G.K Project | 53 | 2100
5 | Bhulta | 174 | 100 | Fenchuganj | 50 | 2200 | Faridpur | 168 | 100
6 | Madanganj | 48 | 100 | Kulawara | 48 | 1900 | Madaripur | 118 | 100
7 | Shitalakhya | 95 | 100 | Sylhet | 138 | 2000 | Gopalganj | 91 | 2200
8 | Rahim steel | 11 | 200 | Chatak | 34 | 2100 | Bagerhat | 89 | 2100
9 | Matuail | 84 | 100 | Sunamganj | 38 | 2200 | Mongla | 36 | 100
10 | Ghorasal | 81 | 100 | Biani Bazar | 48 | 1930 | Satkhira | 101 | 2200
11 | Narsingdi | 139 | 2300 | Comilla (S) | 180 | 2400 | Gallamari | 48 | 2300
12 | Haripur (SBU) | 96 | 100 | Comilla(N) | 127 | 2400 | Magura | 50 | 100
13 | Ullon | 86 | 2000 | Chandpur | 106 | 2300 | Chuadanga | 82 | 2200
14 | Hasnabad | 199 | 100 | Feni | 114 | 2200 | Barisal | 104 | 2200
15 | Magbazar | 112 | 1900 | Chowmuhani | 164 | 2300 | Patuakhali | 100 | 2200
16 | Maniknagar | 92 | 2000 | Ashuganj | 54 | 2300 | Bhandaria | 56 | 2300
17 | Bangabhaban | 16 | 1200 | Daudkandi | 116 | 2000 | Barisal (N) | 43 | 2200
18 | Narinda | 86 | 100 | B.Baria | 142 | 2100 | Sariatpur | 35 | 100
19 | Dhanmondi | 127 | 1900 | Ramganj | 88 | 1930 | Benapol | 40 | 2100
20 | Lalbag | 61 | 2100 | Madunaghat | 56 | 2200 | Borhan Uddin | 37 | 2100
21 | Madartek | 60 | 2100 | Hathazari | 98 | 2000 | Ishurdi | 61 | 200
22 | Mirpur | 106 | 1830 | Khulshi | 172 | 2300 | Ruppur Paromanobik | 2 | 1000
23 | Kalyanpur | 114 | 1900 | Halishahar | 128 | 2100 | Natore | 122 | 100
24 | Gulshan | 126 | 1930 | Baraulia | 160 | 2400 | Bogra | 234 | 2100
25 | Uttara | 85 | 1930 | Sikalbaha | 34 | 2100 | Noagaon | 124 | 100
26 | Uttara New | 15 | 1900 | Dohazari | 90 | 2300 | Rajshahi | 156 | 100
27 | Kamrangirchar | 57 | 1930 | Cox'sbazar | 94 | 2100 | C.Nawabganj | 77 | 2100
28 | Savar | 116 | 1930 | Chandraghona | 28 | 2100 | Amnura | 35 | 1930
29 | Bhasantec | 157 | 1930 | Kaptai | 4 | 1900 | Pabna | 112 | 100
30 | Agargaon | 56 | 1930 | A. Khaer Stl. | 0 | 100 | Shahjadpur | 85 | 2000
31 | Satmosjid | 105 | 1930 | Bakulia | 94 | 2400 | Serajganj | 85 | 2100
32 | Tongi | 128 | 100 | Julda | 18 | 400 | Niyamatpur | 62 | 2100
33 | Kabirpur | 164 | 2000 | TK chemical | 2 | 1100 | Joypurhat | 51 | 100
34 | Basundhara | 120 | 2100 | Modern Steel | 14 | 100 | Mohastangor | 16 | 100
35 | Manikganj | 93 | 2000 | Shahmirpur | 33 | 100 | Rangpur | 143 | 2000
36 | Joydevpur | 208 | 100 | Khagrachhari | 20 | 2000 | Lalmonirhat | 90 | 100
37 | New Tongi | 86 | 1000 | Matarbari | 29 | 2100 | Saidpur | 96 | 100
38 | Korda | 200 | 2100 | Baroiar Hat | 50 | 1900 | Purbasadipur | 108 | 2000
39 | Dhamrai | 54 | 2100 | Rangamati | 12 | 2000 | Thakurgaon | 70 | 2100
40 | Valuka | 102 | 2100 | Abul Khair 230 | 126 | 1400 | Palashbari | 113 | 2000
41 | Tangail | 180 | 2100 | BSRM | 108 | 2100 | Barapukuria | 49 | 100
42 | Mymensing | 204 | 2200 | Goalpara | 26 | 100 | Panchagar | 38 | 100
43 | Kishorganj | 118 | 2100 | Central (S) | 96 | 100 | Joldhaka | 18 | 2000
44 | Netrokona | 95 | 2000 | Noapara | 97 | 100
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-06-21
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 389 | 8:00 | 383 | 19:30 | Kaliakoir | 370 | 9:00 | 362
2 | Bheramara | 396 | 7:00 | 390 | 1:00 | Bhulta | 384 | 19:30 | 376
3 | Ashuganj(N) | 388 | 1:00 | 378 | 12:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
1 | Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 18:00 | 219
2 | Ishurdi | 237 | 3:00 | 226 | 19:30 | Megnaghat | 222 | 1:00 | 219
3 | Ashuganj | 235 | 18:30 | 230 | 12:00 | Fenchuganj | 236 | 6:00 | 231
4 | Serajganj | 232 | 8:00 | 226 | 21:00 | Siddhirganj | 223 | 5:00 | 218
5 | Baghabari | 232 | 12:00 | 224 | 3:00 | Maniknagar | 221 | 18:30 | 217
6 | Barapukuria | 236 | 18:00 | 221 | 13:00 | Old Airport | 218 | 1:00 | 213
7 | Bogra | 227 | 18:00 | 214 | 21:00 | Barisal | 236 | 5:00 | 224
8 | Khulna South | 235 | 2:00 | 223 | 19:00 | AKSML | 220 | 20:00 | 213
9 | Rampura | 221 | 1:00 | 219 | 11:00 | BSRM | 222 | 18:30 | 215
10 | Haripur | 220 | 1:00 | 217 | 12:00 | Bibiyana | 233 | 5:00 | 228
11 | Hasnabad | 220 | 1:00 | 217 | 12:00 | Bhulta | 223 | 8:00 | 218
12 | Aminbazar | 220 | 5:00 | 213 | 12:00 | Ashuganj (S) | 232 | 1:00 | 228
13 | Tongi | 225 | 4:00 | 215 | 12:00 | Kaliakoir | 223 | 1:00 | 218
14 | Comilla (N) | 229 | 18:00 | 224 | 12:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 129 | 1800 | 125 | 1200 | Hathazari | 132 | 1800 | 128
2 | Munsiganj | 130 | 1930 | 125 | 1200 | Khulshi | 130 | 1930 | 125
3 | Megnaghat | 130 | 1830 | 126 | 700 | Halishahar | 134 | 300 | 128
4 | Shyampur | 129 | 1800 | 125 | 1100 | Baraulia | 131 | 100 | 126
5 | Bhulta | 124 | 1300 | 120 | 1100 | Sikalbaha | 134 | 200 | 129
6 | Madanganj | 136 | 100 | 125 | 1100 | Dohazari | 131 | 100 | 128
7 | Shitalakhya | 132 | 1830 | 126 | 1200 | Cox'sbazar | 127 | 1800 | 121
8 | Rahim steal | 130 | 1830 | 127 | 200 | Chandraghona | 132 | 500 | 128
9 | Matuail | 128 | 1800 | 125 | 1200 | Kaptai | 132 | 1800 | 128
10 | Ghorasal | 137 | 100 | 135 | 700 | A. Khaer Stl. | 130 | 1800 | 127
11 | Narsinghdi | 128 | 700 | 122 | 100 | Bakulia | 132 | 100 | 127
12 | Haripur (SBU) | 130 | 1830 | 127 | 1100 | Julda | 133 | 200 | 129
13 | Ullon | 134 | 700 | 130 | 1200 | TK Chemical | 135 | 2000 | 129
14 | Hasnabad | 130 | 800 | 126 | 1200 | Modern Steel | 133 | 100 | 128
15 | Magbazar | 134 | 700 | 130 | 1200 | Shahmirpur | 132 | 100 | 128
16 | Maniknagar | 134 | 600 | 131 | 1200 | Khagrachhari | 130 | 100 | 127
17 | Bangabhaban | 134 | 600 | 131 | 1200 | Matarbari | 129 | 500 | 123
18 | Narinda | 134 | 600 | 131 | 1200 | Baroiar Hat | 128 | 1830 | 122
19 | Dhanmondi | 134 | 700 | 130 | 1200 | Rangamati | 132 | 1930 | 127
20 | Lalbag | 130 | 1800 | 125 | 1200 | Goalpara | 140 | 500 | 134
21 | Madartek | 134 | 700 | 130 | 1900 | Central s/s | 139 | 500 | 133
22 | Mirpur | 133 | 400 | 127 | 1200 | Noapara | 135 | 500 | 129
23 | Kalyanpur | 135 | 600 | 130 | 1200 | Jessore | 132 | 1800 | 120
24 | Gulshan | 133 | 600 | 130 | 1200 | Jhenida | 132 | 1100 | 117
25 | Uttara | 131 | 600 | 125 | 1200 | Bottail | 136 | 1830 | 124
26 | Uttara New | 133 | 200 | 127 | 1200 | G.K.Project | 142 | 1100 | 132
27 | Kamrangirchar | 132 | 200 | 125 | 1200 | Faridpur | 133 | 1800 | 123
28 | Savar | 132 | 600 | 126 | 1200 | Madaripur | 137 | 600 | 127
29 | Bhasantec | 136 | 600 | 131 | 1200 | Gopalganj | 141 | 600 | 128
30 | Agargaon | 137 | 600 | 132 | 1200 | Bagerhat | 136 | 700 | 130
31 | Satmosjid | 136 | 600 | 131 | 1200 | Mongla | 135 | 900 | 129
32 | Tongi | 137 | 400 | 129 | 1200 | Satkhira | 137 | 1100 | 130
33 | Kabirpur | 134 | 1000 | 128 | 2300 | Gallamari | 140 | 500 | 133
34 | Basundhara | 132 | 1930 | 125 | 1200 | Magura | 130 | 1100 | 115
35 | Manikganj | 139 | 100 | 130 | 1500 | Chuadanga | 127 | 1100 | 109
36 | Joydevpur | 137 | 2100 | 131 | 1600 | Barisal | 138 | 700 | 131
37 | New Tongi | 135 | 100 | 126 | 1500 | Patuakhali | 138 | 500 | 128
38 | Kodda | 138 | 100 | 122 | 800 | Bhandaria | 138 | 500 | 129
39 | Dhamrai | 133 | 1800 | 128 | 2100 | Barisal (N) | 140 | 500 | 131
40 | Valuka | 129 | 1700 | 115 | 100 | Sariatpur | 136 | 900 | 126
41 | Tangail | 133 | 1800 | 122 | 1930 | Benapol | 133 | 1830 | 121
42 | Mymensing | 129 | 1200 | 117 | 100 | Ishurdi | 139 | 1830 | 131
43 | Kishorganj | 130 | 700 | 120 | 2100 | Ruppur Paromanobik | 140 | 1800 | 132
44 | Netrokona | 132 | 900 | 116 | 2200 | Natore | 136 | 1830 | 124
45 | Jamalpur | 136 | 600 | 120 | 1900 | Bogra | 134 | 1800 | 125
46 | Sherpur | 135 | 800 | 123 | 1900 | Noagaon | 130 | 1830 | 117
47 | Srimongal | 135 | 500 | 132 | 1900 | Rajshahi | 132 | 1800 | 122
48 | Shahjibazar | 135 | 600 | 130 | 100 | C.Nawabganj | 128 | 1830 | 120
49 | Fenchuganj | 135 | 900 | 131 | 100 | Amnura | 133 | 1800 | 117
50 | Khulawara | 134 | 400 | 130 | 100 | Pabna | 138 | 1830 | 128
51 | Sylhet | 135 | 600 | 129 | 100 | Shahjadpur | 140 | 700 | 135
52 | Chatak | 135 | 600 | 126 | 100 | Serajganj | 135 | 800 | 128
53 | Sunamganj | 134 | 600 | 127 | 100 | Niyamatpur | 126 | 600 | 113
54 | Biani Bazar | 134 | 800 | 126 | 100 | Joypurhat | 130 | 1830 | 115
55 | Comilla(s) | 123 | 800 | 119 | 2200 | Mohastangor | 134 | 1830 | 122
56 | Comilla(n) | 135 | 800 | 130 | 1400 | Rangpur | 130 | 1830 | 117
57 | Chandpur | 130 | 1800 | 122 | 1500 | Lalmonirhat | 127 | 1830 | 112
58 | Feni | 128 | 1900 | 121 | 2300 | Saidpur | 130 | 1830 | 113
59 | Chowmuhani | 124 | 800 | 115 | 1300 | Purbasadipur | 130 | 1830 | 115
60 | Ashuganj | 135 | 4000 | 131 | 2000 | Thakurgaon | 128 | 1830 | 108
61 | Daudkandi | 129 | 1800 | 124 | 1100 | Palashbari | 131 | 1830 | 118
62 | B.Baria | 132 | 800 | 126 | 2100 | Barapukuria | 136 | 1800 | 121

## L-Curve
Date | 2019-06-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 170 | 7792 | 3574 | 11366 |  |  |  | QF-LDC-12
0:30 | 130 | 7779 | 3765 | 11544 | Date: | 2019-06-21
1:00 | 90 | 7766 | 3956 | 11722
1:30 | 105 | 7610.5 | 3942 | 11552.5
2:00 | 120 | 7455 | 3928 | 11383
2:30 | 130 | 7360 | 3894.5 | 11254.5 | [5 empty] | Gen. at Eve. Peak | 11369 | 11369 MW (21:00 )
3:00 | 140 | 7265 | 3861 | 11126 | [6 empty] | 21:00
3:30 | 130 | 7161.5 | 3752.5 | 10914 | [5 empty] | Gen. at Day Peak | 8416.2 | 8416.2 MW (12:00 )
4:00 | 120 | 7058 | 3644 | 10702 | [6 empty] | 12:00
4:30 | 165 | 6989.5 | 3584.5 | 10574 | [5 empty] | Highest Generation | 11722
5:00 | 210 | 6921 | 3525 | 10446 | [6 empty] | 1:00
5:30 | 205 | 6573.15 | 3234 | 9807.15
6:00 | 200 | 6225.3 | 2943 | 9168.3
6:30 | 235 | 5958 | 2834.5 | 8792.5
7:00 | 270 | 5690.7 | 2726 | 8416.7
7:30 | 260 | 5689.6 | 2684.5 | 8374.1
8:00 | 250 | 5688.5 | 2643 | 8331.5
8:30 | 265 | 5681.1 | 2600.5 | 8281.6
9:00 | 280 | 5673.7 | 2558 | 8231.7
9:30 | 280 | 5657.4 | 2522.5 | 8179.9
10:00 | 280 | 5641.1 | 2487 | 8128.1
10:30 | 360 | 5658.4 | 2524 | 8182.4
11:00 | 440 | 5675.7 | 2561 | 8236.7
11:30 | 370 | 5747.95 | 2578.5 | 8326.45
12:00 | 300 | 5820.2 | 2596 | 8416.2
12:30 | 215 | 5989.6 | 2640 | 8629.6
13:00 | 130 | 6159 | 2684 | 8843
13:30 | 190 | 6031.28 | 2643.5 | 8674.78
14:00 | 250 | 5903.56 | 2603 | 8506.56
14:30 | 265 | 5968.94 | 2680.5 | 8649.44
15:00 | 280 | 6034.32 | 2758 | 8792.32
15:30 | 260 | 6049.585 | 2740.5 | 8790.085
16:00 | 240 | 6064.85 | 2723 | 8787.85
16:30 | 250 | 5904.76 | 2688 | 8592.76
17:00 | 260 | 5744.67 | 2653 | 8397.67
17:30 | 300 | 5641.915 | 2633.5 | 8275.415
18:00 | 340 | 5539.16 | 2614 | 8153.16
18:30 | 305 | 6087.08 | 2829.5 | 8916.58
19:00 | 270 | 6635 | 3045 | 9680
19:30 | 200 | 7630 | 3495 | 11125
20:00 | 220 | 7484 | 3572 | 11056 |  |  |  | Executive Engineer
20:30 | 225 | 7594 | 3618.5 | 11212.5 |  |  |  | Network Operation Division
21:00 | 230 | 7704 | 3665 | 11369
21:30 | 225 | 7702.5 | 3642 | 11344.5
22:00 | 220 | 7701 | 3619 | 11320 |  |  |  |  | Page 6 of 7
22:30 | 190 | 7751 | 3609.5 | 11360.5
23:00 | 160 | 7801 | 3600 | 11401
23:30 | 165 | 7796.5 | 3587 | 11383.5
24:00 | 170 | 7792 | 3574 | 11366
11369 MW (21:00 )
8416.2 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-06-21 |  | Energy | 231782655
[10 empty] | 2019-06-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4762 | 930 | 2157 | 2277 | 302 | 41 | 717 | 0 | 180
0:30 | 4430 | 932.5 | 2199 | 2711 | 303 | 36.5 | 755 | 0 | 177 | Date: | 2019-06-21
1:00 | 4098 | 935 | 2241 | 3145 | 304 | 32 | 793 | 0 | 174
1:30 | 4125.5 | 933 | 2246 | 2973 | 304 | 32 | 768 | 0 | 171 | [7 empty] | Total Energy | 231.7827 | Total Energy Gen 231.783 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 231.783 MKWHr
2:00 | 4153 | 931 | 2251 | 2801 | 304 | 32 | 743 | 0 | 168 | [7 empty] | Energy not Served | 0
2:30 | 4174 | 931 | 2250 | 2717.5 | 304 | 31.5 | 679.5 | 0 | 167 | [7 empty] | Energy Requirement | 231.7827
3:00 | 4195 | 931 | 2249 | 2634 | 304 | 31 | 616 | 0 | 166
3:30 | 4192.5 | 931 | 2239.5 | 2520 | 303.5 | 30.5 | 536 | 0 | 161 | [6 empty] | Shortage
4:00 | 4190 | 931 | 2230 | 2406 | 303 | 30 | 456 | 0 | 156
4:30 | 4238.5 | 931 | 2231.5 | 2277.5 | 302.5 | 30 | 420 | 0 | 143
5:00 | 4287 | 931 | 2233 | 2149 | 302 | 30 | 384 | 0 | 130
5:30 | 4214.5 | 931 | 2129 | 1772.5 | 302 | 30 | 298.5 | 0 | 129
6:00 | 4142 | 931 | 2025 | 1396 | 302 | 30 | 213 | 0 | 128
6:30 | 4133.5 | 931 | 1949 | 1127.5 | 301.5 | 32.5 | 190 | 0 | 125 |  |  |  |  | Coal
7:00 | 4125 | 931 | 1873 | 859 | 301 | 35 | 167 | 0 | 122
7:30 | 4187.5 | 931 | 1803 | 827.5 | 303 | 35.5 | 167 | 0 | 114 |  |  |  | Oil |  |  |  | ,
8:00 | 4250 | 931 | 1733 | 796 | 305 | 36 | 167 | 0 | 106
8:30 | 4200 | 931 | 1721.5 | 805.5 | 304 | 36 | 167 | 0 | 107
9:00 | 4150 | 931 | 1710 | 815 | 303 | 36 | 167 | 0 | 108
9:30 | 4150.5 | 931.5 | 1691 | 779.5 | 302.5 | 36 | 166.5 | 0 | 109
10:00 | 4151 | 932 | 1672 | 744 | 302 | 36 | 166 | 0 | 110
10:30 | 4195 | 932 | 1687.5 | 738.5 | 302.5 | 37 | 166 | 0 | 111
11:00 | 4239 | 932 | 1703 | 733 | 303 | 38 | 166 | 0 | 112
11:30 | 4279 | 931.5 | 1757.5 | 727.5 | 302.5 | 38 | 165.5 | 0 | 114
12:00 | 4319 | 931 | 1812 | 722 | 302 | 38 | 165 | 0 | 116
12:30 | 4429 | 931.5 | 1883 | 743 | 303 | 38.5 | 169 | 0 | 123
13:00 | 4539 | 932 | 1954 | 764 | 304 | 39 | 173 | 0 | 130
13:30 | 4539 | 932 | 1954 | 764 | 304 | 39 | 173 | 0 | 130
14:00 | 4539 | 932 | 1954 | 764 | 304 | 39 | 173 | 0 | 130
14:30 | 4477.5 | 931.5 | 1918 | 833.5 | 304 | 38.5 | 173 | 0 | 135
15:00 | 4416 | 931 | 1882 | 903 | 304 | 38 | 173 | 0 | 140
15:30 | 4373 | 931.5 | 1871 | 949.5 | 304 | 38 | 176 | 0 | 140
16:00 | 4330 | 932 | 1860 | 996 | 304 | 38 | 179 | 0 | 140
16:30 | 4237.5 | 931.5 | 1804 | 951 | 304.5 | 38 | 183 | 0 | 138
17:00 | 4145 | 931 | 1748 | 906 | 305 | 38 | 187 | 0 | 136
17:30 | 4063 | 931 | 1672 | 935.5 | 304 | 38 | 202 | 0 | 129
18:00 | 3981 | 931 | 1596 | 965 | 303 | 38 | 217 | 0 | 122
18:30 | 4207 | 931.5 | 1678 | 1170 | 303.5 | 38.5 | 443 | 0 | 145
19:00 | 4433 | 932 | 1760 | 1375 | 304 | 39 | 669 | 0 | 168
19:30 | 4681 | 932 | 2005 | 2220 | 303 | 39 | 775 | 0 | 170
20:00 | 4573 | 931 | 1948 | 2294 | 303 | 39 | 794 | 0 | 174
20:30 | 4641 | 931 | 2004.5 | 2329.5 | 303 | 39.5 | 789 | 0 | 175
21:00 | 4709 | 931 | 2061 | 2365 | 303 | 40 | 784 | 0 | 176
21:30 | 4709.5 | 930 | 2068 | 2339.5 | 302.5 | 40 | 783 | 0 | 172
22:00 | 4710 | 929 | 2075 | 2314 | 302 | 40 | 782 | 0 | 168
22:30 | 4760 | 929.5 | 2079.5 | 2312 | 301.5 | 40.5 | 766.5 | 0 | 171
23:00 | 4810 | 930 | 2084 | 2310 | 301 | 41 | 751 | 0 | 174
23:30 | 4786 | 930 | 2120.5 | 2293.5 | 301.5 | 41 | 734 | 0 | 177 | Max Temp. in Dhaka |  | 34.4° C
24:00 | 4762 | 930 | 2157 | 2277 | 302 | 41 | 717 | 0 | 180
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 231.783 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 231.783 MKWHr
Note on W13: Author:

## Generation
2019-06-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 32 | 32 | 31 | 30 | 30 | 30 | 35 | 36 | 36 | 36 | 38 | 38 | 39 | 39 | 38 | 38 | 38 | 38 |  | 39 | 39 | 39 | 40 | 40 | 41 | 41 | 805200
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 60 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW (RPCL) | 25 | 26 | 26 | 0 | [8 empty] | 0 | 7 | 8 | 8 | 8 | 8 |  | 8 | 10 | 19 | 25 | 25 | 25 | 25 | 265383
| Teknaf Solartech 20MW | [5 empty] | 1.2 | 2.6 | 5 | 5.3 | 7.8 | 4 | 6.4 | 0 |  | 0 | 6.75 | 1.55 | 0.16 | [8 empty] | 57780
6 | Sikalbaha 225MW (Gas) | 206 | 205 | 206 | 204 | 204 | 204 | 205 | 204 | 205 | 205 | 204 | 219 | 206 | 205 | 217 | 204 | 204 | 203 |  | 223 | 203 | 203 | 210 | 210 | 214 | 203 | 4940967
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 145 | 142 | 140 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 130 | 130 | 0 | 0 |  | 15 |  | 31 | 80 | 80 | 100 | 100 | 100 | 100 | 2399598
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 15 | 15 | 15 | 15 | 17 | 17 | 17 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 700832
12 | Hathazari peaking | 32 | 20 | 0 | [14 empty] | 0 |  | 80 | 84 | 84 | 84 | 84 | 84 | 84 | 513464
| Baraka Sikalbaha PL | 17 | 0 | [24 empty] | 29270
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 8 | 8 | 0 | 0 |  |  |  | 7696
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | [15 empty] | 62 | 40 | 35 |  | 40 | 35 | 37 | 40 | 40 | 95 | 95 | 488000
17 | Siddhirganj CCPP-335 MW | 13 | 13 | 13 | 13 | 13 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 160 | 120 | 120 | 120 | 120 | 120 |  | 120 | 180 | 180 | 186 | 180 | 180 | 180 | 2101783
18 | Summit Gazipur -2 | 95 | 0 | [17 empty] | 15 | 105 | 106 | 110 | 110 | 112 | 110 | 762760
19 | Ashuganj 195MW Modular | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 418182
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 824000
21 | Ghorasal GT: Unit-3 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 |  | 200 | 220 | 210 | 220 | 210 | 210 | 210 | 3386400
22 | Ghorasal GT: Unit-4 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 150 |  | 200 | 200 | 200 | 200 | 200 | 201 | 200 | 4554000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 180 | 220 | 220 | 200 | 180 |  | 210 | 220 | 210 | 210 | 210 | 210 | 210 | 5286900
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2461614
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK
33 | Ashuganj CCPP 225 MW | 213 | 215 | 205 | 213 | 214 | 181 | 182 | 182 | 182 | 188 | 190 | 212 | 186 | 183 | 202 | 183 | 182 | 182 |  | 211 | 182 | 183 | 201 | 183 | 200 | 190 | 4731000
34 | Ashuganj CCPP(South) | 320 | 320 | 320 | 320 | 320 | 290 | 330 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 295 | 224 | 260 | 335 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7708000
| Ashuganj CCPP(North) | 320 | 320 | 320 | 280 | 280 | 280 | 280 | 270 | 250 | 250 | 250 | 280 | 280 | 260 | 280 | 270 | 200 | 170 |  | 230 | 260 | 260 | 260 | 260 | 260 | 260 | 6665500
35 | Ashuganj (Precision) 55MW | 56 | 56 | 55 | 56 | 56 | 55 | 56 | 55 | 51 | 51 | 50 | 50 | 51 | 51 | 52 | 53 | 52 | 55 |  | 55 | 56 | 55 | 56 | 56 | 55 | 56 | 1302240
36 | Chandpur CCPP | 50 | 50 | 50 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 87 | 89 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1351860
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 329 | 341 | 330 | 330 | 329 | 328 | 328 | 328 | 327 | 327 | 339 | 348 | 360 | 327 | 361 | 337 | 280 | 280 |  | 280 | 326 | 280 | 280 | 333 | 340 | 338 | 8001530
40 | Meghnaghat CCPP 450MW | 400 | 400 | 400 | 400 | 400 | 370 | 370 | 370 | 370 | 370 | 370 | 400 | 400 | 340 | 360 | 360 | 330 | 310 |  | 330 | 400 | 400 | 400 | 400 | 400 | 400 | 8970250
41 | Haripur Power CCPP 360MW | 351 | 351 | 351 | 351 | 354 | 323 | 303 | 303 | 300 | 300 | 300 | 330 | 330 | 270 | 300 | 300 | 270 | 246 |  | 270 | 300 | 270 | 273 | 274 | 271 | 273 | 7290000
42 | Mymensingh RPCL 210MW | 55 | 86 | 96 | 96 | 97 | 98 | 98 | 97 | 95 | 96 | 98 | 96 | 94 | 95 | 95 | 95 | 93 | 96 |  | 95 | 97 | 97 | 95 | 96 | 96 | 96 | 2172800
43 | Haripur NEPC 110MW | 55 | 0 | [15 empty] | 0 |  | 26 | 26 | 26 | 0 |  |  |  | 135700
44 | Fenchugonj CCPP-1 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 55 | 53 | 53 | 53 | 53 | 53 | 52 | 53 | 53 | 53 |  | 55 | 55 | 54 | 54 | 54 | 54 | 54 | 1267000
45 | Fenchugonj CCPP-2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1370160
46 | Shajibazar 330 MW | 306 | 301 | 306 | 304 | 306 | 305 | 300 | 305 | 305 | 304 | 305 | 310 | 307 | 308 | 313 | 306 | 304 | 308 |  | 326 | 308 | 305 | 309 | 308 | 309 | 305 | 6952000
47 | Shahjibazar GT: Unit- 8, 9 | 61 | 62 | 62 | 63 | 64 | 40 | 63 | 63 | 61 | 61 | 61 | 57 | 62 | 62 | 59 | 61 | 62 | 53 |  | 61 | 40 | 54 | 62 | 63 | 62 | 63 | 1374240
48 | Shahjibazar 86MW | 82 | 82 | 79 | 79 | 79 | 79 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 80 | 82 | 83 | 82 | 82 | 82 | 1076160
49 | Shahjibazar (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 46 | 46 | 46 | 45 | 42 | 42 | 43 | 43 | 20 | 20 | 20 | 20 | 10 |  | 10 | 42 | 43 | 44 | 44 | 44 | 46 | 896760
50 | Sylhet GT 150 MW |  | 0 | 53 | 68 | 69 | 67 | 68 | 67 | 67 | 68 | 66 | 68 | 110 | 119 | 119 | 110 | 113 | 110 |  | 105 | 108 | 108 | 120 | 113 | 125 | 110 | 2059700
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 10 | 10 | 10 | 10 | 10 | 46 | 46 | 45 | 45 | 47 | 10 |  | 46 | 46 | 46 | 47 | 47 | 48 | 48 | 879460
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | [5 empty] | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 181620
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 50 | 50 | 47 | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 14 |  | 24 | 53 | 53 | 53 | 53 | 53 | 53 | 748800
56 | Shahjahanulla 25 MW | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 458184
57 | Summit Bibiana- 2 | 290 | 305 | 310 | 290 | 295 | 265 | 295 | 290 | 280 | 280 | 300 | 290 | 300 | 270 | 320 | 290 | 260 | 270 |  | 280 | 260 | 255 | 300 | 300 | 310 | 310 | 7313700
58 | Southern 55MW | 55 | 55 | 35 | 17 | 17 | 0 | [6 empty] | 0 | 17 | 17 | 17 | 17 | 17 |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 577000
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 513600
60 | Barabkunda (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 506640
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 0 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 444780
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 20 | 20 | 19 | 483012
63 | Tripura | 174 | 168 | 166 | 156 | 130 | 128 | 122 | 106 | 108 | 110 | 112 | 116 | 130 | 130 | 140 | 140 | 136 | 122 |  | 168 | 170 | 174 | 176 | 168 | 174 | 180 | 3416640
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 38 | 39 | 40 | 5 | 26 | 30 | 28 | 26 | 26 | 23 | 26 | 28 | 28 | 27 | 32 | 31 |  | 11 | 26 | 30 | 15 | 28 | 30 | 31 | 693120
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 499680
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 5 | 5 |  | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 162900
67 | Jangalia (Summit) 33MW | [12 empty] | 24 | 25 | 0 |  |  |  |  | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 165600
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 9 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 454820
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 12 | 20 | 28 | 28 | 28 | 467640
71 | Summit Maona | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 629400
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803900
73 | Ghorashal (Regent) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 52 | 52 | 1256636
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | 15 | 0 | [15 empty] | 0 |  | 2 | 7 | 0 |  |  |  |  | 27840
78 | Gazipur (RPCL) | 49 | 49 | 50 | 50 | 0 | [7 empty] | 0 | 0 | 8 | 8 | 8 | 8 |  | 10 | 42 | 44 | 50 | 50 | 50 | 50 | 521040
79 | Kodda 149MW | 125 | 125 | 62 | 48 | 48 | 16 |  |  |  | 0 | 0 | [6 empty] | 0 |  | 98 | 116 | 125 | 125 | 125 | 125 | 130 | 1160160
80 | Jamalpur 95MW | 84 | 84 | 84 | 84 | 84 | 84 | 64 | 64 | 64 | 40 | 40 | 40 | 40 | 40 | 41 | 40 | 40 | 40 |  | 40 | 64 | 70 | 77 | 77 | 77 | 77 | 1534080
81 | Lakdhanvi 52 MW | 52 | 52 | 52 | 52 | 52 | 8 | 0 | 0 |  |  |  |  | 2 | 23 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 570302
| Gazipur 100 MW | 106 | 106 | 106 | 107 | 106 | 52 | 52 | 52 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 42 | 42 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 1962000
| Kaptai Solar | [5 empty] | 0.1 | 0.9 | 1.7 | 5.2 | 5.4 | 6.5 | 4.8 | 5.8 | 4.56 | 3.62 | 1.6 | 0.12 | 0 | [8 empty] | 35520
82 | Madanganj 102MW | 15 | 15 | 0 | [14 empty] | 0 |  | 8 | 8 | 0 | 0 |  | 0 | 10 | 72552
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [12 empty] | 5 | 0 | [5 empty] | 5 | 10 | 0 |  |  |  |  | 42384
86 | Meghnaghat CCPP(Summit) | 273 | 264 | 277 | 278 | 227 | 235 | 264 | 240 | 266 | 270 | 282 | 290 | 270 | 273 | 270 | 285 | 273 | 273 |  | 300 | 225 | 242 | 276 | 260 | 277 | 268 | 6504233
87 | Meghnaghat (IEL) | 75 | 0 | [15 empty] | 0 |  | 5 | 7 | 7 | 0 |  |  |  | 119040
88 | Ghorashal 78MW (MAX) | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 766752
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 309312
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 28 | 46 | 46 | 46 | 46 | 46 | 46 | 751032
93 | Ashuganj (Midland) 51MW | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 20 | 20 | 40 | 40 | 40 | 40 | 642312
94 | Gagnagar (Orion) | 66 | 66 | 24 | 0 | [13 empty] | 0 |  | 7 | 24 | 24 | 24 | 24 | 24 | 24 | 338400
95 | Patenga 50MW | 47 | 47 | 47 | 47 | 46 | 37 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 5 | 16 | 18 | 18 |  | 18 | 18 | 24 | 42 | 46 | 47 | 47 | 702720
96 | Chattogram ECPV 108 MW | 97 | 97 | 97 | 77 | 12 | [14 empty] | 1 | 22 | 12 | 12 | 0 |  |  | 463680
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 18 | 49 | 48 | 19 | 6 | 266928
98 | Bosila 108MW | 74 | 51 | 51 | 74 | 74 | 13 | 8 | 8 | 0 | 0 |  |  | 18 | 24 | 24 | 24 | 8 | 8 |  | 16 | 58 | 24 | 24 | 24 | 24 | 24 | 604800
99 | Madanganj-55 MW | 30 | 0 | [15 empty] | 0 |  | 9 | 15 | 15 | 0 |  |  |  | 82199
100 | Northern 55 MW | 53 | 54 | 53 | 36 | 18 | 55 | 55 | 55 | 55 | 35 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 54 | 54 | 54 | 54 | 54 | 54 | 888519
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 130 | 130 | 163 | 130 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 463680
102 | Sarishabari (Solar) | [6 empty] | 0.2 | 0.8 | 1.2 | 1.9 | 0.2 | 0 | 2.2 | 1 | 1.7 | 0.5 | 0 | [9 empty] | 10000
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 54 | 54 | 54 | 41 | 54 | 54 | 1017360
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 192 | 192 | 192 | 192 | 160 | 50 | 50 | 50 | 50 | 24 | 32 | 32 | 32 | 32 | 36 | 36 | 36 | 36 |  | 36 | 165 | 185 | 183 | 190 | 187 | 187 | 2472000
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 149 | 149 | 92 | 0 | [13 empty] | 0 |  | 6 | 16 | 16 | 0 |  |  |  | 444960
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 50 | 50 | 50 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1513920
116 | Chandpur Desh 200MW | 200 | 200 | 200 | 200 | 195 | 144 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 52 | 50 | 50 | 50 | 50 |  | 50 | 105 | 80 | 105 | 100 | 100 | 100 | 2125440
117 | Midland 150MW | [17 empty] | 0 |  | 6 | 15 | 15 | 18 | 18 | 18 | 18 | 100363
118 | Bibiyana-3 285 MW |  |  | 0 | 28 | 139 | 139 | 140 | 140 | 165 | 200 | 197 | 200 | 250 | 249 | 250 | 249 | 249 | 150 |  | 250 | 302 | 250 | 250 | 251 | 250 | 250 | 4147000
| United Jamalpur PPL | 94 | 94 | 94 | 94 | 94 | 94 | 95 | 95 | 95 | 95 | 94 | 70 | 78 | 70 | 70 | 70 | 70 | 70 |  | 95 | 96 | 96 | 97 | 97 | 87 | 88 | 2115600
| Anwara United | 281 | 281 | 255 | 265 | 263 | 228 | 67 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 120 | 135 | 138 |  | 138 | 200 | 206 | 206 | 206 | 206 | 206 | 3582982
120 | Eastern Zone Total | 7766 | 7455 | 7265 | 7058 | 6921 | 6225.3 | 5690.7 | 5688.5 | 5673.7 | 5641.1 | 5675.7 | 5820.2 | 6159 | 5903.56 | 6034.32 | 6064.85 | 5744.67 | 5539.16 |  | 6635 | 7630 | 7484 | 7704 | 7701 | 7801 | 7792 | 156499701
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 32 | 16 | 0 | [9 empty] | 16 |  | 27 | 70 | 99 | 100 | 115 | 115 | 115 | 1193280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 23 | 23 | 23 | 23 | 14 | 0 | [11 empty] | 6 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 246240
| Khulna CCPP 225MW | 238 | 234 | 234 | 210 | 173 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3532337
129 | Labon Chora 105 MW | 72 | 72 | 72 | 72 | 72 | 72 | 17 | 17 | 17 | 17 | 0 | [6 empty] | 0 |  | 70 | 105 | 105 | 105 | 105 | 105 | 70 | 1051200
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 96 | 96 | 0 | [11 empty] | 16 |  | 24 | 64 | 110 | 110 | 110 | 110 | 110 | 1123488
136 | Barisal GT: Unit-1, 2 | [26 empty] | 11330
137 | Bhola Aggreko 95MW | 96 | 96 | 96 | 96 | 96 | 95 | 94 | 63 | 62 | 42 | 41 | 41 | 50 | 71 | 71 | 72 | 72 | 73 |  | 83 | 89 | 87 | 88 | 91 | 93 | 96 | 1880673
| Bhola CCPP 194MW | 171 | 172 | 172 | 172 | 172 | 172 | 171 | 171 | 171 | 171 | 171 | 172 | 142 | 143 | 143 | 143 | 143 | 143 |  | 143 | 143 | 143 | 143 | 120 | 120 | 120 | 2883000
140 | Bhola (Venture) 33MW | 37 | 36 | 37 | 36 | 33 | 29 | 24 | 25 | 22 | 14 | 22 | 24 | 24 | 24 | 26 | 26 | 24 | 24 |  | 32 | 36 | 32 | 35 | 33 | 34 | 38 | 673452
141 | Bangla Trak Noapara | 100 | 100 | 80 | 0 | [15 empty] | 6 | 90 | 95 | 100 | 100 | 100 | 100 | 843840
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 0 | [11 empty] | 0 | [8 empty] | 222000
143 | Gopalganj Peaking | 50 | 50 | 50 | 0 | [8 empty] | 8 | 8 | 8 | 12 | 20 | 35 |  | 60 | 77 | 70 | 62 | 62 | 45 | 40 | 571648
144 | Bheramara GT-1,2,3 | 28 | 28 | 0 | [16 empty] | 14 | 30 | 30 | 30 | 29 | 29 | 29 | 202600
145 | Madhumati Power Plant | 104 | 104 | 104 | 104 | 104 | 104 | 24 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 16 | 16 |  | 16 | 89 | 89 | 89 | 89 | 91 | 106 | 1463616
146 | Bheramara HVDC | 935 | 931 | 931 | 931 | 931 | 931 | 931 | 931 | 931 | 932 | 932 | 931 | 932 | 931 | 931 | 932 | 931 | 931 |  | 932 | 932 | 931 | 931 | 929 | 930 | 930 | 22348364
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 64 | 64 | 64 | 63 | 63 | 63 | 62 | 66 | 64 | 63 | 64 | 63 | 65 | 65 | 65 | 65 | 65 | 63 |  | 64 | 63 | 63 | 63 | 63 | 61 | 63 | 1535564
152 | Barapukuria Unit-3 | 240 | 240 | 240 | 240 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 240 | 240 |  | 240 | 240 | 240 | 240 | 239 | 240 | 239 | 5822500
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 60 | 60 | 55 | 55 | 55 | 55 | 55 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1375000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 42 | 42 | 42 | 42 | 42 | 0 | [13 empty] | 20 | 50 | 50 | 50 | 50 | 50 | 34 | 473920
157 | Sirajgonj Unit-1 225MW (Gas) | 186 | 194 | 191 | 191 | 187 | 181 | 186 | 185 | 167 | 155 | 182 | 175 | 194 | 181 | 200 | 191 | 178 | 156 |  | 160 | 178 | 179 | 194 | 191 | 194 | 195 | 4663309
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 182 | 190 | 187 | 187 | 183 | 178 | 181 | 179 | 161 | 146 | 175 | 181 | 186 | 177 | 199 | 188 | 175 | 146 |  | 152 | 170 | 174 | 191 | 188 | 191 | 190 | 4502591
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 199 | 207 | 209 | 209 | 206 | 195 | 195 | 196 | 174 | 163 | 186 | 182 | 206 | 185 | 195 | 205 | 202 | 177 |  | 177 | 200 | 194 | 207 | 209 | 208 | 203 | 4904636
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 380 | 380 | 380 | 380 | 380 | 300 | 300 | 270 | 270 | 270 | 270 | 300 | 350 | 270 | 350 | 320 | 320 | 280 |  | 320 | 300 | 280 | 330 | 330 | 330 | 360 | 7751000
161 | Bera Peaking | 26 | 26 | 26 | 26 | 0 | [12 empty] | 0 |  | 18 | 27 | 26 | 26 | 26 | 17 | 0 | 215279
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 18 | 18 | 22 | 18 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504480
163 | Bogra (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 10 | 10 | 10 |  | 14 | 14 | 12 | 14 | 14 | 13 | 13 | 258336
164 | Ullapara (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 203688
165 | Amnura 50MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 |  | 33 | 33 | 33 | 33 | 6 | 6 | 6 | 231670
166 | Katakhali (Northern) | 43 | 16 | 16 | 43 | 24 | 0 | [14 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 192470
167 | Katakhali Peaking | 44 | 44 | 44 | 0 | [13 empty] | 0 |  | 0 | 13 | 39 | 37 | 37 | 37 | 37 | 305700
168 | Santahar Peaking | 28 | 28 | 28 | 0 | [15 empty] | 30 | 30 | 29 | 29 | 28 | 28 | 28 | 255025
169 | Rajlanka 52 MW | 50 | 50 | 50 | 50 | 50 | 0 | [11 empty] | 0 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 324480
170 | Chapainawabganj-100 MW | 90 | 90 | 90 | 90 | 90 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 39 |  | 95 | 95 | 95 | 95 | 95 | 90 | 90 | 1799750
171 | Paramount Baghabari
172 | Confidence Bogura-2 (CPBL) | 108 | 108 | 108 | 108 | 108 | 53 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 17 |  | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 1003488
173 | Rangpur GT | 17 | 0 | [15 empty] | 0 |  | 17 | 16 | 16 | 17 | 17 | 17 | 16 | 115000
175 | Saidpur GT | 16 | 16 | 0 | [14 empty] | 0 |  | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 133000
176 | Confidence Rangpur | 12 | 12 | 12 | 13 | 0 | 12 | 12 | 11 | 11 | 11 | 10 | 15 | 17 | 7 | 16 | 16 | 2 | 16 |  | 22 | 18 | 27 | 23 | 20 | 23 | 23 | 465000
177
178
178 | Western Zone Total | 3956 | 3928 | 3861 | 3644 | 3525 | 2943 | 2726 | 2643 | 2558 | 2487 | 2561 | 2596 | 2684 | 2603 | 2758 | 2723 | 2653 | 2614 | 0 | 3045 | 3495 | 3572 | 3665 | 3619 | 3600 | 3574 | 75282954