## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-02-22 | Tuesday
|  |  | Date (day): | 2022-02-22 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11537.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12170 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-02-21 | 2022-02-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 320 | 320 | 320 | 45 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 34 | 182 | 340 | 350 | 10
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 23 | 12 | 30 |  | 70 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 64 | 90 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 25 | 30 | 30
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 165 | 270 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 3 | 35 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 103 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 78 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 37 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 1448 | 1828 | 2832 | 2933 | 1731 | 994
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 40 | 19 | 40 | 40 |  | 10 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 69 | 69 |  | 161 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 17 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 48 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 50 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 28 | 40 | 8 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 71 | 97 | 90 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 130 | 210 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 17 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 111 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 538 | 697 | 1301 | 1304 | 180 | 897
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 184 | 221 | 221
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 280 | 340 | 350 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 275 | 320 | 320 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 6 | 6 | 6 | 6 | 39 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 15 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 108 | 147 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 124 | 124 | 125 | 125 |  | 38 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 21 | 17 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 94 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 51 | 98 | 98 |  | 16 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 8 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 5 | 0 | 115 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1373 | 1462 | 2086 | 2110 | 644 | 91
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 215 | 160 | 150 | 52 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 154 | 200 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 76 | 55 | 110 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 467 | 514 | 565.6 | 509 | 52 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 260 | 270 | 270 |  | 60 | Machine problem
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 48 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 5 | 5 |  | 6 | Engine problem
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 67 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 81 | 81
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 340 | 300 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1202 | 1308 | 1311 | 1411 | 73 | 894
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 717 | 714 | 729 | 729
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 19 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 10 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 100 | 87 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 911 | 830 | 1014 | 1334 | 410 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 26 | 25 | 30
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 91 | 91 | 91 | 104 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 360 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 187 | 226 | 220 | 220
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 605 | 714 | 1127 | 1232 | 188 | 0
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 2 | 0 | 40 | 43 |  | 9 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40 |  | 31 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 20 | 8 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 37 |  | 13 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 161 | 167 | 220 | 220
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 298 | 300 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 29 | 0 | 30 | 30 |  | 20 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 50 | 100 | 90 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 107 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 869 | 909 | 980 | 1024 | 600 | 494
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 99 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 317 | 299 | 321 | 313 | 74 | 210
|  | Total |  |  |  |  | 22066 | 20985 | 7730 | 8561 | 11537.6 | 12170 | 3952 | 3671
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7376.0507 | 8169 | 11009.3043 | 11612.7473
| A. |  | 2022-02-21 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 8561 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6020 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8561 | MW
| 3 | Day peak Generation : |  |  | 7730 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8169 | MW
| 4 | Evening peak Generation : |  |  | 8561 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 175.2994 | MKWHr | By Solar | 1.3517 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 97.9076 | MKWHr |  | By Oil: | 42.3093 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.5071 | MKWHr |  | By Hydro: | 1.56 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3952 | MW | Dhaka | 2561 | 2561 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3671 | MW | Chittagong | 810 | 810 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7623 | MW | Khulna | 1049 | 1049 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 745.9 | MMCFD |  |  | Rajshahi | 1017 | 1017 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 93678926.374 | ii) Oil : | Taka | 261804852.96 | Comilla | 755 | 755 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 64308664 | Total | Taka | 419792443.334 | Mymensingh | 835 | 835 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.99 | MKWHr. | Sylhet | 300 | 300 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -262 | MW (E to W) at | 19:00 | hrs | Barisal | 240 | 240 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -308 | MW at | 8:00 | hrs | Rangpur | 602 | 602 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 27.8° C |  |  | Total | 8169 | 8169 |  | 0
| B. |  | 2022-02-22 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 28.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12170 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9100 | MW
| 4 | Reserve(Generation end) |  |  |  | 2070 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 206.8128 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5726 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.7331 | MKWHr. | ii) HVDC Flow at Peak Time |  | 714 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9306 | MKWHr. | iii) Maximum HVDC Flow : |  | 738 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.51 |  | (b) Today: | 91.27 |  | (c) Rule Curve: |  | 94.06
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-02-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 233 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 52 | 40 | 18 | 41 | 0 | 0 | 0 | 260 | 265 | 211 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 16 | 72 | 113 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 159 | 71 | 81 | 0 | 164 | 0 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 10 | 0 | 70 | 0 | 0 | 70 | 17 | 0 | 245 | 0 | 0 | 0 | 8 | 0 | 300 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 293 | 53 | 0 | 35 | 0 | 40 | 0 | 0 | 0 | 320 | 210 | 0 | 0 | 0 | 0 | 0 |  | 4727 | 2195 | 6922 | 2569 | 716 | 1634 | 0 | 1339 | 519 | 68 | 0 | 5 | 72 | 0 | 0 | 91.56
2:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 233 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 44 | 4 | 18 | 41 | 0 | 0 | 0 | 260 | 265 | 218 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 15 | 70 | 124 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 160 | 70 | 81 | 0 | 164 | 0 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 70 | 17 | 0 | 210 | 0 | 0 | 0 | 8 | 0 | 300 | 70 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 17 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 292 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 320 | 203 | 0 | 0 | 0 | 0 | 0 |  | 4538 | 1993 | 6531 | 2586 | 623 | 1626 | 0 | 1037 | 519 | 65 | 0 | 5 | 70 | 0 | 0 | 91.55
3:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 233 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 44 | 14 | 18 | 41 | 0 | 0 | 0 | 260 | 265 | 224 | 8 | 122 | 6 | 5 | 0 | 51 | 0 | 0 | 49 | 21 | 8 | 33 | 15 | 66 | 138 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 160 | 71 | 81 | 0 | 164 | 0 | 0 | 9 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 70 | 17 | 0 | 135 | 0 | 0 | 0 | 8 | 0 | 300 | 70 | 0 | 90 | 113 | 0 | 17 | 0 | 0 | 17 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 292 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 181 | 0 | 0 | 0 | 0 | 0 |  | 4404 | 1955 | 6359 | 2605 | 624 | 1612 | 0 | 867 | 519 | 66 | 0 | 0 | 66 | 0 | 0 | 91.54
4:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 233 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 31 | 22 | 33 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 44 | 31 | 18 | 0 | 0 | 0 | 0 | 260 | 265 | 226 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 0 | 15 | 66 | 139 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 159 | 70 | 81 | 0 | 164 | 0 | 0 | 9 | 300 | 5 | 5 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 34 | 17 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 240 | 35 | 0 | 90 | 69 | 0 | 17 | 0 | 0 | 17 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 282 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 182 | 0 | 0 | 0 | 0 | 0 |  | 4116 | 1920 | 6036 | 2504 | 624 | 1572 | 0 | 683 | 520 | 67 | 0 | 0 | 66 | 0 | 0 | 91.53
5:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 233 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 28 | 22 | 33 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 44 | 0 | 18 | 0 | 0 | 0 | 0 | 260 | 265 | 228 | 8 | 122 | 6 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 33 | 15 | 66 | 139 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 160 | 70 | 81 | 0 | 164 | 0 | 0 | 9 | 280 | 5 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 34 | 17 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 230 | 35 | 0 | 90 | 75 | 0 | 17 | 0 | 0 | 17 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 282 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 320 | 182 | 0 | 0 | 0 | 0 | 0 |  | 4098 | 1922 | 6020 | 2525 | 623 | 1551 | 0 | 670 | 520 | 65 | 0 | 0 | 66 | 0 | 0 | 91.52
6:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 195 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 14 | 22 | 25 | 28 | 22 | 33 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 44 | 1 | 18 | 0 | 0 | 0 | 0 | 260 | 265 | 183 | 8 | 122 | 6 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 33 | 15 | 68 | 139 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 158 | 70 | 81 | 0 | 164 | 0 | 0 | 9 | 270 | 5 | 5 | 0 | 25 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 20 | 0 | 0 | 45 | 17 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 200 | 52 | 0 | 154 | 112 | 0 | 17 | 0 | 0 | 28 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 282 | 17 | 0 | 30 | 0 | 34 | 0 | 0 | 0 | 310 | 180 | 0 | 0 | 0 | 0 | 0 |  | 4199 | 1989 | 6188 | 2448 | 623 | 1502 | 0 | 969 | 510 | 68 | 0 | 0 | 68 | 0 | 0 | 91.51
7:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 192 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 28 | 22 | 33 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 34 | 15 | 18 | 0 | 0 | 0 | 0 | 280 | 285 | 199 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 25 | 19 | 8 | 33 | 15 | 66 | 139 | 0 | 20 | 0 | 30 | 42 | 48 | 0 | 110 | 160 | 40 | 81 | 0 | 164 | 0 | 0 | 9 | 280 | 5 | 5 | 0 | 50 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 65 | 0 | 0 | 0 | 8 | 0 | 240 | 104 | 2 | 162 | 112 | 0 | 17 | 2 | 0 | 36 |  | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 284 | 35 | 0 | 35 | 0 | 44 | 0 | 0 | 0 | 310 | 185 | 0 | 0 | 0 | 4 | 0 |  | 4376 | 2141 | 6517 | 2519 | 718 | 1515 | 0 | 1113 | 510 | 68 | 0 | 0 | 66 | 8 | 0 | 91.5
8:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 235 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 29 | 15 | 18 | 0 | 0 | 0 | 0 | 340 | 270 | 234 | 8 | 122 | 6 | 5 | 0 | 51 | 0 | 0 | 27 | 19 | 8 | 33 | 15 | 68 | 139 | 0 | 20 | 0 | 30 | 42 | 45 | 0 | 110 | 159 | 71 | 81 | 0 | 138 | 0 | 0 | 9 | 300 | 5 | 5 | 0 | 84 | 0 | 0 | 154 | 0 | 0 | 3 | 10 | 0 | 55 | 0 | 10 | 70 | 0 | 1 | 85 | 0 | 0 | 0 | 8 | 0 | 260 | 104 | 9 | 162 | 113 | 0 | 17 | 5 | 0 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 149 | 0 | 8 | 0 | 0 | 0 | 281 | 53 | 0 | 75 | 0 | 106 | 0 | 0 | 25 | 320 | 190 | 0 | 0 | 0 | 27 | 0 |  | 4761 | 2338 | 7099 | 2632 | 717 | 1584 | 0 | 1473 | 520 | 60 | 0 | 0 | 68 | 45 | 0 | 91.49
9:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 214 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 50 | 18 | 18 | 0 | 0 | 0 | 0 | 280 | 290 | 194 | 8 | 124 | 6 | 5 | 0 | 43 | 0 | 0 | 50 | 19 | 8 | 33 | 15 | 72 | 139 | 0 | 20 | 1 | 30 | 42 | 45 | 0 | 110 | 160 | 68 | 81 | 0 | 35 | 0 | 0 | 9 | 280 | 5 | 5 | 0 | 115 | 0 | 0 | 192 | 0 | 0 | 6 | 10 | 0 | 60 | 0 | 29 | 70 | 0 | 2 | 100 | 0 | 0 | 0 | 8 | 0 | 320 | 104 | 27 | 162 | 113 | 0 | 17 | 18 | 0 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 156 | 0 | 11 | 0 | 0 | 0 | 283 | 70 | 0 | 111 | 0 | 106 | 0 | 1 | 45 | 300 | 187 | 0 | 0 | 2 | 53 | 0 |  | 4792 | 2429 | 7221 | 2516 | 717 | 1537 | 0 | 1701 | 500 | 68 | 0 | 0 | 72 | 110 | 0 | 91.48
10:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 34 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 70 | 19 | 18 | 21 | 0 | 0 | 0 | 260 | 270 | 183 | 8 | 122 | 6 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 25 | 15 | 72 | 139 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 161 | 40 | 81 | 0 | 0 | 0 | 0 | 9 | 280 | 16 | 5 | 0 | 144 | 0 | 0 | 192 | 0 | 0 | 0 | 10 | 14 | 83 | 0 | 75 | 90 | 15 | 4 | 130 | 0 | 13 | 17 | 8 | 0 | 350 | 104 | 39 | 162 | 113 | 0 | 17 | 27 | 0 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 8 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 0 | 0 | 285 | 90 | 0 | 112 | 0 | 109 | 0 | 3 | 113 | 290 | 190 | 0 | 0 | 4 | 74 | 0 |  | 4803 | 2589 | 7392 | 2439 | 717 | 1381 | 0 | 2041 | 490 | 60 | 0 | 39 | 72 | 153 | 0 | 91.47
11:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 34 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 72 | 30 | 0 | 36 | 0 | 0 | 0 | 260 | 270 | 184 | 8 | 125 | 6 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 33 | 15 | 78 | 139 | 0 | 20 | 2 | 30 | 42 | 42 | 0 | 110 | 162 | 40 | 81 | 0 | 0 | 0 | 0 | 9 | 275 | 16 | 5 | 0 | 160 | 0 | 0 | 150 | 0 | 0 | 6 | 10 | 17 | 100 | 0 | 75 | 90 | 17 | 4 | 130 | 0 | 17 | 17 | 0 | 0 | 350 | 104 | 46 | 162 | 113 | 0 | 17 | 31 | 18 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 52 | 8 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 162 | 0 | 11 | 0 | 0 | 0 | 293 | 90 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 290 | 169 | 0 | 0 | 5 | 88 | 0 |  | 4845 | 2616 | 7461 | 2439 | 717 | 1372 | 0 | 2059 | 490 | 62 | 0 | 58 | 78 | 186 | 0 | 91.46
12:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 34 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 0 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 71 | 40 | 18 | 28 | 0 | 0 | 0 | 295 | 305 | 206 | 8 | 124 | 6 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 33 | 15 | 84 | 152 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 160 | 64 | 81 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 5 | 0 | 165 | 0 | 0 | 154 | 0 | 3 | 19 | 10 | 21 | 108 | 0 | 76 | 90 | 17 | 5 | 130 | 0 | 17 | 17 | 0 | 0 | 350 | 104 | 41 | 162 | 113 | 0 | 17 | 33 | 5 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 50 | 0 | 20 | 0 | 52 | 29 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 161 | 0 | 11 | 0 | 0 | 0 | 298 | 100 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 300 | 187 | 0 | 0 | 5 | 94 | 0 |  | 5028 | 2702 | 7730 | 2557 | 717 | 1408 | 0 | 2110 | 500 | 70 | 0 | 81 | 84 | 203 | 0 | 91.45
13:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 31 |  | 0 | 225 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 81 | 40 | 18 | 36 | 0 | 0 | 0 | 260 | 270 | 184 | 8 | 125 | 6 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 0 | 25 | 16 | 86 | 155 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 161 | 66 | 84 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 218 | 0 | 0 | 172 | 0 | 32 | 19 | 30 | 47 | 127 | 0 | 113 | 105 | 30 | 5 | 170 | 0 | 17 | 52 | 0 | 0 | 400 | 72 | 41 | 162 | 113 | 0 | 0 | 32 | 24 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 42 | 0 | 55 | 0 | 43 | 0 | 52 | 30 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 155 | 0 | 11 | 0 | 0 | 0 | 338 | 70 | 0 | 70 | 0 | 113 | 0 | 4 | 70 | 290 | 225 | 0 | 0 | 3 | 92 | 0 |  | 5284 | 2717 | 8001 | 2526 | 717 | 1489 | 0 | 2304 | 490 | 64 | 0 | 127 | 86 | 198 | 0 | 91.44
14:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 31 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 85 | 40 | 18 | 36 | 0 | 0 | 0 | 260 | 270 | 185 | 8 | 123 | 6 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 0 | 33 | 8 | 90 | 155 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 159 | 40 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 245 | 0 | 0 | 172 | 0 | 30 | 17 | 10 | 34 | 135 | 0 | 113 | 105 | 34 | 4 | 170 | 0 | 17 | 34 | 3 | 0 | 350 | 70 | 35 | 162 | 113 | 0 | 14 | 30 | 25 | 38 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 42 | 0 | 57 | 0 | 43 | 0 | 52 | 28 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 154 | 0 | 11 | 0 | 0 | 0 | 320 | 70 | 0 | 70 | 0 | 113 | 0 | 3 | 70 | 300 | 192 | 0 | 0 | 5 | 84 | 0 |  | 5206 | 2667 | 7873 | 2446 | 717 | 1447 | 0 | 2305 | 500 | 61 | 0 | 127 | 90 | 180 | 0 | 91.43
15:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 31 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 20 | 25 | 33 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 70 | 0 | 18 | 20 | 0 | 0 | 0 | 280 | 270 | 183 | 8 | 123 | 6 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 0 | 17 | 20 | 82 | 160 | 0 | 20 | 2 | 30 | 42 | 48 | 0 | 110 | 160 | 40 | 84 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 195 | 0 | 0 | 140 | 0 | 17 | 14 | 10 | 17 | 135 | 0 | 24 | 70 | 17 | 3 | 155 | 0 | 17 | 17 | 8 | 0 | 350 | 70 | 26 | 108 | 113 | 0 | 17 | 23 | 0 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 42 | 0 | 57 | 0 | 8 | 0 | 24 | 29 | 19 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 156 | 0 | 11 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 80 | 0 | 3 | 35 | 290 | 200 | 0 | 0 | 4 | 64 | 0 |  | 4684 | 2426 | 7110 | 2458 | 717 | 1431 | 0 | 1601 | 489 | 65 | 0 | 128 | 82 | 139 | 0 | 91.42
16:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 85 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 63 | 9 | 18 | 42 | 0 | 0 | 0 | 280 | 270 | 184 | 8 | 122 | 6 | 15 | 0 | 43 | 0 | 0 | 25 | 21 | 0 | 17 | 18 | 78 | 160 | 0 | 22 | 1 | 30 | 42 | 48 | 0 | 110 | 160 | 40 | 30 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 195 | 0 | 0 | 140 | 0 | 17 | 9 | 10 | 17 | 80 | 0 | 24 | 35 | 17 | 2 | 155 | 0 | 17 | 17 | 8 | 0 | 300 | 35 | 18 | 108 | 113 | 0 | 17 | 15 | 0 | 37 |  | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 42 | 0 | 57 | 0 | 8 | 0 | 24 | 29 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 157 | 0 | 11 | 0 | 0 | 0 | 331 | 17 | 0 | 35 | 0 | 54 | 0 | 1 | 35 | 300 | 167 | 0 | 0 | 2 | 42 | 0 |  | 4509 | 2322 | 6831 | 2419 | 670 | 1452 | 0 | 1425 | 500 | 65 | 0 | 132 | 78 | 90 | 0 | 91.41
17:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 145 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 61 | 24 | 18 | 42 | 0 | 0 | 0 | 280 | 270 | 184 | 8 | 124 | 6 | 15 | 0 | 43 | 0 | 0 | 25 | 21 | 0 | 33 | 18 | 78 | 160 | 0 | 22 | 0 | 30 | 42 | 14 | 0 | 110 | 176 | 40 | 30 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 195 | 0 | 0 | 100 | 0 | 17 | 2 | 10 | 17 | 80 | 0 | 24 | 35 | 17 | 1 | 100 | 0 | 17 | 17 | 8 | 0 | 300 | 35 | 7 | 108 | 70 | 0 | 17 | 5 | 0 | 41 |  | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 42 | 0 | 57 | 0 | 8 | 0 | 8 | 29 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 0 | 0 | 282 | 17 | 0 | 35 | 0 | 54 | 0 | 0 | 35 | 300 | 167 | 0 | 0 | 0 | 15 | 0 |  | 4413 | 2230 | 6643 | 2455 | 670 | 1420 | 0 | 1288 | 500 | 70 | 0 | 132 | 78 | 30 | 0 | 91.4
18:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 145 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 16 | 2 | 0 | 0 | 0 | 54 | 35 | 36 | 19 | 25 | 18 | 25 | 33 | 8 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 50 | 0 | 73 | 19 | 18 | 40 | 0 | 0 | 0 | 280 | 270 | 184 | 8 | 122 | 6 | 15 | 0 | 51 | 0 | 14 | 29 | 21 | 0 | 33 | 18 | 100 | 190 | 0 | 22 | 0 | 30 | 42 | 14 | 0 | 110 | 182 | 40 | 30 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 224 | 0 | 0 | 108 | 0 | 18 | 0 | 28 | 17 | 97 | 0 | 28 | 43 | 17 | 0 | 150 | 0 | 17 | 17 | 15 | 0 | 300 | 37 | 0 | 110 | 71 | 0 | 17 | 0 | 0 | 55 |  | 738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 42 | 4 | 98 | 0 | 8 | 22 | 16 | 29 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 161 | 0 | 11 | 0 | 0 | 0 | 282 | 35 | 0 | 37 | 0 | 80 | 0 | 0 | 70 | 310 | 165 | 0 | 0 | 0 | 0 | 0 |  | 4806 | 2457 | 7263 | 2479 | 738 | 1447 | 0 | 1640 | 510 | 65 | 0 | 284 | 100 | 0 | 0 | 91.39
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 182 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 0 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 48 | 0 | 97 | 19 | 18 | 40 | 0 | 0 | 0 | 280 | 275 | 184 | 8 | 124 | 6 | 15 | 0 | 51 | 0 | 50 | 52 | 21 | 8 | 33 | 21 | 94 | 215 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 260 | 67 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 35 | 0 | 50 | 17 | 147 | 0 | 55 | 103 | 17 | 0 | 210 | 0 | 17 | 51 | 8 | 0 | 340 | 78 | 0 | 162 | 111 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 8 | 32 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 0 | 0 | 300 | 87 | 0 | 107 | 0 | 99 | 0 | 0 | 113 | 360 | 226 | 0 | 0 | 0 | 0 | 0 |  | 5809 | 2752 | 8561 | 2691 | 714 | 1648 | 0 | 2525 | 560 | 70 | 0 | 259 | 94 | 0 | 0 | 91.36
19:30 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 202 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 19 | 18 | 42 | 0 | 0 | 0 | 280 | 270 | 225 | 8 | 122 | 6 | 30 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 94 | 218 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 270 | 69 | 84 | 0 | 0 | 0 | 0 | 10 | 275 | 16 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 20 | 0 | 50 | 17 | 150 | 0 | 55 | 105 | 17 | 0 | 210 | 0 | 17 | 51 | 8 | 0 | 370 | 78 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 91 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 8 | 16 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 0 | 0 | 320 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 380 | 222 | 0 | 0 | 0 | 0 | 0 |  | 5765 | 2789 | 8554 | 2774 | 714 | 1685 | 0 | 2516 | 579 | 70 | 0 | 122 | 94 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 211 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 19 | 18 | 42 | 0 | 0 | 0 | 290 | 275 | 225 | 8 | 124 | 6 | 30 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 96 | 216 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 272 | 68 | 84 | 0 | 0 | 0 | 0 | 10 | 285 | 16 | 11 | 0 | 276 | 0 | 0 | 200 | 0 | 18 | 0 | 50 | 17 | 150 | 0 | 24 | 105 | 17 | 0 | 210 | 0 | 17 | 17 | 8 | 0 | 400 | 90 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 0 | 0 | 319 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 50 | 370 | 228 | 0 | 0 | 0 | 0 | 0 |  | 5735 | 2698 | 8433 | 2822 | 717 | 1711 | 0 | 2348 | 569 | 70 | 0 | 100 | 96 | 0 | 0 | 91.37
21:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 230 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 19 | 18 | 42 | 0 | 0 | 0 | 290 | 285 | 231 | 8 | 124 | 6 | 30 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 92 | 219 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 272 | 69 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 245 | 0 | 0 | 200 | 0 | 0 | 0 | 50 | 17 | 150 | 0 | 8 | 105 | 17 | 0 | 210 | 0 | 17 | 0 | 8 | 0 | 390 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 0 | 0 | 319 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 50 | 400 | 227 | 0 | 0 | 0 | 0 | 0 |  | 5687 | 2727 | 8414 | 2836 | 715 | 1744 | 0 | 2259 | 599 | 71 | 0 | 98 | 92 | 0 | 0 | 91.36
22:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 264 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 42 | 0 | 0 | 0 | 280 | 270 | 231 | 8 | 124 | 6 | 30 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 88 | 219 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 269 | 70 | 84 | 0 | 0 | 0 | 0 | 10 | 295 | 16 | 11 | 0 | 30 | 0 | 0 | 200 | 0 | 0 | 0 | 50 | 17 | 150 | 0 | 8 | 105 | 17 | 0 | 210 | 0 | 17 | 0 | 8 | 0 | 360 | 104 | 0 | 162 | 113 | 0 | 13 | 0 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 0 | 0 | 174 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 400 | 228 | 0 | 0 | 0 | 0 | 0 |  | 5412 | 2572 | 7984 | 2785 | 715 | 1629 | 0 | 1998 | 600 | 71 | 0 | 98 | 88 | 0 | 0 | 91.35
23:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 290 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 19 | 18 | 42 | 0 | 0 | 0 | 260 | 265 | 229 | 8 | 123 | 6 | 30 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 84 | 218 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 269 | 71 | 84 | 0 | 0 | 0 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 30 | 0 | 100 | 0 | 0 | 105 | 0 | 0 | 210 | 0 | 0 | 0 | 8 | 0 | 320 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 0 | 0 | 130 | 70 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 370 | 228 | 0 | 0 | 0 | 0 | 0 |  | 5160 | 2315 | 7475 | 2723 | 717 | 1610 | 0 | 1599 | 570 | 72 | 0 | 100 | 84 | 0 | 0 | 91.34
24:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 325 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 74 | 19 | 18 | 42 | 0 | 0 | 0 | 260 | 270 | 229 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 76 | 219 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 270 | 71 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 115 | 0 | 0 | 0 | 8 | 0 | 330 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 0 | 0 | 0 | 76 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 330 | 206 | 0 | 0 | 0 | 0 | 0 |  | 4829 | 2074 | 6903 | 2734 | 716 | 1538 | 0 | 1138 | 530 | 71 | 0 | 100 | 76 | 0 | 0 | 91.33
KWH | 0 | 0 | 0 | 0 | 7884191 | 0 | 0 | 0 | 4066000 |  | 0 | 5300500 | 0 | 0 | 0 | 140532 | 0 | 0 | 0 | 0 | 333504 | 17760 | 31771 | 0 | 0 | 0 | 1118520 | 887269 | 630412 | 464976 | 600000 | 674460 | 600900 | 825900 | 10560 | 0 | 1560000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 530400 | 0 | 68844 | 0 | 1600320 | 515520 | 426864 | 425280 | 0 | 0 | 0 | 6887600 | 6634000 | 4946000 | 200727 | 2938810 | 209736 | 304320 | 0 | 1130484 | 0 | 45328 | 1064054 | 485640 | 138420 | 717100 | 429650 | 1930560 | 3789120 | 0 | 474624 | 12850 | 715000 | 981032 | 1044000 | 0 | 2920581 | 4164000 | 1422816 | 1835520 | 0 | 0 | 0 | 0 | 230580 | 7073500 | 304000 | 153696 | 0 | 3126326 | 0 | 0 | 3340800 | 0 | 203330 | 93150 | 472320 | 312000 | 2114327 | 0 | 753600 | 1939200 | 395599 | 29400 | 3828873 | 0 | 233345 | 315780 | 196 | 0 | 7557700 | 2006400 | 293270 | 3564000 | 2574327 | 0 | 432720 | 221478 | 70080 | 981360 |  | 16733090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30240 | 12928 | 0 | 2165887 | 438200 | 0 | 0 | 0 | 0 | 271156 | 6890 | 1049720 | 0 | 161003 | 42901 | 1075877 | 210883 | 492480 | 0 | 201852 | 0 | 0 | 4866500 | 0 | 0 | 0 | 0 | 3949455 | 0 | 180269 | 0 | 0 | 0 | 6759490 | 1415520 | 0 | 1537824 | 0 | 1789276 | 0 | 27495 | 1045728 | 8640600 | 4762255 | 0 | 0 | 31860 | 642240 | 0 |  | 116757812 | 58541619 | 175299431 | 60743429 | 16733090 | 37164186 | 0 | 40552673 | 13507100 | 1560000 | 0 | 1756650 | 1930560 | 1351743 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8751452.01 | 0 | 0 | 0 | 4187980 |  | 0 | 5777545 | 0 | 0 | 0 | 1188900.72 | 0 | 0 | 0 | 0 | 3041556.48 | 174758.4 | 292928.62 | 0 | 0 | 0 | 8165196 | 6858589.37 | 6215862.32 | 348732 | 450000 | 0 | 0 | 0 | 102115.2 | 0 | 421200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 667786.8 | 0 | 13922784 | 4082918.4 | 537848.64 | 1263081.6 | 0 | 0 | 0 | 5096824 | 6634000 | 4550320 | 258937.83 | 3379631.5 | 237001.68 | 426048 | 0 | 1933127.64 | 0 | 457812.8 | 10161715.7 | 616762.8 | 103815 | 1254925 | 322237.5 | 14479200 | 4016467.2 | 0 | 602772.48 | 204829 | 1172600 | 1569651.2 | 1858320 | 0 | 3329462.34 | 4330560 | 2802947.52 | 3505843.2 | 0 | 0 | 0 | 0 | 470383.2 | 7144235 | 228000 | 116808.96 | 0 | 23635024.56 | 0 | 0 | 17372160 | 0 | 2000767.2 | 1088923.5 | 3849408 | 3385200 | 14906005.35 | 0 | 6872832 | 18325440 | 3445667.29 | 0 | 28946279.88 | 0 | 2051102.55 | 3151484.4 | 1679.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 96382598.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317217.6 | 135485.44 | 0 | 2447452.31 | 679210 | 0 | 0 | 0 | 0 | 2668175.04 | 70002.4 | 9290022 | 0 | 2176760.56 | 415710.69 | 10425248.13 | 2045565.1 | 945561.6 | 0 | 152801.964 | 0 | 0 | 26376430 | 0 | 0 | 0 | 0 | 5213280.6 | 0 | 270403.5 | 0 | 0 | 0 | 6691895.1 | 14778028.8 | 0 | 14593949.76 | 0 | 13884781.76 | 0 | 303819.75 | 7727929.92 | 37932234 | 0 | 0 | 0 | 0 | 0 | 0 |  | 276748449.56 | 255924564.424 | 532673013.984 | 54936892.364 | 96382598.4 | 38742034.01 | 0 | 245562316.69 | 64308664 | 421200 | 0 | 16242536.27 | 14479200 | 1597572.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 34 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 0 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 71 | 40 | 18 | 28 | 0 | 0 | 0 | 295 | 305 | 206 | 8 | 124 | 6 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 33 | 15 | 84 | 152 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 160 | 64 | 81 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 5 | 0 | 165 | 0 | 0 | 154 | 0 | 3 | 19 | 10 | 21 | 108 | 0 | 76 | 90 | 17 | 5 | 130 | 0 | 17 | 17 | 0 | 0 | 350 | 104 | 41 | 162 | 113 | 0 | 17 | 33 | 5 | 37 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 50 | 0 | 20 | 0 | 52 | 29 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 161 | 0 | 11 | 0 | 0 | 0 | 298 | 100 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 300 | 187 | 0 | 0 | 5 | 94 | 0 |  | 7730 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 182 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 0 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 48 | 0 | 97 | 19 | 18 | 40 | 0 | 0 | 0 | 280 | 275 | 184 | 8 | 124 | 6 | 15 | 0 | 51 | 0 | 50 | 52 | 21 | 8 | 33 | 21 | 94 | 215 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 260 | 67 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 270 | 0 | 0 | 200 | 0 | 35 | 0 | 50 | 17 | 147 | 0 | 55 | 103 | 17 | 0 | 210 | 0 | 17 | 51 | 8 | 0 | 340 | 78 | 0 | 162 | 111 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 8 | 32 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 0 | 0 | 300 | 87 | 0 | 107 | 0 | 99 | 0 | 0 | 113 | 360 | 226 | 0 | 0 | 0 | 0 | 0 |  | 8561 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 350 | 0 | 0 | 225 |  | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 30 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 69 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 96 | 40 | 18 | 30 | 0 | 0 | 0 | 350 | 320 | 221 | 8 | 125 | 6 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 11 | 33 | 21 | 163 | 150 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 270 | 66 | 81 | 0 | 0 | 0 | 0 | 10 | 330 | 16 | 5 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 8 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 55 |  | 729 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 91 | 30 | 110 | 0 | 0 | 0 | 43 | 40 | 100 | 0 | 43 | 37 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 100 | 0 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 340 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 90 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 69 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 40 | 18 | 8 | 0 | 0 | 0 | 340 | 320 | 221 | 8 | 125 | 6 | 5 | 0 | 51 | 0 | 50 | 52 | 21 | 8 | 33 | 20 | 138 | 160 | 0 | 22 | 1.6 | 30 | 42 | 51 | 0 | 110 | 270 | 66 | 81 | 0 | 0 | 0 | 0 | 10 | 330 | 16 | 5 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 0 | 110 | 105 | 105 | 5 | 300 | 54 | 110 | 98 | 8 | 100 | 300 | 104 | 50 | 162 | 116 | 0 | 17 | 30 | 115 | 55 |  | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 25 | 110 | 0 | 0 | 0 | 40 | 40 | 90 | 0 | 43 | 0 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 80 | 0 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 220 |  | 50 | 6 | 50
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 | 0 | 0 | 225 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 20 | 33 | 8 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 79 | 25 | 18 | 8 | 0 | 0 | 0 | 280 | 270 | 234 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 51 | 21 | 8 | 33 | 19 | 90 | 221 | 0 | 22 | 1 | 30 | 42 | 48 | 0 | 110 | 272 | 71 | 81 | 0 | 0 | 0 | 0 | 10 | 285 | 16 | 5 | 0 | 133 | 0 | 0 | 185 | 0 | 50 | 7 | 25 | 12 | 122 | 0 | 86 | 105 | 17 | 1 | 190 | 0 | 0 | 51 | 8 | 0 | 280 | 104 | 10 | 144 | 113 | 0 | 17 | 8 | 0 | 55 | 0 | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 181 | 0 | 80 | 0 | 0 | 0 | 0 | 84 | 0 | 107 | 0 | 107 | 0 | 1 | 108 | 300 | 135 | 0 | 0 | 0 | 18 | 0 | 0
199
| Minimum Generation |  | 6020 | 5:00
| Highest Generation |  | 8561 | 19:00
| Day Peak Generation |  | 7730 | 12:00
| Evening Peak Generation |  | 8561 | 19:00
| HVDC Max Flow |  | 738 | 18:00
| HVDC EvPeak Flow |  | 714 | 19:00
| Load factor L.F |  | 85.32%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-02-22
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-02-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7730 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5726 | MW
Evening Peak Generation : |  | 8561 | MW Hour : | 19:00 | Available Max Generation : |  | 12170 | MW
E.P. Demand (at gen end) : |  | 8561 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10100 | MW
Maximum Generation : |  | 8561 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2070 | MW
Total Gen. (MKWH) : |  | 175.2994 | System Load Factor : | 85.32% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -308 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-02-22
Actual : | 91.27 | Ft.(MSL) , | Rule curve : | 94.06 | Ft.( MSL )
Gas Consumed : | Total = | 745.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 93678926.374
: |  | Coal : | 64308664 | Oil : | 261804852.96 | Total : | 419792443.334
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3593.1845 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1219.3096 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1092.0027 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 986.5538 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 891.6241 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 719.5026 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 405.6202 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 185.3402 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 554.9003 |  |  | 0 | 0%
Total | 0 |  | 9648.038 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
|  |  |  | 2) Ghorasal-3,4,5 |  | 11) Siddhirganj peaking
|  |  |  | 3) Ashuganj-4,5 |  | 12) Meghnaghat 450 MW CCPP GT-2
4) Baghabari-71 MW & 100 MW
5) Siddhirganj 335 MW
6) Raozan unit- 1,2
7) Sirajganj Unit 1 & 3
8) Summit Bibiyana-3
9) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sylhet 225 MW ST was shut down at 08:55 due to air filter changing.
b) Sylhet 225 MW GT was shut down at 09:07 due to air filter changing.
c) Cox's Bazar 132/33 kV T-3 transformer was under shut down from 09:12 to 09:56 for R/H maintenance.
d) Barapukuria 132/33 kV T-4 transformer was under shut down from 08:07 to 09:58 for R/H maintenance.
e) Haripur 360 MW CCPP ST was synchronized at 15:47.
f) Shahjibazar 330 MW CCPP Gt-1 was synchronized at 16:45.
g) Sirajganj unit-4 was shut down at 00:12(22/2/2022) due to maintenance work.
h) Aminbazar-Kallyanpur 132 kV Ckt-1 was shut down at 07:40(22/2/2022) for A/M.
i) Ashuganj 230 kV Bus-1 was shut down at 07:33(22/2/2022) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-02-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 7884191 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 182 | 4066000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5300500 | GT-2 S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 140532 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 23 | 31771 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 464976 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 333504 | Low demand.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1118520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 17760 | High Voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 887269
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 630412
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1274460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 600900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 825900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 10560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 3126326 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 35 | 203330 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 103 | 1939200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 78 | 2006400 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3564000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 221478
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 981360
| Dhaka area Total |  |  |  | 5696 | 1828 | 35629349
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 93150
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 515520 | 33 kV feeder problem.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1560000 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 395599 | High Voltage
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 48 | 68844 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 472320 | High Voltage
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 426864 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 425280
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1600320 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29400
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 210 | 3828873 | High Voltage
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | High Voltage
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 233345 | High Voltage
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | High Voltage
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 111 | 2574327
| Chattogram area Total |  |  |  | 2382 | 697 | 12223842
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4946000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 6887600 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6634000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 6 | 209736 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 15 | 304320 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1130484
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 2114327
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 45328
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 124 | 2938810 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 312000 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 485640
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 138420 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 94 | 1930560
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 717100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1064054
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 429650 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 51 | 315780 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 196 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 432720 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 70080
| Cumilla Area Total |  |  |  | 2899 | 1462 | 31307532
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 215 | 3789120 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 474624
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12850
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3340800
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 55 | 753600 | High Voltage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 293270
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 530400
| Mymensingh Area Total |  |  |  | 622 | 514 | 9194664
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 981032 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2920581 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 260 | 4164000 | GT-1 S/D due to gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 1044000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 153696
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1422816
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1835520
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 304000 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7073500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 230580
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 7557700 | Machine problem
| Sylhet Area Total |  |  |  | 2377 | 1308 | 28402425
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 714 | 16733090
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 19 | 30240 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 10 | 12928
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 87 | 1415520 | Low demand.
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 642240
| Khulna Area Total |  |  |  | 2229 | 830 | 18834018
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 438200 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2165887 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 180269 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 360 | 8640600 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 226 | 4762255
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 714 | 16187211
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 271156
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 6890
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 161003 | Low demand.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 42901 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 167 | 3949455 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 300 | 6759490 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 210883 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 492480
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 201852 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1075877
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1049720
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 107 | 1537824 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1045728
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31860
| Rajshahi Area Total |  |  |  | 2129 | 909 | 16837119
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4866500 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 99 | 1789276 | Engine problem
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 27495
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 0 | On test
| Rangpur Area Total |  |  |  | 605 | 299 | 6683271
| Total |  |  |  | 20985 | 8561 | 175299431
| Eastern Grid Total |  |  |  | 13976 | 5809 | 116757812
| Western Grid Total |  |  |  | 7009 | 2752 | 58541619
| National Grid Total |  |  |  | 20985 | 8561 | 175299431
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-02-21
(a) ENTIRE EASTERN GRID : |  | 5261 | MW | (b) ENTIRE WESTERN GRID : |  | 2908 | MW
i) Dhaka area |  | 2561 | MW | i) Khulna area |  | 1049 | MW
ii) Chittagong area |  | 810 | MW | ii) Rajshahi area |  | 1017 | MW
iii) Comilla area |  | 755 | MW | iii) Barisal area |  | 240 | MW
iv) Mymensingh area |  | 835 | MW | iv) Rangpur area |  | 602 | MW
v) Sylhet area |  | 300 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8169 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 72 | 12:00 | Valuka | 70 | 9:00 | Noapara | 30 | 19:00
Munsiganj | 56 | 21:00 | Tangail | 188 | 8:00 | Jessore | 79 | 18:30
Sonargaon | 54 | 21:00 | Mymensing | 184 | 13:00 | Benapol | 40 | 19:00
Bhulta | 171 | 1:00 | Kishoreganj | 102 | 19:30 | Jhenida(Old) | 81 | 19:00
Madanganj | 24 | 1:00 | Netrokona | 109 | 9:00 | Bottail | 78 | 19:00
Rahim steel | 8 | 1:00 | Jamalpur | 125 | 9:00 | G.K Project | 36 | 18:30
Ghorasal | 48 | 19:00 | Sherpur | 124 | 8:00 | Faridpur | 84 | 19:00
Narsingdi | 126 | 19:30 | Srimongal | 30 | 18:30 | Rajbari | 44 | 18:30
Haripur(SBU) | 89 | 1:00 | Shahjibazar | 77 | 19:00 | Madaripur | 69 | 21:00
Sreenagar | 25 | 22:00 | Fenchuganj | 27 | 19:30 | Sariatpur | 42 | 20:00
Shyampur | 156 | 0:00 | Kulawara | 28 | 19:00 | Gopalganj | 66 | 19:00
Shitalakhya | 70 | 12:00 | Sylhet | 89 | 18:00 | Bagerhat | 74 | 18:30
Matuail | 42 | 9:00 | Chatak | 13 | 18:00 | Mongla | 46 | 1:00
Char Saidpur | 36 | 6:00 | Sunamganj | 27 | 20:00 | Satkhira | 78 | 19:00
Ullon | 22 | 13:00 | Biani Bazar | 39 | 19:30 | Gallamari | 24 | 12:00
Hasnabad | 52 | 13:00 | Comilla (S) | 100 | 18:00 | Magura | 40 | 18:30
Magbazar | 62 | 13:00 | Comilla(N) | 85 | 19:00 | Norail | 36 | 19:00
Maniknagar | 38 | 18:30 | Chandpur | 47 | 20:00 | Chuadanga | 62 | 18:30
Bangabhaban | 3 | 1:00 | Feni | 79 | 21:00 | Barisal(N) | 26 | 21:00
Motijheel | 13 | 13:00 | Chowmuhani | 130 | 20:00 | Barisal (S) | 73 | 21:00
Narinda | 30 | 13:00 | Ashuganj | 23 | 12:00 | Patuakhali | 80 | 21:00
Kazla | 60 | 19:30 | Daudkandi | 86 | 20:00 | Bhandaria | 36 | 19:30
Dhanmondi | 85 | 13:00 | B.Baria | 104 | 18:30 | Borguna | 12 | 20:00
Lalbag | 53 | 1:00 | Ramganj | 54 | 21:00 | Borhan Uddin | 29 | 21:00
Madartek | 46 | 13:00 | Chaddagram | 30 | 18:00 | Ishurdi | 45 | 18:30
Dhaka University | 11 | 12:00 | PHP | 8 | 10:00 | Ruppur Paromanobik | 2 | 6:00
Aftabnagar | 18 | 13:00 | Kochua | 36 | 18:30 | Natore | 100 | 13:00
Fatullah | 36 | 1:00 | Madunaghat | 32 | 12:00 | Bogra | 114 | 19:30
Nawabganj | 31 | 21:00 | Hathazari | 61 | 19:00 | Naogaon | 100 | 13:00
Keraniganj | 36 | 14:00 | Khulshi | 108 | 23:00 | Rajshahi | 81 | 19:00
Banani | 28 | 14:00 | Halishahar | 52 | 18:00 | Rajshahi New | 30 | 19:00
Mirpur | 70 | 13:00 | Baraulia | 98 | 4:00 | C.Nawabganj | 52 | 13:00
Kalyanpur | 54 | 13:00 | Sikalbaha | 19 | 1:00 | Amnura | 43 | 19:30
Gulshan | 48 | 13:00 | Dohazari | 70 | 19:00 | Pabna | 65 | 19:00
Uttara | 38 | 13:00 | Cox'sbazar | 77 | 17:00 | Shahjadpur | 82 | 9:00
Uttara New | 18 | 13:00 | Chandraghona | 22 | 18:00 | Serajganj | 87 | 18:30
Kamrangirchar | 41 | 12:00 | Kaptai | 4 | 19:00 | Niyamatpur | 83 | 13:00
Savar | 93 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 51 | 8:00
Bhasantec | 76 | 13:00 | Bakulia | 69 | 18:30 | Sherpur(Bogura) | 48 | 19:00
Agargaon | 44 | 14:00 | Julda | 21 | 1:00 | Mohastangor | 46 | 18:30
Satmosjid | 65 | 14:00 | TK chemical | 24 | 13:00 | Bhangura | 26 | 18:30
Old Tongi | 69 | 3:00 | Modern Steel | 0 | 1:00 | Rangpur | 98 | 14:00
Kabirpur | 145 | 1:00 | Shahmirpur | 30 | 1:00 | Lalmonirhat | 36 | 8:00
Manikgonj | 55 | 19:00 | Khagrachhari | 20 | 18:30 | Saidpur | 85 | 9:00
Joydevpur | 97 | 1:00 | Matarbari | 27 | 18:00 | Purbasadipur | 105 | 12:00
New Tongi | 40 | 1:00 | Baroiar Hat | 42 | 13:00 | Thakurgaon | 63 | 19:00
Kodda | 116 | 1:00 | Rangamati | 10 | 18:30 | Palashbari | 95 | 8:00
Dhamrai | 56 | 19:00 | Abul Khair 230 | 46 | 19:00 | Barapukuria | 48 | 12:00
Rajendrapur | 62 | 1:00 | BSRM | 13 | 9:00 | Panchagar | 41 | 19:00
Bashundara | 85 | 13:00 | GPH Ispat | 149 | 2:00 | Joldhaka | 52 | 9:00
Purbachal | 20 | 19:00 | Agrabad | 91 | 3:00 | Kurigram | 51 | 8:00
Tongi Millgate | 24 | 1:00 | Goalpara | 18 | 13:00 | Mithapukur | 27 | 8:00
Bashundhara Cement |  |  | Central S/S | 72 | 18:30
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-02-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 422 | 5:00 | 414 | 18:00 | Kaliakoir | 417 | 0.125 | 409 | 0.5
| Bheramara | 404 | 5:00 | 394 | 11:00 | Bhulta | 420 | 0.20833 | 410 | 0.5
| Ashuganj(N) | 423 | 8:00 | 412 | 12:00 | Gopalganj | 417 | 0.625 | 409 | 0.54167
| Payra | 417 | 5:00 | 412 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 246 | 7:00 | 244 | 1:00 | Hathazari | 242 | 6:00 | 234 | 12:00
| Ishurdi | 243 | 1:00 | 231 | 9:00 | Megnaghat | 246 | 8:00 | 242 | 5:00
| Ashuganj | 248 | 6:00 | 243 | 11:00 | Fenchuganj | 248 | 6:00 | 244 | 11:00
| Serajganj | 241 | 1:00 | 233 | 9:00 | Siddhirganj | 244 | 5:00 | 238 | 15:00
| Baghabari | 240 | 4:00 | 234 | 9:00 | Maniknagar | 242 | 5:00 | 236 | 12:00
| Barapukuria | 236 | 6:00 | 228 | 9:00 | Agargaon | 244 | 5:00 | 238 | 12:00
| Bogra | 239 | 4:00 | 224 | 9:00 | Barisal | 246 | 8:00 | 241 | 13:00
| Rajshahi | 242 | 18:00 | 227 | 9:00 | Bhola 225 MW | 247 | 2:00 | 244 | 18:30
| Khulna South | 245 | 5:00 | 229 | 13:00 | AKSML | 243 | 8:00 | 233 | 12:00
| Rampura | 242 | 7:00 | 236 | 11:00 | BSRM | 244 | 10:00 | 236 | 12:00
| Haripur | 242 | 8:00 | 237 | 13:00 | Bibiyana | 250 | 18:00 | 243 | 9:00
| Hasnabad | 244 | 7:00 | 237 | 12:00 | Bhulta | 244 | 6:00 | 237 | 13:00
| Shyampur | 243 | 5:00 | 237 | 12:00 | Ashuganj (S) | 244 | 3:00 | 239 | 12:00
| Aminbazar | 244 | 1:00 | 241 | 2:00 | Kaliakoir | 244 | 5:00 | 238 | 12:00
| Tongi | 241 | 7:00 | 235 | 17:00 | GPH | 243 | 10:00 | 233 | 12:00
| Comilla (N) | 242 | 1:00 | 237 | 12:00 | Jhenaidah | 242 | 5:00 | 227 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 5:00 | 134 | 11:00 | PHP | 141 | 6:00 | 135 | 12:00
| Munsiganj | 140 | 8:00 | 135 | 12:00 | Kachua | 141 | 6:00 | 138 | 9:00
| Sonargaon | 140 | 8:00 | 135 | 12:00 | Madanhat | 142 | 2:00 | 138 | 11:00
| Bhulta | 133 | 4:00 | 128 | 11:00 | Hathazari | 143 | 18:00 | 137 | 12:00
| Madanganj | 139 | 8:00 | 134 | 12:00 | Khulshi | 140 | 1:00 | 135 | 12:00
| Rahim steel | 139 | 7:00 | 136 | 12:00 | Halishahar | 142 | 1:00 | 135 | 12:00
| Ghorasal | 143 | 1:00 | 142 | 13:00 | Baraulia | 142 | 3:00 | 133 | 12:00
| Narsingdi | 137 | 6:00 | 133 | 12:00 | Sikalbaha | 142 | 3:00 | 139 | 8:00
| Haripur(SBU) | 139 | 7:00 | 136 | 12:00 | Dohazari | 138 | 10:00 | 133 | 12:00
| Sreenagar | 137 | 1:00 | 134 | 12:00 | Cox'sbazar | 136 | 5:00 | 128 | 12:00
| Shyampur | 135 | 5:00 | 131 | 12:00 | Chandraghona | 142 | 3:00 | 137 | 12:00
| Shitalakhya | 140 | 8:00 | 136 | 12:00 | Kaptai | 142 | 1:00 | 140 | 7:00
| Matuail | 139 | 5:00 | 134 | 11:00 | A. Khaer Stl. | 141 | 1:00 | 136 | 12:00
| Char Saidpur | 140 | 6:00 | 135 | 12:00 | Bakulia | 141 | 1:00 | 136 | 12:00
| Ullon | 136 | 6:00 | 130 | 13:00 | Julda | 141 | 2:00 | 136 | 12:00
| Hasnabad | 140 | 9:00 | 136 | 16:00 | TK Chemical | 141 | 9:00 | 136 | 11:00
| Magbazar | 135 | 6:00 | 130 | 12:00 | Modern Steel | 141 | 1:00 | 138 | 15:00
| Maniknagar | 138 | 6:00 | 133 | 12:00 | Shahmirpur | 141 | 8:00 | 136 | 12:00
| Bangabhaban | 138 | 6:00 | 133 | 12:00 | Khagrachhari | 141 | 21:00 | 138 | 13:00
| Motijheel | 138 | 6:00 | 133 | 12:00 | Matarbari | 137 | 3:00 | 127 | 12:00
| Narinda | 138 | 6:00 | 133 | 12:00 | Baroiar Hat | 140 | 2:00 | 136 | 12:00
| Kazla | 138 | 6:00 | 133 | 12:00 | Rangamati | 141 | 1:00 | 136 | 12:00
| Dhanmondi | 139 | 5:00 | 135 | 12:00 | Agrabad | 141 | 23:00 | 134 | 11:00
| Lalbag | 138 | 5:00 | 134 | 12:00 | Goalpara S/S | 140 | 1:00 | 130 | 13:00
| Madartek | 135 | 5:00 | 130 | 12:00 | Khulna Central S/S | 139 | 1:00 | 130 | 13:00
| Dhaka University | 138 | 5:00 | 134 | 12:00 | Noapara | 139 | 3:00 | 130 | 13:00
| Aftabnagar | 135 | 5:00 | 131 | 13:00 | Jessore | 137 | 2:00 | 127 | 13:00
| Fatullah | 136 | 8:00 | 132 | 12:00 | Benapol | 137 | 1:00 | 127 | 13:00
| Nawabganj | 138 | 2:00 | 134 | 12:00 | Jhenida(Old) | 138 | 4:00 | 129 | 13:00
| Keraniganj | 138 | 5:00 | 134 | 12:00 | Bottail | 139 | 3:00 | 130 | 13:00
| Banani | 136 | 6:00 | 130 | 13:00 | G.K Project | 140 | 3:00 | 133 | 9:00
| Mirpur | 136 | 5:00 | 132 | 12:00 | Faridpur | 138 | 2:00 | 133 | 13:00
| Kalyanpur | 135 | 1:00 | 133 | 12:00 | Rajbari | 137 | 1:00 | 132 | 13:00
| Gulshan | 134 | 5:00 | 130 | 12:00 | Madaripur | 142 | 3:00 | 138 | 13:00
| Uttara | 140 | 18:00 | 136 | 12:00 | Shariyatpur S/S | 142 | 6:00 | 138 | 13:00
| Uttara New | 139 | 6:00 | 135 | 9:00 | Gopalganj | 143 | 4:00 | 137 | 13:00
| Kamrangirchar | 138 | 7:00 | 134 | 13:00 | Bagerhat | 138 | 3:00 | 130 | 15:00
| Savar | 138 | 4:00 | 133 | 13:00 | Mongla | 137 | 5:00 | 130 | 13:00
| Bhasantec | 136 | 5:00 | 131 | 12:00 | Satkhira | 139 | 3:00 | 128 | 13:00
| Agargaon | 136 | 5:00 | 132 | 12:00 | Gallamari | 142 | 5:00 | 136 | 19:00
| Satmosjid | 136 | 8:00 | 131 | 12:00 | Magura | 140 | 1:00 | 130 | 18:30
| Old Tongi | 140 | 7:00 | 136 | 17:00 | Narail | 138 | 1:00 | 129 | 13:00
| Kabirpur | 138 | 19:30 | 134 | 12:00 | Chuadanga | 137 | 4:00 | 125 | 13:00
| Manikgonj | 136 | 4:00 | 131 | 7:00 | Barisal(N) | 144 | 5:00 | 140 | 19:00
| Joydevpur | 145 | 8:00 | 141 | 12:00 | Barisal (S) | 143 | 1:00 | 139 | 21:00
| New Tongi | 140 | 18:00 | 136 | 13:00 | Patuakhali(S) | 138 | 3:00 | 135 | 13:00
| Kodda | 139 | 8:00 | 135 | 1:00 | Bhandaria | 143 | 6:00 | 138 | 13:00
| Dhamrai | 137 | 3:00 | 134 | 12:00 | Borguna | 146 | 7:00 | 140 | 19:00
| Rajendrapur | 140 | 18:00 | 133 | 5:00 | Jhenaidah(New) | 139 | 1:00 | 130 | 13:00
| Bashundara | 140 | 18:00 | 136 | 13:00 | Ishurdi | 140 | 5:00 | 133 | 9:00
| Purbachal | 138 | 18:00 | 131 | 17:00 | Ruppur Paromanobik | 138 | 3:00 | 133 | 13:00
| Tongi Millgate | 138 | 10:00 | 135 | 16:00 | Natore | 140 | 18:00 | 131 | 9:00
| Bashundhara Cement |  |  |  |  | Bogra | 139 | 20:00 | 132 | 13:00
| Valuka | 133 | 22:00 | 122 | 7:00 | Noagaon | 136 | 4:00 | 124 | 9:00
| Tangail | 137 | 23:00 | 130 | 7:00 | Rajshahi | 137 | 2:00 | 131 | 9:00
| Mymensing | 135 | 23:00 | 124 | 7:00 | Rajshahi New | 140 | 18:00 | 129 | 9:00
| Kishorganj | 136 | 23:00 | 129 | 12:00 | C.Nawabganj | 137 | 24:00 | 128 | 9:00
| Netrokona | 133 | 23:00 | 120 | 8:00 | Amnura | 138 | 18:00 | 126 | 9:00
| Jamalpur | 138 | 19:30 | 126 | 6:00 | Pabna | 140 | 5:00 | 133 | 12:00
| Sherpur | 137 | 10:00 | 125 | 7:00 | Shahjadpur | 144 | 2:00 | 135 | 13:00
| Srimongal | 142 | 24:00 | 138 | 11:00 | Serajganj | 140 | 4:00 | 130 | 7:00
| Shahjibazar | 139 | 22:00 | 136 | 1:00 | Niyamatpur | 135 | 3:00 | 120 | 9:00
| Fenchuganj | 141 | 1:00 | 138 | 11:00 | Joypurhat | 137 | 18:00 | 121 | 9:00
| Khulawara | 141 | 1:00 | 138 | 11:00 | Sherpur(Bogura) | 138 | 5:00 | 130 | 9:00
| Sylhet | 138 | 1:00 | 135 | 12:00 | Mohastangor | 139 | 5:00 | 129 | 9:00
| Chatak | 139 | 3:00 | 134 | 12:00 | Bhangura | 141 | 5:00 | 134 | 9:00
| Sunamganj | 138 | 23:00 | 133 | 11:00 | Rangpur | 134 | 3:00 | 123 | 9:00
| Biani Bazar | 138 | 1:00 | 134 | 14:00 | Lalmonirhat | 132 | 2:00 | 122 | 9:00
| Comilla(s) | 131 | 1:00 | 126 | 9:00 | Saidpur | 134 | 5:00 | 122 | 13:00
| Comilla(n) | 143 | 1:00 | 140 | 11:00 | Purbasadipur | 133 | 5:00 | 120 | 13:00
| Chandpur | 141 | 14:00 | 138 | 12:00 | Thakurgaon | 132 | 17:00 | 118 | 9:00
| Feni | 142 | 12:00 | 135 | 20:00 | Palashbari | 136 | 4:00 | 125 | 9:00
| Chowmuhani | 137 | 18:00 | 132 | 12:00 | Barapukuria | 136 | 6:00 | 128 | 13:00
| Ashuganj | 141 | 23:00 | 138 | 7:00 | Panchagar | 136 | 5:00 | 119 | 9:00
| Daudkandi | 141 | 5:00 | 136 | 12:00 | Joldhaka | 134 | 23:00 | 120 | 9:00
| B.Baria | 137 | 22:00 | 133 | 12:00 | Kurigram | 134 | 17:00 | 120 | 13:00
| Ramganj | 140 | 14:00 | 134 | 19:30 | Mithapukur | 138 | 22:00 | 128 | 9:00
| Chaddagram | 141 | 9:00 | 137 | 16:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-02-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 122 | 4829 | 2074 | 6903 |  |  |  | QF-LDC-11
0:30 | 84 | 4778 | 2134.5 | 6912.5 | Date: | 2022-02-21
1:00 | 46 | 4727 | 2195 | 6922
1:30 | 31 | 4632.5 | 2094 | 6726.5
2:00 | 16 | 4538 | 1993 | 6531
2:30 | 22 | 4471 | 1974 | 6445 | [5 empty] | Gen. at Eve. Peak | 8561 | 8561 MW (19:00 )
3:00 | 28 | 4404 | 1955 | 6359 | [6 empty] | 19:00
3:30 | 54 | 4260 | 1937.5 | 6197.5 | [5 empty] | Gen. at Day Peak | 7730 | 7730 MW (12:00 )
4:00 | 80 | 4116 | 1920 | 6036 | [6 empty] | 12:00
4:30 | 99 | 4107 | 1921 | 6028 | [5 empty] | Highest Generation | 8561
5:00 | 118 | 4098 | 1922 | 6020 | [6 empty] | 19:00
5:30 | 66 | 4148.5 | 1955.5 | 6104
6:00 | 14 | 4199 | 1989 | 6188
6:30 | 58 | 4287.5 | 2065 | 6352.5
7:00 | 102 | 4376 | 2141 | 6517
7:30 | 205 | 4568.5 | 2239.5 | 6808
8:00 | 308 | 4761 | 2338 | 7099
8:30 | 259 | 4776.5 | 2383.5 | 7160
9:00 | 210 | 4792 | 2429 | 7221
9:30 | 108 | 4797.5 | 2509 | 7306.5
10:00 | 6 | 4803 | 2589 | 7392
10:30 | 23 | 4824 | 2602.5 | 7426.5
11:00 | 40 | 4845 | 2616 | 7461
11:30 | 43 | 4936.5 | 2659 | 7595.5
12:00 | 46 | 5028 | 2702 | 7730
12:30 | 50 | 5156 | 2709.5 | 7865.5
13:00 | 54 | 5284 | 2717 | 8001
13:30 | 58 | 5245 | 2692 | 7937
14:00 | 62 | 5206 | 2667 | 7873
14:30 | 79 | 4945 | 2546.5 | 7491.5
15:00 | 96 | 4684 | 2426 | 7110
15:30 | 111 | 4596.5 | 2374 | 6970.5
16:00 | 126 | 4509 | 2322 | 6831
16:30 | 118 | 4461 | 2276 | 6737
17:00 | 110 | 4413 | 2230 | 6643
17:30 | 76 | 4609.5 | 2343.5 | 6953
18:00 | 42 | 4806 | 2457 | 7263
18:30 | 152 | 5307.5 | 2604.5 | 7912
19:00 | 262 | 5809 | 2752 | 8561
19:30 | 268 | 5765 | 2789 | 8554
20:00 | 250 | 5735 | 2698 | 8433 |  |  |  | Executive Engineer
20:30 | 196 | 5711 | 2712.5 | 8423.5 |  |  |  | Network Operation Division
21:00 | 142 | 5687 | 2727 | 8414
21:30 | 124 | 5549.5 | 2649.5 | 8199
22:00 | 106 | 5412 | 2572 | 7984 |  |  |  |  | Page 6 of 7
22:30 | 103 | 5286 | 2443.5 | 7729.5
23:00 | 100 | 5160 | 2315 | 7475
23:30 | 111 | 4994.5 | 2194.5 | 7189
24:00 | 122 | 4829 | 2074 | 6903
8561 MW (19:00 )
7730 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-02-21 |  | Energy |  | 175299431
[13 empty] | 2022-02-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2734 | 716 | 1538 | 0 | 1138 | 530 | 71 | 0 | 100 | 76 | 0 | 0
0:30 | 2651.5 | 716 | 1586 | 0 | 1238.5 | 524.5 | 69.5 | 0 | 52.5 | 74 | 0 | 0 | Date: | 2022-02-21
1:00 | 2569 | 716 | 1634 | 0 | 1339 | 519 | 68 | 0 | 5 | 72 | 0 | 0
1:30 | 2577.5 | 669.5 | 1630 | 0 | 1188 | 519 | 66.5 | 0 | 5 | 71 | 0 | 0 | [8 empty] | Total Energy | 175.2994 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 2586 | 623 | 1626 | 0 | 1037 | 519 | 65 | 0 | 5 | 70 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2595.5 | 623.5 | 1619 | 0 | 952 | 519 | 65.5 | 0 | 2.5 | 68 | 0 | 0 | [8 empty] | Energy Requirement | 175.2994
3:00 | 2605 | 624 | 1612 | 0 | 867 | 519 | 66 | 0 | 0 | 66 | 0 | 0
3:30 | 2554.5 | 624 | 1592 | 0 | 775 | 519.5 | 66.5 | 0 | 0 | 66 | 0 | 0 | [6 empty] | Shortage
4:00 | 2504 | 624 | 1572 | 0 | 683 | 520 | 67 | 0 | 0 | 66 | 0 | 0
4:30 | 2514.5 | 623.5 | 1561.5 | 0 | 676.5 | 520 | 66 | 0 | 0 | 66 | 0 | 0
5:00 | 2525 | 623 | 1551 | 0 | 670 | 520 | 65 | 0 | 0 | 66 | 0 | 0
5:30 | 2486.5 | 623 | 1526.5 | 0 | 819.5 | 515 | 66.5 | 0 | 0 | 67 | 0 | 0
6:00 | 2448 | 623 | 1502 | 0 | 969 | 510 | 68 | 0 | 0 | 68 | 0 | 0
6:30 | 2483.5 | 670.5 | 1508.5 | 0 | 1041 | 510 | 68 | 0 | 0 | 67 | 4 | 0 |  |  |  |  | Coal
7:00 | 2519 | 718 | 1515 | 0 | 1113 | 510 | 68 | 0 | 0 | 66 | 8 | 0
7:30 | 2575.5 | 717.5 | 1549.5 | 0 | 1293 | 515 | 64 | 0 | 0 | 67 | 26.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2632 | 717 | 1584 | 0 | 1473 | 520 | 60 | 0 | 0 | 68 | 45 | 0
8:30 | 2574 | 717 | 1560.5 | 0 | 1587 | 510 | 64 | 0 | 0 | 70 | 77.5 | 0
9:00 | 2516 | 717 | 1537 | 0 | 1701 | 500 | 68 | 0 | 0 | 72 | 110 | 0
9:30 | 2477.5 | 717 | 1459 | 0 | 1871 | 495 | 64 | 0 | 19.5 | 72 | 131.5 | 0
10:00 | 2439 | 717 | 1381 | 0 | 2041 | 490 | 60 | 0 | 39 | 72 | 153 | 0
10:30 | 2439 | 717 | 1376.5 | 0 | 2050 | 490 | 61 | 0 | 48.5 | 75 | 169.5 | 0
11:00 | 2439 | 717 | 1372 | 0 | 2059 | 490 | 62 | 0 | 58 | 78 | 186 | 0
11:30 | 2498 | 717 | 1390 | 0 | 2084.5 | 495 | 66 | 0 | 69.5 | 81 | 194.5 | 0
12:00 | 2557 | 717 | 1408 | 0 | 2110 | 500 | 70 | 0 | 81 | 84 | 203 | 0
12:30 | 2541.5 | 717 | 1448.5 | 0 | 2207 | 495 | 67 | 0 | 104 | 85 | 200.5 | 0
13:00 | 2526 | 717 | 1489 | 0 | 2304 | 490 | 64 | 0 | 127 | 86 | 198 | 0
13:30 | 2526 | 717 | 1489 | 0 | 2304 | 490 | 64 | 0 | 127 | 86 | 198 | 0
14:00 | 2526 | 717 | 1489 | 0 | 2304 | 490 | 64 | 0 | 127 | 86 | 198 | 0
14:30 | 2492 | 717 | 1460 | 0 | 1952.5 | 489.5 | 64.5 | 0 | 127.5 | 84 | 168.5 | 0
15:00 | 2458 | 717 | 1431 | 0 | 1601 | 489 | 65 | 0 | 128 | 82 | 139 | 0
15:30 | 2438.5 | 693.5 | 1441.5 | 0 | 1513 | 494.5 | 65 | 0 | 130 | 80 | 114.5 | 0
16:00 | 2419 | 670 | 1452 | 0 | 1425 | 500 | 65 | 0 | 132 | 78 | 90 | 0
16:30 | 2455 | 670 | 1436 | 0 | 1356.5 | 500 | 67.5 | 0 | 132 | 78 | 60 | 0
17:00 | 2455 | 670 | 1420 | 0 | 1288 | 500 | 70 | 0 | 132 | 78 | 30 | 0
17:30 | 2467 | 704 | 1433.5 | 0 | 1464 | 505 | 67.5 | 0 | 208 | 89 | 15 | 0
18:00 | 2479 | 738 | 1447 | 0 | 1640 | 510 | 65 | 0 | 284 | 100 | 0 | 0
18:30 | 2585 | 726 | 1547.5 | 0 | 2082.5 | 535 | 67.5 | 0 | 271.5 | 97 | 0 | 0
19:00 | 2691 | 714 | 1648 | 0 | 2525 | 560 | 70 | 0 | 259 | 94 | 0 | 0
19:30 | 2774 | 714 | 1685 | 0 | 2516 | 579 | 70 | 0 | 122 | 94 | 0 | 0
20:00 | 2822 | 717 | 1711 | 0 | 2348 | 569 | 70 | 0 | 100 | 96 | 0 | 0
20:30 | 2829 | 716 | 1727.5 | 0 | 2303.5 | 584 | 70.5 | 0 | 99 | 94 | 0 | 0
21:00 | 2836 | 715 | 1744 | 0 | 2259 | 599 | 71 | 0 | 98 | 92 | 0 | 0
21:30 | 2810.5 | 715 | 1686.5 | 0 | 2128.5 | 599.5 | 71 | 0 | 98 | 90 | 0 | 0
22:00 | 2785 | 715 | 1629 | 0 | 1998 | 600 | 71 | 0 | 98 | 88 | 0 | 0
22:30 | 2754 | 716 | 1619.5 | 0 | 1798.5 | 585 | 71.5 | 0 | 99 | 86 | 0 | 0
23:00 | 2723 | 717 | 1610 | 0 | 1599 | 570 | 72 | 0 | 100 | 84 | 0 | 0
23:30 | 2728.5 | 716.5 | 1574 | 0 | 1368.5 | 550 | 71.5 | 0 | 100 | 80 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 27.8° C
24:00 | 2734 | 716 | 1538 | 0 | 1138 | 530 | 71 | 0 | 100 | 76 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-02-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 68 | 65 | 66 | 67 | 65 | 68 | 68 | 60 | 68 | 60 | 62 | 70 | 64 | 61 | 65 | 65 | 70 | 65 |  | 70 | 70 | 70 | 71 | 71 | 72 | 71 | 1560000
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 3 | 6 |  | 6 | 19 | 19 | 17 | 14 | 9 | 2 | [9 empty] | 93150
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 50 |  | 48 | [6 empty] | 68844
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 15 | 17 | 17 | 30 | 34 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 395599
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 14 |  | 50 | [6 empty] | 45328
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [5 empty] | 25 | 50 | 84 | 115 | 144 | 160 | 165 | 218 | 245 | 195 | 195 | 195 | 224 |  | 270 | 270 | 276 | 245 | 30 |  |  | 3126326
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7884191
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 209736
33 | Ashuganj 225 MW CCPP | 211 | 218 | 224 | 226 | 228 | 183 | 199 | 234 | 194 | 183 | 184 | 206 | 184 | 185 | 183 | 184 | 184 | 184 |  | 184 | 225 | 225 | 231 | 231 | 229 | 229 | 4946000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 285 | 270 | 290 | 270 | 270 | 305 | 270 | 270 | 270 | 270 | 270 | 270 |  | 275 | 270 | 275 | 285 | 270 | 265 | 270 | 6634000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 280 | 340 | 280 | 260 | 260 | 295 | 260 | 260 | 280 | 280 | 280 | 280 |  | 280 | 280 | 290 | 290 | 280 | 260 | 260 | 6887600
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 |  | 15 | 30 | 30 | 30 | 30 | 30 | 5 | 304320
36 | Chandpur 150 MW CCPP | 124 | 124 | 122 | 124 | 122 | 122 | 124 | 122 | 124 | 122 | 125 | 124 | 125 | 123 | 123 | 122 | 124 | 122 |  | 124 | 122 | 124 | 124 | 124 | 123 | 124 | 2938810
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5300500
41 | Haripur 360MW CCPP(HPL) | 233 | 233 | 233 | 233 | 233 | 195 | 192 | 235 | 214 | 34 | 34 | 34 | 31 | 31 | 31 | 85 | 145 | 145 |  | 182 | 202 | 211 | 230 | 264 | 290 | 325 | 4066000
42 | RPCL 210MW CCPP | 113 | 124 | 138 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 152 | 155 | 155 | 160 | 160 | 160 | 190 |  | 215 | 218 | 216 | 219 | 219 | 218 | 219 | 3789120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 9 | 27 | 39 | 46 | 41 | 41 | 35 | 26 | 18 | 7 | 0 | [8 empty] | 293270
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 981032
46 | Shajibazar 330 MW CCPP | 159 | 160 | 160 | 159 | 160 | 158 | 160 | 159 | 160 | 161 | 162 | 160 | 161 | 159 | 160 | 160 | 176 | 182 |  | 260 | 270 | 272 | 272 | 269 | 269 | 270 | 4164000
47 | Shahjibazar GTPP Unit- 8 & 9 | 71 | 70 | 71 | 70 | 70 | 70 | 40 | 71 | 68 | 40 | 40 | 64 | 66 | 40 | 40 | 40 | 40 | 40 |  | 67 | 69 | 68 | 69 | 70 | 71 | 71 | 1422816
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 84 | 84 | 84 | 30 | 30 | 30 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1835520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 138 | 35
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 230580
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 153696
55 | Fenchugonj 51 MW PP (Barakatullah) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 45 | 42 | 45 | 45 | 45 | 48 | 48 | 14 | 14 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1044000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 5 | 5 | 5 | 5 | 5 | 5 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 304000
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 290 | 300 | 280 | 270 | 280 | 300 | 280 | 280 | 275 | 290 | 280 | 290 | 280 | 290 | 280 | 300 |  | 290 | 275 | 285 | 300 | 295 | 295 | 290 | 7073500
| Bibiyana South 400 MW | 300 | 300 | 300 | 240 | 230 | 200 | 240 | 260 | 320 | 350 | 350 | 350 | 400 | 350 | 350 | 300 | 300 | 300 |  | 340 | 370 | 400 | 390 | 360 | 320 | 330 | 7557700
58 | Nababganj 55 MW PP (Southern power ) | [5 empty] | 14 | 17 | 35 | 35 | 45 | 35 | 35 | 35 | 55 | 17 | 17 | 17 | 36 |  | 55 | 55 | 55 | 55 | 17 |  |  | 630412
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530400
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 426864
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 464976
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 474624
63 | Impoprt (Tripura) | 72 | 70 | 66 | 66 | 66 | 68 | 66 | 68 | 72 | 72 | 78 | 84 | 86 | 90 | 82 | 78 | 78 | 100 |  | 94 | 94 | 96 | 92 | 88 | 84 | 76 | 1930560
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 36 | 28 | 36 | 36 | 20 | 42 | 42 | 40 |  | 40 | 42 | 42 | 42 | 42 | 42 | 42 | 425280
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 485640
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 138420
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 25 | 33 | 17 | 17 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 717100
68 | Cumilla 25 MW PP (Summit) | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 8 | 20 | 18 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 429650
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 28 | 28 | 28 | 28 | 28 | 30 | 30 | 30 | 30 | 30 | 20 | 30 | 30 | 18 |  | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 674460
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 600900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 825900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [9 empty] | 17 | 17 | 17 | 52 | 34 | 17 | 17 | 17 | 17 |  | 51 | 51 | 17 |  |  |  |  | 315780
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 3 | 8 | 8 | 8 | 15 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 90 | 90 | 90 | 154 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 108 | 108 | 108 | 110 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3564000
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [17 empty] | 8 | [8 empty] | 10560
79 | Kodda 150MW PP | [17 empty] | 16 | [8 empty] | 17760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 49 | 25 | 25 | 25 | 25 | 27 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 29 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1064054
| Gazipur 100 MW PP | 70 | 70 | 70 | 34 | 34 | 45 | 70 | 70 | 70 | 90 | 90 | 90 | 105 | 105 | 70 | 35 | 35 | 43 |  | 103 | 105 | 105 | 105 | 105 | 105 | 105 | 1939200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 29400
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [9 empty] | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 233345
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 2 |  | 23 | [6 empty] | 31771
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 70 | 70 | 35 | 35 | 52 | 104 | 104 | 104 | 104 | 104 | 104 | 72 | 70 | 70 | 35 | 35 | 37 |  | 78 | 78 | 90 | 104 | 104 | 104 | 104 | 2006400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1130484
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 7 | 16 | 16 | 16 | 16 | 24 | 40 | 24 | 7 | 7 | 7 | 32 |  | 64 | 64 | 16 |  |  |  |  | 333504
95 | Patenga 50MW PP (Baraka) | 40 | 4 | 14 | 31 |  | 1 | 15 | 15 | 18 | 19 | 30 | 40 | 40 | 40 |  | 9 | 24 | 19 |  | 19 | 19 | 19 | 19 | 25 | 19 | 19 | 515520
96 | Chattogram 108 MW PP (ECPV) | 52 | 44 | 44 | 44 | 44 | 44 | 34 | 29 | 50 | 70 | 72 | 71 | 81 | 85 | 70 | 63 | 61 | 73 |  | 97 | 96 | 96 | 91 | 96 | 96 | 74 | 1600320
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 25 | 15 | 15 | 15 | 15 | 15 |  | 15 | [6 empty] | 140532
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 17 | 17 | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 887269
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2920581
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 12850
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1118520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 70 | 70 | 50 | 50 | 58 | 80 | 106 | 154 | 192 | 192 | 150 | 154 | 172 | 172 | 140 | 140 | 100 | 108 |  | 200 | 200 | 200 | 200 | 200 | 170 | 80 | 3340800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [11 empty] | 3 | 32 | 30 | 17 | 17 | 17 | 18 |  | 35 | 20 | 18 |  |  |  |  | 203330
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 30 | 10 | 10 | 10 | 10 | 28 |  | 50 | 50 | 50 | 50 | 50 | 30 |  | 472320
116 | Chandpur 200MW (Desh energy) | [9 empty] | 14 | 17 | 21 | 47 | 34 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 312000
117 | Ashuganj 150MW PP (Midland) | 70 | 20 | 20 | 20 | 20 | 20 | 26 | 55 | 60 | 83 | 100 | 108 | 127 | 135 | 135 | 80 | 80 | 97 |  | 147 | 150 | 150 | 150 | 150 | 100 | 0 | 2114327
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [7 empty] | 10 | 29 | 75 | 75 | 76 | 113 | 113 | 24 | 24 | 24 | 28 |  | 55 | 55 | 24 | 8 | 8 |  |  | 753600
| Anwara 300 MW PP (United) | 245 | 210 | 135 | 100 | 100 | 100 | 65 | 85 | 100 | 130 | 130 | 130 | 170 | 170 | 155 | 155 | 100 | 150 |  | 210 | 210 | 210 | 210 | 210 | 210 | 115 | 3828873
| Juldah unit-2 (Acorn) | [26 empty] | 0
| Anlima Energy Ltd. | 113 | 113 | 113 | 69 | 75 | 112 | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 71 |  | 111 | 113 | 113 | 113 | 113 | 113 | 113 | 2574327
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 14 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 13 | 17 | 17 | 432720
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 5 | 18 | 27 | 31 | 33 | 32 | 30 | 23 | 15 | 5 | 0 | [8 empty] | 221478
| Chandpur 115(Doreen) | [10 empty] | 18 | 5 | 24 | 25 | 0 | [11 empty] | 70080
| Kanchan Purbachal Power Generation Ltd. | 55 | 17 | 17 | 17 | 17 | 28 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 37 | 37 | 41 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 981360
120 | Eastern Zone Total | 4727 | 4538 | 4404 | 4116 | 4098 | 4199 | 4376 | 4761 | 4792 | 4803 | 4845 | 5028 | 5284 | 5206 | 4684 | 4509 | 4413 | 4806 |  | 5809 | 5765 | 5735 | 5687 | 5412 | 5160 | 4829 | 116757812
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 5 | [13 empty] | 4 | 4 | 3 |  | 19 | 6 | [5 empty] | 30240
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 17 | 17 | 17 | 17 | 17 | 35 | 53 | 70 | 90 | 90 | 100 | 70 | 70 | 17 | 17 | 17 | 35 |  | 87 | 105 | 105 | 105 | 105 | 70 | 17 | 1415520
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 4 | 27 | 53 | 74 | 88 | 94 | 92 | 84 | 64 | 42 | 15 | [9 empty] | 642240
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 210 | 203 | 181 | 182 | 182 | 180 | 185 | 190 | 187 | 190 | 169 | 187 | 225 | 192 | 200 | 167 | 167 | 165 |  | 226 | 222 | 228 | 227 | 228 | 228 | 206 | 4762255
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [7 empty] | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 180269
| Bhola 225 MW CCPP | 90 | 90 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2165887
140 | Bhola 33 MW PP (Venture) | 18 | 18 | 16 | 16 | 15 | 16 | 15 | 14 | 15 | 14 | 13 | 16 | 20 | 19 | 17 | 16 | 16 | 21 |  | 26 | 25 | 27 | 27 | 27 | 26 | 25 | 438200
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 6 |  | 10 | [6 empty] | 12928
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 716 | 623 | 624 | 624 | 623 | 623 | 718 | 717 | 717 | 717 | 717 | 717 | 717 | 717 | 717 | 670 | 670 | 738 |  | 714 | 714 | 717 | 715 | 715 | 717 | 716 | 16733090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 320 | 320 | 320 | 320 | 320 | 310 | 310 | 320 | 300 | 290 | 290 | 300 | 290 | 300 | 290 | 300 | 300 | 310 |  | 360 | 380 | 370 | 400 | 400 | 370 | 330 | 8640600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 |  | 200 | 199 | 199 | 199 | 200 | 200 | 200 | 4866500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [11 empty] | 2 | 42 | 42 | 42 | 42 | 42 | 42 | [8 empty] | 271156
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 4 | 5 | 5 | 3 | 5 | 4 | 2 | 0 | [9 empty] | 31860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 134 | 134 | 134 | 133 | 133 | 133 | 138 | 149 | 156 | 159 | 162 | 161 | 155 | 154 | 156 | 157 | 159 | 161 |  | 167 | 171 | 173 | 177 | 180 | 185 | 186 | 3949455
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 293 | 292 | 292 | 282 | 282 | 282 | 284 | 281 | 283 | 285 | 293 | 298 | 338 | 320 | 320 | 331 | 282 | 282 |  | 300 | 320 | 319 | 319 | 174 | 130 | 76 | 6759490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 4 | [8 empty] | 6890
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 18 | 18 | 18 | 18 | 19 | 21 | 22 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 492480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 201852
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [9 empty] | 8 | 8 | 20 | 43 | 43 | 8 | 8 | 8 | 8 |  | 8 | 8 | [5 empty] | 161003
167 | Katakhali 50 MW Peaking PP | [17 empty] | 22 |  | 32 | 16 | [5 empty] | 42901
168 | Santahar 50 MW Peaking PP | [10 empty] | 8 | 29 | 30 | 28 | 29 | 29 | 29 | 29 | [8 empty] | 210883
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 25 | 28 | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 24 | 24 | 8 | 16 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1075877
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 39 | 50 | 50 | 55 | 57 | 57 | 57 | 57 | 98 |  | 100 | 100 | 100 | 98 | 98 | 100 | 100 | 1049720
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 |  |  |  | 1 | 30 | 35 | 75 | 111 | 112 | 113 | 113 | 70 | 70 | 35 | 35 | 35 | 37 |  | 107 | 113 | 113 | 113 | 113 | 35 |  | 1537824
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 25 | 45 | 113 | 113 | 113 | 70 | 70 | 35 | 35 | 35 | 70 |  | 113 | 113 | 50 | 50 | 35 |  |  | 1045728
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 40 | 10 |  |  |  | 34 | 44 | 106 | 106 | 109 | 113 | 113 | 113 | 113 | 80 | 54 | 54 | 80 |  | 99 | 113 | 113 | 113 | 113 | 70 | 34 | 1789276
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 3 | 3 | 1 | 0 | [9 empty] | 27495
178 | Energypac Power Venture Thakurgaon Ltd. | [26 empty] | 0
178