## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-02-23 | Wednesday
|  |  | Date (day): | 2022-02-23 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11721.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12218 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-02-22 | 2022-02-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 340 | 340 | 340 | 25 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 341 | 350 | 350
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 14 | 11 | 30 | 30 |  | 70 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 85 | 90 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 55 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 25 | 30 | 30
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 290 | 298 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 106 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 91 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144 |  | 18 | Engine problem
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2232 | 2702 | 2882 | 2955 | 1701 | 992
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 2 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 12 | 40 | 40 |  | 10 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 73 | 70 | 72 | 72 |  | 158 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 98 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 6 | 8 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 80 | 98 | 90 | 96 |  | 12 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 260 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 6 | 29 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 60 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 110 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 751 | 987 | 1301 | 1304 | 180 | 894
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 224 | 189 | 221 | 221
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 320 | 340 | 350 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 305 | 320 | 320 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 6 | 26 | 26 | 26 | 19 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 42 | 42 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 147 | 150 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 42 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 124 | 123 | 125 | 125 |  | 38 | Machine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 57 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 116 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 0 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 49 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 8 | 8 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 115 | 0 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1534 | 1624 | 2123 | 2147 | 624 | 75
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 175 | 157 | 160 | 155 | 47 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 192 | 192 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 108 | 103 | 110 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 569 | 496 | 565.6 | 514 | 47 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 272 | 270 | 270 | 270 |  | 60 | Machine problem
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 45 | 45 | 45
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 5 | 5 |  | 6 | Engine problem
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 66 | 67 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 81 | 81
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1377 | 1390 | 1405 | 1405 | 73 | 894
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 715 | 715 | 759 | 759
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 12 | 40 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 4 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 45 | 0 | 0 | 410 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 28 | 80 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 92 | 75 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 913 | 907 | 1044 | 1364 | 410 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 25 | 25 | 30
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 91 | 91 | 91 | 103 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 84 | 81 | 81 | 14 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 400 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 110 | 110 | 110 |  | 110 | GT-2 Under maint
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 526 | 710 | 1087 | 1192 | 117 | 110
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 7 | 44 | 40 | 40 |  | 31 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 43 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 0 | 37 |  | 13 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 223 | 189 | 220 | 220
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 29 | 31 | 30 | 30 |  | 20 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 49 | 100 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 30 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 112 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 40 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 612 | 819 | 993 | 1024 | 600 | 494
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 318 | 312 | 321 | 313 | 74 | 210
|  | Total |  |  |  |  | 22066 | 20985 | 8832 | 9947 | 11721.6 | 12218 | 3826 | 3760
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8527.4483 | 9604 | 11317.4069 | 11796.6897
| A. |  | 2022-02-22 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 9947 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 5726 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9947 | MW
| 3 | Day peak Generation : |  |  | 8832 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9604 | MW
| 4 | Evening peak Generation : |  |  | 9947 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 194.5201 | MKWHr | By Solar | 1.2818 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 101.5337 | MKWHr |  | By Oil: | 56.7019 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.9932 | MKWHr |  | By Hydro: | 1.6065 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3826 | MW | Dhaka | 3458 | 3458 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3760 | MW | Chittagong | 1070 | 1070 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7586 | MW | Khulna | 1118 | 1118 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 762.32 | MMCFD |  |  | Rajshahi | 1027 | 1027 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 98758024.092 | ii) Oil : | Taka | 397566661.05 | Comilla | 778 | 778 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 66441510 | Total | Taka | 562766195.142 | Mymensingh | 865 | 865 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.817 | MKWHr. | Sylhet | 339 | 339 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -504 | MW (E to W) at | 19:00 | hrs | Barisal | 252 | 252 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -576 | MW at | 8:00 | hrs | Rangpur | 697 | 697 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 28.8° C |  |  | Total | 9604 | 9604 |  | 0
| B. |  | 2022-02-23 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 28.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12218 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 2118 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 197.5121 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6502 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1345 | MKWHr. | ii) HVDC Flow at Peak Time |  | 715 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2685 | MKWHr. | iii) Maximum HVDC Flow : |  | 716 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.27 |  | (b) Today: | 91.12 |  | (c) Rule Curve: |  | 93.9
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-02-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 51 | 22 | 18 | 42 | 0 | 0 | 0 | 260 | 275 | 228 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 70 | 220 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 270 | 69 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 80 | 0 | 0 | 0 | 8 | 0 | 340 | 70 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 17 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 203 | 0 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 176 | 0 | 0 | 0 | 0 | 0 |  | 4588 | 1846 | 6434 | 2764 | 715 | 1436 | 0 | 850 | 529 | 70 | 0 | 0 | 70 | 0 | 0 | 91.32
2:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 19 | 25 | 18 | 40 | 0 | 0 | 0 | 295 | 345 | 229 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 18 | 70 | 220 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 272 | 69 | 84 | 0 | 0 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 330 | 17 | 0 | 54 | 113 | 0 | 17 | 0 | 0 | 17 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 205 | 0 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 156 | 0 | 0 | 0 | 0 | 0 |  | 4311 | 1784 | 6095 | 2860 | 715 | 1409 | 0 | 442 | 530 | 69 | 0 | 0 | 70 | 0 | 0 | 91.31
3:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 13 | 25 | 18 | 42 | 0 | 0 | 0 | 260 | 305 | 229 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 19 | 68 | 220 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 269 | 69 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 320 | 17 | 0 | 17 | 113 | 0 | 17 | 0 | 0 | 17 |  | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 212 | 0 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 153 | 0 | 0 | 0 | 0 | 0 |  | 4195 | 1731 | 5926 | 2781 | 668 | 1422 | 0 | 399 | 520 | 68 | 0 | 0 | 68 | 0 | 0 | 91.3
4:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 12 | 25 | 18 | 42 | 0 | 0 | 0 | 260 | 310 | 228 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 33 | 19 | 66 | 220 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 271 | 69 | 10 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 320 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 0 | 17 |  | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 223 | 0 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 153 | 0 | 0 | 0 | 0 | 0 |  | 4032 | 1711 | 5743 | 2797 | 668 | 1338 | 0 | 309 | 500 | 65 | 0 | 0 | 66 | 0 | 0 | 91.29
5:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 12 | 25 | 18 | 42 | 0 | 0 | 0 | 285 | 330 | 228 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 33 | 19 | 68 | 220 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 269 | 69 | 10 | 0 | 0 | 0 | 0 | 10 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 0 | 320 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 0 | 17 |  | 667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 212 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 110 | 0 | 0 | 0 | 0 | 0 |  | 4087 | 1639 | 5726 | 2829 | 667 | 1300 | 0 | 292 | 500 | 70 | 0 | 0 | 68 | 0 | 0 | 91.28
6:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 23 | 25 | 18 | 40 | 0 | 0 | 0 | 260 | 305 | 228 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 25 | 21 | 8 | 33 | 19 | 68 | 221 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 271 | 71 | 81 | 0 | 0 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 5 | 0 | 0 | 24 | 0 | 0 | 0 | 10 | 0 | 13 | 0 | 0 | 17 | 8 | 0 | 88 | 0 | 0 | 0 | 8 | 0 | 300 | 24 | 0 | 57 | 113 | 0 | 17 | 0 | 0 | 30 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 209 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 |  | 4327 | 1745 | 6072 | 2755 | 715 | 1427 | 0 | 542 | 500 | 65 | 0 | 0 | 68 | 0 | 0 | 91.27
7:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 13 | 22 | 25 | 28 | 20 | 33 | 8 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 65 | 25 | 18 | 37 | 0 | 0 | 0 | 265 | 310 | 233 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 26 | 21 | 8 | 33 | 19 | 80 | 222 | 0 | 22 | 0 | 30 | 42 | 48 | 0 | 110 | 271 | 71 | 81 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 30 | 0 | 0 | 65 | 0 | 1 | 2 | 10 | 0 | 48 | 0 | 6 | 42 | 17 | 0 | 115 | 0 | 0 | 17 | 8 | 0 | 300 | 64 | 2 | 144 | 113 | 0 | 17 | 1 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 206 | 0 | 73 | 0 | 0 | 0 | 0 | 25 | 0 | 28 | 0 | 80 | 0 | 0 | 50 | 300 | 120 | 0 | 0 | 0 | 2 | 0 |  | 4808 | 2004 | 6812 | 2768 | 715 | 1439 | 0 | 1233 | 500 | 70 | 0 | 0 | 80 | 7 | 0 | 91.26
8:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 20 | 33 | 8 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 79 | 25 | 18 | 8 | 0 | 0 | 0 | 280 | 270 | 234 | 8 | 124 | 6 | 5 | 0 | 51 | 0 | 0 | 51 | 21 | 8 | 33 | 19 | 90 | 221 | 0 | 22 | 1 | 30 | 42 | 48 | 0 | 110 | 272 | 71 | 81 | 0 | 0 | 0 | 0 | 10 | 285 | 16 | 5 | 0 | 133 | 0 | 0 | 185 | 0 | 50 | 7 | 25 | 12 | 122 | 0 | 86 | 105 | 17 | 1 | 190 | 0 | 0 | 51 | 8 | 0 | 280 | 104 | 10 | 144 | 113 | 0 | 17 | 8 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 181 | 0 | 80 | 0 | 0 | 0 | 0 | 84 | 0 | 107 | 0 | 107 | 0 | 1 | 108 | 300 | 135 | 0 | 0 | 0 | 18 | 0 |  | 5579 | 2258 | 7837 | 2701 | 715 | 1416 | 0 | 2300 | 500 | 69 | 0 | 0 | 90 | 46 | 0 | 91.25
9:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 84 | 32 | 10 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 30 | 33 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 89 | 25 | 18 | 5 | 0 | 0 | 0 | 280 | 270 | 232 | 8 | 124 | 6 | 5 | 0 | 42 | 0 | 33 | 52 | 21 | 8 | 24 | 19 | 92 | 219 | 0 | 22 | 1 | 30 | 42 | 45 | 0 | 110 | 271 | 70 | 81 | 0 | 0 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 268 | 0 | 0 | 189 | 0 | 100 | 13 | 80 | 17 | 132 | 0 | 113 | 105 | 31 | 2 | 260 | 0 | 0 | 51 | 8 | 10 | 290 | 104 | 26 | 144 | 113 | 0 | 17 | 17 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 4 | 49 | 0 | 34 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 0 | 0 | 0 | 0 | 92 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 310 | 200 | 0 | 0 | 2 | 25 | 0 |  | 6184 | 2355 | 8539 | 2710 | 715 | 1421 | 0 | 2815 | 510 | 70 | 0 | 118 | 92 | 88 | 0 | 91.24
10:00 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 16 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 80 | 25 | 18 | 3 | 0 | 0 | 0 | 280 | 270 | 230 | 8 | 124 | 6 | 5 | 0 | 42 | 0 | 33 | 52 | 21 | 8 | 24 | 19 | 104 | 216 | 0 | 22 | 2 | 30 | 42 | 45 | 0 | 110 | 270 | 68 | 81 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 275 | 0 | 0 | 193 | 0 | 128 | 17 | 80 | 17 | 140 | 0 | 113 | 105 | 51 | 4 | 260 | 0 | 0 | 17 | 8 | 10 | 340 | 104 | 37 | 144 | 113 | 0 | 17 | 24 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 4 | 49 | 0 | 34 | 9 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 172 | 0 | 12 | 0 | 0 | 0 | 0 | 88 | 0 | 112 | 0 | 113 | 0 | 4 | 35 | 300 | 202 | 0 | 0 | 4 | 72 | 0 |  | 6270 | 2314 | 8584 | 2739 | 715 | 1410 | 0 | 2767 | 500 | 70 | 0 | 115 | 104 | 164 | 0 | 91.23
11:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 360 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 24 | 30 | 33 | 16 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 78 | 25 | 18 | 2 | 0 | 0 | 0 | 280 | 270 | 231 | 8 | 123 | 6 | 5 | 0 | 42 | 0 | 24 | 52 | 21 | 8 | 25 | 17 | 108 | 192 | 0 | 22 | 2 | 30 | 42 | 42 | 0 | 110 | 269 | 68 | 84 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 275 | 0 | 0 | 193 | 0 | 131 | 19 | 80 | 17 | 145 | 0 | 107 | 105 | 51 | 4 | 260 | 0 | 0 | 17 | 8 | 10 | 400 | 95 | 30 | 144 | 99 | 0 | 17 | 30 | 0 | 55 |  | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 49 | 0 | 34 | 32 | 52 | 7 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 213 | 0 | 12 | 0 | 0 | 0 | 0 | 76 | 0 | 112 | 0 | 113 | 0 | 5 | 35 | 300 | 183 | 0 | 0 | 4 | 88 | 0 |  | 6282 | 2372 | 8654 | 2817 | 714 | 1399 | 0 | 2733 | 500 | 65 | 0 | 136 | 108 | 182 | 0 | 91.22
12:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 347 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 16 | 14 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 28 | 30 | 33 | 16 | 0 | 73 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 80 | 25 | 18 | 2 | 0 | 0 | 0 | 345 | 320 | 224 | 8 | 124 | 6 | 5 | 0 | 42 | 0 | 24 | 49 | 21 | 8 | 25 | 17 | 110 | 175 | 0 | 22 | 2 | 30 | 42 | 42 | 0 | 110 | 272 | 66 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 290 | 0 | 0 | 192 | 0 | 132 | 20 | 90 | 17 | 147 | 0 | 108 | 105 | 51 | 4 | 260 | 0 | 6 | 17 | 8 | 10 | 400 | 92 | 48 | 144 | 110 | 0 | 17 | 33 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 7 | 49 | 0 | 34 | 32 | 52 | 29 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 223 | 0 | 11 | 0 | 0 | 0 | 0 | 92 | 0 | 112 | 0 | 113 | 0 | 5 | 40 | 300 | 110 | 0 | 0 | 5 | 94 | 0 |  | 6463 | 2369 | 8832 | 2924 | 715 | 1331 | 0 | 2799 | 500 | 73 | 0 | 169 | 110 | 211 | 0 | 91.21
13:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 28 | 25 | 33 | 51 | 0 | 72 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 25 | 18 | 7 | 0 | 0 | 0 | 300 | 300 | 225 | 8 | 122 | 6 | 5 | 0 | 42 | 0 | 24 | 43 | 21 | 8 | 16 | 17 | 110 | 146 | 0 | 22 | 2 | 30 | 42 | 42 | 0 | 110 | 268 | 66 | 84 | 0 | 0 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 298 | 0 | 0 | 192 | 0 | 138 | 20 | 90 | 41 | 145 | 0 | 108 | 105 | 102 | 4 | 300 | 0 | 17 | 34 | 8 | 80 | 400 | 93 | 45 | 144 | 113 | 0 | 17 | 32 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 28 | 7 | 49 | 0 | 34 | 32 | 52 | 29 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 221 | 0 | 12 | 0 | 0 | 0 | 0 | 84 | 0 | 112 | 0 | 113 | 0 | 6 | 100 | 340 | 110 | 0 | 0 | 5 | 92 | 0 |  | 6631 | 2492 | 9123 | 2808 | 715 | 1347 | 0 | 3127 | 540 | 72 | 0 | 198 | 110 | 206 | 0 | 91.21
14:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 336 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 40 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 28 | 25 | 33 | 16 | 0 | 60 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 25 | 18 | 7 | 0 | 0 | 0 | 280 | 275 | 223 | 8 | 124 | 6 | 5 | 0 | 42 | 0 | 32 | 47 | 21 | 8 | 25 | 17 | 110 | 145 | 0 | 20 | 2 | 30 | 42 | 42 | 0 | 110 | 271 | 40 | 84 | 0 | 0 | 0 | 0 | 10 | 275 | 16 | 5 | 0 | 298 | 0 | 0 | 192 | 0 | 98 | 18 | 50 | 85 | 145 | 0 | 109 | 105 | 51 | 4 | 245 | 0 | 17 | 17 | 8 | 20 | 400 | 98 | 41 | 144 | 113 | 0 | 17 | 28 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 42 | 26 | 49 | 0 | 34 | 32 | 52 | 29 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 223 | 0 | 30 | 0 | 0 | 0 | 0 | 76 | 0 | 70 | 0 | 113 | 0 | 5 | 70 | 330 | 110 | 0 | 0 | 4 | 53 | 0 |  | 6222 | 2417 | 8639 | 2749 | 715 | 1325 | 0 | 2755 | 530 | 60 | 0 | 240 | 110 | 155 | 0 | 0
15:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 337 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 40 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 25 | 33 | 16 | 0 | 67 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 78 | 26 | 18 | 2 | 0 | 0 | 0 | 280 | 270 | 226 | 8 | 122 | 6 | 5 | 0 | 42 | 0 | 32 | 48 | 21 | 8 | 33 | 17 | 106 | 156 | 0 | 20 | 1 | 30 | 42 | 45 | 0 | 110 | 272 | 40 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 290 | 0 | 0 | 192 | 0 | 70 | 14 | 50 | 17 | 143 | 0 | 75 | 105 | 51 | 3 | 245 | 0 | 17 | 17 | 8 | 20 | 400 | 96 | 30 | 144 | 113 | 0 | 17 | 24 | 0 | 55 |  | 716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 42 | 51 | 57 | 0 | 34 | 32 | 52 | 29 | 18 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 213 | 0 | 82 | 0 | 0 | 0 | 0 | 75 | 0 | 70 | 0 | 113 | 0 | 4 | 70 | 320 | 110 | 0 | 0 | 2 | 68 | 0 |  | 6054 | 2487 | 8541 | 2745 | 716 | 1386 | 0 | 2584 | 519 | 67 | 0 | 272 | 106 | 146 | 0 | 0
16:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 335 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 25 | 33 | 16 | 0 | 34 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 26 | 18 | 2 | 0 | 0 | 0 | 290 | 280 | 224 | 8 | 125 | 6 | 5 | 0 | 42 | 0 | 32 | 45 | 21 | 8 | 0 | 16 | 108 | 156 | 0 | 20 | 1 | 30 | 42 | 45 | 0 | 110 | 268 | 40 | 84 | 0 | 0 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 283 | 0 | 0 | 192 | 0 | 45 | 8 | 20 | 17 | 145 | 0 | 75 | 105 | 51 | 2 | 245 | 0 | 17 | 17 | 8 | 10 | 400 | 91 | 17 | 144 | 113 | 0 | 17 | 14 | 0 | 55 |  | 716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 42 | 46 | 57 | 0 | 34 | 32 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 197 | 0 | 83 | 0 | 0 | 0 | 0 | 75 | 0 | 35 | 0 | 113 | 0 | 3 | 35 | 300 | 110 | 0 | 0 | 1 | 29 | 20 |  | 5831 | 2359 | 8190 | 2712 | 716 | 1368 | 0 | 2411 | 499 | 34 | 0 | 267 | 108 | 75 | 0 | 0
17:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 335 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 16 | 11 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 30 | 25 | 33 | 16 | 0 | 70 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 84 | 26 | 18 | 7 | 0 | 0 | 0 | 280 | 270 | 190 | 8 | 124 | 6 | 5 | 0 | 42 | 0 | 42 | 45 | 21 | 8 | 0 | 17 | 106 | 156 | 0 | 20 | 0 | 30 | 42 | 45 | 0 | 110 | 272 | 40 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 290 | 0 | 0 | 192 | 0 | 35 | 3 | 20 | 17 | 148 | 0 | 75 | 105 | 51 | 0 | 245 | 0 | 17 | 17 | 14 | 10 | 400 | 91 | 5 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 42 | 45 | 49 | 0 | 34 | 32 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 186 | 0 | 84 | 0 | 0 | 0 | 0 | 70 | 0 | 35 | 0 | 113 | 0 | 1 | 35 | 300 | 110 | 0 | 0 | 0 | 8 | 20 |  | 5804 | 2348 | 8152 | 2702 | 716 | 1395 | 0 | 2373 | 500 | 70 | 0 | 273 | 106 | 17 | 0 | 0
18:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 292 |  | 0 | 225 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 48 | 115 | 12 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 18 | 25 | 33 | 35 | 0 | 63 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 90 | 25 | 18 | 12 | 0 | 0 | 0 | 280 | 300 | 188 | 8 | 124 | 16 | 5 | 0 | 42 | 0 | 42 | 49 | 21 | 8 | 0 | 17 | 116 | 157 | 0 | 20 | 0 | 30 | 42 | 45 | 0 | 110 | 274 | 67 | 81 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 298 | 0 | 0 | 192 | 0 | 103 | 0 | 70 | 24 | 150 | 0 | 90 | 105 | 64 | 0 | 260 | 5 | 17 | 36 | 8 | 30 | 400 | 92 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 42 | 46 | 92 | 0 | 43 | 32 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 172 | 0 | 84 | 0 | 0 | 0 | 0 | 75 | 0 | 55 | 0 | 113 | 0 | 0 | 90 | 290 | 110 | 0 | 0 | 0 | 1 | 20 |  | 6272 | 2459 | 8731 | 2744 | 715 | 1349 | 0 | 2780 | 490 | 63 | 0 | 473 | 116 | 1 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 341 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 85 | 150 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 51 | 0 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 98 | 12 | 18 | 6 | 0 | 0 | 0 | 320 | 305 | 189 | 8 | 123 | 26 | 5 | 0 | 42 | 0 | 42 | 52 | 21 | 8 | 0 | 21 | 116 | 157 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 270 | 67 | 84 | 0 | 0 | 0 | 0 | 10 | 305 | 16 | 11 | 0 | 298 | 106 | 100 | 192 | 100 | 149 | 0 | 90 | 57 | 150 | 0 | 103 | 105 | 98 | 0 | 300 | 17 | 29 | 114 | 8 | 60 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 91 | 25 | 0 | 0 | 0 | 0 | 43 | 44 | 100 | 0 | 43 | 32 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 189 | 0 | 84 | 28 | 0 | 0 | 0 | 75 | 30 | 112 | 0 | 113 | 0 | 0 | 113 | 400 | 110 | 0 | 0 | 0 | 0 | 0 |  | 7199 | 2748 | 9947 | 2851 | 715 | 1422 | 364 | 3273 | 599 | 70 | 0 | 537 | 116 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 51 | 0 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 103 | 18 | 18 | 8 | 0 | 0 | 0 | 310 | 300 | 187 | 8 | 124 | 26 | 5 | 0 | 42 | 0 | 33 | 52 | 21 | 8 | 0 | 21 | 116 | 159 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 271 | 67 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 298 | 52 | 50 | 192 | 50 | 149 | 0 | 90 | 85 | 150 | 0 | 99 | 105 | 105 | 0 | 300 | 17 | 51 | 114 | 8 | 60 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 35 | 8 | 0 | 91 | 25 | 0 | 0 | 0 | 0 | 43 | 44 | 100 | 0 | 43 | 32 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 173 | 0 | 84 | 10 | 0 | 0 | 0 | 75 | 10 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 110 | 0 | 0 | 0 | 0 | 0 |  | 7094 | 2735 | 9829 | 2822 | 716 | 1420 | 172 | 3347 | 639 | 70 | 0 | 527 | 116 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 51 | 0 | 67 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 104 | 19 | 18 | 13 | 0 | 0 | 0 | 310 | 300 | 185 | 8 | 122 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 21 | 8 | 0 | 21 | 120 | 160 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 268 | 67 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 300 | 11 | 25 | 193 | 25 | 149 | 0 | 90 | 85 | 150 | 0 | 99 | 105 | 105 | 0 | 300 | 17 | 51 | 114 | 8 | 40 | 400 | 92 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 35 | 10 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 44 | 100 | 0 | 43 | 32 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 174 | 0 | 82 | 0 | 0 | 0 | 0 | 75 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 110 | 0 | 0 | 0 | 0 | 0 |  | 6982 | 2784 | 9766 | 2883 | 715 | 1423 | 61 | 3321 | 649 | 67 | 0 | 527 | 120 | 0 | 0 | 0
21:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 345 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 51 | 0 | 67 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 103 | 19 | 18 | 30 | 0 | 0 | 0 | 280 | 265 | 168 | 8 | 122 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 21 | 8 | 0 | 21 | 112 | 152 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 268 | 68 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 298 | 0 | 0 | 193 | 0 | 149 | 0 | 90 | 85 | 150 | 0 | 104 | 105 | 85 | 0 | 300 | 17 | 17 | 114 | 8 | 10 | 400 | 104 | 0 | 144 | 100 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 43 | 24 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 176 | 0 | 83 | 0 | 0 | 0 | 0 | 93 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 110 | 0 | 0 | 0 | 0 | 0 |  | 6690 | 2793 | 9483 | 2858 | 716 | 1444 | 0 | 3239 | 660 | 67 | 0 | 387 | 112 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 345 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 104 | 25 | 18 | 38 | 0 | 0 | 0 | 260 | 265 | 205 | 8 | 123 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 0 | 21 | 106 | 145 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 269 | 69 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 298 | 0 | 0 | 193 | 0 | 130 | 0 | 60 | 85 | 150 | 0 | 109 | 105 | 51 | 0 | 283 | 0 | 17 | 114 | 8 | 0 | 400 | 104 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 179 | 0 | 83 | 0 | 0 | 0 | 0 | 93 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 110 | 0 | 0 | 0 | 0 | 0 |  | 6319 | 2752 | 9071 | 2884 | 715 | 1462 | 0 | 3023 | 660 | 70 | 0 | 151 | 106 | 0 | 0 | 91.16
23:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 103 | 25 | 18 | 32 | 0 | 0 | 0 | 260 | 265 | 219 | 8 | 123 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 102 | 155 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 271 | 68 | 84 | 0 | 0 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 195 | 0 | 0 | 192 | 0 | 0 | 0 | 60 | 34 | 150 | 0 | 8 | 105 | 51 | 0 | 282 | 0 | 17 | 17 | 8 | 0 | 400 | 104 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 179 | 0 | 83 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 50 | 430 | 110 | 0 | 0 | 0 | 0 | 0 |  | 5744 | 2486 | 8230 | 2942 | 715 | 1430 | 0 | 2296 | 630 | 70 | 0 | 45 | 102 | 0 | 0 | 91.16
24:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 103 | 25 | 18 | 32 | 0 | 0 | 0 | 260 | 270 | 227 | 8 | 123 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 90 | 153 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 274 | 70 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 30 | 0 | 0 | 160 | 0 | 0 | 0 | 60 | 34 | 148 | 0 | 0 | 105 | 51 | 0 | 283 | 0 | 17 | 0 | 8 | 0 | 400 | 104 | 0 | 144 | 112 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 179 | 0 | 83 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 0 | 49 | 0 | 0 | 0 | 420 | 110 | 0 | 0 | 0 | 0 | 0 |  | 5542 | 2237 | 7779 | 2955 | 715 | 1449 | 0 | 1880 | 620 | 70 | 0 | 0 | 90 | 0 | 0 | 91.15
KWH | 0 | 0 | 0 | 0 | 7630155 | 0 | 0 | 0 | 8096000 |  | 0 | 5280150 | 0 | 0 | 0 | 507508 | 0 | 0 | 0 | 0 | 1071648 | 688320 | 140811 | 0 | 0 | 0 | 1090440 | 947081 | 840251 | 387396 | 600000 | 663660 | 646900 | 832700 | 435360 | 0 | 1606473 | 0 | 0 | 0 | 176857 | 0 | 0 | 0 | 0 |  | 530880 | 0 | 147490 | 0 | 1727040 | 586080 | 437088 | 492720 | 0 | 0 | 0 | 7183000 | 7158000 | 5288000 | 217454 | 2952580 | 322128 | 142080 | 0 | 1108864 | 0 | 388440 | 1123493 | 502416 | 184500 | 524900 | 491130 | 2268480 | 4350720 | 0 | 483084 | 13350 | 715000 | 976552 | 1092600 | 0 | 2922463 | 6210000 | 1473888 | 1848960 | 0 | 0 | 0 | 0 | 252000 | 7210500 | 384000 | 169536 | 0 | 4616726 | 148242 | 139409 | 3528000 | 136669 | 1668530 | 133785 | 1156800 | 752160 | 2529152 | 0 | 1555200 | 2097600 | 1149999 | 29371 | 5000618 | 64763 | 281854 | 833340 | 228480 | 369600 | 8662700 | 1959360 | 299480 | 3072960 | 2547982 | 0 | 444960 | 210729 | 0 | 1170360 |  | 17134545 | 0 | 897984 | 0 | 0 | 0 | 0 | 0 | 181440 | 9856 | 0 | 2199795 | 461300 | 0 | 0 | 0 | 0 | 396928 | 336740 | 985608 | 0 | 559556 | 315079 | 1073818 | 286255 | 513120 | 0 | 197586 | 0 | 0 | 4865400 | 0 | 0 | 0 | 0 | 4944336 | 0 | 1161667 | 42240 | 0 | 0 | 11709 | 1448640 | 37365 | 1733856 | 0 | 1953388 | 0 | 41778 | 1419264 | 9127800 | 3252409 | 0 | 0 | 31320 | 522000 | 67392 |  | 138309955 | 56210174 | 194520129 | 67469734 | 17134545 | 34063996 | 503925 | 52461807 | 13993200 | 1606473 | 0 | 3736156 | 2268480 | 1281813 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8469472.05 | 0 | 0 | 0 | 8338880 |  | 0 | 5755363.5 | 0 | 0 | 0 | 4293517.68 | 0 | 0 | 0 | 0 | 9773429.76 | 6773068.8 | 1298277.42 | 0 | 0 | 0 | 7960212 | 7320936.13 | 8284874.86 | 290547 | 450000 | 0 | 0 | 0 | 4209931.2 | 0 | 433747.71 | 0 | 0 | 0 | 1643001.53 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1430653 | 0 | 15025248 | 4641753.6 | 550730.88 | 1463378.4 | 0 | 0 | 0 | 5315420 | 7158000 | 4864960 | 280515.66 | 3395467 | 364004.64 | 198912 | 0 | 1896157.44 | 0 | 3923244 | 10729358.15 | 638068.32 | 138375 | 918575 | 368347.5 | 17013600 | 4611763.2 | 0 | 613516.68 | 212799 | 1172600 | 1562483.2 | 1944828 | 0 | 3331607.82 | 6458400 | 2903559.36 | 3531513.6 | 0 | 0 | 0 | 0 | 514080 | 7282605 | 288000 | 128847.36 | 0 | 34902448.56 | 2517149.16 | 2330918.48 | 18345600 | 2285105.68 | 16418335.2 | 1563946.65 | 9427920 | 8160936 | 17830521.6 | 0 | 14183424 | 19822320 | 10016491.29 | 0 | 37804672.08 | 564085.73 | 2477496.66 | 8316733.2 | 1958073.6 | 2461536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98694979.2 | 0 | 942883.2 | 0 | 0 | 0 | 0 | 0 | 1903305.6 | 103290.88 | 0 | 2485768.35 | 715015 | 0 | 0 | 0 | 0 | 3905771.52 | 3421278.4 | 8722630.8 | 0 | 7565197.12 | 3053115.51 | 10405296.42 | 2776673.5 | 985190.4 | 0 | 149572.602 | 0 | 0 | 26370468 | 0 | 0 | 0 | 0 | 6526523.52 | 0 | 1742500.5 | 718502.4 | 0 | 0 | 11591.91 | 15123801.6 | 635578.65 | 16454293.44 | 0 | 15158290.88 | 0 | 461646.9 | 10488360.96 | 40071042 | 0 | 0 | 0 | 0 | 0 | 0 |  | 401554345.34 | 279592569.262 | 681146914.602 | 60765884.862 | 98694979.2 | 37992139.23 | 8487254.37 | 353066374.67 | 66441510 | 433747.71 | 0 | 36013032.01 | 17013600 | 2238392.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 347 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 16 | 14 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 25 | 28 | 30 | 33 | 16 | 0 | 73 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 80 | 25 | 18 | 2 | 0 | 0 | 0 | 345 | 320 | 224 | 8 | 124 | 6 | 5 | 0 | 42 | 0 | 24 | 49 | 21 | 8 | 25 | 17 | 110 | 175 | 0 | 22 | 2 | 30 | 42 | 42 | 0 | 110 | 272 | 66 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 290 | 0 | 0 | 192 | 0 | 132 | 20 | 90 | 17 | 147 | 0 | 108 | 105 | 51 | 4 | 260 | 0 | 6 | 17 | 8 | 10 | 400 | 92 | 48 | 144 | 110 | 0 | 17 | 33 | 0 | 55 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 7 | 49 | 0 | 34 | 32 | 52 | 29 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 223 | 0 | 11 | 0 | 0 | 0 | 0 | 92 | 0 | 112 | 0 | 113 | 0 | 5 | 40 | 300 | 110 | 0 | 0 | 5 | 94 | 0 |  | 8832 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 341 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 85 | 150 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 51 | 0 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 0 | 98 | 12 | 18 | 6 | 0 | 0 | 0 | 320 | 305 | 189 | 8 | 123 | 26 | 5 | 0 | 42 | 0 | 42 | 52 | 21 | 8 | 0 | 21 | 116 | 157 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 270 | 67 | 84 | 0 | 0 | 0 | 0 | 10 | 305 | 16 | 11 | 0 | 298 | 106 | 100 | 192 | 100 | 149 | 0 | 90 | 57 | 150 | 0 | 103 | 105 | 98 | 0 | 300 | 17 | 29 | 114 | 8 | 60 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 715 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 91 | 25 | 0 | 0 | 0 | 0 | 43 | 44 | 100 | 0 | 43 | 32 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 189 | 0 | 84 | 28 | 0 | 0 | 0 | 75 | 30 | 112 | 0 | 113 | 0 | 0 | 113 | 400 | 110 | 0 | 0 | 0 | 0 | 0 |  | 9947 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 | 0 | 0 | 225 |  | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 30 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 72 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 96 | 40 | 18 | 30 | 0 | 0 | 0 | 350 | 320 | 221 | 8 | 125 | 26 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 163 | 155 | 0 | 22 | 0 | 30 | 42 | 45 | 0 | 110 | 270 | 66 | 81 | 0 | 0 | 0 | 0 | 10 | 330 | 16 | 5 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 104 | 0 | 144 | 113 | 0 | 17 |  |  | 55 |  | 759 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 91 | 30 | 110 | 0 | 0 | 0 | 43 | 40 | 100 | 0 | 43 | 37 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 81 | 100 | 0 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 110 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 90 | 150 | 30 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 72 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 40 | 18 | 8 | 0 | 0 | 0 | 340 | 320 | 221 | 8 | 125 | 26 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 20 | 138 | 160 | 0 | 22 | 1.6 | 30 | 42 | 45 | 0 | 110 | 270 | 66 | 81 | 0 | 0 | 0 | 0 | 10 | 330 | 16 | 5 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 0 | 110 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 104 | 50 | 144 | 113 | 0 | 17 | 30 | 115 | 55 |  | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 25 | 110 | 0 | 0 | 0 | 43 | 40 | 100 | 0 | 43 | 0 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 81 | 80 | 0 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 110 |  | 50 | 6 | 50
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 350 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 8 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 82 | 26 | 18 | 10 | 0 | 0 | 0 | 305 | 270 | 205 | 8 | 123 | 27 | 5 | 0 | 0 | 0 | 0 | 52 | 22 | 8 | 25 | 21 | 96 | 155 | 0 | 22 | 1 | 30 | 42 | 45 | 0 | 110 | 269 | 68 | 81 | 0 | 0 | 0 | 0 | 10 | 305 | 16 | 0 | 0 | 158 | 0 | 0 | 185 | 0 | 46 | 7 | 50 | 3 | 0 | 0 | 70 | 105 | 20 | 1 | 283 | 0 | 3 | 17 | 8 | 0 | 400 | 92 | 14 | 144 | 113 | 0 | 17 | 9 | 0 | 42 | 0 | 719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 190 | 0 | 81 | 0 | 0 | 0 | 0 | 93 | 0 | 96 | 0 | 98 | 0 | 2 | 113 | 310 | 111 | 0 | 0 | 1 | 12 | 0 | 0
199
| Minimum Generation |  | 5726 | 5:00
| Highest Generation |  | 9947 | 19:00
| Day Peak Generation |  | 8832 | 12:00
| Evening Peak Generation |  | 9947 | 19:00
| HVDC Max Flow |  | 716 | 15:00
| HVDC EvPeak Flow |  | 715 | 19:00
| Load factor L.F |  | 81.48%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-02-23
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-02-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8832 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6502 | MW
Evening Peak Generation : |  | 9947 | MW Hour : | 19:00 | Available Max Generation : |  | 12218 | MW
E.P. Demand (at gen end) : |  | 9947 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10100 | MW
Maximum Generation : |  | 9947 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2118 | MW
Total Gen. (MKWH) : |  | 194.5201 | System Load Factor : | 81.48% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -576 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-02-23
Actual : | 91.12 | Ft.(MSL) , | Rule curve : | 93.9 | Ft.( MSL )
Gas Consumed : | Total = | 762.32 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 98758024.092
: |  | Coal : | 66441510 | Oil : | 397566661.05 | Total : | 562766195.142
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3634.1007 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1233.52 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1104.7876 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 998.1248 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 902.0703 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 727.9331 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 409.9524 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 187.5007 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 561.4041 |  |  | 0 | 0%
Total | 0 |  | 9759.3938 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
|  |  |  | 2) Ghorasal-3,4,5 |  | 11) Meghnaghat 450 MW CCPP GT-1
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Siddhirganj 335 MW
6) Raozan unit- 1,2
7) Sirajganj Unit 1 & 3
8) Summit Bibiyana-3
9) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Haripur-Norsingdi 132 kV Ckt was under shut down from 09:12 to 16:27 for A/M.
b) Bakulia-Khulsi 132 kV Ckt-1 was under shut down from 08:48 to 15:14 for A/M.
c) Shahjibazar-Cumilla(N) 230 kV Ckt-2 was under shut down from 09:10 to 16:22 for A/M.
d) Cumilla(N) 132/33 kV T-3 transformer was shut down at 09:16 for C/M.
e) Ashuganj-Cumilla(N) 230 kV Ckt-2 was under shut down from 09:32 to 10:13 for C/M.
f) Sunamganj 132/33 kV T-1 transformer was under shut down from 09:21 to 17:24 for D/W.
g) Rangamati 132/33 kV T-1 transformer was under shut down from 09:43 to 16:13 for A/M.
h) Ashuganj-Cumilla(N) 230 kV Ckt-1 was under shut down from 10:19 to 12:39 for C/M.
i) Jhenaidah-Jashore 132 kV Ckt-1 was under shut down from 09:41 to 17:52 for A/M.
j) Jhenaidah(Old)-Jhenaidah(New) 132 kV Ckt-1 was under shut down from 09:29 to 18:30 for D/W.
k) Jhenaidah 230/132 kV T-02 transformer was under shut down from 10:09 to 18:33 for D/W.
l) Jhenaidah New 132 kV Bus was shut down at 10:32 for D/W.
m) Gollamari 132/33 kV T-2 transformer was under shut down from 09:04 to 15:04 for A/M.
n) Patuakhali-Payra 132 kV Ckt-2 was under shut down from 09:18 to 18:23 for A/M.
o) Barishal(N) 132/33 kV T-4 transformer was under shut down from 10:24 to 14:04 for A/M.
p) Nawabganj-Keraniganj 132 kV Ckt-1 was under shut down from 11:18 to 17:17 for A/M.
q) Payra P/S dia-4 mid CB was closed at 11:25.
r) HVDC 10C04C Bus reactor-2 was under shut down from 11:27 to 16:13 for C/M.
s) Manikganj-Bangabhaban 132 kV Ckt was shut down at 10:49 for D/W by DPDC.
t) Bhola Natun Bidyut GT-2 tripped at 11:51.
u) Tongi 230/132 kV T-01 transformer was under shut down from 09:34 to 17:30 for C/M.
v) Ashuganj 230 kV Bus-01 was under shut down from 07:33 to 17:58 for C/M.
w) Payra 132 kV Bus-2 was under shut down from 09:33 to 18:21 for C/M.
x) Ashuganj 400/230 kV T-02 transformer tripped at 16:06 showing OLTC Oil temperature high and was
switched on at 16:45.
y) Ullon-Dhanmondi 132 kV Ckt-1 was under shut down from 17:08 to 00:25(23/02/2022) for C/M.
z) Bheramara GK 132/33 kV T-3 transformer was under shut down from 16:40 to 17:57 for C/M. | [5 empty] | About 05 MW power interruption occurred under
Bheramara GK S/S area from 16:40 to 17:57.
aa) Ashuganj-Ashuganj(S) 230 kV Ckt-2 was opened at 18:11 from Ashuganj end due to R-phase flushing.
ab) Ullon-Dhanmondi 132 kV Ckt-3 was shut down at 00:05(23/02/2022) for C/M.
ac) Aminbazar-Kallyanpur 132 kV Ckt-1 was shut down at 06:46(23/02/2022) for A/M.
ad) Kallyanpur 132/33 kV T-3 transformer was shut down at 06:40(23/02/2022) for C/M.
ae) Aminbazar-Kallyanpur 230 kV Ckt-2 was shut down at 07:43(23/02/2022) for A/M.
af) Sunamganj 132/33 kV T-1 & T-2 transformers were shut down at 07:45(23/02/2022) for D/W. | [5 empty] | About 20 MW power interruption has been running
under Sunamganj S/S area since 07:45(23/02/2022).
ag) Bheramara 360 MW CCPP tripped at 07:55(23/02/2022) due to RMS outlet pressure low.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-02-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 7630155
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 341 | 8096000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5280150 | GT-2 S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 507508
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 11 | 140811 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 387396
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 85 | 1071648 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1090440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 688320
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 947081
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 840251
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1263660 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 646900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 832700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 435360 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 4616726
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 106 | 148242 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 139409
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 136669
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1668530
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2097600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 1959360 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3072960 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 210729
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1170360
| Dhaka area Total |  |  |  | 5696 | 2702 | 45078965
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 176857
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 133785
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 586080 | 33 kV feeder problem.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1606473 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 98 | 1149999
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 147490 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1156800 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 437088 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 6 | 492720
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 98 | 1727040 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29371
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 5000618
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 64763 | High Voltage
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 29 | 281854 | High Voltage
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 369600
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2547982
| Chattogram area Total |  |  |  | 2382 | 987 | 15908520
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 5288000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7183000 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7158000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 322128 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 142080 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 42 | 1108864 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 2529152
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 388440 | Engine problem
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 123 | 2952580 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 57 | 752160 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 502416
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 184500 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2268480
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 524900 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1123493
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 491130
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 833340
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 228480 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444960 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 0 | 0
| Cumilla Area Total |  |  |  | 2899 | 1624 | 34643557
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 4350720 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 483084
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13350
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 3528000
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 103 | 1555200 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 299480
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 530880
| Mymensingh Area Total |  |  |  | 622 | 496 | 10760714
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 976552 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2922463 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 270 | 6210000 | GT-1 S/D due to gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 45 | 1092600 | Engine problem
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 169536
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1473888
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1848960
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 384000 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7210500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252000
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8662700
| Sylhet Area Total |  |  |  | 2377 | 1390 | 31918199
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 715 | 17134545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 181440 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 4 | 9856
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 45 | 897984 | Synchronized at 15:30.
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 28 | 42240 | Low demand.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 1448640 | Engine problem
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 522000
| Khulna Area Total |  |  |  | 2229 | 907 | 20236705
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 461300 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2199795 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 84 | 1161667 | Engine problem
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 400 | 9127800 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 3252409
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 710 | 16202971
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 396928 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 44 | 336740 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 559556 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 315079 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 189 | 4944336 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 11709 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 286255 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 513120
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 197586 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1073818
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 985608
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 30 | 37365 | Low demand.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 112 | 1733856
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1419264
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31320
| Rajshahi Area Total |  |  |  | 2129 | 819 | 12842540
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4865400 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1953388
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41778
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 67392 | On test
| Rangpur Area Total |  |  |  | 605 | 312 | 6927958
| Total |  |  |  | 20985 | 9947 | 194520129
| Eastern Grid Total |  |  |  | 13976 | 7199 | 138309955
| Western Grid Total |  |  |  | 7009 | 2748 | 56210174
| National Grid Total |  |  |  | 20985 | 9947 | 194520129
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-02-22
(a) ENTIRE EASTERN GRID : |  | 6510 | MW | (b) ENTIRE WESTERN GRID : |  | 3094 | MW
i) Dhaka area |  | 3458 | MW | i) Khulna area |  | 1118 | MW
ii) Chittagong area |  | 1070 | MW | ii) Rajshahi area |  | 1027 | MW
iii) Comilla area |  | 778 | MW | iii) Barisal area |  | 252 | MW
iv) Mymensingh area |  | 865 | MW | iv) Rangpur area |  | 697 | MW
v) Sylhet area |  | 339 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9604 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 99 | 19:00 | Valuka | 96 | 9:00 | Noapara | 40 | 19:00
Munsiganj | 64 | 21:00 | Tangail | 176 | 18:30 | Jessore | 90 | 19:00
Sonargaon | 60 | 18:30 | Mymensing | 180 | 18:30 | Benapol | 44 | 12:00
Bhulta | 196 | 12:00 | Kishoreganj | 110 | 20:00 | Jhenida(Old) | 83 | 19:00
Madanganj | 35 | 13:00 | Netrokona | 112 | 8:00 | Bottail | 98 | 18:30
Rahim steel | 8 | 18:00 | Jamalpur | 125 | 8:00 | G.K Project | 35 | 19:00
Ghorasal | 60 | 22:00 | Sherpur | 132 | 8:00 | Faridpur | 96 | 21:00
Narsingdi | 139 | 19:30 | Srimongal | 41 | 19:00 | Rajbari | 44 | 18:30
Haripur(SBU) | 106 | 10:00 | Shahjibazar | 72 | 20:00 | Madaripur | 64 | 20:00
Sreenagar | 28 | 21:00 | Fenchuganj | 28 | 18:00 | Sariatpur | 44 | 21:00
Shyampur | 164 | 11:00 | Kulawara | 28 | 19:00 | Gopalganj | 60 | 19:00
Shitalakhya | 94 | 11:00 | Sylhet | 91 | 19:30 | Bagerhat | 71 | 22:00
Matuail | 48 | 10:00 | Chatak | 13 | 18:00 | Mongla | 42 | 13:00
Char Saidpur | 39 | 18:00 | Sunamganj | 32 | 18:30 | Satkhira | 74 | 20:00
Ullon | 22 | 18:00 | Biani Bazar | 39 | 18:30 | Gallamari | 28 | 13:00
Hasnabad | 63 | 13:00 | Comilla (S) | 120 | 20:00 | Magura | 40 | 18:30
Magbazar | 70 | 14:00 | Comilla(N) | 80 | 19:00 | Norail | 30 | 19:00
Maniknagar | 47 | 13:00 | Chandpur | 48 | 21:00 | Chuadanga | 64 | 19:00
Bangabhaban | 5 | 9:00 | Feni | 81 | 18:00 | Barisal(N) | 29 | 19:30
Motijheel | 28 | 13:00 | Chowmuhani | 134 | 21:00 | Barisal (S) | 80 | 20:00
Narinda | 40 | 14:00 | Ashuganj | 24 | 13:00 | Patuakhali | 76 | 20:00
Kazla | 66 | 18:00 | Daudkandi | 86 | 19:00 | Bhandaria | 38 | 19:00
Dhanmondi | 118 | 13:00 | B.Baria | 104 | 18:30 | Borguna | 12 | 21:00
Lalbag | 75 | 13:00 | Ramganj | 56 | 20:00 | Borhan Uddin | 29 | 22:00
Madartek | 45 | 21:00 | Chaddagram | 26 | 9:00 | Ishurdi | 49 | 19:00
Dhaka University | 21 | 13:00 | PHP | 6 | 1:00 | Ruppur Paromanobik | 3 | 15:00
Aftabnagar | 19 | 13:00 | Kochua | 40 | 18:30 | Natore | 97 | 19:00
Fatullah | 48 | 12:00 | Madunaghat | 36 | 18:00 | Bogra | 105 | 8:00
Nawabganj | 32 | 21:00 | Hathazari | 66 | 19:00 | Naogaon | 104 | 13:00
Keraniganj | 50 | 18:30 | Khulshi | 147 | 15:00 | Rajshahi | 86 | 19:00
Banani | 37 | 15:00 | Halishahar | 65 | 17:00 | Rajshahi New | 32 | 20:00
Mirpur | 84 | 18:30 | Baraulia | 112 | 10:00 | C.Nawabganj | 61 | 13:00
Kalyanpur | 60 | 18:30 | Sikalbaha | 21 | 18:30 | Amnura | 44 | 19:00
Gulshan | 70 | 14:00 | Dohazari | 74 | 18:30 | Pabna | 72 | 19:00
Uttara | 42 | 18:30 | Cox'sbazar | 81 | 18:30 | Shahjadpur | 82 | 8:00
Uttara New | 22 | 18:00 | Chandraghona | 22 | 18:00 | Serajganj | 90 | 19:30
Kamrangirchar | 55 | 19:00 | Kaptai | 4 | 18:30 | Niyamatpur | 85 | 9:00
Savar | 135 | 10:00 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 51 | 8:00
Bhasantec | 86 | 18:30 | Bakulia | 88 | 19:00 | Sherpur(Bogura) | 50 | 18:30
Agargaon | 53 | 13:00 | Julda | 24 | 14:00 | Mohastangor | 48 | 18:30
Satmosjid | 67 | 13:00 | TK chemical | 21 | 18:30 | Bhangura | 28 | 7:00
Old Tongi | 95 | 12:00 | Modern Steel | 0 | 1:00 | Rangpur | 106 | 19:00
Kabirpur | 197 | 12:00 | Shahmirpur | 28 | 8:00 | Lalmonirhat | 36 | 18:30
Manikgonj | 63 | 19:00 | Khagrachhari | 20 | 18:30 | Saidpur | 92 | 18:30
Joydevpur | 155 | 18:30 | Matarbari | 28 | 18:00 | Purbasadipur | 99 | 13:00
New Tongi | 61 | 12:00 | Baroiar Hat | 33 | 18:30 | Thakurgaon | 67 | 19:00
Kodda | 203 | 18:30 | Rangamati | 10 | 18:30 | Palashbari | 96 | 8:00
Dhamrai | 76 | 18:30 | Abul Khair 230 | 15 | 18:00 | Barapukuria | 50 | 11:00
Rajendrapur | 88 | 19:00 | BSRM | 166 | 16:00 | Panchagar | 46 | 19:00
Bashundara | 98 | 19:00 | GPH Ispat | 98 | 2:00 | Joldhaka | 49 | 19:00
Purbachal | 12 | 12:00 | Agrabad | 52 | 21:00 | Kurigram | 49 | 18:30
Tongi Millgate | 38 | 11:00 | Goalpara | 21 | 13:00 | Mithapukur | 29 | 19:00
Bashundhara Cement |  |  | Central S/S | 75 | 20:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-02-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 419 | 7:00 | 411 | 16:00 | Kaliakoir | 414 | 0.125 | 400 | 0.66667
| Bheramara | 401 | 20:00 | 393 | 10:00 | Bhulta | 417 | 0.29167 | 399 | 0.5
| Ashuganj(N) | 420 | 7:00 | 403 | 12:00 | Gopalganj | 417 | 0.625 | 410 | 0.79167
| Payra | 418 | 7:00 | 411 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 245 | 1:00 | 245 | 1:00 | Hathazari | 244 | 22:00 | 233 | 12:00
| Ishurdi | 242 | 3:00 | 225 | 8:00 | Megnaghat | 246 | 1:00 | 239 | 14:00
| Ashuganj | 247 | 6:00 | 236 | 12:00 | Fenchuganj | 246 | 6:00 | 243 | 13:00
| Serajganj | 241 | 22:00 | 227 | 8:00 | Siddhirganj | 242 | 6:00 | 232 | 16:00
| Baghabari | 241 | 23:00 | 227 | 9:00 | Maniknagar | 240 | 6:00 | 230 | 16:00
| Barapukuria | 236 | 1:00 | 224 | 12:00 | Agargaon | 242 | 1:00 | 232 | 12:00
| Bogra | 238 | 22:00 | 221 | 9:00 | Barisal | 245 | 7:00 | 242 | 12:00
| Rajshahi | 242 | 22:00 | 222 | 8:00 | Bhola 225 MW | 249 | 3:00 | 245 | 10:00
| Khulna South | 245 | 3:00 | 223 | 8:00 | AKSML | 244 | 7:00 | 227 | 5:00
| Rampura | 241 | 1:00 | 231 | 12:00 | BSRM | 243 | 24:00 | 231 | 12:00
| Haripur | 241 | 6:00 | 230 | 12:00 | Bibiyana | 248 | 1:00 | 241 | 12:00
| Hasnabad | 242 | 8:00 | 231 | 17:00 | Bhulta | 242 | 7:00 | 231 | 12:00
| Shyampur | 241 | 7:00 | 230 | 12:00 | Ashuganj (S) | 243 | 4:00 | 234 | 12:00
| Aminbazar | 243 | 1:00 | 234 | 2:00 | Kaliakoir | 241 | 1:00 | 232 | 12:00
| Tongi | 239 | 18:30 | 232 | 12:00 | GPH | 243 | 24:00 | 229 | 5:00
| Comilla (N) | 242 | 7:00 | 232 | 12:00 | Jhenaidah | 241 | 3:00 | 220 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 7:00 | 131 | 12:00 | PHP | 140 | 7:00 | 134 | 12:00
| Munsiganj | 139 | 8:00 | 132 | 16:00 | Kachua | 141 | 7:00 | 136 | 12:00
| Sonargaon | 136 | 1:00 | 133 | 15:00 | Madanhat | 142 | 21:00 | 136 | 10:00
| Bhulta | 132 | 3:00 | 124 | 12:00 | Hathazari | 143 | 22:00 | 135 | 12:00
| Madanganj | 138 | 8:00 | 130 | 16:00 | Khulshi | 140 | 0:00 | 134 | 11:00
| Rahim steel | 137 | 1:00 | 131 | 12:00 | Halishahar | 142 | 7:00 | 135 | 11:00
| Ghorasal | 146 | 22:00 | 145 | 1:00 | Baraulia | 142 | 7:00 | 133 | 4:00
| Narsingdi | 137 | 5:00 | 132 | 12:00 | Sikalbaha | 142 | 19:00 | 133 | 4:00
| Haripur(SBU) | 137 | 1:00 | 131 | 12:00 | Dohazari | 138 | 9:00 | 132 | 15:00
| Sreenagar | 137 | 4:00 | 129 | 12:00 | Cox'sbazar | 132 | 4:00 | 127 | 12:00
| Shyampur | 134 | 6:00 | 127 | 12:00 | Chandraghona | 143 | 22:00 | 135 | 5:00
| Shitalakhya | 138 | 7:00 | 131 | 16:00 | Kaptai | 140 | 1:00 | 135 | 11:00
| Matuail | 138 | 7:00 | 131 | 12:00 | A. Khaer Stl. | 141 | 1:00 | 136 | 10:00
| Char Saidpur | 138 | 7:00 | 131 | 17:00 | Bakulia | 142 | 7:00 | 134 | 12:00
| Ullon | 134 | 4:00 | 127 | 12:00 | Julda | 140 | 1:00 | 134 | 11:00
| Hasnabad | 139 | 7:00 | 131 | 17:00 | TK Chemical | 141 | 7:00 | 134 | 12:00
| Magbazar | 135 | 2:00 | 127 | 12:00 | Modern Steel | 142 | 19:30 | 136 | 7:00
| Maniknagar | 136 | 1:00 | 130 | 12:00 | Shahmirpur | 142 | 20:00 | 132 | 3:00
| Bangabhaban | 136 | 1:00 | 130 | 12:00 | Khagrachhari | 141 | 21:00 | 135 | 5:00
| Motijheel | 136 | 1:00 | 130 | 12:00 | Matarbari | 134 | 9:00 | 128 | 12:00
| Narinda | 136 | 1:00 | 130 | 12:00 | Baroiar Hat | 140 | 1:00 | 135 | 11:00
| Kazla | 136 | 1:00 | 130 | 12:00 | Rangamati | 141 | 1:00 | 136 | 11:00
| Dhanmondi | 138 | 1:00 | 131 | 12:00 | Agrabad | 141 | 20:00 | 134 | 4:00
| Lalbag | 137 | 5:00 | 129 | 12:00 | Goalpara S/S | 139 | 3:00 | 128 | 8:00
| Madartek | 133 | 1:00 | 127 | 12:00 | Khulna Central S/S | 139 | 3:00 | 130 | 12:00
| Dhaka University | 136 | 1:00 | 130 | 12:00 | Noapara | 139 | 4:00 | 126 | 8:00
| Aftabnagar | 134 | 7:00 | 127 | 12:00 | Jessore | 136 | 23:00 | 124 | 8:00
| Fatullah | 135 | 7:00 | 128 | 12:00 | Benapol | 137 | 3:00 | 123 | 8:00
| Nawabganj | 135 | 21:00 | 129 | 12:00 | Jhenida(Old) | 137 | 22:00 | 127 | 8:00
| Keraniganj | 137 | 6:00 | 130 | 12:00 | Bottail | 140 | 3:00 | 127 | 8:00
| Banani | 134 | 6:00 | 127 | 16:00 | G.K Project | 141 | 22:00 | 132 | 8:00
| Mirpur | 136 | 3:00 | 128 | 12:00 | Faridpur | 138 | 18:00 | 132 | 11:00
| Kalyanpur | 135 | 1:00 | 128 | 15:00 | Rajbari | 138 | 3:00 | 131 | 8:00
| Gulshan | 134 | 4:00 | 126 | 12:00 | Madaripur | 143 | 5:00 | 139 | 8:00
| Uttara | 139 | 8:00 | 131 | 16:00 | Shariyatpur S/S | 142 | 3:00 | 138 | 9:00
| Uttara New | 138 | 1:00 | 131 | 12:00 | Gopalganj | 141 | 1:00 | 138 | 6:00
| Kamrangirchar | 137 | 1:00 | 130 | 12:00 | Bagerhat | 138 | 4:00 | 126 | 8:00
| Savar | 136 | 7:00 | 129 | 12:00 | Mongla | 136 | 4:00 | 127 | 8:00
| Bhasantec | 134 | 3:00 | 128 | 12:00 | Satkhira | 137 | 4:00 | 125 | 8:00
| Agargaon | 135 | 6:00 | 128 | 16:00 | Gallamari | 142 | 4:00 | 136 | 8:00
| Satmosjid | 134 | 1:00 | 128 | 16:00 | Magura | 139 | 1:00 | 128 | 8:00
| Old Tongi | 139 | 7:00 | 134 | 12:00 | Narail | 138 | 3:00 | 125 | 8:00
| Kabirpur | 138 | 1:00 | 129 | 12:00 | Chuadanga | 135 | 1:00 | 123 | 12:00
| Manikgonj | 135 | 0:00 | 127 | 16:00 | Barisal(N) | 143 | 1:00 | 141 | 9:00
| Joydevpur | 144 | 1:00 | 137 | 12:00 | Barisal (S) | 143 | 3:00 | 139 | 12:00
| New Tongi | 140 | 7:00 | 131 | 15:00 | Patuakhali(S) | 137 | 4:00 | 134 | 13:00
| Kodda | 140 | 7:00 | 130 | 15:00 | Bhandaria | 144 | 6:00 | 138 | 18:30
| Dhamrai | 137 | 3:00 | 130 | 16:00 | Borguna | 144 | 5:00 | 140 | 12:00
| Rajendrapur | 138 | 8:00 | 128 | 16:00 | Jhenaidah(New) | 139 | 3:00 | 127 | 8:00
| Bashundara | 138 | 2:00 | 129 | 16:00 | Ishurdi | 140 | 18:00 | 129 | 8:00
| Purbachal | 134 | 1:00 | 127 | 12:00 | Ruppur Paromanobik | 138 | 20:00 | 130 | 8:00
| Tongi Millgate | 138 | 1:00 | 131 | 17:00 | Natore | 140 | 18:00 | 128 | 8:00
| Bashundhara Cement |  |  |  |  | Bogra | 139 | 2:00 | 131 | 8:00
| Valuka | 132 | 1:00 | 121 | 12:00 | Noagaon | 136 | 18:00 | 121 | 8:00
| Tangail | 135 | 1:00 | 127 | 12:00 | Rajshahi | 139 | 18:00 | 128 | 8:00
| Mymensing | 133 | 1:00 | 124 | 12:00 | Rajshahi New | 138 | 18:00 | 126 | 7:00
| Kishorganj | 136 | 1:00 | 129 | 12:00 | C.Nawabganj | 138 | 18:00 | 127 | 12:00
| Netrokona | 133 | 1:00 | 120 | 12:00 | Amnura | 138 | 18:00 | 122 | 8:00
| Jamalpur | 140 | 22:00 | 128 | 6:00 | Pabna | 139 | 18:00 | 130 | 8:00
| Sherpur | 138 | 22:00 | 126 | 6:00 | Shahjadpur | 143 | 18:00 | 133 | 7:00
| Srimongal | 143 | 6:00 | 138 | 16:00 | Serajganj | 138 | 3:00 | 127 | 8:00
| Shahjibazar | 140 | 7:00 | 136 | 12:00 | Niyamatpur | 134 | 18:00 | 115 | 8:00
| Fenchuganj | 141 | 6:00 | 138 | 13:00 | Joypurhat | 136 | 18:00 | 119 | 8:00
| Khulawara | 141 | 1:00 | 138 | 12:00 | Sherpur(Bogura) | 139 | 18:00 | 128 | 8:00
| Sylhet | 139 | 1:00 | 135 | 12:00 | Mohastangor | 138 | 18:00 | 127 | 8:00
| Chatak | 139 | 1:00 | 134 | 13:00 | Bhangura | 141 | 3:00 | 132 | 10:00
| Sunamganj | 138 | 1:00 | 132 | 18:00 | Rangpur | 135 | 18:00 | 122 | 8:00
| Biani Bazar | 139 | 3:00 | 134 | 12:00 | Lalmonirhat | 133 | 2:00 | 121 | 8:00
| Comilla(s) | 129 | 1:00 | 125 | 11:00 | Saidpur | 135 | 18:00 | 120 | 9:00
| Comilla(n) | 143 | 7:00 | 137 | 12:00 | Purbasadipur | 133 | 2:00 | 116 | 8:00
| Chandpur | 141 | 13:00 | 137 | 16:00 | Thakurgaon | 134 | 4:00 | 116 | 8:00
| Feni | 140 | 7:00 | 135 | 11:00 | Palashbari | 134 | 18:00 | 126 | 8:00
| Chowmuhani | 138 | 13:00 | 133 | 12:00 | Barapukuria | 136 | 1:00 | 124 | 12:00
| Ashuganj | 142 | 7:00 | 139 | 12:00 | Panchagar | 135 | 4:00 | 118 | 9:00
| Daudkandi | 139 | 1:00 | 133 | 16:00 | Joldhaka | 135 | 3:00 | 117 | 8:00
| B.Baria | 139 | 7:00 | 134 | 12:00 | Kurigram | 133 | 2:00 | 119 | 9:00
| Ramganj | 138 | 1:00 | 134 | 12:00 | Mithapukur | 137 | 18:30 | 125 | 8:00
| Chaddagram | 140 | 9:00 | 136 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-02-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 160 | 5542 | 2237 | 7779 |  |  |  | QF-LDC-11
0:30 | 156 | 5065 | 2041.5 | 7106.5 | Date: | 2022-02-22
1:00 | 152 | 4588 | 1846 | 6434
1:30 | 128 | 4449.5 | 1815 | 6264.5
2:00 | 104 | 4311 | 1784 | 6095
2:30 | 103 | 4253 | 1757.5 | 6010.5 | [5 empty] | Gen. at Eve. Peak | 9947 | 9947 MW (19:00 )
3:00 | 102 | 4195 | 1731 | 5926 | [6 empty] | 19:00
3:30 | 93 | 4113.5 | 1721 | 5834.5 | [5 empty] | Gen. at Day Peak | 8832 | 8832 MW (12:00 )
4:00 | 84 | 4032 | 1711 | 5743 | [6 empty] | 12:00
4:30 | 106 | 4059.5 | 1675 | 5734.5 | [5 empty] | Highest Generation | 9947
5:00 | 128 | 4087 | 1639 | 5726 | [6 empty] | 19:00
5:30 | 178 | 4207 | 1692 | 5899
6:00 | 228 | 4327 | 1745 | 6072
6:30 | 316 | 4567.5 | 1874.5 | 6442
7:00 | 404 | 4808 | 2004 | 6812
7:30 | 490 | 5193.5 | 2131 | 7324.5
8:00 | 576 | 5579 | 2258 | 7837
8:30 | 534 | 5881.5 | 2306.5 | 8188
9:00 | 492 | 6184 | 2355 | 8539
9:30 | 422 | 6227 | 2334.5 | 8561.5
10:00 | 352 | 6270 | 2314 | 8584
10:30 | 360 | 6276 | 2343 | 8619
11:00 | 368 | 6282 | 2372 | 8654
11:30 | 358 | 6372.5 | 2370.5 | 8743
12:00 | 348 | 6463 | 2369 | 8832
12:30 | 355 | 6547 | 2430.5 | 8977.5
13:00 | 362 | 6631 | 2492 | 9123
13:30 | 264 | 6426.5 | 2454.5 | 8881
14:00 | 166 | 6222 | 2417 | 8639
14:30 | 97 | 6138 | 2452 | 8590
15:00 | 28 | 6054 | 2487 | 8541
15:30 | 55 | 5942.5 | 2423 | 8365.5
16:00 | 82 | 5831 | 2359 | 8190
16:30 | 62 | 5817.5 | 2353.5 | 8171
17:00 | 42 | 5804 | 2348 | 8152
17:30 | 69 | 6038 | 2403.5 | 8441.5
18:00 | 96 | 6272 | 2459 | 8731
18:30 | 300 | 6735.5 | 2603.5 | 9339
19:00 | 504 | 7199 | 2748 | 9947
19:30 | 462 | 7094 | 2735 | 9829
20:00 | 442 | 6982 | 2784 | 9766 |  |  |  | Executive Engineer
20:30 | 369 | 6836 | 2788.5 | 9624.5 |  |  |  | Network Operation Division
21:00 | 296 | 6690 | 2793 | 9483
21:30 | 210 | 6504.5 | 2772.5 | 9277
22:00 | 124 | 6319 | 2752 | 9071 |  |  |  |  | Page 6 of 7
22:30 | 96 | 6031.5 | 2619 | 8650.5
23:00 | 68 | 5744 | 2486 | 8230
23:30 | 114 | 5643 | 2361.5 | 8004.5
24:00 | 160 | 5542 | 2237 | 7779
9947 MW (19:00 )
8832 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-02-22 |  | Energy |  | 194520129
[13 empty] | 2022-02-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2955 | 715 | 1449 | 0 | 1880 | 620 | 70 | 0 | 0 | 90 | 0 | 0
0:30 | 2859.5 | 715 | 1442.5 | 0 | 1365 | 574.5 | 70 | 0 | 0 | 80 | 0 | 0 | Date: | 2022-02-22
1:00 | 2764 | 715 | 1436 | 0 | 850 | 529 | 70 | 0 | 0 | 70 | 0 | 0
1:30 | 2812 | 715 | 1422.5 | 0 | 646 | 529.5 | 69.5 | 0 | 0 | 70 | 0 | 0 | [8 empty] | Total Energy | 194.5201 | Total Energy Gen 194.520 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 194.520 MKWHr
2:00 | 2860 | 715 | 1409 | 0 | 442 | 530 | 69 | 0 | 0 | 70 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2820.5 | 691.5 | 1415.5 | 0 | 420.5 | 525 | 68.5 | 0 | 0 | 69 | 0 | 0 | [8 empty] | Energy Requirement | 194.5201
3:00 | 2781 | 668 | 1422 | 0 | 399 | 520 | 68 | 0 | 0 | 68 | 0 | 0
3:30 | 2789 | 668 | 1380 | 0 | 354 | 510 | 66.5 | 0 | 0 | 67 | 0 | 0 | [6 empty] | Shortage
4:00 | 2797 | 668 | 1338 | 0 | 309 | 500 | 65 | 0 | 0 | 66 | 0 | 0
4:30 | 2813 | 667.5 | 1319 | 0 | 300.5 | 500 | 67.5 | 0 | 0 | 67 | 0 | 0
5:00 | 2829 | 667 | 1300 | 0 | 292 | 500 | 70 | 0 | 0 | 68 | 0 | 0
5:30 | 2792 | 691 | 1363.5 | 0 | 417 | 500 | 67.5 | 0 | 0 | 68 | 0 | 0
6:00 | 2755 | 715 | 1427 | 0 | 542 | 500 | 65 | 0 | 0 | 68 | 0 | 0
6:30 | 2761.5 | 715 | 1433 | 0 | 887.5 | 500 | 67.5 | 0 | 0 | 74 | 3.5 | 0 |  |  |  |  | Coal
7:00 | 2768 | 715 | 1439 | 0 | 1233 | 500 | 70 | 0 | 0 | 80 | 7 | 0
7:30 | 2734.5 | 715 | 1427.5 | 0 | 1766.5 | 500 | 69.5 | 0 | 0 | 85 | 26.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2701 | 715 | 1416 | 0 | 2300 | 500 | 69 | 0 | 0 | 90 | 46 | 0
8:30 | 2705.5 | 715 | 1418.5 | 0 | 2557.5 | 505 | 69.5 | 0 | 59 | 91 | 67 | 0
9:00 | 2710 | 715 | 1421 | 0 | 2815 | 510 | 70 | 0 | 118 | 92 | 88 | 0
9:30 | 2724.5 | 715 | 1415.5 | 0 | 2791 | 505 | 70 | 0 | 116.5 | 98 | 126 | 0
10:00 | 2739 | 715 | 1410 | 0 | 2767 | 500 | 70 | 0 | 115 | 104 | 164 | 0
10:30 | 2778 | 714.5 | 1404.5 | 0 | 2750 | 500 | 67.5 | 0 | 125.5 | 106 | 173 | 0
11:00 | 2817 | 714 | 1399 | 0 | 2733 | 500 | 65 | 0 | 136 | 108 | 182 | 0
11:30 | 2870.5 | 714.5 | 1365 | 0 | 2766 | 500 | 69 | 0 | 152.5 | 109 | 196.5 | 0
12:00 | 2924 | 715 | 1331 | 0 | 2799 | 500 | 73 | 0 | 169 | 110 | 211 | 0
12:30 | 2866 | 715 | 1339 | 0 | 2963 | 520 | 72.5 | 0 | 183.5 | 110 | 208.5 | 0
13:00 | 2808 | 715 | 1347 | 0 | 3127 | 540 | 72 | 0 | 198 | 110 | 206 | 0
13:30 | 2808 | 715 | 1347 | 0 | 3127 | 540 | 72 | 0 | 198 | 110 | 206 | 0
14:00 | 2808 | 715 | 1347 | 0 | 3127 | 540 | 72 | 0 | 198 | 110 | 206 | 0
14:30 | 2776.5 | 715.5 | 1366.5 | 0 | 2855.5 | 529.5 | 69.5 | 0 | 235 | 108 | 176 | 0
15:00 | 2745 | 716 | 1386 | 0 | 2584 | 519 | 67 | 0 | 272 | 106 | 146 | 0
15:30 | 2728.5 | 716 | 1377 | 0 | 2497.5 | 509 | 50.5 | 0 | 269.5 | 107 | 110.5 | 0
16:00 | 2712 | 716 | 1368 | 0 | 2411 | 499 | 34 | 0 | 267 | 108 | 75 | 0
16:30 | 2702 | 716 | 1381.5 | 0 | 2392 | 499.5 | 52 | 0 | 270 | 107 | 46 | 0
17:00 | 2702 | 716 | 1395 | 0 | 2373 | 500 | 70 | 0 | 273 | 106 | 17 | 0
17:30 | 2723 | 715.5 | 1372 | 0 | 2576.5 | 495 | 66.5 | 0 | 373 | 111 | 9 | 0
18:00 | 2744 | 715 | 1349 | 0 | 2780 | 490 | 63 | 0 | 473 | 116 | 1 | 0
18:30 | 2797.5 | 715 | 1385.5 | 182 | 3026.5 | 544.5 | 66.5 | 0 | 505 | 116 | 0.5 | 0
19:00 | 2851 | 715 | 1422 | 364 | 3273 | 599 | 70 | 0 | 537 | 116 | 0 | 0
19:30 | 2822 | 716 | 1420 | 172 | 3347 | 639 | 70 | 0 | 527 | 116 | 0 | 0
20:00 | 2883 | 715 | 1423 | 61 | 3321 | 649 | 67 | 0 | 527 | 120 | 0 | 0
20:30 | 2870.5 | 715.5 | 1433.5 | 30.5 | 3280 | 654.5 | 67 | 0 | 457 | 116 | 0 | 0
21:00 | 2858 | 716 | 1444 | 0 | 3239 | 660 | 67 | 0 | 387 | 112 | 0 | 0
21:30 | 2871 | 715.5 | 1453 | 0 | 3131 | 660 | 68.5 | 0 | 269 | 109 | 0 | 0
22:00 | 2884 | 715 | 1462 | 0 | 3023 | 660 | 70 | 0 | 151 | 106 | 0 | 0
22:30 | 2913 | 715 | 1446 | 0 | 2659.5 | 645 | 70 | 0 | 98 | 104 | 0 | 0
23:00 | 2942 | 715 | 1430 | 0 | 2296 | 630 | 70 | 0 | 45 | 102 | 0 | 0
23:30 | 2948.5 | 715 | 1439.5 | 0 | 2088 | 625 | 70 | 0 | 22.5 | 96 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 28.8° C
24:00 | 2955 | 715 | 1449 | 0 | 1880 | 620 | 70 | 0 | 0 | 90 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 194.520 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 194.520 MKWHr
Note on W13: Author:

## Generation
g | 2022-02-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 70 | 69 | 68 | 65 | 70 | 65 | 70 | 69 | 70 | 70 | 65 | 73 | 72 | 60 | 67 | 34 | 70 | 63 |  | 70 | 70 | 67 | 67 | 70 | 70 | 70 | 1606473
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 2 | 20 | 25 | 25 | 8 | 8 | 14 |  | 25 | 25 | 25 | 8 |  |  | 0 | 176857
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 7 | 13 | 17 | 19 | 20 | 20 | 18 | 14 | 8 | 3 | [9 empty] | 133785
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 |  |  |  | 0 | 147490
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [5 empty] | 8 | 17 | 17 | 31 | 51 | 51 | 51 | 102 | 51 | 51 | 51 | 51 | 64 |  | 98 | 105 | 105 | 85 | 51 | 51 | 51 | 1149999
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [8 empty] | 33 | 33 | 24 | 24 | 24 | 32 | 32 | 32 | 42 | 42 |  | 42 | 33 | 33 | 33 |  |  | 0 | 388440
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [5 empty] | 5 | 30 | 133 | 268 | 275 | 275 | 290 | 298 | 298 | 290 | 283 | 290 | 298 |  | 298 | 298 | 300 | 298 | 298 | 195 | 30 | 4616726
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 7630155
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 16 |  | 26 | 26 | 29 | 29 | 29 | 26 | 29 | 322128
33 | Ashuganj 225 MW CCPP | 228 | 229 | 229 | 228 | 228 | 228 | 233 | 234 | 232 | 230 | 231 | 224 | 225 | 223 | 226 | 224 | 190 | 188 |  | 189 | 187 | 185 | 168 | 205 | 219 | 227 | 5288000
34 | Ashuganj 450 MW CCPP(South) | 275 | 345 | 305 | 310 | 330 | 305 | 310 | 270 | 270 | 270 | 270 | 320 | 300 | 275 | 270 | 280 | 270 | 300 |  | 305 | 300 | 300 | 265 | 265 | 265 | 270 | 7158000
| Ashuganj 450 MW CCPP(North) | 260 | 295 | 260 | 260 | 285 | 260 | 265 | 280 | 280 | 280 | 280 | 345 | 300 | 280 | 280 | 290 | 280 | 280 |  | 320 | 310 | 310 | 280 | 260 | 260 | 260 | 7183000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142080
36 | Chandpur 150 MW CCPP | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 123 | 124 | 122 | 124 | 122 | 125 | 124 | 124 |  | 123 | 124 | 122 | 122 | 123 | 123 | 123 | 2952580
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5280150
41 | Haripur 360MW CCPP(HPL) | 332 | 332 | 332 | 332 | 332 | 332 | 332 | 332 | 332 | 342 | 360 | 347 | 342 | 336 | 337 | 335 | 335 | 292 |  | 341 | 342 | 342 | 345 | 345 | 350 | 350 | 8096000
42 | RPCL 210MW CCPP | 220 | 220 | 220 | 220 | 220 | 221 | 222 | 221 | 219 | 216 | 192 | 175 | 146 | 145 | 156 | 156 | 156 | 157 |  | 157 | 159 | 160 | 152 | 145 | 155 | 153 | 4350720
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 10 | 26 | 37 | 30 | 48 | 45 | 41 | 30 | 17 | 5 | 0 | [8 empty] | 299480
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 976552
46 | Shajibazar 330 MW CCPP | 270 | 272 | 269 | 271 | 269 | 271 | 271 | 272 | 271 | 270 | 269 | 272 | 268 | 271 | 272 | 268 | 272 | 274 |  | 270 | 271 | 268 | 268 | 269 | 271 | 274 | 6210000
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 69 | 69 | 69 | 69 | 71 | 71 | 71 | 70 | 68 | 68 | 66 | 66 | 40 | 40 | 40 | 40 | 67 |  | 67 | 67 | 67 | 68 | 69 | 68 | 70 | 1473888
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 10 | 10 | 81 | 81 | 81 | 81 | 81 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1848960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252000
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 169536
55 | Fenchugonj 51 MW PP (Barakatullah) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 42 | 42 | 42 | 42 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1092600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384000
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 300 | 300 | 305 | 310 | 300 | 285 | 310 | 290 | 280 | 300 | 310 | 275 | 290 | 270 | 290 | 280 |  | 305 | 300 | 290 | 290 | 300 | 270 | 290 | 7210500
| Bibiyana South 400 MW | 340 | 330 | 320 | 320 | 320 | 300 | 300 | 280 | 290 | 340 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8662700
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 13 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 840251
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530880
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 437088
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 10 | 10 | 10 |  |  | 19 | 16 |  | 19 | 19 | 22 | 19 | 19 | 22 | 19 | 387396
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 483084
63 | Impoprt (Tripura) | 70 | 70 | 68 | 66 | 68 | 68 | 80 | 90 | 92 | 104 | 108 | 110 | 110 | 110 | 106 | 108 | 106 | 116 |  | 116 | 116 | 120 | 112 | 106 | 102 | 90 | 2268480
64 | Malancha, Ctg. EPZ (United) | 42 | 40 | 42 | 42 | 42 | 40 | 37 | 8 | 5 | 3 | 2 | 2 | 7 | 7 | 2 | 2 | 7 | 12 |  | 6 | 8 | 13 | 30 | 38 | 32 | 32 | 492720
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 502416
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 184500
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 25 | 25 | 16 | 25 | 33 | [9 empty] | 33 | 33 | 524900
68 | Cumilla 25 MW PP (Summit) | 21 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 491130
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 28 | 28 | 30 | 30 | 30 | 24 | 28 | 28 | 28 | 28 | 28 | 30 | 18 |  | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 663660
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 646900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 832700
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [6 empty] | 17 | 51 | 51 | 17 | 17 | 17 | 34 | 17 | 17 | 17 | 17 | 36 |  | 114 | 114 | 114 | 114 | 114 | 17 | 0 | 833340
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 14 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 228480
| Manikgonj 162MW PP(MPGL) | 162 | 54 | 17 | 17 | 17 | 57 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3072960
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 35 | 16 | 16 | 16 | 51 | 16 | 16 | 16 | 16 | 35 |  | 51 | 51 | 51 | 51 |  |  | 0 | 435360
79 | Kodda 150MW PP | [8 empty] | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 115 |  | 150 | 150 | 150 | 150 |  |  | 0 | 688320
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 25 | 25 | 25 | 26 | 51 | 52 | 52 | 52 | 49 | 43 | 47 | 48 | 45 | 45 | 49 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1123493
| Gazipur 100 MW PP | 90 | 17 | 17 | 17 | 17 | 17 | 42 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2097600
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 29371
| Jodiac Power | [17 empty] | 5 |  | 17 | 17 | 17 | 17 |  |  | 0 | 64763
| Karnaphuli Power Ltd. | [11 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 |  | 29 | 51 | 51 | 17 | 17 | 17 | 17 | 281854
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 10 | 11 | 12 | 14 | 12 | 12 | 11 | 11 | 11 | 12 |  | 11 | 12 |  |  |  |  | 0 | 140811
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 70 | 17 | 17 | 17 | 17 | 24 | 64 | 104 | 104 | 104 | 95 | 92 | 93 | 98 | 96 | 91 | 91 | 92 |  | 91 | 91 | 92 | 104 | 104 | 104 | 104 | 1959360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 51 | 51 | 51 | 51 | 51 | 1108864
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 60 | 84 | 93 | 93 | 93 | 93 | 40 | 40 | 7 | 7 | 48 |  | 85 | 93 | 93 | 93 | 93 |  | 0 | 1071648
95 | Patenga 50MW PP (Baraka) | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 25 |  | 12 | 18 | 19 | 19 | 25 | 25 | 25 | 586080
96 | Chattogram 108 MW PP (ECPV) | 51 | 19 | 13 | 12 | 12 | 23 | 65 | 79 | 89 | 80 | 78 | 80 | 82 | 82 | 78 | 83 | 84 | 90 |  | 98 | 103 | 104 | 103 | 104 | 103 | 103 | 1727040
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 2 | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 15 | 15 | 20 |  | 55 | 55 | 55 | 55 |  |  | 0 | 507508
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 947081
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2922463
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13350
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1090440
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 106 | 52 | 11 |  |  |  | 0 | 148242
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 100 | 50 | 25 |  |  |  | 0 | 139409
106 | Mymensingh 200 MW PP (United) | 60 | 24 | 24 | 24 | 24 | 24 | 65 | 185 | 189 | 193 | 193 | 192 | 192 | 192 | 192 | 192 | 192 | 192 |  | 192 | 192 | 193 | 193 | 193 | 192 | 160 | 3528000
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 100 | 50 | 25 |  |  |  | 0 | 136669
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 1 | 50 | 100 | 128 | 131 | 132 | 138 | 98 | 70 | 45 | 35 | 103 |  | 149 | 149 | 149 | 149 | 130 |  | 0 | 1668530
115 | Juldah 100 MW PP Unit-3 (Acorn) | [5 empty] | 10 | 10 | 25 | 80 | 80 | 80 | 90 | 90 | 50 | 50 | 20 | 20 | 70 |  | 90 | 90 | 90 | 90 | 60 | 60 | 60 | 1156800
116 | Chandpur 200MW (Desh energy) | [7 empty] | 12 | 17 | 17 | 17 | 17 | 41 | 85 | 17 | 17 | 17 | 24 |  | 57 | 85 | 85 | 85 | 85 | 34 | 34 | 752160
117 | Ashuganj 150MW PP (Midland) | [5 empty] | 13 | 48 | 122 | 132 | 140 | 145 | 147 | 145 | 145 | 143 | 145 | 148 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 148 | 2529152
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [6 empty] | 6 | 86 | 113 | 113 | 107 | 108 | 108 | 109 | 75 | 75 | 75 | 90 |  | 103 | 99 | 99 | 104 | 109 | 8 | 0 | 1555200
| Anwara 300 MW PP (United) | 80 | 15 | 15 | 15 | 15 | 88 | 115 | 190 | 260 | 260 | 260 | 260 | 300 | 245 | 245 | 245 | 245 | 260 |  | 300 | 300 | 300 | 300 | 283 | 282 | 283 | 5000618
| Juldah unit-2 (Acorn) | [8 empty] | 10 | 10 | 10 | 10 | 80 | 20 | 20 | 10 | 10 | 30 |  | 60 | 60 | 40 | 10 |  |  | 0 | 369600
| Anlima Energy Ltd. | 113 | 113 | 113 | 51 | 51 | 113 | 113 | 113 | 113 | 113 | 99 | 110 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 100 | 113 | 113 | 112 | 2547982
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444960
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 8 | 17 | 24 | 30 | 33 | 32 | 28 | 24 | 14 | [10 empty] | 210729
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1170360
120 | Eastern Zone Total | 4588 | 4311 | 4195 | 4032 | 4087 | 4327 | 4808 | 5579 | 6184 | 6270 | 6282 | 6463 | 6631 | 6222 | 6054 | 5831 | 5804 | 6272 |  | 7199 | 7094 | 6982 | 6690 | 6319 | 5744 | 5542 | 138309955
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [9 empty] | 4 | 4 | 12 | 13 | 14 | 13 | 13 | 18 | 24 |  | 40 | 35 | 35 | 8 | 8 |  |  | 181440
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 |  |  | 25 | 84 | 92 | 88 | 76 | 92 | 84 | 76 | 75 | 75 | 70 | 75 |  | 75 | 75 | 75 | 93 | 93 | 70 | 35 | 1448640
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 18 | 25 | 72 | 88 | 94 | 92 | 53 | 68 | 29 | 8 | 1 | [8 empty] | 522000
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 176 | 156 | 153 | 153 | 110 | 120 | 120 | 135 | 200 | 202 | 183 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3252409
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 48 | 73 | 80 | 11 | 12 | 12 | 11 | 12 | 30 | 82 | 83 | 84 | 84 |  | 84 | 84 | 82 | 83 | 83 | 83 | 83 | 1161667
| Bhola 225 MW CCPP | 91 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 91 | 91 | 90 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 2199795
140 | Bhola 33 MW PP (Venture) | 22 | 22 | 21 | 15 | 15 | 17 | 17 | 16 | 15 | 13 | 14 | 14 | 19 | 20 | 18 | 17 | 18 | 23 |  | 25 | 25 | 26 | 26 | 26 | 25 | 24 | 461300
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 28 | 10 |  |  |  |  | 0 | 42240
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 4 | 8 | 10 |  |  |  |  | 9856
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 715 | 715 | 668 | 668 | 667 | 715 | 715 | 715 | 715 | 715 | 714 | 715 | 715 | 715 | 716 | 716 | 716 | 715 |  | 715 | 716 | 715 | 716 | 715 | 715 | 715 | 17134545
147 | Bheramara 410 MW CCPP | [16 empty] | 30 | 30 |  | 45 | 45 | 105 | 170 | 180 | 180 | 180 | 897984
148 | Payra 1320 MW | 330 | 330 | 320 | 300 | 300 | 300 | 300 | 300 | 310 | 300 | 300 | 300 | 340 | 330 | 320 | 300 | 300 | 290 |  | 400 | 440 | 450 | 460 | 460 | 430 | 420 | 9127800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 200 | 200 |  | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 4865400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 28 | 42 | 42 | 42 | 42 | 42 |  | 43 | 43 | 43 | 43 | 43 |  |  | 396928
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 4 | 4 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 31320
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 203 | 205 | 212 | 223 | 212 | 209 | 206 | 181 | 184 | 172 | 213 | 223 | 221 | 223 | 213 | 197 | 186 | 172 |  | 189 | 173 | 174 | 176 | 179 | 179 | 179 | 4944336
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | [25 empty] | 0 | 11709
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [8 empty] | 4 | 4 | 4 | 7 | 7 | 26 | 51 | 46 | 45 | 46 |  | 44 | 44 | 44 |  |  |  |  | 336740
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 18 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 513120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 197586
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 16 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 43 |  | 43 | 43 | 43 | 43 | 43 |  | 0 | 559556
167 | Katakhali 50 MW Peaking PP | [9 empty] | 9 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 24 |  |  |  | 315079
168 | Santahar 50 MW Peaking PP | [10 empty] | 7 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 31 | 31 | 29 | 29 |  |  |  | 286255
169 | Natore 52 MW PP (Rajlanka) | 52 | 8 | 8 | 8 | 8 | 16 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1073818
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 49 | 49 | 49 | 49 | 49 | 49 | 57 | 57 | 49 | 92 |  | 100 | 100 | 100 | 100 | 100 | 45 | 0 | 985608
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 30 | 10 |  |  |  |  | 0 | 37365
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 28 | 107 | 113 | 112 | 112 | 112 | 112 | 70 | 70 | 35 | 35 | 55 |  | 112 | 113 | 113 | 113 | 113 | 113 | 70 | 1733856
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 50 | 108 | 113 | 35 | 35 | 40 | 100 | 70 | 70 | 35 | 35 | 90 |  | 113 | 113 | 113 | 113 | 113 | 50 | 0 | 1419264
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 80 | 107 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 49 | 1953388
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 6 | 5 | 4 | 3 | 1 | [9 empty] | 41778
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 20 | 20 | 20 | [8 empty] | 67392
178