## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-02-27 | Sunday
|  |  | Date (day): | 2022-02-27 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11838.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12431 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-02-26 | 2022-02-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 340 | 340 | 340
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 338 | 333 | 350 | 350
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 11 | 11 | 12 | 12 |  | 88 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 80 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 40 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 49 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 30 | 30
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 11 | 33 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 245 | 263 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 162 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 70 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 89 | 135 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2098 | 2682 | 2885 | 2955 | 1676 | 992
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 7 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 25 | 25 | 25 |  | 25 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 46 | 46 | 46 |  | 184 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 18 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 30 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 13 | 8 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 89 | 89 | 100 | 100
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 15 | 24 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 9 | 83 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 100 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 734 | 1112 | 1270 | 1257 | 180 | 923
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 179 | 190 | 180 | 180 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 320 | 340 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 275 | 320 | 340 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 50 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 90 | 146 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 124 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 23 | 30 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 48 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 0 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 40 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 82 | 108 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 0 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 22 | 115 | 115 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1275 | 1391 | 1933 | 2109 | 621 | 200
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 132 | 93 | 70 | 70 | 132 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 174 | 180 | 180 | 180 |  | 20 | Engine problem
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 82 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 19 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 479 | 429 | 460.6 | 409 | 132 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 248 | 250 | 250 | 250 |  | 80 | Machine problem
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 51 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 66 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 81 | 84
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 177 | 177 | 180 | 180 |  | 51 | Machine problem
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1522 | 1550 | 1564 | 1567 | 73 | 740
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 716 | 710 | 725 | 725
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 5 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 305 | 305 | 305 | 105 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 40 | 80 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1223 | 1203 | 1315 | 1635 | 105 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 23 | 25 | 25
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 91 | 90 | 90 | 104 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 12 | 12 | 83 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 410 | 520 | 600
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 640 | 755 | 1027 | 1207 | 187 | 0
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 46 | 40 | 45 |  | 26 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 43 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 40 | 0 | 35 |  | 15 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 209 | 200 | 170 | 170
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 21 | 30 | 30 | 32 |  | 18 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 48 | 100 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 20 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 90 | 105 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 620 | 822 | 943 | 979 | 600 | 489
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 99 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 119 | 118 | 120 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 437 | 417 | 441 | 313 | 74 | 210
|  | Total |  |  |  |  | 22066 | 20985 | 9028 | 10361 | 11838.6 | 12431 | 3648 | 3645
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8700.3745 | 9985 | 11408.978 | 11979.8798
| A. |  | 2022-02-26 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 10381 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6227 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10361 | MW
| 3 | Day peak Generation : |  |  | 9028 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9985 | MW
| 4 | Evening peak Generation : |  |  | 10361 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 202.458 | MKWHr | By Solar | 1.3657 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 106.2686 | MKWHr |  | By Oil: | 60.7325 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.7072 | MKWHr |  | By Hydro: | 1.0569 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3648 | MW | Dhaka | 3700 | 3700 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3645 | MW | Chittagong | 1122 | 1122 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7293 | MW | Khulna | 1182 | 1182 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 791.28 | MMCFD |  |  | Rajshahi | 1050 | 1050 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 103976569.126 | ii) Oil : | Taka | 412037963.12 | Comilla | 796 | 796 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 65209042 | Total | Taka | 581223574.246 | Mymensingh | 890 | 890 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.29 | MKWHr. | Sylhet | 344 | 344 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -114 | MW (E to W) at | 19:00 | hrs | Barisal | 260 | 260 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -174 | MW at | 8:00 | hrs | Rangpur | 641 | 641 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.8° C |  |  | Total | 9985 | 9985 |  | 0
| B. |  | 2022-02-27 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12431 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1931 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 204.7788 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6754 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.8349 | MKWHr. | ii) HVDC Flow at Peak Time |  | 710 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4922 | MKWHr. | iii) Maximum HVDC Flow : |  | 718 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.76 |  | (b) Today: | 90.64 |  | (c) Rule Curve: |  | 93.45
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-02-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 344 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 103 | 25 | 18 | 42 | 0 | 0 | 0 | 270 | 275 | 185 | 73 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 90 | 155 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 249 | 68 | 84 | 0 | 136 | 0 | 0 | 10 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 17 | 0 | 0 | 230 | 0 | 0 | 34 | 8 | 0 | 324 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 17 |  | 709 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 225 | 0 | 0 | 0 | 0 | 120 |  | 4834 | 2143 | 6977 | 2882 | 709 | 1539 | 0 | 1231 | 480 | 46 | 0 | 0 | 90 | 0 | 0 | 90.79
2:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 344 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 25 | 18 | 42 | 0 | 0 | 0 | 270 | 275 | 184 | 73 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 88 | 160 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 249 | 70 | 84 | 0 | 136 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 17 | 0 | 0 | 190 | 0 | 0 | 17 | 8 | 0 | 250 | 46 | 0 | 72 | 113 | 0 | 17 | 0 | 0 | 17 |  | 625 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 225 | 0 | 0 | 0 | 0 | 120 |  | 4523 | 2094 | 6617 | 2837 | 625 | 1543 | 0 | 988 | 490 | 46 | 0 | 0 | 88 | 0 | 0 | 90.78
3:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 344 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 28 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 103 | 25 | 18 | 42 | 0 | 0 | 0 | 270 | 275 | 184 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 19 | 86 | 163 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 248 | 69 | 84 | 0 | 175 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 0 | 0 | 190 | 0 | 0 | 17 | 8 | 0 | 250 | 17 | 0 | 72 | 113 | 0 | 17 | 0 | 0 | 17 |  | 619 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 195 | 0 | 0 | 0 | 0 | 120 |  | 4509 | 2035 | 6544 | 2848 | 619 | 1512 | 0 | 943 | 490 | 46 | 0 | 0 | 86 | 0 | 0 | 90.78
4:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 344 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 28 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 70 | 25 | 18 | 42 | 0 | 0 | 0 | 270 | 275 | 184 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 25 | 19 | 84 | 160 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 250 | 40 | 20 | 0 | 175 | 0 | 0 | 10 | 265 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 0 | 0 | 155 | 0 | 0 | 17 | 8 | 0 | 200 | 17 | 0 | 17 | 113 | 0 | 17 | 0 | 0 | 17 |  | 619 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 201 | 0 | 0 | 0 | 0 | 120 |  | 4227 | 2000 | 6227 | 2746 | 619 | 1449 | 0 | 793 | 490 | 46 | 0 | 0 | 84 | 0 | 0 | 90.77
5:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 347 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 28 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 64 | 25 | 18 | 42 | 0 | 0 | 0 | 270 | 275 | 184 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 17 | 84 | 163 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 252 | 40 | 20 | 0 | 175 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 2 | 17 | 0 | 0 | 155 | 0 | 0 | 17 | 8 | 0 | 180 | 17 | 0 | 17 | 113 | 0 | 17 | 0 | 0 | 17 |  | 622 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 201 | 0 | 0 | 0 | 0 | 120 |  | 4242 | 2013 | 6255 | 2737 | 622 | 1477 | 0 | 789 | 500 | 46 | 0 | 0 | 84 | 0 | 0 | 90.77
6:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 347 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 10 | 10 | 15 | 25 | 28 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 64 | 25 | 18 | 38 | 0 | 0 | 0 | 270 | 305 | 184 | 73 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 17 | 86 | 161 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 251 | 40 | 79 | 0 | 175 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 2 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 34 | 3 | 0 | 8 | 32 | 0 | 0 | 175 | 0 | 0 | 17 | 8 | 0 | 180 | 22 | 0 | 30 | 113 | 0 | 17 | 0 | 0 | 30 |  | 621 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 128 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 202 | 0 | 0 | 0 | 0 | 120 |  | 4470 | 2043 | 6513 | 2792 | 621 | 1538 | 0 | 930 | 500 | 46 | 0 | 0 | 86 | 0 | 0 | 90.76
7:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 15 | 25 | 28 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 69 | 25 | 18 | 35 | 0 | 0 | 0 | 270 | 305 | 187 | 45 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 19 | 88 | 162 | 0 | 22 | 0 | 30 | 42 | 51 | 0 | 110 | 251 | 70 | 79 | 0 | 175 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 30 | 0 | 0 | 91 | 0 | 2 | 2 | 0 | 44 | 24 | 0 | 20 | 72 | 0 | 0 | 210 | 0 | 0 | 17 | 0 | 0 | 180 | 74 | 3 | 78 | 113 | 0 | 17 | 2 | 0 | 55 |  | 716 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 145 | 0 | 0 | 37 | 0 | 12 | 0 | 34 | 0 | 0 | 0 | 290 | 202 | 0 | 0 | 0 | 5 | 120 |  | 4883 | 2280 | 7163 | 2867 | 716 | 1504 | 0 | 1440 | 490 | 46 | 0 | 0 | 88 | 12 | 0 | 90.75
8:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 45 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 25 | 31 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 6 | 0 | 0 | 0 | 260 | 305 | 187 | 45 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 45 | 19 | 8 | 33 | 0 | 94 | 163 | 0 | 22 | 1 | 30 | 42 | 50 | 0 | 110 | 250 | 68 | 79 | 0 | 175 | 0 | 0 | 10 | 275 | 16 | 8 | 0 | 120 | 0 | 0 | 166 | 0 | 37 | 8 | 30 | 68 | 24 | 0 | 50 | 90 | 0 | 1 | 245 | 0 | 0 | 51 | 0 | 0 | 180 | 104 | 14 | 162 | 113 | 0 | 17 | 8 | 0 | 55 |  | 716 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 151 | 0 | 0 | 80 | 0 | 80 | 0 | 70 | 0 | 1 | 35 | 290 | 223 | 0 | 0 | 1 | 24 | 119 |  | 5361 | 2561 | 7922 | 2859 | 716 | 1417 | 0 | 2226 | 490 | 46 | 0 | 16 | 94 | 58 | 0 | 0
9:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 343 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 74 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 35 | 15 | 25 | 31 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 183 | 45 | 0 | 29 | 5 | 0 | 0 | 0 | 0 | 52 | 19 | 8 | 33 | 0 | 104 | 160 | 0 | 22 | 1 | 30 | 42 | 50 | 0 | 110 | 249 | 67 | 79 | 0 | 201 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 225 | 0 | 0 | 167 | 0 | 60 | 13 | 60 | 74 | 0 | 0 | 75 | 90 | 0 | 3 | 300 | 0 | 0 | 70 | 0 | 0 | 210 | 104 | 29 | 162 | 113 | 0 | 17 | 16 | 0 | 55 |  | 717 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 174 | 0 | 0 | 70 | 0 | 70 | 0 | 100 | 0 | 3 | 90 | 290 | 190 | 0 | 0 | 3 | 51 | 119 |  | 5699 | 2619 | 8318 | 2892 | 717 | 1375 | 0 | 2559 | 490 | 46 | 0 | 16 | 104 | 119 | 0 | 0
10:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 303 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 74 | 16 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 31 | 25 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 94 | 26 | 16 | 2 | 0 | 0 | 0 | 260 | 275 | 197 | 45 | 0 | 23 | 5 | 0 | 0 | 0 | 42 | 52 | 19 | 11 | 33 | 21 | 120 | 142 | 0 | 22 | 2 | 30 | 42 | 50 | 0 | 110 | 250 | 40 | 78 | 0 | 208 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 228 | 0 | 0 | 166 | 0 | 88 | 17 | 20 | 85 | 0 | 0 | 75 | 90 | 0 | 4 | 300 | 0 | 0 | 70 | 0 | 0 | 335 | 104 | 41 | 162 | 113 | 0 | 17 | 21 | 0 | 55 |  | 716 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 30 | 0 | 25 | 16 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 218 | 0 | 0 | 70 | 0 | 70 | 0 | 71 | 0 | 3 | 113 | 280 | 216 | 0 | 0 | 4 | 71 | 119 |  | 5819 | 2731 | 8550 | 3026 | 716 | 1371 | 0 | 2536 | 480 | 30 | 0 | 108 | 120 | 163 | 0 | 0
11:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 303 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 74 | 16 | 12 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 31 | 25 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 25 | 16 | 2 | 0 | 0 | 0 | 295 | 305 | 185 | 45 | 0 | 23 | 5 | 0 | 0 | 0 | 42 | 52 | 19 | 8 | 33 | 21 | 118 | 142 | 0 | 22 | 2 | 30 | 42 | 50 | 0 | 110 | 247 | 40 | 84 | 0 | 189 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 230 | 0 | 0 | 166 | 0 | 87 | 20 | 26 | 85 | 0 | 0 | 75 | 90 | 0 | 5 | 300 | 0 | 0 | 70 | 0 | 0 | 400 | 104 | 47 | 162 | 113 | 0 | 17 | 24 | 0 | 55 |  | 716 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 0 | 25 | 16 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 211 | 0 | 0 | 75 | 0 | 70 | 0 | 80 | 0 | 5 | 113 | 280 | 222 | 0 | 0 | 5 | 84 | 119 |  | 5929 | 2784 | 8713 | 3122 | 716 | 1386 | 0 | 2550 | 480 | 30 | 0 | 119 | 118 | 192 | 0 | 0
12:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 338 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 80 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 40 | 15 | 25 | 31 | 25 | 33 | 11 | 0 | 40 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 89 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 179 | 45 | 0 | 23 | 5 | 0 | 0 | 0 | 50 | 48 | 19 | 8 | 23 | 21 | 130 | 132 | 0 | 22 | 2 | 30 | 30 | 50 | 0 | 110 | 248 | 62 | 81 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 245 | 0 | 0 | 174 | 0 | 89 | 20 | 76 | 90 | 0 | 0 | 82 | 90 | 18 | 5 | 300 | 15 | 9 | 82 | 0 | 10 | 400 | 104 | 49 | 162 | 100 | 0 | 17 | 24 | 0 | 55 |  | 716 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 5 | 48 | 0 | 34 | 16 | 52 | 21 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 209 | 0 | 0 | 105 | 0 | 90 | 0 | 113 | 0 | 5 | 113 | 300 | 220 | 0 | 0 | 5 | 92 | 119 |  | 6108 | 2920 | 9028 | 3035 | 716 | 1437 | 0 | 2812 | 500 | 40 | 0 | 156 | 130 | 202 | 0 | 0
13:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 335 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 88 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 174 | 45 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 52 | 19 | 0 | 23 | 21 | 122 | 110 | 0 | 22 | 2 | 30 | 30 | 50 | 0 | 110 | 250 | 64 | 81 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 260 | 0 | 0 | 174 | 0 | 128 | 19 | 76 | 130 | 0 | 0 | 115 | 92 | 74 | 5 | 300 | 17 | 34 | 109 | 0 | 30 | 400 | 104 | 30 | 162 | 94 | 0 | 17 | 26 | 0 | 55 |  | 717 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 10 | 29 | 48 | 0 | 34 | 16 | 52 | 30 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 207 | 0 | 0 | 105 | 0 | 112 | 0 | 113 | 0 | 6 | 113 | 300 | 193 | 0 | 0 | 5 | 91 | 119 |  | 6359 | 2967 | 9326 | 3021 | 717 | 1397 | 0 | 3140 | 500 | 46 | 0 | 199 | 122 | 184 | 0 | 0
14:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 331 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 88 | 24 | 17 | 2 | 0 | 0 | 0 | 260 | 275 | 163 | 45 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 52 | 19 | 8 | 25 | 21 | 122 | 107 | 0 | 22 | 2 | 30 | 30 | 50 | 0 | 110 | 252 | 64 | 84 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 260 | 0 | 0 | 174 | 0 | 131 | 17 | 50 | 100 | 0 | 0 | 75 | 103 | 85 | 4 | 300 | 17 | 17 | 51 | 0 | 30 | 350 | 104 | 23 | 162 | 94 | 0 | 17 | 24 | 0 | 53 |  | 717 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 43 | 48 | 48 | 0 | 16 | 16 | 52 | 31 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 204 | 0 | 0 | 70 | 0 | 70 | 0 | 75 | 0 | 6 | 70 | 290 | 219 | 0 | 0 | 5 | 80 | 119 |  | 6031 | 2836 | 8867 | 2953 | 717 | 1402 | 0 | 2724 | 490 | 46 | 0 | 252 | 122 | 161 | 0 | 90.72
15:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 24 | 17 | 2 | 0 | 0 | 0 | 265 | 275 | 179 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 52 | 19 | 8 | 25 | 20 | 122 | 68 | 0 | 22 | 1 | 30 | 30 | 50 | 0 | 110 | 250 | 60 | 84 | 0 | 176 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 260 | 0 | 0 | 174 | 0 | 122 | 14 | 50 | 100 | 0 | 0 | 75 | 99 | 85 | 3 | 300 | 17 | 17 | 51 | 6 | 10 | 395 | 104 | 33 | 155 | 77 | 0 | 17 | 19 | 0 | 55 |  | 718 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 43 | 46 | 48 | 0 | 16 | 16 | 52 | 30 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 203 | 0 | 0 | 70 | 0 | 50 | 0 | 70 | 0 | 3 | 50 | 310 | 220 | 0 | 0 | 4 | 62 | 119 |  | 6003 | 2786 | 8789 | 2976 | 718 | 1396 | 0 | 2633 | 510 | 46 | 0 | 249 | 122 | 139 | 0 | 90.71
16:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 302 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 24 | 17 | 2 | 0 | 0 | 0 | 260 | 270 | 204 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 45 | 19 | 8 | 25 | 20 | 120 | 93 | 0 | 22 | 1 | 30 | 30 | 50 | 0 | 110 | 252 | 40 | 84 | 0 | 176 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 263 | 0 | 0 | 172 | 0 | 122 | 9 | 50 | 100 | 0 | 0 | 75 | 105 | 68 | 2 | 300 | 17 | 17 | 51 | 8 | 10 | 400 | 104 | 23 | 144 | 99 | 0 | 17 | 12 | 0 | 55 |  | 717 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 43 | 45 | 48 | 0 | 16 | 16 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 203 | 0 | 0 | 70 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 320 | 205 | 0 | 0 | 1 | 37 | 119 |  | 5952 | 2690 | 8642 | 3005 | 717 | 1332 | 0 | 2564 | 520 | 46 | 0 | 251 | 120 | 87 | 0 | 90.71
17:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 283 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 31 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 25 | 17 | 4 | 0 | 0 | 0 | 260 | 280 | 210 | 8 | 0 | 27 | 5 | 0 | 0 | 0 | 50 | 43 | 19 | 8 | 28 | 20 | 110 | 100 | 0 | 22 | 0 | 30 | 30 | 11 | 0 | 110 | 252 | 40 | 40 | 0 | 178 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 263 | 0 | 0 | 181 | 0 | 122 | 3 | 50 | 100 | 0 | 0 | 75 | 105 | 68 | 1 | 300 | 17 | 17 | 51 | 8 | 10 | 400 | 104 | 6 | 162 | 113 | 0 | 17 | 3 | 0 | 55 |  | 717 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 43 | 46 | 48 | 0 | 16 | 34 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 203 | 0 | 0 | 70 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 320 | 173 | 0 | 0 | 0 | 13 | 119 |  | 5896 | 2651 | 8547 | 3037 | 717 | 1218 | 0 | 2600 | 520 | 46 | 0 | 272 | 110 | 27 | 0 | 90.7
18:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 282 |  | 0 | 225 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 32 | 64 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 18 | 31 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 21 | 0 | 51 | 0 | 89 | 25 | 18 | 7 | 0 | 0 | 0 | 285 | 305 | 198 | 8 | 0 | 27 | 5 | 0 | 0 | 0 | 50 | 46 | 19 | 8 | 33 | 0 | 128 | 94 | 0 | 22 | 0 | 30 | 30 | 24 | 0 | 110 | 251 | 64 | 84 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 263 | 12 | 100 | 184 | 7 | 122 | 0 | 70 | 100 | 0 | 0 | 84 | 105 | 72 | 0 | 300 | 17 | 17 | 96 | 8 | 20 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 718 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 90 | 23 | 0 | 0 | 0 | 0 | 43 | 46 | 96 | 0 | 16 | 40 | 52 | 31 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 202 | 0 | 0 | 76 | 0 | 41 | 0 | 42 | 0 | 0 | 70 | 320 | 175 | 0 | 0 | 0 | 3 | 118 |  | 6331 | 2767 | 9098 | 3059 | 718 | 1296 | 119 | 2769 | 520 | 46 | 0 | 440 | 128 | 3 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 333 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 33 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 51 | 30 | 89 | 25 | 18 | 13 | 0 | 0 | 0 | 260 | 275 | 190 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 52 | 19 | 8 | 30 | 20 | 124 | 93 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 250 | 66 | 84 | 0 | 177 | 0 | 0 | 10 | 315 | 16 | 11 | 40 | 263 | 162 | 100 | 180 | 70 | 135 | 0 | 90 | 146 | 0 | 0 | 115 | 105 | 105 | 0 | 300 | 24 | 83 | 108 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 22 | 55 |  | 710 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 38 | 5 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 43 | 46 | 100 | 0 | 43 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 40 | 200 | 0 | 0 | 105 | 20 | 105 | 0 | 99 | 0 | 0 | 113 | 410 | 220 | 0 | 0 | 0 | 0 | 118 |  | 7184 | 3197 | 10381 | 3025 | 710 | 1430 | 432 | 3451 | 610 | 46 | 0 | 553 | 124 | 0 | 0 | 90.68
19:30 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 36 | 30 | 89 | 25 | 18 | 20 | 0 | 0 | 0 | 270 | 285 | 202 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 52 | 19 | 8 | 32 | 20 | 124 | 93 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 252 | 67 | 84 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 278 | 10 | 40 | 180 | 30 | 136 | 0 | 90 | 184 | 0 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 108 | 108 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 17 | 55 |  | 710 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 39 | 8 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 43 | 46 | 100 | 0 | 43 | 40 | 52 | 32 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 199 | 0 | 0 | 105 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 430 | 224 | 0 | 0 | 0 | 0 | 119 |  | 7052 | 3181 | 10233 | 3067 | 710 | 1425 | 80 | 3607 | 630 | 46 | 0 | 544 | 124 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 49 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 46 | 30 | 90 | 25 | 18 | 22 | 0 | 0 | 0 | 260 | 275 | 208 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 52 | 19 | 8 | 30 | 20 | 122 | 94 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 250 | 68 | 84 | 0 | 177 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 280 | 0 | 0 | 180 | 0 | 135 | 0 | 90 | 180 | 0 | 0 | 115 | 105 | 105 | 0 | 300 | 53 | 105 | 108 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 17 | 55 |  | 710 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 91 | 24 | 0 | 0 | 0 | 0 | 43 | 42 | 100 | 0 | 43 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 199 | 0 | 0 | 105 | 0 | 113 | 0 | 108 | 0 | 0 | 113 | 450 | 224 | 0 | 0 | 0 | 0 | 119 |  | 6938 | 3190 | 10128 | 3051 | 710 | 1408 | 0 | 3602 | 649 | 46 | 0 | 540 | 122 | 0 | 0 | 90.69
21:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 82 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 0 | 95 | 25 | 18 | 30 | 0 | 0 | 0 | 260 | 275 | 218 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 0 | 52 | 19 | 8 | 30 | 21 | 118 | 93 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 246 | 68 | 84 | 0 | 177 | 0 | 0 | 10 | 295 | 16 | 11 | 0 | 280 | 0 | 0 | 182 | 0 | 140 | 0 | 90 | 181 | 0 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 108 | 108 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 710 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 24 | 0 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 43 | 21 | 52 | 23 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 199 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 224 | 0 | 0 | 0 | 0 | 118 |  | 6822 | 3097 | 9919 | 3057 | 710 | 1431 | 0 | 3578 | 659 | 46 | 0 | 320 | 118 | 0 | 0 | 90.68
22:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 30 | 0 | 0 | 0 | 260 | 270 | 222 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 0 | 52 | 19 | 8 | 28 | 21 | 112 | 93 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 250 | 69 | 84 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 280 | 0 | 0 | 181 | 0 | 112 | 0 | 90 | 182 | 0 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 70 | 8 | 60 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 710 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 8 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 199 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 215 | 0 | 0 | 0 | 0 | 119 |  | 6454 | 2946 | 9400 | 3059 | 710 | 1426 | 0 | 3277 | 640 | 46 | 0 | 130 | 112 | 0 | 0 | 90.68
23:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 95 | 25 | 18 | 30 | 0 | 0 | 0 | 260 | 270 | 225 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 0 | 52 | 19 | 8 | 25 | 21 | 104 | 93 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 249 | 40 | 84 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 245 | 0 | 0 | 181 | 0 | 35 | 0 | 90 | 188 | 11 | 0 | 40 | 105 | 105 | 0 | 300 | 54 | 110 | 17 | 8 | 10 | 350 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 709 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 8 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 194 | 0 | 0 | 105 | 0 | 35 | 0 | 39 | 0 | 0 | 0 | 400 | 224 | 0 | 0 | 0 | 0 | 119 |  | 5958 | 2643 | 8601 | 2974 | 709 | 1404 | 0 | 2666 | 600 | 46 | 0 | 98 | 104 | 0 | 0 | 90.67
24:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 42 | 0 | 0 | 0 | 270 | 285 | 225 | 8 | 0 | 29 | 5 | 0 | 14 | 0 | 0 | 52 | 19 | 8 | 25 | 21 | 96 | 93 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 247 | 40 | 84 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 30 | 0 | 0 | 173 | 0 | 11 | 0 | 90 | 100 | 73 | 0 | 0 | 105 | 105 | 0 | 300 | 54 | 110 | 0 | 8 | 0 | 350 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 709 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 370 | 225 | 0 | 0 | 0 | 0 | 119 |  | 5642 | 2386 | 8028 | 2980 | 709 | 1450 | 0 | 2177 | 570 | 46 | 0 | 0 | 96 | 0 | 0 | 90.67
KWH | 0 | 0 | 0 | 0 | 8202991 | 0 | 0 | 0 | 7894000 |  | 0 | 5200700 | 0 | 0 | 0 | 455689 | 0 | 0 | 0 | 0 | 904896 | 613920 | 158935 | 0 | 0 | 0 | 1055520 | 957681 | 913853 | 384300 | 600000 | 676440 | 665300 | 807300 | 312480 | 0 | 1056900 | 0 | 0 | 0 | 243045 | 0 | 0 | 0 | 0 |  | 517440 | 0 | 167523 | 45120 | 2129280 | 604800 | 402528 | 500640 | 0 | 0 | 0 | 6812000 | 6927000 | 4664000 | 953454 | 0 | 628992 | 144960 | 0 | 402324 | 0 | 526688 | 1233797 | 446508 | 181260 | 720100 | 456600 | 2492160 | 2947200 | 0 | 497808 | 14700 | 715000 | 838240 | 1140000 | 0 | 2918700 | 5723000 | 1329600 | 1772160 | 0 | 4214890 | 0 | 0 | 252180 | 7086500 | 384522 | 210240 | 44928 | 4185162 | 150585 | 128510 | 3446400 | 87274 | 1707260 | 142695 | 1058880 | 2437440 | 163927 | 0 | 1556400 | 1978800 | 1142472 | 32160 | 6348000 | 424203 | 771963 | 1332660 | 145320 | 478080 | 7764800 | 2143680 | 302750 | 3287520 | 2601927 | 0 | 444240 | 178118 | 58560 | 1166040 |  | 16834909 | 0 | 7452000 | 0 | 0 | 0 | 0 | 0 | 79680 | 3968 | 0 | 2204813 | 445900 | 0 | 0 | 0 | 0 | 362256 | 351991 | 921352 | 0 | 451901 | 254665 | 1177920 | 269606 | 520320 | 0 | 162468 | 0 | 0 | 4887800 | 0 | 0 | 0 | 0 | 50809 | 0 | 270488 | 58560 | 4570073 | 0 | 0 | 1687200 | 20407 | 1435296 | 0 | 1390060 | 0 | 45104 | 1331712 | 8819400 | 5125445 | 0 | 0 | 35340 | 614880 | 2805046 |  | 137816618 | 64641369 | 202457987 | 71640782 | 16834909 | 34627771 | 490264 | 56690605 | 13707200 | 1056900 | 0 | 3551649 | 2492160 | 1365747 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 9105320.01 | 0 | 0 | 0 | 8130820 |  | 0 | 5668763 | 0 | 0 | 0 | 3855128.94 | 0 | 0 | 0 | 0 | 8252651.52 | 6040972.8 | 1465380.7 | 0 | 0 | 0 | 7705296 | 7402874.13 | 9010590.58 | 288225 | 450000 | 0 | 0 | 0 | 3021681.6 | 0 | 285363 | 0 | 0 | 0 | 2257888.05 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1624973.1 | 430896 | 18524736 | 4790016 | 507185.28 | 1486900.8 | 0 | 0 | 0 | 5040880 | 6927000 | 4290880 | 1229955.66 | 0 | 710760.96 | 202944 | 0 | 687974.04 | 0 | 5319548.8 | 11782761.35 | 567065.16 | 135945 | 1260175 | 342450 | 18691200 | 3124032 | 0 | 632216.16 | 234318 | 1172600 | 1341184 | 2029200 | 0 | 3327318 | 5951920 | 2619312 | 3384825.6 | 0 | 7291759.7 | 0 | 0 | 514447.2 | 7157365 | 288391.5 | 159782.4 | 764225.28 | 31639824.72 | 2556933.3 | 2148687.2 | 17921280 | 1459221.28 | 16799438.4 | 1668104.55 | 8629872 | 26446224 | 1155685.35 | 0 | 14194368 | 18699660 | 9950931.12 | 0 | 47990880 | 3694808.13 | 6785554.77 | 13299946.8 | 1245392.4 | 3184012.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 96969075.84 | 0 | 7824600 | 0 | 0 | 0 | 0 | 0 | 835843.2 | 41584.64 | 0 | 2491438.69 | 691145 | 0 | 0 | 0 | 0 | 3564599.04 | 3576228.56 | 8153965.2 | 0 | 6109701.52 | 2467703.85 | 11414044.8 | 2615178.2 | 999014.4 | 0 | 122988.276 | 0 | 0 | 26491876 | 0 | 0 | 0 | 0 | 67067.88 | 0 | 405732 | 996105.6 | 5346985.41 | 0 | 0 | 17614368 | 347123.07 | 13620959.04 | 0 | 10786865.6 | 0 | 498399.2 | 9841351.68 | 38717166 | 0 | 0 | 0 | 0 | 0 | 0 |  | 426958924.14 | 272611110.696 | 699570034.836 | 68060164.426 | 96969075.84 | 35916404.7 | 8272295.73 | 369525070 | 65209042 | 285363 | 0 | 34240597.39 | 18691200 | 2400821.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 338 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 80 | 16 | 11 | 0 | 0 | 0 | 54 | 55 | 40 | 15 | 25 | 31 | 25 | 33 | 11 | 0 | 40 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 89 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 179 | 45 | 0 | 23 | 5 | 0 | 0 | 0 | 50 | 48 | 19 | 8 | 23 | 21 | 130 | 132 | 0 | 22 | 2 | 30 | 30 | 50 | 0 | 110 | 248 | 62 | 81 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 245 | 0 | 0 | 174 | 0 | 89 | 20 | 76 | 90 | 0 | 0 | 82 | 90 | 18 | 5 | 300 | 15 | 9 | 82 | 0 | 10 | 400 | 104 | 49 | 162 | 100 | 0 | 17 | 24 | 0 | 55 |  | 716 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 5 | 48 | 0 | 34 | 16 | 52 | 21 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 209 | 0 | 0 | 105 | 0 | 90 | 0 | 113 | 0 | 5 | 113 | 300 | 220 | 0 | 0 | 5 | 92 | 119 |  | 9028 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 333 | 0 | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 33 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 51 | 30 | 89 | 25 | 18 | 13 | 0 | 0 | 0 | 260 | 275 | 190 | 8 | 0 | 29 | 5 | 0 | 0 | 0 | 50 | 52 | 19 | 8 | 30 | 0 | 124 | 93 | 0 | 22 | 0 | 30 | 30 | 51 | 0 | 110 | 250 | 66 | 84 | 0 | 177 | 0 | 0 | 10 | 315 | 16 | 11 | 40 | 263 | 162 | 100 | 180 | 70 | 135 | 0 | 90 | 146 | 0 | 0 | 115 | 105 | 105 | 0 | 300 | 24 | 83 | 108 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 22 | 55 |  | 710 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 38 | 5 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 43 | 46 | 100 | 0 | 43 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 40 | 200 | 0 | 0 | 105 | 20 | 105 | 0 | 99 | 0 | 0 | 113 | 410 | 220 | 0 | 0 | 0 | 0 | 118 |  | 10361 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 | 0 | 0 | 225 |  | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 25 | 18 | 20 | 0 | 0 | 0 | 340 | 340 | 180 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 163 | 70 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 250 | 66 | 84 | 0 | 180 | 0 | 0 | 10 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 180 | 100 | 149 | 0 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 |  | 115 | 55 |  | 725 | 0 | 305 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 90 | 25 | 110 | 0 | 0 | 0 | 43 | 45 | 100 | 0 | 43 | 35 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 100 | 170 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 25 | 18 | 8 | 0 | 0 | 0 | 320 | 320 | 180 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 138 | 70 | 0 | 22 | 1.6 | 30 | 30 | 50 | 0 | 110 | 250 | 66 | 81 | 0 | 180 | 0 | 0 | 10 | 330 | 16 | 11 | 100 | 300 | 200 | 100 | 180 | 100 | 149 | 20 | 90 | 200 | 150 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 50 | 162 | 113 | 0 | 17 | 30 | 115 | 55 |  | 725 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 25 | 110 | 0 | 0 | 0 | 43 | 40 | 100 | 0 | 43 | 0 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 170 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 520 | 220 |  | 50 | 6 | 50 | 120
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 255 | 0 | 0 | 225 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 13 | 0 | 46 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 77 | 25 | 18 | 8 | 0 | 0 | 0 | 260 | 310 | 189 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 25 | 13 | 80 | 92 | 0 | 22 | 1 | 30 | 30 | 48 | 0 | 110 | 254 | 40 | 84 | 0 | 176 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 238 | 0 | 0 | 183 | 0 | 40 | 9 | 40 | 64 | 90 | 0 | 83 | 90 | 93 | 2 | 282 | 7 | 68 | 34 | 0 | 20 | 210 | 104 | 14 | 162 | 113 | 0 | 11 | 8 | 0 | 55 | 0 | 710 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 157 | 0 | 0 | 105 | 0 | 90 | 0 | 91 | 0 | 0 | 90 | 290 | 166 | 0 | 0 | 1 | 25 | 119 | 0
199
| Minimum Generation |  | 6227 | 4:00
| Highest Generation |  | 10381 | 19:00
| Day Peak Generation |  | 9028 | 12:00
| Evening Peak Generation |  | 10361 | 19:00
| HVDC Max Flow |  | 718 | 15:00
| HVDC EvPeak Flow |  | 710 | 19:00
| Load factor L.F |  | 81.26%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-02-27
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-02-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9028 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6754 | MW
Evening Peak Generation : |  | 10361 | MW Hour : | 19:00 | Available Max Generation : |  | 12431 | MW
E.P. Demand (at gen end) : |  | 10361 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 10381 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1931 | MW
Total Gen. (MKWH) : |  | 202.458 | System Load Factor : | 81.26% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -174 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-02-27
Actual : | 90.64 | Ft.(MSL) , | Rule curve : | 93.45 | Ft.( MSL )
Gas Consumed : | Total = | 791.28 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 103976569.126
: |  | Coal : | 65209042 | Oil : | 412037963.12 | Total : | 581223574.246
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3769.1876 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1280.4364 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1146.9976 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1036.3271 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 936.559 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 755.7667 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 424.2553 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 194.6337 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 582.8768 |  |  | 0 | 0%
Total | 0 |  | 10127.0404 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
|  |  |  | 2) Ghorasal-3,4,5 |  | 11) Meghnaghat 450 MW CCPP GT-1
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Siddhirganj 335 MW
6) Raozan unit- 1,2
7) Sirajganj Unit 1,2 & 4.
8) Summit Bibiyana-3
9) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Chandpur Desh- Chandpur S/S 132 kV Ckt-1 was under shut down from 08:17 to 08:36 for A/M.
b) Hasnabad-Shympur 230 kV Ckt-1 was under shut down from 08:24 to 15:08 for A/M.
c) Narshingdi-B.Baria 132 kV Ckt-1 was under shut down from 08:24 to 17:45 for A/M.
d) Sikalbaha-Juldah 132 kV Ckt was under shut down from 08:41 to 12:30 for A/M.
e) Ashuganj-Midland 150 MW 230 kV Ckt was under shut down from 08:30 to 20:31 for A/M.
f) Savar 132/33 kV T-2 transformer was shut down at 08:50 for C/M.
g) Tongi 230/132 kV T02 transformer was under shut down from 09:25 to 18:27 for A/M.
h) Tongi S/S-Tongi P/S 132 kV Ckt was under shut down from 10:02 to 15:20 for A/M.
i) Khulna(S)-Jhenaidah 230 kV Ckt-1 was under shut down from 08:55 to 14:53 for D/W.
j) Khulna(S) 230 kV Bus-2 was under shut down from 09:32 to 13:52 for D/W.
k) Sirajganj S/S-Sirajganj unit-4 230 kV was under shut down from 10:55 to 22:36 for C/M.
l) Tongi 132/33 kV T-1 transformer tripped at 12:15 showing O/C relay due to 33 kV DESCO feeder fault | [5 empty] | About 32 MW power interruption occurred under
an was switched on at 12:50. | [5 empty] | Tongi S/S area from 12:15 to 12:50.
m) Bibiyana unit-3 ST unit transformer with 400 kV Ckt was shut down at 11:38 for C/M.
n) Comilla(S) 132/33 kV T-4 was under shut down from 10:17 to 14:48 for C/M.
o) Gopalganj-Payra 400 kV Ckt-1 was charged at 15:07 from Gopalganj end.
p) Gopalganj(o) 132/33 kV T-1 transformer and 33 kV Bus were under shut down from 07:16(27/2/2022) | [5 empty] | About 10 MW power interruption occurred under
08:52 for C/M. | [5 empty] | Gopalganj S/S area from 07:16(27/2/2022) to 08:52.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-02-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 8202991
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 333 | 7894000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5200700 | GT-2 S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 455689
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 11 | 158935 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 384300
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 904896 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1055520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 613920
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 957681
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 913853
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1276440 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 665300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 807300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 33 | 312480 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 263 | 4185162 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 162 | 150585 | High Voltage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 128510
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 70 | 87274 | High Voltage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 135 | 1707260 | High Voltage
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1978800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2143680
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3287520
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178118
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1166040
| Dhaka area Total |  |  |  | 5696 | 2682 | 44816954
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 243045
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 142695
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 604800 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1056900 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1142472
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 167523 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 45120 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1058880 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 402528
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 500640
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 89 | 2129280 | High Voltage
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32160
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 6348000
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 24 | 424203 | High Voltage
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 83 | 771963 | High Voltage
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 478080 | High Voltage
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2601927
| Chattogram area Total |  |  |  | 2382 | 1112 | 18150216
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 190 | 4664000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6812000 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6927000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 628992 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 144960 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 953454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 402324 | Under maint.
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 163927 | Under maint.
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 526688
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | tripped at 18:51 due to exaust temp high.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 146 | 2437440 | High Voltage
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 446508
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 181260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2492160
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 30 | 720100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1233797
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 456600 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 40 | 44928 | High Voltage
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 1332660
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 145320 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 22 | 58560 | High Voltage
| Cumilla Area Total |  |  |  | 2899 | 1391 | 31216918
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 93 | 2947200 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 497808
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14700
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 180 | 3446400 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1556400
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 302750
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 19 | 517440
| Mymensingh Area Total |  |  |  | 622 | 429 | 9282698
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 838240 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2918700 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 250 | 5723000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 1140000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210240
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1329600
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1772160
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 177 | 4214890 | ST under maint
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 384522 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7086500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252180
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 7764800
| Sylhet Area Total |  |  |  | 2377 | 1550 | 34349832
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 710 | 16834909
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 79680 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 5 | 3968 | High Voltage
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 305 | 7452000 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 40 | 58560 | High Voltage
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1687200
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 614880
| Khulna Area Total |  |  |  | 2229 | 1203 | 26731197
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 23 | 445900 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2204813 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 270488 | Engine problem
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 410 | 8819400 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5125445
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 755 | 16866046
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 362256 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 46 | 351991 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 451901 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 254665 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 50809 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 200 | 4570073 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 269606 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 520320
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 162468 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1177920
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 921352
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 20 | 20407 | High Voltage
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 105 | 1435296
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1331712
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35340
| Rajshahi Area Total |  |  |  | 2129 | 822 | 11916116
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4887800 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 99 | 1390060
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45104
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 118 | 2805046 | On test
| Rangpur Area Total |  |  |  | 605 | 417 | 9128010
| Total |  |  |  | 20985 | 10361 | 202457987
| Eastern Grid Total |  |  |  | 13976 | 7164 | 137816618
| Western Grid Total |  |  |  | 7009 | 3197 | 64641369
| National Grid Total |  |  |  | 20985 | 10361 | 202457987
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-02-26
(a) ENTIRE EASTERN GRID : |  | 6852 | MW | (b) ENTIRE WESTERN GRID : |  | 3133 | MW
i) Dhaka area |  | 3700 | MW | i) Khulna area |  | 1182 | MW
ii) Chittagong area |  | 1122 | MW | ii) Rajshahi area |  | 1050 | MW
iii) Comilla area |  | 796 | MW | iii) Barisal area |  | 260 | MW
iv) Mymensingh area |  | 890 | MW | iv) Rangpur area |  | 641 | MW
v) Sylhet area |  | 344 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9985 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 99 | 12:00 | Valuka | 98 | 9:00 | Noapara | 37 | 19:00
Munsiganj | 66 | 21:00 | Tangail | 180 | 7:00 | Jessore | 94 | 19:00
Sonargaon | 64 | 12:00 | Mymensing | 186 | 13:00 | Benapol | 42 | 19:00
Bhulta | 184 | 11:00 | Kishoreganj | 108 | 20:00 | Jhenida(Old) | 94 | 19:00
Madanganj | 28 | 18:30 | Netrokona | 118 | 18:30 | Bottail | 109 | 19:00
Rahim steel | 12 | 15:00 | Jamalpur | 130 | 13:00 | G.K Project | 40 | 19:00
Ghorasal | 67 | 19:00 | Sherpur | 126 | 8:00 | Faridpur | 97 | 19:00
Narsingdi | 139 | 19:00 | Srimongal | 35 | 19:00 | Rajbari | 46 | 19:00
Haripur(SBU) | 115 | 12:00 | Shahjibazar | 85 | 21:00 | Madaripur | 71 | 20:00
Sreenagar | 28 | 19:00 | Fenchuganj | 28 | 18:00 | Sariatpur | 44 | 20:00
Shyampur | 160 | 0:00 | Kulawara | 26 | 18:30 | Gopalganj | 70 | 20:00
Shitalakhya | 97 | 16:00 | Sylhet | 96 | 18:30 | Bagerhat | 94 | 19:00
Matuail | 54 | 12:00 | Chatak | 20 | 19:30 | Mongla | 40 | 12:00
Char Saidpur | 42 | 10:00 | Sunamganj | 33 | 20:00 | Satkhira | 83 | 19:00
Ullon | 23 | 19:00 | Biani Bazar | 37 | 19:30 | Gallamari | 42 | 13:00
Hasnabad | 64 | 12:00 | Comilla (S) | 136 | 18:30 | Magura | 42 | 18:30
Magbazar | 78 | 13:00 | Comilla(N) | 87 | 19:30 | Norail | 33 | 19:00
Maniknagar | 49 | 18:30 | Chandpur | 48 | 21:00 | Chuadanga | 60 | 19:00
Bangabhaban | 0 | 1:00 | Feni | 88 | 19:00 | Barisal(N) | 27 | 19:00
Motijheel | 24 | 13:00 | Chowmuhani | 137 | 18:30 | Barisal (S) | 82 | 21:00
Narinda | 36 | 18:30 | Ashuganj | 26 | 18:30 | Patuakhali | 78 | 19:30
Kazla | 68 | 18:30 | Daudkandi | 100 | 19:30 | Bhandaria | 38 | 19:00
Dhanmondi | 124 | 13:00 | B.Baria | 110 | 21:00 | Borguna | 12 | 18:30
Lalbag | 74 | 13:00 | Ramganj | 56 | 19:00 | Borhan Uddin | 30 | 21:00
Madartek | 51 | 19:00 | Chaddagram | 33 | 18:30 | Ishurdi | 56 | 19:00
Dhaka University | 21 | 12:00 | PHP | 8 | 6:00 | Ruppur Paromanobik | 3 | 12:00
Aftabnagar | 21 | 18:00 | Kochua | 42 | 18:00 | Natore | 100 | 19:00
Fatullah | 52 | 12:00 | Madunaghat | 38 | 18:30 | Bogra | 115 | 19:00
Nawabganj | 34 | 21:00 | Hathazari | 72 | 18:30 | Naogaon | 100 | 13:00
Keraniganj | 54 | 19:00 | Khulshi | 140 | 12:00 | Rajshahi | 85 | 13:00
Banani | 28 | 13:00 | Halishahar | 70 | 19:30 | Rajshahi New | 33 | 19:00
Mirpur | 91 | 19:00 | Baraulia | 97 | 9:00 | C.Nawabganj | 59 | 12:00
Kalyanpur | 63 | 18:30 | Sikalbaha | 27 | 20:00 | Amnura | 44 | 18:30
Gulshan | 70 | 13:00 | Dohazari | 62 | 18:30 | Pabna | 73 | 19:00
Uttara | 58 | 18:30 | Cox'sbazar | 102 | 18:30 | Shahjadpur | 79 | 9:00
Uttara New | 25 | 18:30 | Chandraghona | 22 | 18:00 | Serajganj | 82 | 19:00
Kamrangirchar | 57 | 18:30 | Kaptai | 4 | 19:00 | Niyamatpur | 89 | 9:00
Savar | 133 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 53 | 8:00
Bhasantec | 92 | 18:30 | Bakulia | 96 | 18:30 | Sherpur(Bogura) | 52 | 8:00
Agargaon | 53 | 13:00 | Julda | 27 | 11:00 | Mohastangor | 50 | 18:30
Satmosjid | 75 | 19:00 | TK chemical | 21 | 19:00 | Bhangura | 25 | 19:00
Old Tongi | 125 | 18:00 | Modern Steel | 0 | 1:00 | Rangpur | 113 | 19:00
Kabirpur | 207 | 18:30 | Shahmirpur | 40 | 18:30 | Lalmonirhat | 32 | 20:00
Manikgonj | 67 | 21:00 | Khagrachhari | 22 | 18:30 | Saidpur | 84 | 9:00
Joydevpur | 170 | 18:30 | Matarbari | 28 | 19:00 | Purbasadipur | 95 | 18:30
New Tongi | 70 | 12:00 | Baroiar Hat | 34 | 18:30 | Thakurgaon | 65 | 19:00
Kodda | 202 | 16:00 | Rangamati | 10 | 18:00 | Palashbari | 100 | 8:00
Dhamrai | 94 | 13:00 | Abul Khair 230 | 22 | 9:00 | Barapukuria | 50 | 9:00
Rajendrapur | 100 | 19:00 | BSRM | 157 | 2:00 | Panchagar | 42 | 18:30
Bashundara | 117 | 18:30 | GPH Ispat | 101 | 18:00 | Joldhaka | 46 | 19:00
Purbachal | 1 | 1:00 | Agrabad | 48 | 18:30 | Kurigram | 33 | 19:00
Tongi Millgate | 36 | 9:00 | Goalpara | 20 | 19:00 | Mithapukur | 25 | 18:30
Bashundhara Cement |  |  | Central S/S | 66 | 19:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-02-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 420 | 6:00 | 410 | 11:00 | Kaliakoir | 411 | 0.125 | 396 | 0.625
| Bheramara | 406 | 2:00 | 393 | 13:00 | Bhulta | 414 | 0.25 | 396 | 0.625
| Ashuganj(N) | 417 | 6:00 | 400 | 15:00 | Gopalganj | 415 | 0.625 | 402 | 0.875
| Payra | 420 | 6:00 | 413 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 244 | 1:00 | 240 | 21:00 | Hathazari | 243 | 21:00 | 229 | 11:00
| Ishurdi | 243 | 3:00 | 233 | 11:00 | Megnaghat | 246 | 6:00 | 241 | 22:00
| Ashuganj | 246 | 1:00 | 235 | 15:00 | Fenchuganj | 247 | 6:00 | 241 | 18:00
| Serajganj | 240 | 3:00 | 233 | 11:00 | Siddhirganj | 240 | 6:00 | 230 | 17:00
| Baghabari | 242 | 2:00 | 231 | 9:00 | Maniknagar | 239 | 6:00 | 228 | 15:00
| Barapukuria | 237 | 3:00 | 232 | 7:00 | Agargaon | 240 | 3:00 | 229 | 15:00
| Bogra | 238 | 22:00 | 230 | 11:00 | Barisal | 244 | 19:00 | 239 | 19:30
| Rajshahi | 241 | 2:00 | 231 | 9:00 | Bhola 225 MW | 247 | 9:00 | 243 | 21:00
| Khulna South | 242 | 1:00 | 229 | 11:00 | AKSML | 244 | 19:00 | 230 | 11:00
| Rampura | 237 | 1:00 | 227 | 15:00 | BSRM | 241 | 3:00 | 230 | 11:00
| Haripur | 237 | 8:00 | 228 | 12:00 | Bibiyana | 245 | 2:00 | 239 | 15:00
| Hasnabad | 240 | 1:00 | 230 | 11:00 | Bhulta | 239 | 6:00 | 230 | 15:00
| Shyampur | 239 | 6:00 | 228 | 15:00 | Ashuganj (S) | 242 | 1:00 | 232 | 15:00
| Aminbazar | 241 | 1:00 | 232 | 2:00 | Kaliakoir | 238 | 1:00 | 229 | 15:00
| Tongi | 240 | 1:00 | 230 | 15:00 | GPH | 242 | 1:00 | 230 | 11:00
| Comilla (N) | 240 | 6:00 | 233 | 11:00 | Jhenaidah | 239 | 3:00 | 231 | 14:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 7:00 | 130 | 14:00 | PHP | 140 | 8:00 | 134 | 11:00
| Munsiganj | 138 | 8:00 | 130 | 17:00 | Kachua | 141 | 19:00 | 134 | 0:00
| Sonargaon | 136 | 1:00 | 132 | 11:00 | Madanhat | 142 | 19:00 | 135 | 14:00
| Bhulta | 133 | 1:00 | 126 | 14:00 | Hathazari | 142 | 21:00 | 136 | 5:00
| Madanganj | 137 | 7:00 | 130 | 16:00 | Khulshi | 140 | 22:00 | 130 | 11:00
| Rahim steel | 136 | 8:00 | 130 | 16:00 | Halishahar | 141 | 22:00 | 133 | 15:00
| Ghorasal | 143 | 1:00 | 140 | 22:00 | Baraulia | 142 | 1:00 | 135 | 18:00
| Narsingdi | 134 | 7:00 | 128 | 15:00 | Sikalbaha | 141 | 4:00 | 135 | 15:00
| Haripur(SBU) | 136 | 8:00 | 130 | 16:00 | Dohazari | 139 | 19:00 | 130 | 11:00
| Sreenagar | 136 | 6:00 | 128 | 15:00 | Cox'sbazar | 130 | 1:00 | 123 | 18:30
| Shyampur | 133 | 6:00 | 126 | 15:00 | Chandraghona | 143 | 20:00 | 135 | 11:00
| Shitalakhya | 137 | 6:00 | 130 | 15:00 | Kaptai | 140 | 1:00 | 140 | 1:00
| Matuail | 136 | 7:00 | 130 | 14:00 | A. Khaer Stl. | 141 | 19:30 | 135 | 11:00
| Char Saidpur | 138 | 6:00 | 130 | 15:00 | Bakulia | 141 | 19:30 | 133 | 11:00
| Ullon | 132 | 3:00 | 125 | 11:00 | Julda | 141 | 19:00 | 133 | 11:00
| Hasnabad | 138 | 1:00 | 131 | 16:00 | TK Chemical | 142 | 19:00 | 134 | 18:00
| Magbazar | 132 | 3:00 | 125 | 15:00 | Modern Steel | 141 | 20:00 | 135 | 18:30
| Maniknagar | 135 | 1:00 | 128 | 15:00 | Shahmirpur | 141 | 19:00 | 133 | 11:00
| Bangabhaban | 135 | 1:00 | 128 | 15:00 | Khagrachhari | 141 | 21:00 | 134 | 11:00
| Motijheel | 135 | 1:00 | 128 | 15:00 | Matarbari | 134 | 3:00 | 124 | 18:00
| Narinda | 135 | 1:00 | 128 | 15:00 | Baroiar Hat | 140 | 8:00 | 134 | 11:00
| Kazla | 135 | 1:00 | 128 | 15:00 | Rangamati | 142 | 20:00 | 134 | 11:00
| Dhanmondi | 137 | 5:00 | 130 | 16:00 | Agrabad | 140 | 19:00 | 134 | 18:00
| Lalbag | 136 | 6:00 | 128 | 15:00 | Goalpara S/S | 140 | 3:00 | 132 | 11:00
| Madartek | 132 | 3:00 | 124 | 15:00 | Khulna Central S/S | 137 | 1:00 | 132 | 11:00
| Dhaka University | 131 | 1:00 | 124 | 15:00 | Noapara | 138 | 2:00 | 129 | 11:00
| Aftabnagar | 132 | 6:00 | 125 | 11:00 | Jessore | 136 | 4:00 | 128 | 11:00
| Fatullah | 134 | 19:00 | 127 | 15:00 | Benapol | 137 | 4:00 | 128 | 11:00
| Nawabganj | 135 | 1:00 | 128 | 15:00 | Jhenida(Old) | 139 | 2:00 | 131 | 11:00
| Keraniganj | 136 | 6:00 | 128 | 15:00 | Bottail | 140 | 3:00 | 134 | 19:30
| Banani | 131 | 1:00 | 125 | 12:00 | G.K Project | 143 | 3:00 | 138 | 12:00
| Mirpur | 133 | 2:00 | 126 | 12:00 | Faridpur | 140 | 1:00 | 135 | 15:00
| Kalyanpur | 134 | 6:00 | 127 | 15:00 | Rajbari | 140 | 3:00 | 134 | 11:00
| Gulshan | 132 | 5:00 | 125 | 11:00 | Madaripur | 144 | 5:00 | 139 | 11:00
| Uttara | 136 | 6:00 | 127 | 12:00 | Shariyatpur S/S | 142 | 1:00 | 137 | 19:30
| Uttara New | 135 | 1:00 | 128 | 11:00 | Gopalganj | 143 | 3:00 | 137 | 8:00
| Kamrangirchar | 135 | 1:00 | 128 | 16:00 | Bagerhat | 136 | 5:00 | 130 | 11:00
| Savar | 135 | 7:00 | 127 | 15:00 | Mongla | 136 | 17:00 | 131 | 12:00
| Bhasantec | 133 | 3:00 | 125 | 15:00 | Satkhira | 137 | 3:00 | 129 | 11:00
| Agargaon | 133 | 3:00 | 126 | 15:00 | Gallamari | 141 | 3:00 | 135 | 8:00
| Satmosjid | 133 | 3:00 | 126 | 15:00 | Magura | 140 | 1:00 | 132 | 11:00
| Old Tongi | 140 | 1:00 | 130 | 11:00 | Narail | 138 | 2:00 | 130 | 11:00
| Kabirpur | 137 | 1:00 | 129 | 15:00 | Chuadanga | 137 | 3:00 | 128 | 11:00
| Manikgonj | 134 | 1:00 | 127 | 18:30 | Barisal(N) | 143 | 3:00 | 139 | 13:00
| Joydevpur | 142 | 2:00 | 134 | 15:00 | Barisal (S) | 142 | 2:00 | 135 | 18:30
| New Tongi | 137 | 2:00 | 131 | 15:00 | Patuakhali(S) | 138 | 4:00 | 135 | 21:00
| Kodda | 137 | 19:30 | 130 | 10:00 | Bhandaria | 141 | 5:00 | 136 | 12:00
| Dhamrai | 135 | 3:00 | 127 | 15:00 | Borguna | 142 | 3:00 | 137 | 18:30
| Rajendrapur | 137 | 21:00 | 124 | 12:00 | Jhenaidah(New) | 138 | 3:00 | 130 | 11:00
| Bashundara | 136 | 18:30 | 128 | 11:00 | Ishurdi | 141 | 3:00 | 135 | 11:00
| Purbachal | 132 | 1:00 | 125 | 14:00 | Ruppur Paromanobik | 139 | 5:00 | 135 | 11:00
| Tongi Millgate | 136 | 7.00 | 128 | 11:00 | Natore | 140 | 1:00 | 134 | 11:00
| Bashundhara Cement |  |  |  |  | Bogra | 139 | 1:00 | 132 | 7:00
| Valuka | 129 | 4:00 | 117 | 18:30 | Noagaon | 136 | 3:00 | 127 | 11:00
| Tangail | 136 | 2:00 | 124 | 17:00 | Rajshahi | 139 | 18:00 | 133 | 7:00
| Mymensing | 131 | 5:00 | 119 | 18:30 | Rajshahi New | 138 | 2:00 | 132 | 11:00
| Kishorganj | 133 | 1:00 | 122 | 18:30 | C.Nawabganj | 137 | 3:00 | 129 | 7:00
| Netrokona | 131 | 1:00 | 116 | 15:00 | Amnura | 138 | 19:00 | 129 | 8:00
| Jamalpur | 137 | 22:00 | 126 | 15:00 | Pabna | 140 | 3:00 | 133 | 11:00
| Sherpur | 137 | 22:00 | 125 | 17:00 | Shahjadpur | 144 | 1:00 | 136 | 11:00
| Srimongal | 140 | 1:00 | 136 | 18:30 | Serajganj | 139 | 1:00 | 132 | 11:00
| Shahjibazar | 137 | 3:00 | 133 | 11:00 | Niyamatpur | 133 | 2:00 | 123 | 11:00
| Fenchuganj | 140 | 3:00 | 137 | 18:00 | Joypurhat | 137 | 1:00 | 125 | 8:00
| Khulawara | 140 | 1:00 | 137 | 11:00 | Sherpur(Bogura) | 139 | 2:00 | 132 | 11:00
| Sylhet | 137 | 1:00 | 133 | 19:00 | Mohastangor | 138 | 3:00 | 133 | 11:00
| Chatak | 137 | 1:00 | 134 | 18:00 | Bhangura | 141 | 4:00 | 134 | 11:00
| Sunamganj | 136 | 2:00 | 132 | 18:30 | Rangpur | 137 | 5:00 | 130 | 11:00
| Biani Bazar | 137 | 1:00 | 135 | 11:00 | Lalmonirhat | 134 | 1:00 | 130 | 14:00
| Comilla(s) | 130 | 1:00 | 125 | 12:00 | Saidpur | 136 | 6:00 | 130 | 18:30
| Comilla(n) | 141 | 1:00 | 137 | 14:00 | Purbasadipur | 137 | 5:00 | 129 | 18:30
| Chandpur | 141 | 18:30 | 134 | 0:00 | Thakurgaon | 139 | 5:00 | 130 | 18:30
| Feni | 140 | 9:00 | 135 | 11:00 | Palashbari | 136 | 4:00 | 129 | 8:00
| Chowmuhani | 135 | 1:00 | 130 | 11:00 | Barapukuria | 137 | 4:00 | 132 | 7:00
| Ashuganj | 138 | 1:00 | 135 | 11:00 | Panchagar | 139 | 3:00 | 130 | 11:00
| Daudkandi | 138 | 5:00 | 133 | 11:00 | Joldhaka | 136 | 4:00 | 128 | 11:00
| B.Baria | 135 | 4:00 | 129 | 11:00 | Kurigram | 134 | 6:00 | 129 | 8:00
| Ramganj | 140 | 19:0 | 132 | 15:00 | Mithapukur | 137 | 3:00 | 132 | 16:00
| Chaddagram | 142 | 20:00 | 135 | 18:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-02-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 8 | 5642 | 2386 | 8028 |  |  |  | QF-LDC-11
0:30 | 52 | 5238 | 2264.5 | 7502.5 | Date: | 2022-02-26
1:00 | 96 | 4834 | 2143 | 6977
1:30 | 115 | 4678.5 | 2118.5 | 6797
2:00 | 134 | 4523 | 2094 | 6617
2:30 | 140 | 4516 | 2064.5 | 6580.5 | [5 empty] | Gen. at Eve. Peak | 10361 | 10361 MW (19:00 )
3:00 | 146 | 4509 | 2035 | 6544 | [6 empty] | 19:00
3:30 | 165 | 4368 | 2017.5 | 6385.5 | [5 empty] | Gen. at Day Peak | 9028 | 9028 MW (12:00 )
4:00 | 184 | 4227 | 2000 | 6227 | [6 empty] | 12:00
4:30 | 185 | 4234.5 | 2006.5 | 6241 | [5 empty] | Highest Generation | 10381
5:00 | 186 | 4242 | 2013 | 6255 | [6 empty] | 19:00
5:30 | 158 | 4356 | 2028 | 6384
6:00 | 130 | 4470 | 2043 | 6513
6:30 | 125 | 4676.5 | 2161.5 | 6838
7:00 | 120 | 4883 | 2280 | 7163
7:30 | 147 | 5122 | 2420.5 | 7542.5
8:00 | 174 | 5361 | 2561 | 7922
8:30 | 101 | 5530 | 2590 | 8120
9:00 | 28 | 5699 | 2619 | 8318
9:30 | 104 | 5759 | 2675 | 8434
10:00 | 180 | 5819 | 2731 | 8550
10:30 | 208 | 5874 | 2757.5 | 8631.5
11:00 | 236 | 5929 | 2784 | 8713
11:30 | 210 | 6018.5 | 2852 | 8870.5
12:00 | 184 | 6108 | 2920 | 9028
12:30 | 140 | 6233.5 | 2943.5 | 9177
13:00 | 96 | 6359 | 2967 | 9326
13:30 | 162 | 6195 | 2901.5 | 9096.5
14:00 | 228 | 6031 | 2836 | 8867
14:30 | 297 | 6017 | 2811 | 8828
15:00 | 366 | 6003 | 2786 | 8789
15:30 | 349 | 5977.5 | 2738 | 8715.5
16:00 | 332 | 5952 | 2690 | 8642
16:30 | 339 | 5924 | 2670.5 | 8594.5
17:00 | 346 | 5896 | 2651 | 8547
17:30 | 346 | 6113.5 | 2709 | 8822.5
18:00 | 346 | 6331 | 2767 | 9098
18:30 | 230 | 6757.5 | 2982 | 9739.5
19:00 | 114 | 7184 | 3197 | 10381
19:30 | 12 | 7052 | 3181 | 10233
20:00 | 34 | 6938 | 3190 | 10128 |  |  |  | Executive Engineer
20:30 | 26 | 6880 | 3143.5 | 10023.5 |  |  |  | Network Operation Division
21:00 | 18 | 6822 | 3097 | 9919
21:30 | 56 | 6638 | 3021.5 | 9659.5
22:00 | 94 | 6454 | 2946 | 9400 |  |  |  |  | Page 6 of 7
22:30 | 90 | 6206 | 2794.5 | 9000.5
23:00 | 86 | 5958 | 2643 | 8601
23:30 | 47 | 5800 | 2514.5 | 8314.5
24:00 | 8 | 5642 | 2386 | 8028
10361 MW (19:00 )
9028 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-02-26 |  | Energy |  | 202457987
[13 empty] | 2022-02-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2980 | 709 | 1450 | 0 | 2177 | 570 | 46 | 0 | 0 | 96 | 0 | 0
0:30 | 2931 | 709 | 1494.5 | 0 | 1704 | 525 | 46 | 0 | 0 | 93 | 0 | 0 | Date: | 2022-02-26
1:00 | 2882 | 709 | 1539 | 0 | 1231 | 480 | 46 | 0 | 0 | 90 | 0 | 0
1:30 | 2859.5 | 667 | 1541 | 0 | 1109.5 | 485 | 46 | 0 | 0 | 89 | 0 | 0 | [8 empty] | Total Energy | 202.458 | Total Energy Gen 202.458 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 202.458 MKWHr
2:00 | 2837 | 625 | 1543 | 0 | 988 | 490 | 46 | 0 | 0 | 88 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2842.5 | 622 | 1527.5 | 0 | 965.5 | 490 | 46 | 0 | 0 | 87 | 0 | 0 | [8 empty] | Energy Requirement | 202.458
3:00 | 2848 | 619 | 1512 | 0 | 943 | 490 | 46 | 0 | 0 | 86 | 0 | 0
3:30 | 2797 | 619 | 1480.5 | 0 | 868 | 490 | 46 | 0 | 0 | 85 | 0 | 0 | [6 empty] | Shortage
4:00 | 2746 | 619 | 1449 | 0 | 793 | 490 | 46 | 0 | 0 | 84 | 0 | 0
4:30 | 2741.5 | 620.5 | 1463 | 0 | 791 | 495 | 46 | 0 | 0 | 84 | 0 | 0
5:00 | 2737 | 622 | 1477 | 0 | 789 | 500 | 46 | 0 | 0 | 84 | 0 | 0
5:30 | 2764.5 | 621.5 | 1507.5 | 0 | 859.5 | 500 | 46 | 0 | 0 | 85 | 0 | 0
6:00 | 2792 | 621 | 1538 | 0 | 930 | 500 | 46 | 0 | 0 | 86 | 0 | 0
6:30 | 2829.5 | 668.5 | 1521 | 0 | 1185 | 495 | 46 | 0 | 0 | 87 | 6 | 0 |  |  |  |  | Coal
7:00 | 2867 | 716 | 1504 | 0 | 1440 | 490 | 46 | 0 | 0 | 88 | 12 | 0
7:30 | 2863 | 716 | 1460.5 | 0 | 1833 | 490 | 46 | 0 | 8 | 91 | 35 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2859 | 716 | 1417 | 0 | 2226 | 490 | 46 | 0 | 16 | 94 | 58 | 0
8:30 | 2875.5 | 716.5 | 1396 | 0 | 2392.5 | 490 | 46 | 0 | 16 | 99 | 88.5 | 0
9:00 | 2892 | 717 | 1375 | 0 | 2559 | 490 | 46 | 0 | 16 | 104 | 119 | 0
9:30 | 2959 | 716.5 | 1373 | 0 | 2547.5 | 485 | 38 | 0 | 62 | 112 | 141 | 0
10:00 | 3026 | 716 | 1371 | 0 | 2536 | 480 | 30 | 0 | 108 | 120 | 163 | 0
10:30 | 3074 | 716 | 1378.5 | 0 | 2543 | 480 | 30 | 0 | 113.5 | 119 | 177.5 | 0
11:00 | 3122 | 716 | 1386 | 0 | 2550 | 480 | 30 | 0 | 119 | 118 | 192 | 0
11:30 | 3078.5 | 716 | 1411.5 | 0 | 2681 | 490 | 35 | 0 | 137.5 | 124 | 197 | 0
12:00 | 3035 | 716 | 1437 | 0 | 2812 | 500 | 40 | 0 | 156 | 130 | 202 | 0
12:30 | 3028 | 716.5 | 1417 | 0 | 2976 | 500 | 43 | 0 | 177.5 | 126 | 193 | 0
13:00 | 3021 | 717 | 1397 | 0 | 3140 | 500 | 46 | 0 | 199 | 122 | 184 | 0
13:30 | 3021 | 717 | 1397 | 0 | 3140 | 500 | 46 | 0 | 199 | 122 | 184 | 0
14:00 | 3021 | 717 | 1397 | 0 | 3140 | 500 | 46 | 0 | 199 | 122 | 184 | 0
14:30 | 2998.5 | 717.5 | 1396.5 | 0 | 2886.5 | 505 | 46 | 0 | 224 | 122 | 161.5 | 0
15:00 | 2976 | 718 | 1396 | 0 | 2633 | 510 | 46 | 0 | 249 | 122 | 139 | 0
15:30 | 2990.5 | 717.5 | 1364 | 0 | 2598.5 | 515 | 46 | 0 | 250 | 121 | 113 | 0
16:00 | 3005 | 717 | 1332 | 0 | 2564 | 520 | 46 | 0 | 251 | 120 | 87 | 0
16:30 | 3037 | 717 | 1275 | 0 | 2582 | 520 | 46 | 0 | 261.5 | 115 | 57 | 0
17:00 | 3037 | 717 | 1218 | 0 | 2600 | 520 | 46 | 0 | 272 | 110 | 27 | 0
17:30 | 3048 | 717.5 | 1257 | 59.5 | 2684.5 | 520 | 46 | 0 | 356 | 119 | 15 | 0
18:00 | 3059 | 718 | 1296 | 119 | 2769 | 520 | 46 | 0 | 440 | 128 | 3 | 0
18:30 | 3042 | 714 | 1363 | 275.5 | 3110 | 565 | 46 | 0 | 496.5 | 126 | 1.5 | 0
19:00 | 3025 | 710 | 1430 | 432 | 3451 | 610 | 46 | 0 | 553 | 124 | 0 | 0
19:30 | 3067 | 710 | 1425 | 80 | 3607 | 630 | 46 | 0 | 544 | 124 | 0 | 0
20:00 | 3051 | 710 | 1408 | 0 | 3602 | 649 | 46 | 0 | 540 | 122 | 0 | 0
20:30 | 3054 | 710 | 1419.5 | 0 | 3590 | 654 | 46 | 0 | 430 | 120 | 0 | 0
21:00 | 3057 | 710 | 1431 | 0 | 3578 | 659 | 46 | 0 | 320 | 118 | 0 | 0
21:30 | 3058 | 710 | 1428.5 | 0 | 3427.5 | 649.5 | 46 | 0 | 225 | 115 | 0 | 0
22:00 | 3059 | 710 | 1426 | 0 | 3277 | 640 | 46 | 0 | 130 | 112 | 0 | 0
22:30 | 3016.5 | 709.5 | 1415 | 0 | 2971.5 | 620 | 46 | 0 | 114 | 108 | 0 | 0
23:00 | 2974 | 709 | 1404 | 0 | 2666 | 600 | 46 | 0 | 98 | 104 | 0 | 0
23:30 | 2977 | 709 | 1427 | 0 | 2421.5 | 585 | 46 | 0 | 49 | 100 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 30.8° C
24:00 | 2980 | 709 | 1450 | 0 | 2177 | 570 | 46 | 0 | 0 | 96 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 202.458 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 202.458 MKWHr
Note on W13: Author:

## Generation
g | 2022-02-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 30 | 30 | 40 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1056900
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 7 | 5 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  | 0 | 243045
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 8 | 13 | 17 | 20 | 20 | 19 | 17 | 14 | 9 | 3 | [9 empty] | 142695
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 36 | 46 | 51 |  |  | 0 | 167523
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 18 | 74 | 85 | 85 | 68 | 68 | 72 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1142472
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 40 | [6 empty] | 44928
14 | Titas 50 MW Peaking PP | [9 empty] | 42 | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 |  |  |  | 0 | 526688
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [5 empty] | 2 | 30 | 120 | 225 | 228 | 230 | 245 | 260 | 260 | 260 | 263 | 263 | 263 |  | 263 | 278 | 280 | 280 | 280 | 245 | 30 | 4185162
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 73 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 953454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8202991
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 26 | 26 | 26 | 26 | 23 | 26 | 29 | 23 | 23 | 23 | 29 | 29 | 29 | 29 | 27 | 27 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 628992
33 | Ashuganj 225 MW CCPP | 185 | 184 | 184 | 184 | 184 | 184 | 187 | 187 | 183 | 197 | 185 | 179 | 174 | 163 | 179 | 204 | 210 | 198 |  | 190 | 202 | 208 | 218 | 222 | 225 | 225 | 4664000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 275 | 275 | 305 | 305 | 305 | 275 | 275 | 305 | 275 | 275 | 275 | 275 | 270 | 280 | 305 |  | 275 | 285 | 275 | 275 | 270 | 270 | 285 | 6927000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 260 | 260 | 260 | 295 | 260 | 260 | 260 | 265 | 260 | 260 | 285 |  | 260 | 270 | 260 | 260 | 260 | 260 | 270 | 6812000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 144960
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5200700
41 | Haripur 360MW CCPP(HPL) | 344 | 344 | 344 | 344 | 347 | 347 | 342 | 342 | 343 | 303 | 303 | 338 | 335 | 331 | 332 | 302 | 283 | 282 |  | 333 | 332 | 332 | 332 | 332 | 332 | 332 | 7894000
42 | RPCL 210MW CCPP | 155 | 160 | 163 | 160 | 163 | 161 | 162 | 163 | 160 | 142 | 142 | 132 | 110 | 107 | 68 | 93 | 100 | 94 |  | 93 | 93 | 94 | 93 | 93 | 93 | 93 | 2947200
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 14 | 29 | 41 | 47 | 49 | 30 | 23 | 33 | 23 | 6 | 0 | [8 empty] | 302750
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 838240
46 | Shajibazar 330 MW CCPP | 249 | 249 | 248 | 250 | 252 | 251 | 251 | 250 | 249 | 250 | 247 | 248 | 250 | 252 | 250 | 252 | 252 | 251 |  | 250 | 252 | 250 | 246 | 250 | 249 | 247 | 5723000
47 | Shahjibazar GTPP Unit- 8 & 9 | 68 | 70 | 69 | 40 | 40 | 40 | 70 | 68 | 67 | 40 | 40 | 62 | 64 | 64 | 60 | 40 | 40 | 64 |  | 66 | 67 | 68 | 68 | 69 | 40 | 40 | 1329600
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 20 | 20 | 79 | 79 | 79 | 79 | 78 | 84 | 81 | 81 | 84 | 84 | 84 | 40 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1772160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 136 | 175 | 175 | 175 | 175 | 175 | 175 | 201 | 208 | 189 | 177 | 177 | 177 | 176 | 176 | 178 | 177 |  | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 4214890
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252180
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210240
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 11 | 24 |  | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 1140000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384522
57 | Bibiana-II 341 MW CCPP (Summit) | 265 | 270 | 270 | 265 | 290 | 295 | 300 | 275 | 270 | 280 | 280 | 300 | 290 | 270 | 300 | 280 | 300 | 310 |  | 315 | 300 | 280 | 295 | 300 | 270 | 290 | 7086500
| Bibiyana South 400 MW | 324 | 250 | 250 | 200 | 180 | 180 | 180 | 180 | 210 | 335 | 400 | 400 | 400 | 350 | 395 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 350 | 350 | 7764800
58 | Nababganj 55 MW PP (Southern power ) | [5 empty] | 10 | 45 | 55 | 35 | 35 | 35 | 40 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 913853
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 22 | 22 | 22 | 21 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 517440
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 18 | 18 | 17 | 17 | 17 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 402528
61 | Narshingdi 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  | 15 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 384300
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 497808
63 | Impoprt (Tripura) | 90 | 88 | 86 | 84 | 84 | 86 | 88 | 94 | 104 | 120 | 118 | 130 | 122 | 122 | 122 | 120 | 110 | 128 |  | 124 | 124 | 122 | 118 | 112 | 104 | 96 | 2492160
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 38 | 35 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 7 |  | 13 | 20 | 22 | 30 | 30 | 30 | 42 | 500640
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 446508
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 181260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 23 | 23 | 25 | 25 | 25 | 28 | 33 |  | 30 | 32 | 30 | 30 | 28 | 25 | 25 | 720100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 19 | 19 | 17 | 17 | 19 |  |  | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 |  |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 456600
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 31 | 31 | 31 | 31 | 31 | 30 | 28 | 30 | 30 | 30 | 18 |  | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 676440
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 31 | 31 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 665300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 807300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 70 | 70 | 70 | 82 | 109 | 51 | 51 | 51 | 51 | 96 |  | 108 | 108 | 108 | 108 | 70 | 17 | 0 | 1332660
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | [8 empty] | 6 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 145320
| Manikgonj 162MW PP(MPGL) | 162 | 72 | 72 | 17 | 17 | 30 | 78 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 155 | 144 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3287520
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 8 | 8 | 8 | 8 | 11 | 25 | 16 | 16 | 16 | 16 | 16 |  | 33 | 51 | 49 | 51 |  |  | 0 | 312480
79 | Kodda 150MW PP | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 64 |  | 150 | 150 | 150 | 82 | 32 |  | 0 | 613920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 45 | 52 | 52 | 52 | 48 | 52 | 52 | 52 | 45 | 43 | 46 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1233797
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 32 | 72 | 90 | 90 | 90 | 90 | 90 | 92 | 103 | 99 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1978800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 32160
| Jodiac Power | [11 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 17 |  | 24 | 54 | 53 | 54 | 54 | 54 | 54 | 424203
| Karnaphuli Power Ltd. | [11 empty] | 9 | 34 | 17 | 17 | 17 | 17 | 17 |  | 83 | 108 | 105 | 108 | 110 | 110 | 110 | 771963
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 10 | 12 | 12 | 11 | 11 | 11 | 10 | 11 | 12 | 11 |  | 11 | 12 | 12 | 12 |  |  | 0 | 158935
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 46 | 17 | 17 | 17 | 22 | 74 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2143680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 30 | 30 | 30 |  |  |  | 0 | 45120
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | [18 empty] | 14 | 402324
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 16 | 45 | 74 | 74 | 74 | 80 | 93 | 16 | 16 | 16 | 16 | 32 |  | 93 | 93 | 93 | 93 | 32 |  | 0 | 904896
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604800
96 | Chattogram 108 MW PP (ECPV) | 103 | 102 | 103 | 70 | 64 | 64 | 69 | 96 | 96 | 94 | 88 | 89 | 88 | 88 | 88 | 88 | 83 | 89 |  | 89 | 89 | 90 | 95 | 96 | 95 | 96 | 2129280
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 10 | 30 | 30 | 30 | 30 | 40 | 15 | 15 | 15 | 15 | 16 |  | 40 | 55 | 55 | 55 | 15 |  | 0 | 455689
100 | Manikganj 55 MW PP (Northern) | [5 empty] | 10 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 957681
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2918700
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14700
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 45 | 54 | 54 | 54 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1055520
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 12 |  | 162 | 10 |  |  |  |  | 0 | 150585
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 100 |  | 100 | 40 |  |  |  |  | 0 | 128510
106 | Mymensingh 200 MW PP (United) | 70 | 50 | 50 | 50 | 50 | 64 | 91 | 166 | 167 | 166 | 166 | 174 | 174 | 174 | 174 | 172 | 181 | 184 |  | 180 | 180 | 180 | 182 | 181 | 181 | 173 | 3446400
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 7 |  | 70 | 30 |  |  |  |  | 0 | 87274
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 2 | 37 | 60 | 88 | 87 | 89 | 128 | 131 | 122 | 122 | 122 | 122 |  | 135 | 136 | 135 | 140 | 112 | 35 | 11 | 1707260
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 30 | 60 | 20 | 26 | 76 | 76 | 50 | 50 | 50 | 50 | 70 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1058880
116 | Chandpur 200MW (Desh energy) | 68 | 51 | 34 | 34 | 34 | 34 | 44 | 68 | 74 | 85 | 85 | 90 | 130 | 100 | 100 | 100 | 100 | 100 |  | 146 | 184 | 180 | 181 | 182 | 188 | 100 | 2437440
117 | Ashuganj 150MW PP (Midland) | [5 empty] | 3 | 24 | 24 | [16 empty] | 11 | 73 | 163927
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) |  |  |  |  | 2 | 8 | 20 | 50 | 75 | 75 | 75 | 82 | 115 | 75 | 75 | 75 | 75 | 84 |  | 115 | 115 | 115 | 115 | 115 | 40 | 0 | 1556400
| Anwara 300 MW PP (United) | 230 | 190 | 190 | 155 | 155 | 175 | 210 | 245 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6348000
| Juldah unit-2 (Acorn) | [11 empty] | 10 | 30 | 30 | 10 | 10 | 10 | 20 |  | 100 | 100 | 100 | 100 | 60 | 10 | 0 | 478080
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 100 | 94 | 94 | 77 | 99 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2601927
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 8 | 16 | 21 | 24 | 24 | 26 | 24 | 19 | 12 | 3 | 0 | [8 empty] | 178118
| Chandpur 115(Doreen) | [19 empty] | 22 | 17 | 17 |  |  |  | 0 | 58560
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 53 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1166040
120 | Eastern Zone Total | 4834 | 4523 | 4509 | 4227 | 4242 | 4470 | 4883 | 5361 | 5699 | 5819 | 5929 | 6108 | 6359 | 6031 | 6003 | 5952 | 5896 | 6331 |  | 7184 | 7052 | 6938 | 6822 | 6454 | 5958 | 5642 | 137816618
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 3 | 4 | 19 |  | 38 | 39 | 39 |  |  |  |  | 79680
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [5 empty] | 2 | 37 | 80 | 70 | 70 | 75 | 105 | 105 | 70 | 70 | 70 | 70 | 76 |  | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 1687200
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 5 | 24 | 51 | 71 | 84 | 92 | 91 | 80 | 62 | 37 | 13 | 3 | [8 empty] | 614880
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 225 | 225 | 195 | 201 | 201 | 202 | 202 | 223 | 190 | 216 | 222 | 220 | 193 | 219 | 220 | 205 | 173 | 175 |  | 220 | 224 | 224 | 224 | 215 | 224 | 225 | 5125445
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 270488
| Bhola 225 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 90 | 90 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2204813
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 19 | 19 | 19 | 19 | 16 | 14 | 13 | 14 | 17 | 18 | 18 | 18 | 17 | 18 | 16 | 23 |  | 23 | 23 | 24 | 24 | 24 | 23 | 22 | 445900
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 40 | [5 empty] | 0 | 58560
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 5 | 8 | [5 empty] | 3968
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 709 | 625 | 619 | 619 | 622 | 621 | 716 | 716 | 717 | 716 | 716 | 716 | 717 | 717 | 718 | 717 | 717 | 718 |  | 710 | 710 | 710 | 710 | 710 | 709 | 709 | 16834909
147 | Bheramara 410 MW CCPP | 265 | 270 | 270 | 270 | 275 | 295 | 320 | 330 | 320 | 310 | 320 | 310 | 320 | 310 | 310 | 310 | 310 | 305 |  | 305 | 305 | 305 | 305 | 305 | 305 | 300 | 7452000
148 | Payra 1320 MW | 280 | 290 | 290 | 290 | 300 | 300 | 290 | 290 | 290 | 280 | 280 | 300 | 300 | 290 | 310 | 320 | 320 | 320 |  | 410 | 430 | 450 | 460 | 440 | 400 | 370 | 8819400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 199 | 199 | 200 | 200 | 200 | 4887800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 10 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 |  |  |  | 362256
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 4 | 1 | 0 | [9 empty] | 35340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [26 empty] | 50809
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 161 | 139 | 125 | 120 | 128 | 145 | 151 | 174 | 218 | 211 | 209 | 207 | 204 | 203 | 203 | 203 | 202 |  | 200 | 199 | 199 | 199 | 199 | 194 | 182 | 4570073
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [9 empty] | 4 | 5 | 5 | 29 | 48 | 46 | 45 | 46 | 46 |  | 46 | 46 | 42 |  |  |  |  | 351991
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 162468
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 43 | 25 | 25 | 25 | 34 | 34 | 16 | 16 | 16 | 16 | 16 |  | 43 | 43 | 43 | 43 | 8 | 8 | 0 | 451901
167 | Katakhali 50 MW Peaking PP | [9 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 34 | 40 |  | 40 | 40 | 40 | 21 |  |  |  | 254665
168 | Santahar 50 MW Peaking PP | [11 empty] | 21 | 30 | 31 | 30 | 30 | 31 | 31 |  | 30 | 32 | 30 | 23 |  |  |  | 269606
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 25 | 25 | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1177920
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 30 | 40 | 48 | 48 | 48 | 48 | 48 | 48 | 96 |  | 100 | 100 | 100 | 100 | 98 | 98 | 0 | 921352
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 20 | [5 empty] | 0 | 20407
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 12 | 80 | 70 | 70 | 70 | 90 | 112 | 70 | 50 | 35 | 35 | 41 |  | 105 | 113 | 113 | 113 | 113 | 35 | 0 | 1435296
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 35 | 90 | 113 | 113 | 113 | 113 | 70 | 50 | 35 | 35 | 70 |  | 113 | 113 | 113 | 113 | 113 |  | 0 | 1331712
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 34 | 70 | 100 | 71 | 80 | 113 | 113 | 75 | 70 | 34 | 34 | 42 |  | 99 | 105 | 108 | 113 | 113 | 39 | 5 | 1390060
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 3 | 5 | 5 | 6 | 6 | 3 | 2 | 1 | [9 empty] | 45104
178 | Energypac Power Venture Thakurgaon Ltd. | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 118 |  | 118 | 119 | 119 | 118 | 119 | 119 | 119 | 2805046
178