## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-02-28 | Monday
|  |  | Date (day): | 2022-02-28 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11895.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12463 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-02-27 | 2022-02-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 340 | 340 | 340
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 342 | 333 | 350 | 350
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 11 | 22 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 25 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 0 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 18 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 280 | 254 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 122 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 130 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 72 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2381 | 2611 | 2901 | 2971 | 1676 | 979
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 25 | 25 | 25 |  | 25 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 12 | 46 | 46 | 46 |  | 184 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 30 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 76 | 76 | 76 |  | 24 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 21 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 91 | 100 | 100
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 282 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 22 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 59 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 30 | 70 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 918 | 1043 | 1258 | 1243 | 180 | 937
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 186 | 200 | 200 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 290 | 320 | 340 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 275 | 320 | 340 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 102 | 97 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 39 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 145 | 184 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 114 | 108 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 32 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 45 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 108 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 0 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 0 | 30 | 115 | 115 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1431 | 1587 | 1945 | 2121 | 621 | 200
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 69 | 68 | 90 | 90 | 112 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 170 | 180 | 180 | 180 |  | 20 | Engine problem
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 446 | 407 | 480.6 | 429 | 112 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 22 | 22 |  | 68 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 249 | 249 | 250 | 250 |  | 80 | Machine problem
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 48 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 37 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 177 | 177 | 180 | 180 |  | 51 | Machine problem
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1492 | 1501 | 1559 | 1559 | 73 | 748
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 711 | 707 | 732 | 732
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 5 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 260 | 225 | 305 | 305 | 105 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 40 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1158 | 977 | 1342 | 1642 | 105 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 22 | 25 | 25
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 92 | 91 | 90 | 90 | 104 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 310 | 320 | 520 | 600
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 224 | 220 | 220
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 651 | 668 | 1026 | 1206 | 188 | 0
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 30 | 34 | 43 | 43 |  | 9 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 40 | 45 |  | 26 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 40 | 0 | 35 |  | 15 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 163 | 182 | 170 | 170
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 32 |  | 18 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 48 | 92 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 20 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 103 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 95 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 508 | 722 | 943 | 979 | 600 | 489
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 105 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 119 | 118 | 120 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 437 | 423 | 441 | 313 | 74 | 210
|  | Total |  |  |  |  | 22066 | 20985 | 9422 | 9939 | 11895.6 | 12463 | 3629 | 3654
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9116.7496 | 9617 | 11510.2108 | 12059.2284
| A. |  | 2022-02-27 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 9939 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6754 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9939 | MW
| 3 | Day peak Generation : |  |  | 9422 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9617 | MW
| 4 | Evening peak Generation : |  |  | 9939 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 207.5155 | MKWHr | By Solar | 1.2513 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 104.0179 | MKWHr |  | By Oil: | 68.3994 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.4197 | MKWHr |  | By Hydro: | 0.9789 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3629 | MW | Dhaka | 3739 | 3739 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3654 | MW | Chittagong | 1159 | 1159 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7283 | MW | Khulna | 789 | 789 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 773.89 | MMCFD |  |  | Rajshahi | 988 | 988 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 101387161.694 | ii) Oil : | Taka | 466498648.39 | Comilla | 852 | 852 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 63909734 | Total | Taka | 631795544.084 | Mymensingh | 857 | 857 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.662 | MKWHr. | Sylhet | 358 | 358 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -42 | MW (E to W) at | 19:00 | hrs | Barisal | 189 | 189 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -200 | MW at | 7:00 | hrs | Rangpur | 686 | 686 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32° C |  |  | Total | 9617 | 9617 |  | 0
| B. |  | 2022-02-28 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 30.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12463 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2063 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 217.1407 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6716 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0378 | MKWHr. | ii) HVDC Flow at Peak Time |  | 707 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4106 | MKWHr. | iii) Maximum HVDC Flow : |  | 711 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.64 |  | (b) Today: | 90.53 |  | (c) Rule Curve: |  | 93.32
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-02-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 95 | 25 | 18 | 42 | 0 | 0 | 0 | 260 | 270 | 225 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 5 | 25 | 12 | 92 | 101 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 250 | 40 | 84 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 105 | 105 | 0 | 300 | 0 | 110 | 0 | 8 | 0 | 350 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 710 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 225 | 0 | 0 | 0 | 0 | 119 |  | 5284 | 2281 | 7565 | 2951 | 710 | 1478 | 0 | 1748 | 540 | 46 | 0 | 0 | 92 | 0 | 0 | 90.66
2:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 42 | 0 | 0 | 0 | 295 | 305 | 214 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 5 | 25 | 17 | 88 | 105 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 250 | 68 | 84 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 34 | 0 | 282 | 0 | 0 | 0 | 8 | 0 | 310 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 710 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 209 | 0 | 0 | 0 | 0 | 119 |  | 4894 | 2244 | 7138 | 3007 | 710 | 1479 | 0 | 1288 | 520 | 46 | 0 | 0 | 88 | 0 | 0 | 90.66
3:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 0 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 42 | 0 | 0 | 0 | 260 | 270 | 213 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 5 | 25 | 17 | 86 | 108 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 249 | 70 | 84 | 0 | 176 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 34 | 0 | 282 | 0 | 0 | 0 | 8 | 0 | 310 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 | 0 | 119 |  | 4801 | 2231 | 7032 | 2902 | 711 | 1499 | 0 | 1288 | 500 | 46 | 0 | 0 | 86 | 0 | 0 | 90.65
4:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 0 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 42 | 0 | 0 | 0 | 270 | 275 | 221 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 5 | 25 | 17 | 84 | 108 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 251 | 55 | 84 | 0 | 188 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 34 | 0 | 282 | 0 | 0 | 0 | 8 | 0 | 310 | 104 | 0 | 162 | 95 | 0 | 17 | 0 | 0 | 17 |  | 664 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 170 | 0 | 0 | 0 | 0 | 119 |  | 4715 | 2129 | 6844 | 2919 | 664 | 1439 | 0 | 1192 | 500 | 46 | 0 | 0 | 84 | 0 | 0 | 90.65
5:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 306 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 25 | 18 | 42 | 0 | 0 | 0 | 260 | 270 | 219 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 5 | 25 | 17 | 84 | 108 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 250 | 40 | 84 | 0 | 188 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 34 | 0 | 282 | 0 | 0 | 0 | 8 | 0 | 260 | 75 | 0 | 162 | 111 | 0 | 17 | 0 | 0 | 17 |  | 663 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 165 | 0 | 0 | 0 | 0 | 119 |  | 4630 | 2124 | 6754 | 2864 | 663 | 1418 | 0 | 1179 | 500 | 46 | 0 | 0 | 84 | 0 | 0 | 90.64
6:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 25 | 18 | 42 | 0 | 0 | 0 | 295 | 305 | 187 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 25 | 17 | 84 | 108 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 251 | 68 | 84 | 0 | 188 | 0 | 0 | 10 | 320 | 16 | 5 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 20 | 19 | 2 | 0 | 10 | 50 | 37 | 0 | 282 | 0 | 7 | 17 | 8 | 0 | 190 | 74 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 17 |  | 711 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 164 | 0 | 0 | 0 | 0 | 119 |  | 4774 | 2203 | 6977 | 2883 | 711 | 1451 | 0 | 1302 | 500 | 46 | 0 | 0 | 84 | 0 | 0 | 90.64
7:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 332 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 48 | 10 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 25 | 0 | 38 | 0 | 0 | 0 | 280 | 295 | 191 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 25 | 13 | 82 | 104 | 0 | 22 | 0 | 30 | 30 | 48 | 0 | 110 | 250 | 68 | 84 | 0 | 189 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 89 | 0 | 0 | 130 | 0 | 29 | 2 | 60 | 51 | 20 | 0 | 37 | 82 | 70 | 0 | 282 | 0 | 37 | 34 | 0 | 0 | 180 | 82 | 4 | 162 | 113 | 0 | 17 | 2 | 0 | 45 |  | 710 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 70 | 0 | 27 | 0 | 80 | 0 | 0 | 20 | 300 | 164 | 0 | 0 | 0 | 5 | 119 |  | 5239 | 2381 | 7620 | 2820 | 710 | 1437 | 0 | 2012 | 500 | 46 | 0 | 0 | 82 | 13 | 0 | 90.63
8:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 255 |  | 0 | 225 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 13 | 0 | 46 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 25 | 18 | 8 | 0 | 0 | 0 | 260 | 310 | 189 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 25 | 13 | 80 | 92 | 0 | 22 | 1 | 30 | 30 | 48 | 0 | 110 | 254 | 40 | 84 | 0 | 176 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 238 | 0 | 0 | 183 | 0 | 40 | 9 | 40 | 64 | 90 | 0 | 83 | 90 | 93 | 2 | 282 | 7 | 68 | 34 | 0 | 20 | 210 | 104 | 14 | 162 | 113 | 0 | 11 | 8 | 0 | 55 |  | 710 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 157 | 0 | 0 | 105 | 0 | 90 | 0 | 91 | 0 | 0 | 90 | 290 | 166 | 0 | 0 | 1 | 25 | 119 |  | 5690 | 2585 | 8275 | 2799 | 710 | 1311 | 0 | 2747 | 490 | 46 | 0 | 32 | 80 | 60 | 0 | 90.63
9:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 302 |  | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 70 | 62 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 33 | 13 | 0 | 46 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 71 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 181 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 8 | 23 | 13 | 96 | 79 | 0 | 22 | 1 | 30 | 0 | 48 | 0 | 110 | 252 | 64 | 81 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 278 | 0 | 0 | 174 | 0 | 107 | 14 | 60 | 112 | 107 | 0 | 115 | 86 | 105 | 3 | 282 | 17 | 90 | 52 | 0 | 20 | 220 | 104 | 27 | 162 | 113 | 0 | 17 | 15 | 0 | 55 |  | 711 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 164 | 0 | 0 | 105 | 0 | 110 | 0 | 113 | 0 | 1 | 95 | 310 | 200 | 0 | 0 | 2 | 50 | 119 |  | 6037 | 2721 | 8758 | 2709 | 711 | 1385 | 0 | 3126 | 510 | 46 | 0 | 62 | 96 | 113 | 0 | 90.62
10:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 302 |  | 0 | 225 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 93 | 62 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 33 | 32 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 209 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 43 | 19 | 8 | 23 | 13 | 102 | 69 | 0 | 22 | 2 | 30 | 0 | 48 | 0 | 110 | 248 | 25 | 84 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 280 | 0 | 0 | 174 | 0 | 128 | 19 | 60 | 136 | 103 | 0 | 115 | 72 | 105 | 4 | 282 | 17 | 105 | 70 | 0 | 10 | 310 | 104 | 39 | 162 | 113 | 0 | 17 | 20 | 0 | 55 |  | 710 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 34 | 0 | 52 | 0 | 10 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 0 | 105 | 0 | 112 | 0 | 113 | 0 | 2 | 95 | 280 | 200 | 0 | 0 | 3 | 71 | 119 |  | 6238 | 2733 | 8971 | 2764 | 710 | 1342 | 0 | 3277 | 480 | 30 | 0 | 106 | 102 | 160 | 0 | 90.62
11:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 281 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 70 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 33 | 16 | 0 | 12 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 214 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 26 | 43 | 19 | 8 | 23 | 16 | 114 | 69 | 0 | 22 | 2 | 30 | 0 | 48 | 0 | 110 | 250 | 20 | 84 | 0 | 177 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 280 | 0 | 0 | 162 | 0 | 135 | 20 | 60 | 136 | 102 | 0 | 115 | 90 | 105 | 5 | 282 | 17 | 110 | 70 | 0 | 10 | 400 | 104 | 46 | 162 | 113 | 0 | 17 | 23 | 0 | 55 |  | 711 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 34 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 169 | 0 | 0 | 105 | 0 | 70 | 0 | 113 | 0 | 4 | 50 | 270 | 200 | 0 | 0 | 4 | 82 | 119 |  | 6357 | 2657 | 9014 | 2849 | 711 | 1343 | 0 | 3185 | 470 | 12 | 0 | 144 | 114 | 186 | 0 | 90.61
12:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 18 | 0 | 12 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 202 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 39 | 45 | 13 | 0 | 16 | 16 | 114 | 69 | 0 | 22 | 2 | 30 | 22 | 48 | 0 | 110 | 249 | 31 | 84 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 280 | 0 | 0 | 170 | 0 | 149 | 20 | 76 | 145 | 102 | 0 | 115 | 90 | 105 | 5 | 282 | 17 | 110 | 105 | 0 | 30 | 400 | 104 | 46 | 162 | 113 | 0 | 17 | 24 | 0 | 55 |  | 711 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 18 | 0 | 0 | 0 | 0 | 30 | 0 | 48 | 0 | 34 | 16 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 70 | 0 | 113 | 0 | 5 | 60 | 310 | 220 | 0 | 0 | 5 | 82 | 119 |  | 6668 | 2754 | 9422 | 2844 | 711 | 1458 | 0 | 3301 | 510 | 12 | 0 | 283 | 114 | 189 | 0 | 90.61
13:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 336 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 38 | 0 | 12 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 25 | 18 | 3 | 0 | 0 | 0 | 260 | 275 | 206 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 48 | 45 | 13 | 8 | 17 | 16 | 114 | 69 | 0 | 22 | 1 | 30 | 22 | 48 | 0 | 110 | 250 | 32 | 84 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 280 | 37 | 0 | 170 | 0 | 149 | 20 | 90 | 164 | 97 | 0 | 115 | 90 | 105 | 5 | 300 | 17 | 110 | 105 | 0 | 30 | 400 | 104 | 25 | 162 | 113 | 0 | 17 | 27 | 0 | 55 |  | 706 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 43 | 0 | 48 | 0 | 34 | 16 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 190 | 0 | 0 | 105 | 0 | 90 | 0 | 113 | 0 | 6 | 90 | 340 | 216 | 0 | 0 | 2 | 83 | 119 |  | 6764 | 2857 | 9621 | 2882 | 706 | 1438 | 37 | 3418 | 540 | 12 | 0 | 305 | 114 | 169 | 0 | 90.6
14:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 333 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 82 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 32 | 47 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 219 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 19 | 8 | 25 | 16 | 108 | 69 | 0 | 22 | 1 | 30 | 22 | 48 | 0 | 110 | 253 | 20 | 84 | 0 | 177 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 210 | 0 | 0 | 171 | 0 | 106 | 18 | 60 | 170 | 97 | 0 | 115 | 90 | 68 | 4 | 300 | 17 | 34 | 60 | 0 | 10 | 400 | 104 | 38 | 162 | 113 | 0 | 17 | 22 | 0 | 55 |  | 706 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 34 | 0 | 48 | 0 | 8 | 16 | 52 | 27 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 193 | 0 | 0 | 105 | 0 | 108 | 0 | 112 | 0 | 5 | 50 | 300 | 210 | 0 | 0 | 4 | 73 | 119 |  | 6382 | 2749 | 9131 | 2880 | 706 | 1398 | 0 | 3071 | 500 | 46 | 0 | 257 | 108 | 165 | 0 | 90.6
15:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 329 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 82 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 76 | 19 | 18 | 2 | 0 | 0 | 0 | 280 | 270 | 220 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 48 | 43 | 19 | 8 | 33 | 20 | 96 | 65 | 0 | 22 | 0 | 30 | 22 | 45 | 0 | 110 | 250 | 20 | 84 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 210 | 0 | 0 | 170 | 0 | 90 | 14 | 60 | 155 | 100 | 0 | 115 | 86 | 68 | 3 | 300 | 17 | 34 | 50 | 6 | 10 | 400 | 104 | 13 | 162 | 113 | 0 | 16 | 18 | 0 | 55 |  | 708 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 34 | 0 | 48 | 0 | 8 | 16 | 52 | 28 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 193 | 0 | 0 | 105 | 0 | 112 | 0 | 111 | 0 | 4 | 50 | 310 | 217 | 0 | 0 | 1 | 55 | 119 |  | 6342 | 2743 | 9085 | 2897 | 708 | 1426 | 0 | 3038 | 510 | 46 | 0 | 256 | 96 | 108 | 0 | 90.59
16:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 327 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 74 | 64 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 76 | 0 | 18 | 2 | 0 | 0 | 0 | 280 | 270 | 216 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 43 | 19 | 8 | 33 | 20 | 96 | 67 | 0 | 22 | 0 | 30 | 22 | 45 | 0 | 110 | 252 | 20 | 84 | 0 | 177 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 210 | 0 | 0 | 170 | 0 | 90 | 9 | 60 | 155 | 95 | 0 | 80 | 72 | 51 | 2 | 300 | 17 | 34 | 50 | 8 | 10 | 400 | 104 | 18 | 162 | 113 | 0 | 35 | 3 | 0 | 55 |  | 707 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 34 | 0 | 48 | 0 | 8 | 16 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 192 | 0 | 0 | 70 | 0 | 35 | 0 | 70 | 0 | 2 | 35 | 300 | 220 | 0 | 0 | 0 | 33 | 119 |  | 6174 | 2538 | 8712 | 2891 | 707 | 1409 | 0 | 2756 | 499 | 46 | 0 | 241 | 96 | 67 | 0 | 90.59
17:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 329 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 74 | 64 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 84 | 0 | 18 | 2 | 0 | 0 | 0 | 280 | 270 | 211 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 43 | 19 | 8 | 33 | 20 | 94 | 68 | 0 | 22 | 0 | 30 | 22 | 47 | 0 | 110 | 250 | 20 | 84 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 210 | 0 | 0 | 171 | 0 | 90 | 3 | 20 | 136 | 92 | 0 | 80 | 70 | 51 | 1 | 300 | 17 | 34 | 50 | 8 | 10 | 400 | 104 | 2 | 162 | 113 | 0 | 35 | 1 | 0 | 55 |  | 706 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 34 | 0 | 48 | 0 | 8 | 24 | 52 | 30 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 189 | 0 | 0 | 53 | 0 | 35 | 0 | 70 | 0 | 1 | 35 | 310 | 218 | 0 | 0 | 0 | 10 | 118 |  | 6100 | 2513 | 8613 | 2882 | 706 | 1420 | 0 | 2683 | 510 | 46 | 0 | 254 | 94 | 18 | 0 | 90.59
18:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 338 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 84 | 82 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 24 | 88 | 10 | 18 | 5 | 0 | 0 | 0 | 320 | 305 | 186 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 47 | 19 | 8 | 33 | 20 | 110 | 68 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 250 | 32 | 84 | 0 | 177 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 210 | 37 | 25 | 171 | 25 | 90 | 0 | 76 | 136 | 92 | 0 | 90 | 85 | 54 | 0 | 300 | 17 | 34 | 40 | 8 | 35 | 400 | 104 | 0 | 162 | 113 | 0 | 35 | 0 | 2 | 55 |  | 706 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 34 | 5 | 100 | 0 | 16 | 34 | 52 | 29 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 187 | 0 | 0 | 36 | 0 | 37 | 0 | 90 | 0 | 0 | 50 | 300 | 202 | 0 | 0 | 0 | 0 | 118 |  | 6464 | 2571 | 9035 | 2922 | 706 | 1410 | 87 | 2865 | 500 | 46 | 0 | 389 | 110 | 0 | 0 | 90.58
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 333 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 0 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 30 | 91 | 25 | 18 | 21 | 0 | 0 | 0 | 290 | 275 | 186 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 19 | 8 | 32 | 20 | 108 | 68 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 249 | 37 | 84 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 254 | 122 | 100 | 180 | 100 | 130 | 0 | 76 | 184 | 97 | 0 | 115 | 72 | 105 | 0 | 300 | 22 | 59 | 108 | 8 | 70 | 400 | 104 | 0 | 162 | 113 | 0 | 35 | 0 | 30 | 55 |  | 707 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 34 | 10 | 92 | 0 | 34 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 0 | 40 | 20 | 103 | 0 | 105 | 0 | 0 | 95 | 320 | 224 | 0 | 0 | 0 | 0 | 118 |  | 7149 | 2790 | 9939 | 2832 | 707 | 1476 | 342 | 3446 | 520 | 46 | 0 | 462 | 108 | 0 | 0 | 90.57
19:30 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 334 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 16 | 0 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 17 | 0 | 95 | 25 | 18 | 17 | 0 | 0 | 0 | 280 | 270 | 209 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 50 | 52 | 19 | 8 | 33 | 20 | 104 | 68 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 255 | 66 | 84 | 0 | 176 | 0 | 0 | 10 | 285 | 16 | 11 | 0 | 278 | 72 | 70 | 180 | 70 | 149 | 0 | 76 | 200 | 97 | 0 | 115 | 72 | 105 | 0 | 300 | 17 | 51 | 108 | 8 | 20 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 35 | 55 |  | 706 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 34 | 32 | 100 | 0 | 34 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 181 | 0 | 0 | 105 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 320 | 224 | 0 | 0 | 0 | 0 | 118 |  | 6991 | 2886 | 9877 | 2890 | 706 | 1442 | 212 | 3504 | 520 | 46 | 0 | 453 | 104 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 335 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 0 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 17 | 0 | 95 | 25 | 18 | 21 | 0 | 0 | 0 | 280 | 270 | 202 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 19 | 8 | 33 | 20 | 104 | 68 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 251 | 65 | 84 | 0 | 177 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 280 | 20 | 70 | 180 | 25 | 149 | 0 | 63 | 200 | 97 | 0 | 115 | 72 | 105 | 0 | 300 | 17 | 51 | 108 | 8 | 20 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 35 | 55 |  | 707 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 34 | 37 | 100 | 0 | 34 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 181 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 330 | 224 | 0 | 0 | 0 | 0 | 118 |  | 6892 | 2907 | 9799 | 2890 | 707 | 1455 | 115 | 3494 | 530 | 46 | 0 | 458 | 104 | 0 | 0 | 90.58
21:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 337 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 10 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 97 | 25 | 18 | 28 | 0 | 0 | 0 | 280 | 270 | 211 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 19 | 8 | 33 | 20 | 96 | 68 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 250 | 67 | 84 | 0 | 176 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 280 | 0 | 0 | 171 | 0 | 149 | 0 | 76 | 200 | 102 | 0 | 115 | 72 | 105 | 0 | 300 | 17 | 51 | 108 | 8 | 20 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 35 | 55 |  | 710 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 34 | 40 | 100 | 0 | 43 | 40 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 370 | 225 | 0 | 0 | 0 | 0 | 119 |  | 6805 | 2972 | 9777 | 2919 | 710 | 1478 | 0 | 3515 | 570 | 46 | 0 | 443 | 96 | 0 | 0 | 90.57
22:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 338 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 93 | 48 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 25 | 18 | 37 | 0 | 0 | 0 | 280 | 270 | 217 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 20 | 100 | 68 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 250 | 68 | 84 | 0 | 176 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 280 | 0 | 0 | 190 | 0 | 143 | 0 | 60 | 200 | 105 | 0 | 115 | 72 | 68 | 0 | 300 | 0 | 34 | 108 | 8 | 0 | 400 | 104 | 0 | 162 | 96 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 181 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 420 | 222 | 0 | 0 | 0 | 0 | 105 |  | 6474 | 2869 | 9343 | 2953 | 711 | 1477 | 0 | 3288 | 620 | 46 | 0 | 148 | 100 | 0 | 0 | 90.57
23:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 25 | 18 | 37 | 0 | 0 | 0 | 305 | 300 | 213 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 48 | 19 | 8 | 33 | 20 | 102 | 70 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 240 | 67 | 84 | 0 | 169 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 64 | 0 | 60 | 200 | 110 | 0 | 45 | 72 | 68 | 0 | 300 | 0 | 34 | 34 | 8 | 0 | 350 | 104 | 0 | 162 | 94 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 16 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 0 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 50 | 380 | 225 | 0 | 0 | 0 | 0 | 60 |  | 5950 | 2653 | 8603 | 2932 | 711 | 1473 | 0 | 2659 | 580 | 46 | 0 | 100 | 102 | 0 | 0 | 90.56
24:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 25 | 18 | 41 | 0 | 0 | 0 | 270 | 270 | 218 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 49 | 19 | 8 | 33 | 21 | 102 | 89 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 241 | 60 | 84 | 0 | 169 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 145 | 0 | 0 | 172 | 0 | 35 | 0 | 60 | 155 | 145 | 0 | 24 | 72 | 34 | 0 | 300 | 0 | 17 | 17 | 8 | 0 | 350 | 104 | 0 | 162 | 95 | 0 | 17 | 0 | 0 | 55 |  | 711 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 151 | 0 | 0 | 70 | 0 | 70 | 0 | 98 | 0 | 0 | 35 | 340 | 226 | 0 | 0 | 0 | 0 | 55 |  | 5709 | 2396 | 8105 | 2864 | 711 | 1476 | 0 | 2366 | 540 | 46 | 0 | 0 | 102 | 0 | 0 | 90.56
KWH | 0 | 0 | 0 | 0 | 8108545 | 0 | 0 | 0 | 7778000 |  | 0 | 5178950 | 0 | 0 | 0 | 679622 | 0 | 0 | 0 | 0 | 1309968 | 1413600 | 218432 | 0 | 0 | 0 | 1149480 | 971599 | 950650 | 488808 | 600000 | 448740 | 685500 | 816900 | 518400 | 0 | 978900 | 0 | 0 | 0 | 233040 | 0 | 0 | 0 | 0 |  | 531600 | 0 | 92693 | 139800 | 2099520 | 539520 | 42072 | 482400 | 0 | 0 | 0 | 7042000 | 6939000 | 5017000 | 200727 | 0 | 655848 | 142080 | 0 | 1083688 | 0 | 474744 | 1193347 | 440028 | 179640 | 658300 | 438440 | 2410560 | 1920960 | 0 | 507204 | 9550 | 717000 | 516456 | 1155000 | 0 | 2914936 | 5703000 | 1067040 | 2016960 | 0 | 4284550 | 0 | 0 | 251460 | 7228500 | 380592 | 168576 | 0 | 4368325 | 177392 | 183999 | 3508800 | 138281 | 1900370 | 150525 | 1177920 | 2839200 | 1915272 | 0 | 1833600 | 1906800 | 1901054 | 33121 | 6962727 | 300618 | 1364103 | 1252860 | 146160 | 319680 | 8088300 | 2505600 | 267300 | 3954240 | 2638309 | 0 | 514440 | 153835 | 122880 | 1236960 |  | 17037818 | 0 | 6597216 | 0 | 0 | 0 | 0 | 0 | 20640 | 0 | 0 | 2216085 | 453600 | 0 | 0 | 0 | 0 | 322266 | 86951 | 960377 | 0 | 410679 | 221732 | 1240320 | 214091 | 498240 | 0 | 175752 | 0 | 0 | 4851700 | 0 | 0 | 0 | 0 | 0 | 0 | 269568 | 0 | 4462136 | 0 | 0 | 1741440 | 24589 | 1664928 | 0 | 1809321 | 0 | 37354 | 1318560 | 8568000 | 4998109 | 0 | 0 | 27900 | 571680 | 2677889 |  | 144036596 | 63478941 | 207515537 | 69365688 | 17037818 | 34652218 | 524261 | 64068033 | 13419700 | 978900 | 0 | 3807094 | 2410560 | 1251265 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 9000484.95 | 0 | 0 | 0 | 8011340 |  | 0 | 5645055.5 | 0 | 0 | 0 | 5749602.12 | 0 | 0 | 0 | 0 | 11946908.16 | 13909824 | 2013943.04 | 0 | 0 | 0 | 8391204 | 7510460.27 | 9373409 | 366606 | 450000 | 0 | 0 | 0 | 5012928 | 0 | 264303 | 0 | 0 | 0 | 2164941.6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 899122.1 | 1335090 | 18265824 | 4272998.4 | 53010.72 | 1432728 | 0 | 0 | 0 | 5211080 | 6939000 | 4615640 | 258937.83 | 0 | 741108.24 | 198912 | 0 | 1853106.48 | 0 | 4794914.4 | 11396463.85 | 558835.56 | 134730 | 1152025 | 328830 | 18079200 | 2036217.6 | 0 | 644149.08 | 152227 | 1175880 | 826329.6 | 2055900 | 0 | 3323027.04 | 5931120 | 2102068.8 | 3852393.6 | 0 | 7412271.5 | 0 | 0 | 512978.4 | 7300785 | 285444 | 128117.76 | 0 | 33024537 | 3012116.16 | 3076463.28 | 18245760 | 2312058.32 | 18699640.8 | 1759637.25 | 9600048 | 30805320 | 13502667.6 | 0 | 16722432 | 18019260 | 16558180.34 | 0 | 52638216.12 | 2618382.78 | 11990465.37 | 12503542.8 | 1252591.2 | 2129068.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98137831.68 | 0 | 6927076.8 | 0 | 0 | 0 | 0 | 0 | 216513.6 | 0 | 0 | 2504176.05 | 703080 | 0 | 0 | 0 | 0 | 3171097.44 | 883422.16 | 8499336.45 | 0 | 5552380.08 | 2148583.08 | 12018700.8 | 2076682.7 | 956620.8 | 0 | 133044.264 | 0 | 0 | 26296214 | 0 | 0 | 0 | 0 | 0 | 0 | 404352 | 0 | 5220699.12 | 0 | 0 | 18180633.6 | 418258.89 | 15800166.72 | 0 | 14040330.96 | 0 | 412761.7 | 9744158.4 | 37613520 | 0 | 0 | 0 | 0 | 0 | 0 |  | 478541863.42 | 272059641.294 | 750601504.714 | 64877945.044 | 98137831.68 | 36509216.65 | 8818896.65 | 421080255.81 | 63909734 | 264303 | 0 | 36599495.93 | 18079200 | 2324625.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 342 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 11 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 18 | 0 | 12 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 77 | 25 | 18 | 2 | 0 | 0 | 0 | 260 | 275 | 202 | 8 | 0 | 26 | 5 | 0 | 43 | 0 | 39 | 45 | 13 | 0 | 16 | 16 | 114 | 69 | 0 | 22 | 2 | 30 | 22 | 48 | 0 | 110 | 249 | 31 | 84 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 280 | 0 | 0 | 170 | 0 | 149 | 20 | 76 | 145 | 102 | 0 | 115 | 90 | 105 | 5 | 282 | 17 | 110 | 105 | 0 | 30 | 400 | 104 | 46 | 162 | 113 | 0 | 17 | 24 | 0 | 55 |  | 711 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 18 | 0 | 0 | 0 | 0 | 30 | 0 | 48 | 0 | 34 | 16 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 70 | 0 | 113 | 0 | 5 | 60 | 310 | 220 | 0 | 0 | 5 | 82 | 119 |  | 9422 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 333 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 0 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 30 | 91 | 25 | 18 | 21 | 0 | 0 | 0 | 290 | 275 | 186 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 19 | 8 | 32 | 20 | 108 | 68 | 0 | 22 | 0 | 30 | 22 | 48 | 0 | 110 | 249 | 37 | 84 | 0 | 177 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 254 | 122 | 100 | 180 | 100 | 130 | 0 | 76 | 184 | 97 | 0 | 115 | 72 | 105 | 0 | 300 | 22 | 59 | 108 | 8 | 70 | 400 | 104 | 0 | 162 | 113 | 0 | 35 | 0 | 30 | 55 |  | 707 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 34 | 10 | 92 | 0 | 34 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 0 | 40 | 20 | 103 | 0 | 105 | 0 | 0 | 95 | 320 | 224 | 0 | 0 | 0 | 0 | 118 |  | 9939 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 | 0 | 0 | 225 |  | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 25 | 18 | 20 | 0 | 0 | 0 | 340 | 340 | 200 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 163 | 90 | 0 | 22 | 0 | 30 | 22 | 50 | 0 | 110 | 250 | 66 | 84 | 0 | 180 | 0 | 0 | 10 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 180 | 100 | 149 | 0 | 76 | 200 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 |  | 115 | 55 |  | 732 | 0 | 305 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 90 | 25 | 110 | 0 | 0 | 0 | 43 | 45 | 100 | 0 | 43 | 35 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 170 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 600 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 350 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 25 | 18 | 10 | 0 | 0 | 0 | 320 | 320 | 200 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 138 | 90 | 0 | 22 | 1.6 | 30 | 22 | 50 | 0 | 110 | 250 | 66 | 84 | 0 | 180 | 0 | 0 | 10 | 330 | 16 | 11 | 100 | 300 | 200 | 100 | 180 | 100 | 149 | 20 | 76 | 200 | 150 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 50 | 162 | 113 | 0 | 17 | 30 | 115 | 55 |  | 732 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 25 | 110 | 0 | 0 | 0 | 43 | 40 | 100 | 0 | 43 | 0 | 52 | 30 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 170 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 520 | 220 |  | 50 | 6 | 50 | 120
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 344 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 30 | 33 | 5 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 82 | 25 | 18 | 10 | 0 | 0 | 0 | 285 | 275 | 189 | 8 | 0 | 29 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 25 | 20 | 94 | 92 | 0 | 22 | 1 | 30 | 22 | 48 | 0 | 110 | 240 | 60 | 84 | 0 | 176 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 180 | 0 | 0 | 180 | 0 | 50 | 8 | 60 | 120 | 115 | 0 | 86 | 72 | 44 | 1 | 282 | 0 | 17 | 18 | 0 | 0 | 290 | 104 | 12 | 162 | 94 | 0 | 17 | 6 | 0 | 37 | 0 | 717 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 144 | 0 | 0 | 90 | 0 | 70 | 0 | 70 | 0 | 0 | 113 | 290 | 205 | 0 | 0 | 1 | 27 | 119 | 0
199
| Minimum Generation |  | 6754 | 5:00
| Highest Generation |  | 9939 | 19:00
| Day Peak Generation |  | 9422 | 12:00
| Evening Peak Generation |  | 9939 | 19:00
| HVDC Max Flow |  | 711 | 3:00
| HVDC EvPeak Flow |  | 707 | 19:00
| Load factor L.F |  | 87%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-02-28
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-02-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9422 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6716 | MW
Evening Peak Generation : |  | 9939 | MW Hour : | 19:00 | Available Max Generation : |  | 12463 | MW
E.P. Demand (at gen end) : |  | 9939 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10400 | MW
Maximum Generation : |  | 9939 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2063 | MW
Total Gen. (MKWH) : |  | 207.5155 | System Load Factor : | 87% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -200 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-02-28
Actual : | 90.53 | Ft.(MSL) , | Rule curve : | 93.32 | Ft.( MSL )
Gas Consumed : | Total = | 773.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 101387161.694
: |  | Coal : | 63909734 | Oil : | 466498648.39 | Total : | 631795544.084
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3748.2957 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1273.1805 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1140.4696 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1030.419 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 931.2252 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 751.4621 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 422.0433 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 193.5306 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 579.556 |  |  | 0 | 0%
Total | 0 |  | 10070.182 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Meghnaghat Summit 305 MW CCPP
|  |  |  | 2) Ghorasal-3,4,5 |  | 11) Meghnaghat 450 MW CCPP GT-1
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Siddhirganj 335 MW
6) Raozan unit- 1,2
7) Sirajganj Unit 1,2 & 4.
8) Summit Bibiyana-3
9) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Juldah-Shahmirpur 132 kV Ckt-1 was under shut down from 08:17 to 14:32 for A/M.
b) Hasnabad-APR 230 kV Ckt-2 was under shut down from 08:20 to 13:20 for A/M.
c) Chandpur-Chandpur Desh P.P. 132 kV Ckt-2 was under shut down from 08:32 to 17:15 for A/M.
d) Kallyanpur 132/33 kV T-3 transformer was under shut down from 08:24 to 17:01 for C/M.
e) B.Baria-Narshingdhi 132 kV Ckt-1 was under shut down from 08:48 to 17:56 for A/M.
f) Feni-Chowddagram 132 kV Ckt-2 was under shut down from 08:21 to 15:31 for A/M.
g) Kodda-Rajendrapur 132 kV Ckt-1 was under shut down from 09:24 to 14:38 for D/W.
h) Tongi-Uttara 132 kV Ckt was under shut down from 09:22 to 17:18 for C/M.
i) Madanganj S/S-Madanganj P.P. 132 kV Ckt was shut down at 09:26 for C/M.
j) Bogura-Sirajganj 230 kV Ckt-1&2 tripped at 09:27 showing ARC and were switched on at 09:40.
k) Nawabganj 132/33 kV T-1 transformer was under shut down from 09:44 to 17:08 for A/M.
l) Cumilla(S) 132/33 kV T-2 transformer was under shut down from 10:02 to 12:56 for C/M.
m) Matuail-Maniknagar 132 kV Ckt was under shut down from 10:48 to 13:38 for C/M.
n) Meghnaghat-Shyampur 230 kV Ckt-1 was under shut down from 12:40 to 17:44 for C/M.
o) Shyampur-APR 230 kV Ckt was under shut down from 13:33 to 17:09 for A/M.
p) Khulna GT-Goalpara 132 kV Ckt tripped at 17:50 from both ends showing Differential ABC at Khulna end
& Differential Y-phase at Goalpara end.
q) 33 kV Side of Madaripur 132/33 kV T-1, T-2 & T-3 transformers tripped at 18:05 due to bad weather | [5 empty] | About 20 MW power interruption occurred under
and were switched on at 18:15. | [5 empty] | Madaripur S/S area from 18:05 to 18:15.
r) Hathazari-Baroirhat 132 kV Ckt-2 tripped at 22:42 from both ends showing Dist. Z1, B-phase at Hathazari
end & Dist. Z1 at Baroirhat end and was switched on at 23:03.
s) Kallyanpur 132/33 kV T-3 transformer was shut down at 07:12(28/02/2022) for C/M.
t) Kallyanpur 132 kV reserve Bus was shut down at 07:28(28/02/2022) for C/M.
u) Juldah-Shahmirpur 132 kV Ckt-2 was shut down at 07:37(28/02/2022) for A/M.
v) Bibiyana-Kaliakoir 400 kV Ckt-1 was shut down at 07:40(28/02/2022) for C/M.
w) Bhaluka 132/33 kV T-1 transformer along with 33 kV Bus was under shut down from 07:26(28/02/2022) | [5 empty] | About 40 MW power interruption has been running
for D/W. | [5 empty] | under Bhaluka S/S area since 07:26(28/02/2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-02-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 8108545
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 333 | 7778000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5178950 | GT-2 S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 679622
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 22 | 218432 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 488808
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1309968 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1149480
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1413600
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 971599
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 950650
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 25 | 1048740 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 685500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 816900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 518400 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 254 | 4368325 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 122 | 177392 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 183999
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 138281
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 130 | 1900370 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 72 | 1906800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2505600
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3954240
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 153835
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1236960
| Dhaka area Total |  |  |  | 5696 | 2611 | 47842996
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 233040 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 150525
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 539520 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 978900 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1901054
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 92693 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 139800 | High Voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 76 | 1177920 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 42072
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 482400
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 2099520 | High Voltage
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33121
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 6962727
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 22 | 300618 | High Voltage
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 59 | 1364103 | High Voltage
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 70 | 319680
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2638309
| Chattogram area Total |  |  |  | 2382 | 1043 | 19456002
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 186 | 5017000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7042000 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6939000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 655848 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 142080 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1083688 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 97 | 1915272 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 474744
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 184 | 2839200 | Engine problem
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 440028
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 179640 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2410560
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 658300
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1193347
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 438440 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | High Voltage
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 1252860
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 146160 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 514440 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 30 | 122880
| Cumilla Area Total |  |  |  | 2899 | 1587 | 33666214
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 68 | 1920960 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507204
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9550
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 180 | 3508800 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1833600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 267300
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 531600
| Mymensingh Area Total |  |  |  | 622 | 407 | 8579014
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 717000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 516456 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2914936 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 249 | 5703000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 1155000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 168576 | Engine problem
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 37 | 1067040
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2016960
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 177 | 4284550 | Machine problem
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 380592 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7228500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251460
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8088300
| Sylhet Area Total |  |  |  | 2377 | 1501 | 34492370
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 707 | 17037818
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 5 | 20640 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 6597216 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 40 | 1741440 | Low demand
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 571680
| Khulna Area Total |  |  |  | 2229 | 977 | 25968794
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 453600 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2216085 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 269568 | Engine problem
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 320 | 8568000 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 4998109
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 668 | 16505362
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 322266 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 86951 | Low demand
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 410679 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 221732 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4462136 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Gas shortage
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 214091 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 498240
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 175752 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1240320
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 960377 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 20 | 24589 | Low demand
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 103 | 1664928 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1318560 | Engine problem
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27900
| Rajshahi Area Total |  |  |  | 2129 | 722 | 11628521
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4851700 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 105 | 1809321
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37354
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 118 | 2677889 | On test
| Rangpur Area Total |  |  |  | 605 | 423 | 9376264
| Total |  |  |  | 20985 | 9939 | 207515537
| Eastern Grid Total |  |  |  | 13976 | 7149 | 144036596
| Western Grid Total |  |  |  | 7009 | 2790 | 63478941
| National Grid Total |  |  |  | 20985 | 9939 | 207515537
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-02-27
(a) ENTIRE EASTERN GRID : |  | 6965 | MW | (b) ENTIRE WESTERN GRID : |  | 2652 | MW
i) Dhaka area |  | 3739 | MW | i) Khulna area |  | 789 | MW
ii) Chittagong area |  | 1159 | MW | ii) Rajshahi area |  | 988 | MW
iii) Comilla area |  | 852 | MW | iii) Barisal area |  | 189 | MW
iv) Mymensingh area |  | 857 | MW | iv) Rangpur area |  | 686 | MW
v) Sylhet area |  | 358 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9617 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 103 | 15:00 | Valuka | 104 | 10:00 | Noapara | 31 | 8:00
Munsiganj | 62 | 19:00 | Tangail | 182 | 8:00 | Jessore | 92 | 13:00
Sonargaon | 67 | 19:00 | Mymensing | 183 | 18:30 | Benapol | 38 | 13:00
Bhulta | 186 | 22:00 | Kishoreganj | 104 | 20:00 | Jhenida(Old) | 72 | 8:00
Madanganj | 33 | 22:00 | Netrokona | 110 | 8:00 | Bottail | 103 | 18:30
Rahim steel | 10 | 1:00 | Jamalpur | 127 | 8:00 | G.K Project | 38 | 19:00
Ghorasal | 72 | 21:00 | Sherpur | 122 | 18:00 | Faridpur | 94 | 19:30
Narsingdi | 138 | 19:30 | Srimongal | 37 | 18:30 | Rajbari | 44 | 19:00
Haripur(SBU) | 111 | 13:00 | Shahjibazar | 84 | 19:00 | Madaripur | 62 | 21:00
Sreenagar | 28 | 20:00 | Fenchuganj | 29 | 18:00 | Sariatpur | 44 | 19:00
Shyampur | 178 | 10:00 | Kulawara | 28 | 18:30 | Gopalganj | 57 | 21:00
Shitalakhya | 98 | 17:00 | Sylhet | 100 | 14:00 | Bagerhat | 60 | 13:00
Matuail | 60 | 10:00 | Chatak | 19 | 18:00 | Mongla | 42 | 8:00
Char Saidpur | 37 | 10:00 | Sunamganj | 35 | 18:30 | Satkhira | 66 | 7:00
Ullon | 26 | 19:30 | Biani Bazar | 37 | 19:30 | Gallamari | 42 | 12:00
Hasnabad | 63 | 18:00 | Comilla (S) | 114 | 11:00 | Magura | 34 | 18:30
Magbazar | 87 | 12:00 | Comilla(N) | 116 | 19:00 | Norail | 24 | 7:00
Maniknagar | 57 | 13:00 | Chandpur | 48 | 21:00 | Chuadanga | 54 | 13:00
Bangabhaban | 0 | 1:00 | Feni | 88 | 19:00 | Barisal(N) | 35 | 21:00
Motijheel | 32 | 13:00 | Chowmuhani | 142 | 19:30 | Barisal (S) | 74 | 21:00
Narinda | 46 | 13:00 | Ashuganj | 27 | 13:00 | Patuakhali | 77 | 22:00
Kazla | 70 | 19:00 | Daudkandi | 94 | 18:30 | Bhandaria | 34 | 18:00
Dhanmondi | 139 | 13:00 | B.Baria | 114 | 19:30 | Borguna | 10 | 18:00
Lalbag | 77 | 13:00 | Ramganj | 58 | 19:00 | Borhan Uddin | 19 | 21:00
Madartek | 52 | 19:00 | Chaddagram | 32 | 13:00 | Ishurdi | 49 | 19:00
Dhaka University | 25 | 12:00 | PHP | 7 | 4:00 | Ruppur Paromanobik | 4 | 18:30
Aftabnagar | 22 | 13:00 | Kochua | 44 | 19:00 | Natore | 94 | 19:00
Fatullah | 56 | 12:00 | Madunaghat | 38 | 18:00 | Bogra | 113 | 19:00
Nawabganj | 32 | 20:00 | Hathazari | 73 | 19:00 | Naogaon | 100 | 13:00
Keraniganj | 54 | 13:00 | Khulshi | 131 | 11:00 | Rajshahi | 84 | 13:00
Banani | 32 | 13:00 | Halishahar | 79 | 18:30 | Rajshahi New | 30 | 12:00
Mirpur | 94 | 19:00 | Baraulia | 111 | 12:00 | C.Nawabganj | 53 | 7:00
Kalyanpur | 66 | 18:30 | Sikalbaha | 20 | 9:00 | Amnura | 46 | 8:00
Gulshan | 80 | 13:00 | Dohazari | 62 | 18:30 | Pabna | 75 | 19:00
Uttara | 58 | 12:00 | Cox'sbazar | 92 | 18:30 | Shahjadpur | 82 | 7:00
Uttara New | 26 | 12:00 | Chandraghona | 22 | 18:30 | Serajganj | 82 | 19:00
Kamrangirchar | 61 | 13:00 | Kaptai | 4 | 18:30 | Niyamatpur | 89 | 12:00
Savar | 141 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 52 | 8:00
Bhasantec | 93 | 12:00 | Bakulia | 98 | 19:00 | Sherpur(Bogura) | 50 | 7:00
Agargaon | 60 | 13:00 | Julda | 27 | 9:00 | Mohastangor | 52 | 8:00
Satmosjid | 78 | 14:00 | TK chemical | 21 | 19:00 | Bhangura | 28 | 8:00
Old Tongi | 109 | 17:00 | Modern Steel | 0 | 1:00 | Rangpur | 108 | 19:00
Kabirpur | 224 | 15:00 | Shahmirpur | 35.5 | 18:00 | Lalmonirhat | 35 | 19:00
Manikgonj | 65 | 19:30 | Khagrachhari | 20 | 18:30 | Saidpur | 88 | 9:00
Joydevpur | 180 | 12:00 | Matarbari | 29 | 18:30 | Purbasadipur | 99 | 8:00
New Tongi | 77 | 12:00 | Baroiar Hat | 34 | 18:30 | Thakurgaon | 63 | 19:00
Kodda | 248 | 19:00 | Rangamati | 10 | 18:00 | Palashbari | 96 | 18:30
Dhamrai | 96 | 18:30 | Abul Khair 230 | 10 | 20:00 | Barapukuria | 53 | 9:00
Rajendrapur | 98 | 19:00 | BSRM | 159 | 2:00 | Panchagar | 44 | 19:00
Bashundara | 120 | 13:00 | GPH Ispat | 104 | 13:00 | Joldhaka | 49 | 18:30
Purbachal | 2 | 15:00 | Agrabad | 50 | 19:00 | Kurigram | 46 | 19:00
Tongi Millgate | 38 | 18:00 | Goalpara | 21 | 13:00 | Mithapukur | 40 | 8:00
Bashundhara Cement |  |  | Central S/S | 60 | 12:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-02-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 6:00 | 409 | 16:00 | Kaliakoir | 407 | 0.20833 | 393 | 0.625
| Bheramara | 404 | 3:00 | 396 | 8:00 | Bhulta | 408 | 0.25 | 396 | 0.625
| Ashuganj(N) | 412 | 7:00 | 400 | 13:00 | Gopalganj | 414 | 0.625 | 404 | 0.625
| Payra | 420 | 7:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 241 | 13:00 | 231 | 15:00
| Ishurdi | 243 | 21:00 | 233 | 12:00 | Megnaghat | 245 | 9:00 | 241 | 11:00
| Ashuganj | 242 | 4:00 | 235 | 15:00 | Fenchuganj | 245 | 4:00 | 241 | 11:00
| Serajganj | 240 | 22:00 | 232 | 8:00 | Siddhirganj | 236 | 5:00 | 229 | 12:00
| Baghabari | 240 | 23:00 | 231 | 12:00 | Maniknagar | 235 | 5:00 | 227 | 15:00
| Barapukuria | 236 | 21:00 | 231 | 8:00 | Agargaon | 237 | 4:00 | 227 | 17:00
| Bogra | 238 | 21:00 | 227 | 12:00 | Barisal | 244 | 6:00 | 240 | 12:00
| Rajshahi | 243 | 20:00 | 230 | 7:00 | Bhola 225 MW | 246 | 3:00 | 244 | 9:00
| Khulna South | 244 | 18:30 | 232 | 12:00 | AKSML | 240 | 6:00 | 234 | 2:00
| Rampura | 237 | 4:00 | 227 | 16:00 | BSRM | 240 | 6:00 | 233 | 2:00
| Haripur | 234 | 1:00 | 229 | 11:00 | Bibiyana | 245 | 5:00 | 239 | 17:00
| Hasnabad | 237 | 18:30 | 228 | 15:00 | Bhulta | 236 | 5:00 | 229 | 12:00
| Shyampur | 236 | 7:00 | 228 | 12:00 | Ashuganj (S) | 240 | 22:00 | 233 | 12:00
| Aminbazar | 236 | 1:00 | 229 | 2:00 | Kaliakoir | 236 | 6:00 | 227 | 16:00
| Tongi | 234 | 13:00 | 226 | 15:00 | GPH | 240 | 11:00 | 232 | 23:00
| Comilla (N) | 238 | 8:00 | 232 | 15:00 | Jhenaidah | 241 | 22:00 | 230 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 5:00 | 129 | 16:00 | PHP | 138 | 7:00 | 133 | 23:00
| Munsiganj | 136 | 19:00 | 131 | 16:00 | Kachua | 140 | 21:00 | 133 | 1:00
| Sonargaon | 135 | 20:00 | 132 | 11:00 | Madanhat | 141 | 10:00 | 136 | 14:00
| Bhulta | 131 | 2:00 | 125 | 11:00 | Hathazari | 142 | 13:00 | 136 | 17:00
| Madanganj | 136 | 19:00 | 130 | 15:00 | Khulshi | 139 | 21:00 | 134 | 15:00
| Rahim steel | 134 | 2:00 | 130 | 11:00 | Halishahar | 140 | 21:00 | 134 | 15:00
| Ghorasal | 140 | 1:00 | 135 | 11:00 | Baraulia | 142 | 3:00 | 135 | 19:30
| Narsingdi | 132 | 6:00 | 128 | 11:00 | Sikalbaha | 141 | 10:00 | 136 | 19:00
| Haripur(SBU) | 134 | 2:00 | 130 | 11:00 | Dohazari | 139 | 9:00 | 132 | 15:00
| Sreenagar | 133 | 6:00 | 127 | 14:00 | Cox'sbazar | 130 | 9:00 | 123 | 18:30
| Shyampur | 131 | 19:00 | 125 | 12:00 | Chandraghona | 141 | 21:00 | 135 | 14:00
| Shitalakhya | 137 | 20:00 | 132 | 2:00 | Kaptai | 140 | 1:00 | 138 | 23:00
| Matuail | 134 | 5:00 | 129 | 16:00 | A. Khaer Stl. | 140 | 9:00 | 136 | 10:00
| Char Saidpur | 136 | 19:00 | 131 | 12:00 | Bakulia | 140 | 14:00 | 136 | 2:00
| Ullon | 132 | 4:00 | 124 | 12:00 | Julda | 140 | 19:00 | 136 | 14:00
| Hasnabad | 136 | 10:00 | 131 | 15:00 | TK Chemical | 141 | 19:00 | 135 | 17:00
| Magbazar | 131 | 4:00 | 125 | 11:00 | Modern Steel | 139 | 9:00 | 135 | 17:00
| Maniknagar | 133 | 4:00 | 127 | 16:00 | Shahmirpur | 140 | 10:00 | 135 | 16:00
| Bangabhaban | 133 | 4:00 | 127 | 16:00 | Khagrachhari | 141 | 21:00 | 135 | 2:00
| Motijheel | 133 | 4:00 | 127 | 16:00 | Matarbari | 132 | 5:00 | 125 | 18:30
| Narinda | 133 | 4:00 | 127 | 16:00 | Baroiar Hat | 141 | 23:00 | 132 | 2:00
| Kazla | 133 | 4:00 | 127 | 16:00 | Rangamati | 140 | 7:00 | 136 | 14:00
| Dhanmondi | 136 | 3:00 | 130 | 12:00 | Agrabad | 142 | 19:30 | 134 | 17:00
| Lalbag | 134 | 5:00 | 127 | 12:00 | Goalpara S/S | 139 | 18:00 | 132 | 12:00
| Madartek | 130 | 4:00 | 123 | 16:00 | Khulna Central S/S | 139 | 18:30 | 132 | 12:00
| Dhaka University | 130 | 7:00 | 124 | 11:00 | Noapara | 138 | 17:00 | 130 | 12:00
| Aftabnagar | 130 | 3:00 | 124 | 10:00 | Jessore | 136 | 18:30 | 128 | 12:00
| Fatullah | 133 | 19:00 | 126 | 12:00 | Benapol | 137 | 4:00 | 128 | 12:00
| Nawabganj | 137 | 4:00 | 127 | 15:00 | Jhenida(Old) | 138 | 17:00 | 130 | 12:00
| Keraniganj | 134 | 7:00 | 127 | 12:00 | Bottail | 139 | 4:00 | 133 | 12:00
| Banani | 133 | 23:00 | 124 | 12:00 | G.K Project | 142 | 22:00 | 137 | 12:00
| Mirpur | 132 | 7:00 | 125 | 12:00 | Faridpur | 140 | 4:00 | 135 | 11:00
| Kalyanpur | 132 | 5:00 | 127 | 12:00 | Rajbari | 140 | 5:00 | 133 | 12:00
| Gulshan | 129 | 5:00 | 123 | 16:00 | Madaripur | 142 | 5:00 | 139 | 12:00
| Uttara | 135 | 8:00 | 125 | 16:00 | Shariyatpur S/S | 143 | 5:00 | 137 | 22:00
| Uttara New | 135 | 14:00 | 128 | 16:00 | Gopalganj | 143 | 4:00 | 138 | 12:00
| Kamrangirchar | 134 | 4:00 | 127 | 11:00 | Bagerhat | 140 | 18:30 | 130 | 1:00
| Savar | 133 | 7:00 | 126 | 12:00 | Mongla | 142 | 18:30 | 131 | 1:00
| Bhasantec | 131 | 4:00 | 124 | 12:00 | Satkhira | 140 | 18:00 | 129 | 12:00
| Agargaon | 131 | 4:00 | 126 | 12:00 | Gallamari | 142 | 4:00 | 136 | 12:00
| Satmosjid | 132 | 7:00 | 125 | 12:00 | Magura | 140 | 18:00 | 132 | 8:00
| Old Tongi | 136 | 13:00 | 130 | 15:00 | Narail | 138 | 3:00 | 130 | 12:00
| Kabirpur | 134 | 5:00 | 126 | 12:00 | Chuadanga | 137 | 17:00 | 127 | 12:00
| Manikgonj | 132 | 2:00 | 124 | 15:00 | Barisal(N) | 143 | 5:00 | 139 | 15:00
| Joydevpur | 143 | 13:00 | 134 | 16:00 | Barisal (S) | 141 | 4:00 | 139 | 15:00
| New Tongi | 136 | 7:00 | 129 | 16:00 | Patuakhali(S) | 139 | 5:00 | 135 | 12:00
| Kodda | 136 | 13:00 | 125 | 18:00 | Bhandaria | 142 | 18:30 | 137 | 22:00
| Dhamrai | 134 | 7:00 | 126 | 16:00 | Borguna | 142 | 5:00 | 139 | 10:00
| Rajendrapur | 135 | 21:00 | 126 | 18:00 | Jhenaidah(New) | 138 | 4:00 | 131 | 12:00
| Bashundara | 134 | 7:00 | 128 | 16:00 | Ishurdi | 141 | 19:30 | 135 | 12:00
| Purbachal | 130 | 1:00 | 124 | 14:00 | Ruppur Paromanobik | 140 | 20:00 | 135 | 8:00
| Tongi Millgate | 135 | 21:00 | 129 | 18:00 | Natore | 140 | 19:30 | 133 | 11:00
| Bashundhara Cement |  |  |  |  | Bogra | 140 | 19:30 | 133 | 11:00
| Valuka | 129 | 22:00 | 116 | 7:00 | Noagaon | 135 | 19:00 | 126 | 9:00
| Tangail | 133 | 22:00 | 126 | 7:00 | Rajshahi | 139 | 18:00 | 132 | 7:00
| Mymensing | 129 | 22:00 | 119 | 8:00 | Rajshahi New | 139 | 18:30 | 131 | 8:00
| Kishorganj | 130 | 3:00 | 124 | 9:00 | C.Nawabganj | 138 | 19:30 | 128 | 7:00
| Netrokona | 128 | 6:00 | 115 | 8:00 | Amnura | 138 | 18:00 | 128 | 8:00
| Jamalpur | 139 | 22:00 | 127 | 1:00 | Pabna | 139 | 4:00 | 133 | 12:00
| Sherpur | 138 | 21:00 | 125 | 1:00 | Shahjadpur | 144 | 2:00 | 136 | 12:00
| Srimongal | 138 | 1:00 | 136 | 15:00 | Serajganj | 140 | 5:00 | 131 | 11:00
| Shahjibazar | 135 | 5:00 | 132 | 16:00 | Niyamatpur | 134 | 19:30 | 121 | 9:00
| Fenchuganj | 139 | 6:00 | 136 | 13:00 | Joypurhat | 137 | 20:00 | 125 | 8:00
| Khulawara | 139 | 1:00 | 137 | 11:00 | Sherpur(Bogura) | 139 | 18:00 | 132 | 7:00
| Sylhet | 136 | 1:00 | 134 | 15:00 | Mohastangor | 138 | 19:30 | 131 | 8:00
| Chatak | 137 | 1:00 | 135 | 10:00 | Bhangura | 140 | 4:00 | 133 | 12:00
| Sunamganj | 135 | 2:00 | 133 | 11:00 | Rangpur | 135 | 4:00 | 129 | 9:00
| Biani Bazar | 138 | 4:00 | 134 | 14:00 | Lalmonirhat | 134 | 2:00 | 124 | 9:00
| Comilla(s) | 130 | 1:00 | 127 | 10:00 | Saidpur | 135 | 4:00 | 128 | 9:00
| Comilla(n) | 140 | 6:00 | 137 | 16:00 | Purbasadipur | 136 | 3:00 | 127 | 8:00
| Chandpur | 141 | 18:30 | 132 | 1:00 | Thakurgaon | 138 | 2:00 | 128 | 19:00
| Feni | 139 | 6:00 | 134 | 2:00 | Palashbari | 135 | 14:00 | 129 | 12:00
| Chowmuhani | 135 | 7:00 | 130 | 10:00 | Barapukuria | 135 | 15:00 | 131 | 8:00
| Ashuganj | 136 | 6:00 | 135 | 1:00 | Panchagar | 138 | 4:00 | 128 | 12:00
| Daudkandi | 136 | 6:00 | 133 | 10:00 | Joldhaka | 135 | 3:00 | 126 | 19:00
| B.Baria | 133 | 4:00 | 130 | 12:00 | Kurigram | 134 | 5:00 | 126 | 8:00
| Ramganj | 138 | 10:00 | 129 | 2:00 | Mithapukur | 136 | 18:00 | 130 | 8:00
| Chaddagram | 140 | 6:00 | 135 | 1:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-02-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 66 | 5709 | 2396 | 8105 |  |  |  | QF-LDC-11
0:30 | 77 | 5496.5 | 2338.5 | 7835 | Date: | 2022-02-27
1:00 | 88 | 5284 | 2281 | 7565
1:30 | 113 | 5089 | 2262.5 | 7351.5
2:00 | 138 | 4894 | 2244 | 7138
2:30 | 155 | 4847.5 | 2237.5 | 7085 | [5 empty] | Gen. at Eve. Peak | 9939 | 9939 MW (19:00 )
3:00 | 172 | 4801 | 2231 | 7032 | [6 empty] | 19:00
3:30 | 168 | 4758 | 2180 | 6938 | [5 empty] | Gen. at Day Peak | 9422 | 9422 MW (12:00 )
4:00 | 164 | 4715 | 2129 | 6844 | [6 empty] | 12:00
4:30 | 160 | 4672.5 | 2126.5 | 6799 | [5 empty] | Highest Generation | 9939
5:00 | 156 | 4630 | 2124 | 6754 | [6 empty] | 19:00
5:30 | 96 | 4702 | 2163.5 | 6865.5
6:00 | 36 | 4774 | 2203 | 6977
6:30 | 118 | 5006.5 | 2292 | 7298.5
7:00 | 200 | 5239 | 2381 | 7620
7:30 | 199 | 5464.5 | 2483 | 7947.5
8:00 | 198 | 5690 | 2585 | 8275
8:30 | 113 | 5863.5 | 2653 | 8516.5
9:00 | 28 | 6037 | 2721 | 8758
9:30 | 37 | 6137.5 | 2727 | 8864.5
10:00 | 46 | 6238 | 2733 | 8971
10:30 | 34 | 6297.5 | 2695 | 8992.5
11:00 | 22 | 6357 | 2657 | 9014
11:30 | 40 | 6512.5 | 2705.5 | 9218
12:00 | 58 | 6668 | 2754 | 9422
12:30 | 36 | 6716 | 2805.5 | 9521.5
13:00 | 14 | 6764 | 2857 | 9621
13:30 | 86 | 6573 | 2803 | 9376
14:00 | 158 | 6382 | 2749 | 9131
14:30 | 239 | 6362 | 2746 | 9108
15:00 | 320 | 6342 | 2743 | 9085
15:30 | 316 | 6258 | 2640.5 | 8898.5
16:00 | 312 | 6174 | 2538 | 8712
16:30 | 342 | 6137 | 2525.5 | 8662.5
17:00 | 372 | 6100 | 2513 | 8613
17:30 | 349 | 6282 | 2542 | 8824
18:00 | 326 | 6464 | 2571 | 9035
18:30 | 184 | 6806.5 | 2680.5 | 9487
19:00 | 42 | 7149 | 2790 | 9939
19:30 | 48 | 6991 | 2886 | 9877
20:00 | 0 | 6892 | 2907 | 9799 |  |  |  | Executive Engineer
20:30 | 41 | 6848.5 | 2939.5 | 9788 |  |  |  | Network Operation Division
21:00 | 82 | 6805 | 2972 | 9777
21:30 | 99 | 6639.5 | 2920.5 | 9560
22:00 | 116 | 6474 | 2869 | 9343 |  |  |  |  | Page 6 of 7
22:30 | 117 | 6212 | 2761 | 8973
23:00 | 118 | 5950 | 2653 | 8603
23:30 | 92 | 5829.5 | 2524.5 | 8354
24:00 | 66 | 5709 | 2396 | 8105
9939 MW (19:00 )
9422 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-02-27 |  | Energy |  | 207515537
[13 empty] | 2022-02-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2864 | 711 | 1476 | 0 | 2366 | 540 | 46 | 0 | 0 | 102 | 0 | 0
0:30 | 2907.5 | 710.5 | 1477 | 0 | 2057 | 540 | 46 | 0 | 0 | 97 | 0 | 0 | Date: | 2022-02-27
1:00 | 2951 | 710 | 1478 | 0 | 1748 | 540 | 46 | 0 | 0 | 92 | 0 | 0
1:30 | 2979 | 710 | 1478.5 | 0 | 1518 | 530 | 46 | 0 | 0 | 90 | 0 | 0 | [8 empty] | Total Energy | 207.5155 | Total Energy Gen 207.516 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 207.516 MKWHr
2:00 | 3007 | 710 | 1479 | 0 | 1288 | 520 | 46 | 0 | 0 | 88 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2954.5 | 710.5 | 1489 | 0 | 1288 | 510 | 46 | 0 | 0 | 87 | 0 | 0 | [8 empty] | Energy Requirement | 207.5155
3:00 | 2902 | 711 | 1499 | 0 | 1288 | 500 | 46 | 0 | 0 | 86 | 0 | 0
3:30 | 2910.5 | 687.5 | 1469 | 0 | 1240 | 500 | 46 | 0 | 0 | 85 | 0 | 0 | [6 empty] | Shortage
4:00 | 2919 | 664 | 1439 | 0 | 1192 | 500 | 46 | 0 | 0 | 84 | 0 | 0
4:30 | 2891.5 | 663.5 | 1428.5 | 0 | 1185.5 | 500 | 46 | 0 | 0 | 84 | 0 | 0
5:00 | 2864 | 663 | 1418 | 0 | 1179 | 500 | 46 | 0 | 0 | 84 | 0 | 0
5:30 | 2873.5 | 687 | 1434.5 | 0 | 1240.5 | 500 | 46 | 0 | 0 | 84 | 0 | 0
6:00 | 2883 | 711 | 1451 | 0 | 1302 | 500 | 46 | 0 | 0 | 84 | 0 | 0
6:30 | 2851.5 | 710.5 | 1444 | 0 | 1657 | 500 | 46 | 0 | 0 | 83 | 6.5 | 0 |  |  |  |  | Coal
7:00 | 2820 | 710 | 1437 | 0 | 2012 | 500 | 46 | 0 | 0 | 82 | 13 | 0
7:30 | 2809.5 | 710 | 1374 | 0 | 2379.5 | 495 | 46 | 0 | 16 | 81 | 36.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2799 | 710 | 1311 | 0 | 2747 | 490 | 46 | 0 | 32 | 80 | 60 | 0
8:30 | 2754 | 710.5 | 1348 | 0 | 2936.5 | 500 | 46 | 0 | 47 | 88 | 86.5 | 0
9:00 | 2709 | 711 | 1385 | 0 | 3126 | 510 | 46 | 0 | 62 | 96 | 113 | 0
9:30 | 2736.5 | 710.5 | 1363.5 | 0 | 3201.5 | 495 | 38 | 0 | 84 | 99 | 136.5 | 0
10:00 | 2764 | 710 | 1342 | 0 | 3277 | 480 | 30 | 0 | 106 | 102 | 160 | 0
10:30 | 2806.5 | 710.5 | 1342.5 | 0 | 3231 | 475 | 21 | 0 | 125 | 108 | 173 | 0
11:00 | 2849 | 711 | 1343 | 0 | 3185 | 470 | 12 | 0 | 144 | 114 | 186 | 0
11:30 | 2846.5 | 711 | 1400.5 | 0 | 3243 | 490 | 12 | 0 | 213.5 | 114 | 187.5 | 0
12:00 | 2844 | 711 | 1458 | 0 | 3301 | 510 | 12 | 0 | 283 | 114 | 189 | 0
12:30 | 2863 | 708.5 | 1448 | 18.5 | 3359.5 | 525 | 12 | 0 | 294 | 114 | 179 | 0
13:00 | 2882 | 706 | 1438 | 37 | 3418 | 540 | 12 | 0 | 305 | 114 | 169 | 0
13:30 | 2882 | 706 | 1438 | 37 | 3418 | 540 | 12 | 0 | 305 | 114 | 169 | 0
14:00 | 2882 | 706 | 1438 | 37 | 3418 | 540 | 12 | 0 | 305 | 114 | 169 | 0
14:30 | 2889.5 | 707 | 1432 | 18.5 | 3228 | 525 | 29 | 0 | 280.5 | 105 | 138.5 | 0
15:00 | 2897 | 708 | 1426 | 0 | 3038 | 510 | 46 | 0 | 256 | 96 | 108 | 0
15:30 | 2894 | 707.5 | 1417.5 | 0 | 2897 | 504.5 | 46 | 0 | 248.5 | 96 | 87.5 | 0
16:00 | 2891 | 707 | 1409 | 0 | 2756 | 499 | 46 | 0 | 241 | 96 | 67 | 0
16:30 | 2882 | 706.5 | 1414.5 | 0 | 2719.5 | 504.5 | 46 | 0 | 247.5 | 95 | 42.5 | 0
17:00 | 2882 | 706 | 1420 | 0 | 2683 | 510 | 46 | 0 | 254 | 94 | 18 | 0
17:30 | 2902 | 706 | 1415 | 43.5 | 2774 | 505 | 46 | 0 | 321.5 | 102 | 9 | 0
18:00 | 2922 | 706 | 1410 | 87 | 2865 | 500 | 46 | 0 | 389 | 110 | 0 | 0
18:30 | 2877 | 706.5 | 1443 | 214.5 | 3155.5 | 510 | 46 | 0 | 425.5 | 109 | 0 | 0
19:00 | 2832 | 707 | 1476 | 342 | 3446 | 520 | 46 | 0 | 462 | 108 | 0 | 0
19:30 | 2890 | 706 | 1442 | 212 | 3504 | 520 | 46 | 0 | 453 | 104 | 0 | 0
20:00 | 2890 | 707 | 1455 | 115 | 3494 | 530 | 46 | 0 | 458 | 104 | 0 | 0
20:30 | 2904.5 | 708.5 | 1466.5 | 57.5 | 3504.5 | 550 | 46 | 0 | 450.5 | 100 | 0 | 0
21:00 | 2919 | 710 | 1478 | 0 | 3515 | 570 | 46 | 0 | 443 | 96 | 0 | 0
21:30 | 2936 | 710.5 | 1477.5 | 0 | 3401.5 | 595 | 46 | 0 | 295.5 | 98 | 0 | 0
22:00 | 2953 | 711 | 1477 | 0 | 3288 | 620 | 46 | 0 | 148 | 100 | 0 | 0
22:30 | 2942.5 | 711 | 1475 | 0 | 2973.5 | 600 | 46 | 0 | 124 | 101 | 0 | 0
23:00 | 2932 | 711 | 1473 | 0 | 2659 | 580 | 46 | 0 | 100 | 102 | 0 | 0
23:30 | 2898 | 711 | 1474.5 | 0 | 2512.5 | 560 | 46 | 0 | 50 | 102 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 32° C
24:00 | 2864 | 711 | 1476 | 0 | 2366 | 540 | 46 | 0 | 0 | 102 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 207.516 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 207.516 MKWHr
Note on W13: Author:

## Generation
g | 2022-02-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 30 | 12 | 12 | 12 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 978900
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 3 | 9 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 17 |  |  | 233040
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 9 | 14 | 19 | 20 | 20 | 20 | 18 | 14 | 9 | 3 | [9 empty] | 150525
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 17 | 17 |  |  |  |  | 92693
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 34 | 34 | 34 | 34 | 37 | 70 | 93 | 105 | 105 | 105 | 105 | 105 | 68 | 68 | 51 | 51 | 54 |  | 105 | 105 | 105 | 105 | 68 | 68 | 34 | 1901054
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [10 empty] | 26 | 39 | 48 | 50 | 48 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 |  |  |  | 474744
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 89 | 238 | 278 | 280 | 280 | 280 | 280 | 210 | 210 | 210 | 210 | 210 |  | 254 | 278 | 280 | 280 | 280 | 195 | 145 | 4368325
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8108545
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 26 | 29 | 29 | 29 | 29 | 29 | 655848
33 | Ashuganj 225 MW CCPP | 225 | 214 | 213 | 221 | 219 | 187 | 191 | 189 | 181 | 209 | 214 | 202 | 206 | 219 | 220 | 216 | 211 | 186 |  | 186 | 209 | 202 | 211 | 217 | 213 | 218 | 5017000
34 | Ashuganj 450 MW CCPP(South) | 270 | 305 | 270 | 275 | 270 | 305 | 295 | 310 | 275 | 275 | 275 | 275 | 275 | 275 | 270 | 270 | 270 | 305 |  | 275 | 270 | 270 | 270 | 270 | 300 | 270 | 6939000
| Ashuganj 450 MW CCPP(North) | 260 | 295 | 260 | 270 | 260 | 295 | 280 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 280 | 280 | 280 | 320 |  | 290 | 280 | 280 | 280 | 280 | 305 | 270 | 7042000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142080
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5178950
41 | Haripur 360MW CCPP(HPL) | 332 | 332 | 332 | 332 | 306 | 332 | 332 | 255 | 302 | 302 | 281 | 342 | 336 | 333 | 329 | 327 | 329 | 338 |  | 333 | 334 | 335 | 337 | 338 | 342 | 342 | 7778000
42 | RPCL 210MW CCPP | 101 | 105 | 108 | 108 | 108 | 108 | 104 | 92 | 79 | 69 | 69 | 69 | 69 | 69 | 65 | 67 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 70 | 89 | 1920960
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 14 | 27 | 39 | 46 | 46 | 25 | 38 | 13 | 18 | 2 | 0 | [8 empty] | 267300
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 717000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 516456
46 | Shajibazar 330 MW CCPP | 250 | 250 | 249 | 251 | 250 | 251 | 250 | 254 | 252 | 248 | 250 | 249 | 250 | 253 | 250 | 252 | 250 | 250 |  | 249 | 255 | 251 | 250 | 250 | 240 | 241 | 5703000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 68 | 70 | 55 | 40 | 68 | 68 | 40 | 64 | 25 | 20 | 31 | 32 | 20 | 20 | 20 | 20 | 32 |  | 37 | 66 | 65 | 67 | 68 | 67 | 60 | 1067040
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 2016960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 177 | 177 | 176 | 188 | 188 | 188 | 189 | 176 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 |  | 177 | 176 | 177 | 176 | 176 | 169 | 169 | 4284550
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251460
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 168576
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 47 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1155000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 380592
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 310 | 300 | 310 | 320 | 310 | 290 | 300 | 270 | 280 | 310 | 300 | 270 | 300 | 280 | 290 | 280 |  | 310 | 285 | 290 | 300 | 290 | 280 | 280 | 7228500
| Bibiyana South 400 MW | 350 | 310 | 310 | 310 | 260 | 190 | 180 | 210 | 220 | 310 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 350 | 350 | 8088300
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 10 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 950650
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531600
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 42072
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488808
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507204
63 | Impoprt (Tripura) | 92 | 88 | 86 | 84 | 84 | 84 | 82 | 80 | 96 | 102 | 114 | 114 | 114 | 108 | 96 | 96 | 94 | 110 |  | 108 | 104 | 104 | 96 | 100 | 102 | 102 | 2410560
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 8 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 5 |  | 21 | 17 | 21 | 28 | 37 | 37 | 41 | 482400
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 13 | 13 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440028
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 179640
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 23 | 23 | 23 | 16 | 17 | 25 | 33 | 33 | 33 | 33 |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 658300
68 | Cumilla 25 MW PP (Summit) | 12 | 17 | 17 | 17 | 17 | 17 | 13 | 13 | 13 | 13 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 438440
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 0 | 0 | 27 | 28 | 28 | 30 | 0 | 0 | 0 | 21 | 20 | 20 | 20 | 20 | 20 | 0 |  | 0 | 16 | 24 | 28 | 28 | 30 | 30 | 448740
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 0 | 0 | 0 | 10 | 33 | 33 | 33 | 685500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power |  |  |  |  | 0 | 17 | 34 | 34 | 52 | 70 | 70 | 105 | 105 | 60 | 50 | 50 | 50 | 40 |  | 108 | 108 | 108 | 108 | 108 | 34 | 17 | 1252860
| Chowmuhani 113 MW | 8 | 8 | 8 | 8 | 8 | 8 | [8 empty] | 6 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 146160
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3954240
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 13 | 13 | 32 | 16 | 18 | 38 | 47 | 51 | 25 | 25 | 25 |  | 50 | 51 | 51 | 51 |  |  |  | 518400
79 | Kodda 150MW PP | [7 empty] | 32 | 62 | 62 | 70 | 150 | 150 | 82 | 82 | 64 | 64 | 82 |  | 150 | 150 | 150 | 150 | 48 |  |  | 1413600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 43 | 43 | 45 | 45 | 52 | 43 | 43 | 43 | 47 |  | 52 | 52 | 52 | 52 | 52 | 48 | 49 | 1193347
| Gazipur 100 MW PP | 105 | 70 | 70 | 50 | 50 | 50 | 82 | 90 | 86 | 72 | 90 | 90 | 90 | 90 | 86 | 72 | 70 | 85 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1906800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 33121
| Jodiac Power | [7 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 22 | 17 | 17 | 17 |  |  |  | 300618
| Karnaphuli Power Ltd. | 110 | 0 |  |  | 0 | 7 | 37 | 68 | 90 | 105 | 110 | 110 | 110 | 34 | 34 | 34 | 34 | 34 |  | 59 | 51 | 51 | 51 | 34 | 34 | 17 | 1364103
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [9 empty] | 11 | 11 | 11 | 12 | 12 | 11 | 11 | 11 | 22 |  | 22 | 23 | 22 | 22 | 22 |  |  | 218432
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 75 | 74 | 82 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2505600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 24 |  | 30 | [6 empty] | 139800
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1083688
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 16 | 40 | 70 | 93 | 93 | 93 | 93 | 93 | 93 | 74 | 74 | 84 |  | 93 | 93 | 93 | 93 | 93 | 32 | 7 | 1309968
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 19 |  |  | 10 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 539520
96 | Chattogram 108 MW PP (ECPV) | 95 | 96 | 96 | 96 | 96 | 91 | 77 | 77 | 71 | 77 | 77 | 77 | 77 | 77 | 76 | 76 | 84 | 88 |  | 91 | 95 | 95 | 97 | 102 | 102 | 102 | 2099520
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 2 | 15 | 45 | 40 | 40 | 40 | 40 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 30 |  |  | 679622
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 971599
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2914936
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | [9 empty] | 9550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1149480
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 37 |  |  |  |  | 37 |  | 122 | 72 | 20 |  |  |  |  | 177392
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 25 |  | 100 | 70 | 70 |  |  |  |  | 183999
106 | Mymensingh 200 MW PP (United) | 100 | 60 | 60 | 40 | 40 | 72 | 130 | 183 | 174 | 174 | 162 | 170 | 170 | 171 | 170 | 170 | 171 | 171 |  | 180 | 180 | 180 | 171 | 190 | 170 | 172 | 3508800
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 25 |  | 100 | 70 | 25 |  |  |  |  | 138281
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 29 | 40 | 107 | 128 | 135 | 149 | 149 | 106 | 90 | 90 | 90 | 90 |  | 130 | 149 | 149 | 149 | 143 | 64 | 35 | 1900370
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 0 |  |  | 0 | 20 | 60 | 40 | 60 | 60 | 60 | 76 | 90 | 60 | 60 | 60 | 20 | 76 |  | 76 | 76 | 63 | 76 | 60 | 60 | 60 | 1177920
116 | Chandpur 200MW (Desh energy) |  |  |  |  | 0 | 19 | 51 | 64 | 112 | 136 | 136 | 145 | 164 | 170 | 155 | 155 | 136 | 136 |  | 184 | 200 | 200 | 200 | 200 | 200 | 155 | 2839200
117 | Ashuganj 150MW PP (Midland) | 100 | 0 |  |  | 0 | 2 | 20 | 90 | 107 | 103 | 102 | 102 | 97 | 97 | 100 | 95 | 92 | 92 |  | 97 | 97 | 97 | 102 | 105 | 110 | 145 | 1915272
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) |  |  |  |  | 0 | 10 | 37 | 83 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 80 | 80 | 90 |  | 115 | 115 | 115 | 115 | 115 | 45 | 24 | 1833600
| Anwara 300 MW PP (United) | 300 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6962727
| Juldah unit-2 (Acorn) | [7 empty] | 20 | 20 | 10 | 10 | 30 | 30 | 10 | 10 | 10 | 10 | 35 |  | 70 | 20 | 20 | 20 |  |  |  | 319680
| Anlima Energy Ltd. | 113 | 113 | 113 | 95 | 111 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 96 | 94 | 95 | 2638309
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 35 | 35 | 35 |  | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 514440
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 8 | 15 | 20 | 23 | 24 | 27 | 22 | 18 | 3 | 1 | [9 empty] | 153835
| Chandpur 115(Doreen) | [17 empty] | 2 |  | 30 | 35 | 35 | 35 |  |  |  | 122880
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 17 | 17 | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1236960
120 | Eastern Zone Total | 5284 | 4894 | 4801 | 4715 | 4630 | 4774 | 5239 | 5690 | 6037 | 6238 | 6357 | 6668 | 6764 | 6382 | 6342 | 6174 | 6100 | 6464 |  | 7149 | 6991 | 6892 | 6805 | 6474 | 5950 | 5709 | 144036596
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 4 |  | 5 | [6 empty] | 20640
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) |  |  |  |  | 0 | 17 | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 53 | 36 |  | 40 | 105 | 105 | 105 | 105 | 70 | 70 | 1741440
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 5 | 25 | 50 | 71 | 82 | 82 | 83 | 73 | 55 | 33 | 10 | [9 empty] | 571680
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 225 | 209 | 220 | 170 | 165 | 164 | 164 | 166 | 200 | 200 | 200 | 220 | 216 | 210 | 217 | 220 | 218 | 202 |  | 224 | 224 | 224 | 225 | 222 | 225 | 226 | 4998109
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 269568
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 91 | 91 | 91 | 92 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2216085
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 14 | 14 | 18 | 18 | 18 | 17 | 17 | 17 | 20 |  | 22 | 16 | 19 | 22 | 24 | 23 | 21 | 453600
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 710 | 710 | 711 | 664 | 663 | 711 | 710 | 710 | 711 | 710 | 711 | 711 | 706 | 706 | 708 | 707 | 706 | 706 |  | 707 | 706 | 707 | 710 | 711 | 711 | 711 | 17037818
147 | Bheramara 410 MW CCPP | 300 | 300 | 300 | 300 | 305 | 320 | 320 | 315 | 305 | 290 | 280 | 260 | 255 | 230 | 225 | 220 | 220 | 220 |  | 225 | 225 | 225 | 230 | 235 | 235 | 235 | 6597216
148 | Payra 1320 MW | 340 | 320 | 300 | 300 | 300 | 300 | 300 | 290 | 310 | 280 | 270 | 310 | 340 | 300 | 310 | 300 | 310 | 300 |  | 320 | 320 | 330 | 370 | 420 | 380 | 340 | 8568000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4851700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [11 empty] | 30 | 43 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 |  |  |  | 322266
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 2 | 4 | 1 | 0 | 0 | [9 empty] | 27900
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 182 | 182 | 178 | 173 | 169 | 169 | 163 | 157 | 164 | 169 | 169 | 163 | 190 | 193 | 193 | 192 | 189 | 187 |  | 182 | 181 | 181 | 182 | 181 | 173 | 151 | 4462136
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 10 | 32 | 37 | 40 |  |  |  | 86951
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 22 | 22 | 21 | 21 | 20 | 22 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 498240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 175752
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 25 | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 16 |  | 34 | 34 | 34 | 43 | 43 | 16 |  | 410679
167 | Katakhali 50 MW Peaking PP | [11 empty] | 16 | 16 | 16 | 16 | 16 | 24 | 34 |  | 40 | 40 | 40 | 40 |  |  |  | 221732
168 | Santahar 50 MW Peaking PP | [13 empty] | 27 | 28 | 29 | 30 | 29 |  | 30 | 30 | 30 | 29 |  |  |  | 214091
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1240320
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 44 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 100 |  | 92 | 100 | 100 | 100 | 100 | 100 | 0 | 960377
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 20 | [6 empty] | 24589
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 27 | 90 | 110 | 112 | 70 | 70 | 90 | 108 | 112 | 35 | 35 | 37 |  | 103 | 113 | 113 | 113 | 113 | 113 | 70 | 1664928
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 20 | 90 | 95 | 95 | 50 | 60 | 90 | 50 | 50 | 35 | 35 | 50 |  | 95 | 113 | 113 | 113 | 113 | 50 | 35 | 1318560
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 80 | 91 | 113 | 113 | 113 | 113 | 113 | 112 | 111 | 70 | 70 | 90 |  | 105 | 111 | 113 | 113 | 113 | 113 | 98 | 1809321
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 4 | 5 | 6 | 5 | 4 | 2 | 1 | [9 empty] | 37354
178 | Energypac Power Venture Thakurgaon Ltd. | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 118 | 118 |  | 118 | 118 | 118 | 119 | 105 | 60 | 55 | 2677889
178