## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-04 | Friday
|  |  | Date (day): | 2022-03-04 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11958.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12360 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-03 | 2022-03-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 340 | 340 | 340
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 23 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 213 | 219 | 200 | 200 | 135 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 49 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 278 | 280 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 300 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 37 | 43 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2302 | 2841 | 2826 | 2896 | 1401 | 979
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 24
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 39 | 42 | 42 |  | 8 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 |  | 184 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 89 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 20 | 70 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 24 | 35 | 35
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 70 | 85 | 100 | 100 |  | 8 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 280 | 290 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 102 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 55 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 94 | 115 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 964 | 1222 | 1316 | 1290 | 180 | 914
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 218 | 190 | 190 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 260 | 340 | 320 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 330 | 310 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 17 | 24 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 137 | 135 | 140 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 33 | 31 | 33 | 33 |  | 19 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 140 | 170 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 10 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 128 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 16 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 70 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 53 | 72 | 115 | 115 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1573 | 1682 | 1916 | 2020 | 645 | 219
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 67 | 84 | 140 | 125 | 77 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 186 | 197 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 109 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 454 | 428 | 550.6 | 484 | 77 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 140 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 159 | 160 | 160 | 170 |  | Gas shortage
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 53 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 84 | 86
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 24 | 16 | 16 |  | 9 | Engine problem
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 140 | 140 | 140 | 140 | 260 |  | Gas shortage
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1378 | 1443 | 1437 | 1439 | 734 | 209
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 712 | 713 | 733 | 733
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 12 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 230 | 215 | 300 | 300 | 110 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 83 | 100 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1136 | 1161 | 1338 | 1638 | 110 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 8 | 9 | 10 | 10 |  |  | Engine problem
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 92 | 91 | 90 | 91 | 103 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 440 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 225 | 225
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 632 | 771 | 1116 | 1217 | 187 | 0
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 34 | 34 |  | 18 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 41 |  | 30 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 43 | 50
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 40 | 0 | 40 |  | 10 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 163 | 180 | 180 | 60 |  | Gas shortage
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 28 | 22 | 22 |  | 28 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 34 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 48 | 99 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 100 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 537 | 787 | 936 | 978 | 660 | 500
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 82 | 85
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 111 | 116 | 120 | 0 |  |  | On test
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 510 | 509 | 523 | 398 | 74 | 125
|  | Total |  |  |  |  | 22066 | 20985 | 9486 | 10844 | 11958.6 | 12360 | 4068 | 3037
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9101.9762 | 10405 | 11474.4774 | 11859.6274
| A. |  | 2022-03-03 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 10844 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6983 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10844 | MW
| 3 | Day peak Generation : |  |  | 9486 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10405 | MW
| 4 | Evening peak Generation : |  |  | 10844 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 217.2745 | MKWHr | By Solar | 1.4838 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 100.095 | MKWHr |  | By Oil: | 78.4991 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.3227 | MKWHr |  | By Hydro: | 1.095 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4068 | MW | Dhaka | 3847 | 3847 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3037 | MW | Chittagong | 1173 | 1173 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 7105 | MW | Khulna | 1203 | 1203 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 761.8 | MMCFD |  |  | Rajshahi | 1078 | 1078 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 93109874.792 | ii) Oil : | Taka | 561043671.66 | Comilla | 858 | 858 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 79909781.89 | Total | Taka | 734063328.342 | Mymensingh | 921 | 921 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.8455 | MKWHr. | Sylhet | 364 | 364 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -174 | MW (E to W) at | 19:00 | hrs | Barisal | 258 | 258 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -258 | MW at | 8:00 | hrs | Rangpur | 703 | 703 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.2° C |  |  | Total | 10405 | 10405 |  | 0
| B. |  | 2022-03-04 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 31.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12360 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2360 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 200.3638 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6980 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.136 | MKWHr. | ii) HVDC Flow at Peak Time |  | 713 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6429 | MKWHr. | iii) Maximum HVDC Flow : |  | 716 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.17 |  | (b) Today: | 90.05 |  | (c) Rule Curve: |  | 92.52
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 7 | 0 | 22 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 97 | 19 | 20 | 41 | 0 | 0 | 0 | 310 | 305 | 168 | 8 | 0 | 26 | 5 | 0 | 24 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 96 | 90 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 148 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 95 | 0 | 0 | 190 | 0 | 126 | 0 | 90 | 0 | 147 | 140 | 8 | 90 | 105 | 0 | 294 | 0 | 68 | 17 | 0 | 20 | 360 | 91 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 713 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 166 | 0 | 0 | 70 | 0 | 113 | 0 | 48 | 0 | 0 | 70 | 360 | 210 | 0 | 0 | 0 | 0 | 0 |  | 5502 | 2419 | 7921 | 2947 | 713 | 1157 | 0 | 2317 | 645 | 46 | 0 | 0 | 96 | 0 | 0 | 90.19
2:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 7 | 0 | 22 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 92 | 25 | 20 | 41 | 0 | 0 | 0 | 310 | 305 | 176 | 8 | 0 | 26 | 5 | 0 | 24 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 90 | 100 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 147 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 260 | 16 | 8 | 0 | 45 | 0 | 0 | 200 | 0 | 113 | 0 | 90 | 0 | 135 | 139 | 8 | 40 | 68 | 0 | 290 | 0 | 68 | 17 | 0 | 20 | 330 | 91 | 0 | 162 | 90 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 0 | 35 | 0 | 70 | 0 | 9 | 0 | 0 | 35 | 360 | 217 | 0 | 0 | 0 | 0 | 0 |  | 5294 | 2281 | 7575 | 2937 | 716 | 1154 | 0 | 1987 | 645 | 46 | 0 | 0 | 90 | 0 | 0 | 90.19
3:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 7 | 0 | 22 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 90 | 25 | 20 | 41 | 0 | 0 | 0 | 310 | 305 | 186 | 8 | 0 | 26 | 5 | 0 | 24 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 86 | 100 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 147 | 40 | 40 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 15 | 0 | 0 | 160 | 0 | 90 | 0 | 90 | 0 | 135 | 140 | 8 | 17 | 68 | 0 | 298 | 0 | 68 | 17 | 0 | 20 | 220 | 40 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 47 |  | 716 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 165 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 300 | 220 | 0 | 0 | 0 | 0 | 0 |  | 4933 | 2226 | 7159 | 2848 | 716 | 1132 | 0 | 1746 | 585 | 46 | 0 | 0 | 86 | 0 | 0 | 90.18
4:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 90 | 25 | 20 | 41 | 0 | 0 | 0 | 310 | 305 | 187 | 8 | 0 | 26 | 5 | 0 | 24 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 84 | 110 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 148 | 40 | 40 | 0 | 0 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 160 | 0 | 90 | 0 | 90 | 0 | 133 | 140 | 8 | 17 | 68 | 0 | 283 | 0 | 68 | 17 | 0 | 20 | 200 | 35 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 55 |  | 669 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 86 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 165 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 300 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4904 | 2164 | 7068 | 2845 | 669 | 1129 | 0 | 1709 | 586 | 46 | 0 | 0 | 84 | 0 | 0 | 90.18
5:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 92 | 32 | 20 | 41 | 0 | 0 | 0 | 310 | 305 | 190 | 8 | 0 | 26 | 5 | 0 | 24 | 0 | 0 | 43 | 22 | 11 | 25 | 15 | 86 | 104 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 146 | 40 | 40 | 0 | 0 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 15 | 0 | 0 | 120 | 0 | 90 | 0 | 60 | 0 | 140 | 140 | 8 | 17 | 34 | 0 | 283 | 0 | 68 | 17 | 0 | 20 | 230 | 35 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 55 |  | 668 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 84 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 290 | 200 | 0 | 0 | 0 | 0 | 0 |  | 4833 | 2150 | 6983 | 2892 | 668 | 1105 | 0 | 1612 | 574 | 46 | 0 | 0 | 86 | 0 | 0 | 90.17
6:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 40 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 90 | 32 | 20 | 41 | 0 | 0 | 0 | 310 | 305 | 192 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 46 | 22 | 11 | 25 | 15 | 88 | 112 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 147 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 15 | 0 | 0 | 139 | 0 | 95 | 0 | 60 | 0 | 142 | 140 | 8 | 17 | 34 | 0 | 283 | 0 | 80 | 17 | 0 | 20 | 250 | 49 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 0 | 35 | 0 | 83 | 0 | 34 | 0 | 0 | 35 | 300 | 200 | 0 | 0 | 0 | 0 | 0 |  | 5083 | 2259 | 7342 | 2983 | 716 | 1191 | 0 | 1735 | 583 | 46 | 0 | 0 | 88 | 0 | 0 | 90.17
7:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 55 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 92 | 32 | 20 | 37 | 0 | 0 | 0 | 360 | 355 | 162 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 88 | 109 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 148 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 30 | 0 | 0 | 190 | 0 | 133 | 3 | 68 | 3 | 143 | 139 | 32 | 19 | 38 | 1 | 283 | 0 | 108 | 70 | 0 | 40 | 240 | 90 | 4 | 162 | 80 | 0 | 0 | 2 | 3 | 55 |  | 715 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 0 | 49 | 0 | 94 | 0 | 100 | 0 | 0 | 100 | 300 | 225 | 0 | 0 | 0 | 6 | 0 |  | 5482 | 2456 | 7938 | 3037 | 715 | 1227 | 0 | 2227 | 582 | 46 | 0 | 0 | 88 | 16 | 0 | 90.16
8:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 228 | 0 | 0 | 0 | 93 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 9 | 25 | 33 | 13 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 91 | 32 | 20 | 10 | 0 | 0 | 0 | 330 | 300 | 150 | 8 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 0 | 0 | 25 | 15 | 94 | 93 | 0 | 20 | 1 | 30 | 30 | 48 | 0 | 110 | 147 | 60 | 84 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 200 | 0 | 0 | 191 | 0 | 149 | 10 | 76 | 17 | 137 | 139 | 113 | 52 | 68 | 2 | 283 | 15 | 110 | 114 | 0 | 50 | 280 | 91 | 19 | 162 | 113 | 0 | 13 | 11 | 51 | 55 |  | 716 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 84 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 199 | 0 | 0 | 90 | 0 | 94 | 0 | 113 | 0 | 1 | 113 | 340 | 225 | 0 | 0 | 1 | 29 | 16 |  | 5970 | 2664 | 8634 | 2920 | 716 | 1171 | 0 | 2957 | 624 | 46 | 0 | 32 | 94 | 74 | 0 | 90.16
9:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 228 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 9 | 26 | 33 | 32 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 79 | 32 | 20 | 2 | 0 | 0 | 0 | 280 | 275 | 159 | 8 | 0 | 26 | 5 | 0 | 17 | 0 | 33 | 52 | 18 | 0 | 0 | 0 | 102 | 93 | 0 | 20 | 1 | 30 | 30 | 45 | 0 | 110 | 137 | 60 | 82 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 268 | 0 | 0 | 189 | 0 | 149 | 18 | 76 | 42 | 147 | 140 | 115 | 73 | 71 | 3 | 283 | 41 | 110 | 114 | 0 | 20 | 379 | 91 | 32 | 162 | 113 | 0 | 17 | 20 | 53 | 55 |  | 715 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 20 | 0 | 8 | 85 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 205 | 0 | 0 | 94 | 0 | 94 | 0 | 110 | 0 | 3 | 113 | 320 | 214 | 0 | 0 | 3 | 55 | 60 |  | 6317 | 2701 | 9018 | 2916 | 715 | 1116 | 0 | 3201 | 604 | 46 | 0 | 183 | 102 | 135 | 0 | 90.15
10:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 180 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 16 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 84 | 32 | 18 | 2 | 0 | 0 | 0 | 285 | 285 | 210 | 8 | 0 | 5 | 5 | 0 | 17 | 0 | 33 | 43 | 18 | 11 | 10 | 0 | 110 | 67 | 0 | 20 | 2 | 30 | 30 | 45 | 0 | 110 | 140 | 40 | 84 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 278 | 0 | 0 | 199 | 0 | 149 | 19 | 76 | 100 | 133 | 140 | 115 | 90 | 85 | 4 | 283 | 54 | 110 | 114 | 0 | 20 | 380 | 91 | 43 | 162 | 87 | 0 | 17 | 28 | 53 | 55 |  | 714 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 8 | 34 | 0 | 20 | 0 | 8 | 84 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 189 | 0 | 0 | 94 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 280 | 175 | 0 | 0 | 4 | 71 | 78 |  | 6421 | 2686 | 9107 | 2889 | 714 | 1074 | 0 | 3300 | 564 | 46 | 0 | 235 | 110 | 175 | 0 | 90.15
11:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 40 | 223 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 16 | 25 | 30 | 33 | 25 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 80 | 31 | 18 | 2 | 0 | 0 | 0 | 280 | 280 | 220 | 8 | 0 | 5 | 5 | 0 | 17 | 0 | 33 | 43 | 20 | 11 | 25 | 8 | 122 | 67 | 0 | 17 | 2 | 30 | 30 | 45 | 0 | 110 | 159 | 40 | 84 | 0 | 0 | 0 | 0 | 7 | 295 | 8 | 5 | 0 | 280 | 0 | 0 | 199 | 0 | 149 | 20 | 76 | 100 | 130 | 140 | 115 | 90 | 85 | 5 | 283 | 54 | 110 | 114 | 0 | 20 | 400 | 91 | 50 | 162 | 87 | 0 | 17 | 31 | 53 | 27 |  | 712 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 24 | 34 | 0 | 20 | 0 | 8 | 83 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 280 | 222 | 0 | 0 | 5 | 82 | 91 |  | 6514 | 2769 | 9283 | 2974 | 712 | 1133 | 0 | 3277 | 563 | 46 | 0 | 256 | 122 | 200 | 0 | 90.14
12:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 40 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 16 | 25 | 30 | 33 | 25 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 70 | 32 | 18 | 3 | 0 | 0 | 0 | 300 | 300 | 205 | 8 | 0 | 5 | 5 | 0 | 17 | 0 | 33 | 43 | 21 | 11 | 25 | 15 | 124 | 67 | 0 | 17 | 2 | 30 | 30 | 45 | 0 | 110 | 159 | 60 | 84 | 0 | 0 | 0 | 0 | 9 | 300 | 14 | 5 | 0 | 278 | 0 | 0 | 186 | 0 | 149 | 20 | 76 | 140 | 137 | 140 | 109 | 90 | 89 | 5 | 280 | 54 | 102 | 114 | 0 | 55 | 392 | 91 | 51 | 162 | 94 | 0 | 17 | 34 | 53 | 37 |  | 712 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 24 | 34 | 14 | 18 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 179 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 300 | 221 | 0 | 0 | 5 | 89 | 111 |  | 6671 | 2815 | 9486 | 3005 | 712 | 1139 | 0 | 3399 | 580 | 46 | 0 | 269 | 124 | 212 | 0 | 90.14
13:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 47 | 190 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 25 | 50 | 0 | 46 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 60 | 72 | 37 | 18 | 6 | 0 | 0 | 0 | 280 | 275 | 205 | 8 | 0 | 5 | 5 | 0 | 17 | 0 | 32 | 43 | 21 | 11 | 16 | 15 | 112 | 65 | 0 | 17 | 2 | 30 | 30 | 49 | 0 | 110 | 158 | 60 | 86 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 5 | 0 | 280 | 52 | 25 | 196 | 25 | 149 | 20 | 76 | 200 | 143 | 140 | 109 | 90 | 93 | 5 | 270 | 54 | 102 | 114 | 0 | 100 | 398 | 91 | 50 | 162 | 115 | 0 | 17 | 32 | 53 | 37 |  | 712 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 92 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 24 | 34 | 15 | 18 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 0 | 105 | 0 | 94 | 0 | 109 | 0 | 6 | 113 | 340 | 221 | 0 | 0 | 5 | 85 | 110 |  | 6906 | 2842 | 9748 | 2927 | 712 | 1148 | 102 | 3603 | 620 | 46 | 0 | 273 | 112 | 205 | 0 | 90.13
14:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 180 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 25 | 50 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 77 | 38 | 18 | 2 | 0 | 0 | 0 | 260 | 280 | 215 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 32 | 43 | 21 | 11 | 16 | 15 | 122 | 65 | 0 | 17 | 2 | 30 | 30 | 51 | 0 | 110 | 158 | 40 | 84 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 5 | 0 | 278 | 0 | 0 | 197 | 0 | 149 | 20 | 76 | 200 | 140 | 140 | 109 | 90 | 68 | 4 | 283 | 54 | 97 | 114 | 0 | 70 | 350 | 91 | 47 | 162 | 115 | 0 | 17 | 29 | 53 | 37 |  | 712 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 92 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 24 | 34 | 15 | 18 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 170 | 0 | 0 | 105 | 0 | 94 | 0 | 112 | 0 | 6 | 113 | 340 | 218 | 0 | 0 | 5 | 75 | 99 |  | 6660 | 2815 | 9475 | 2839 | 712 | 1138 | 0 | 3538 | 619 | 46 | 0 | 273 | 122 | 188 | 0 | 90.13
15:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 214 | 0 | 0 | 0 | 93 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 70 | 37 | 18 | 2 | 0 | 0 | 0 | 260 | 280 | 210 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 32 | 44 | 21 | 11 | 25 | 14 | 124 | 66 | 0 | 17 | 1 | 30 | 30 | 50 | 0 | 110 | 159 | 60 | 84 | 0 | 0 | 0 | 0 | 9 | 300 | 22 | 8 | 0 | 278 | 0 | 0 | 194 | 0 | 149 | 15 | 76 | 200 | 132 | 140 | 99 | 90 | 72 | 3 | 283 | 54 | 110 | 114 | 0 | 62 | 395 | 91 | 36 | 162 | 115 | 0 | 17 | 23 | 53 | 37 |  | 711 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 24 | 34 | 21 | 18 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 168 | 0 | 0 | 105 | 0 | 94 | 0 | 112 | 0 | 4 | 113 | 340 | 220 | 0 | 0 | 4 | 59 | 117 |  | 6674 | 2815 | 9489 | 2952 | 711 | 1149 | 0 | 3497 | 621 | 46 | 0 | 244 | 124 | 145 | 0 | 90.12
16:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 215 | 0 | 0 | 0 | 93 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 70 | 37 | 18 | 2 | 0 | 0 | 0 | 260 | 280 | 215 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 31 | 44 | 21 | 11 | 25 | 14 | 122 | 82 | 0 | 17 | 1 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 81 | 0 | 0 | 0 | 0 | 10 | 285 | 22 | 8 | 0 | 280 | 0 | 0 | 193 | 0 | 149 | 10 | 76 | 155 | 130 | 140 | 109 | 70 | 105 | 2 | 283 | 51 | 110 | 70 | 0 | 70 | 397 | 90 | 23 | 162 | 115 | 0 | 17 | 14 | 54 | 37 |  | 709 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 24 | 34 | 27 | 18 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 165 | 0 | 0 | 105 | 0 | 94 | 0 | 112 | 0 | 3 | 113 | 340 | 220 | 0 | 0 | 3 | 37 | 117 |  | 6494 | 2792 | 9286 | 2977 | 709 | 1129 | 0 | 3372 | 620 | 46 | 0 | 218 | 122 | 93 | 0 | 90.12
17:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 218 | 0 | 0 | 0 | 93 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 66 | 37 | 18 | 5 | 0 | 0 | 0 | 260 | 280 | 217 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 31 | 52 | 21 | 11 | 25 | 14 | 120 | 84 | 0 | 20 | 0 | 30 | 30 | 49 | 0 | 110 | 159 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 8 | 0 | 278 | 0 | 0 | 193 | 0 | 149 | 4 | 90 | 136 | 135 | 140 | 85 | 80 | 105 | 1 | 283 | 54 | 110 | 70 | 0 | 70 | 395 | 104 | 9 | 162 | 115 | 0 | 17 | 4 | 54 | 37 |  | 710 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 24 | 34 | 27 | 18 | 0 | 8 | 80 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 70 | 0 | 2 | 70 | 340 | 220 | 0 | 0 | 1 | 13 | 117 |  | 6505 | 2680 | 9185 | 2982 | 710 | 1143 | 0 | 3311 | 619 | 46 | 0 | 220 | 120 | 34 | 0 | 90.11
18:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 222 | 0 | 0 | 0 | 93 | 150 | 4 | 0 | 0 | 0 | 54 | 44 | 55 | 22 | 25 | 30 | 33 | 33 | 26 | 0 | 46 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 73 | 37 | 18 | 6 | 0 | 0 | 0 | 260 | 280 | 218 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 31 | 52 | 21 | 11 | 25 | 10 | 128 | 83 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 158 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 8 | 0 | 280 | 36 | 25 | 194 | 25 | 149 | 0 | 90 | 137 | 138 | 140 | 108 | 90 | 105 | 0 | 283 | 54 | 110 | 80 | 0 | 38 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 71 | 37 |  | 710 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 27 | 12 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 34 | 0 | 75 | 0 | 0 | 40 | 34 | 28 | 20 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 90 | 0 | 0 | 100 | 340 | 220 | 0 | 0 | 0 | 0 | 117 |  | 6774 | 2822 | 9596 | 2981 | 710 | 1141 | 86 | 3436 | 620 | 46 | 0 | 448 | 128 | 0 | 0 | 90.11
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 219 | 0 | 0 | 0 | 93 | 150 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 70 | 85 | 39 | 18 | 24 | 0 | 0 | 0 | 260 | 300 | 218 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 31 | 52 | 21 | 11 | 25 | 16 | 128 | 84 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 140 | 159 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 70 | 280 | 300 | 100 | 197 | 100 | 149 | 0 | 90 | 170 | 135 | 140 | 109 | 90 | 105 | 0 | 290 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 72 | 43 |  | 713 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 33 | 12 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 34 | 0 | 99 | 0 | 34 | 40 | 52 | 28 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 83 | 163 | 0 | 0 | 105 | 100 | 94 | 0 | 113 | 0 | 0 | 113 | 440 | 220 | 0 | 0 | 0 | 0 | 116 |  | 7616 | 3228 | 10844 | 3005 | 713 | 1212 | 753 | 3789 | 720 | 46 | 0 | 478 | 128 | 0 | 0 | 90.09
19:30 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 218 | 0 | 0 | 0 | 93 | 150 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 70 | 88 | 42 | 18 | 19 | 0 | 0 | 0 | 270 | 295 | 219 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 31 | 52 | 21 | 11 | 25 | 19 | 130 | 84 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 140 | 157 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 280 | 240 | 100 | 197 | 100 | 149 | 0 | 90 | 200 | 140 | 140 | 109 | 100 | 105 | 0 | 290 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 72 | 55 |  | 714 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 34 | 0 | 99 | 0 | 50 | 41 | 52 | 30 | 22 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 163 | 0 | 0 | 105 | 10 | 94 | 0 | 113 | 0 | 0 | 113 | 460 | 220 | 0 | 0 | 0 | 0 | 116 |  | 7528 | 3130 | 10658 | 3017 | 714 | 1177 | 500 | 3868 | 741 | 46 | 0 | 465 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 217 | 0 | 0 | 0 | 93 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 51 | 70 | 90 | 42 | 18 | 14 | 0 | 0 | 0 | 280 | 300 | 219 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 32 | 52 | 21 | 11 | 25 | 19 | 124 | 84 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 140 | 158 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 275 | 24 | 11 | 0 | 280 | 63 | 100 | 197 | 70 | 149 | 0 | 90 | 200 | 138 | 140 | 109 | 90 | 105 | 0 | 290 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 72 | 55 |  | 713 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 34 | 13 | 99 | 0 | 50 | 41 | 52 | 29 | 22 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 480 | 220 | 0 | 0 | 0 | 0 | 117 |  | 7337 | 3102 | 10439 | 3032 | 713 | 1175 | 233 | 3877 | 761 | 46 | 0 | 478 | 124 | 0 | 0 | 90.1
21:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 217 | 0 | 0 | 0 | 93 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 50 | 92 | 42 | 19 | 33 | 0 | 0 | 0 | 280 | 300 | 221 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 32 | 52 | 21 | 11 | 25 | 19 | 124 | 101 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 159 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 280 | 0 | 0 | 197 | 0 | 149 | 0 | 90 | 200 | 145 | 140 | 109 | 90 | 105 | 0 | 300 | 54 | 102 | 114 | 0 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 72 | 55 |  | 714 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 34 | 26 | 99 | 0 | 50 | 40 | 52 | 29 | 22 | 0 | 8 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 500 | 220 | 0 | 0 | 0 | 0 | 117 |  | 7121 | 3125 | 10246 | 3063 | 714 | 1176 | 0 | 3872 | 782 | 46 | 0 | 469 | 124 | 0 | 0 | 90.09
22:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 212 | 0 | 0 | 0 | 93 | 32 | 22 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 42 | 19 | 37 | 0 | 0 | 0 | 280 | 300 | 225 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 0 | 52 | 21 | 11 | 25 | 19 | 116 | 101 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 158 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 265 | 24 | 11 | 0 | 288 | 0 | 0 | 197 | 0 | 149 | 0 | 90 | 155 | 150 | 140 | 109 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 74 | 55 |  | 714 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 0 | 40 | 99 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 83 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 470 | 200 | 0 | 0 | 0 | 0 | 117 |  | 6712 | 2934 | 9646 | 3066 | 714 | 1140 | 0 | 3640 | 753 | 46 | 0 | 171 | 116 | 0 | 0 | 90.09
23:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 40 | 212 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 103 | 42 | 19 | 41 | 0 | 0 | 0 | 290 | 305 | 222 | 8 | 0 | 5 | 5 | 0 | 25 | 0 | 0 | 53 | 21 | 11 | 25 | 19 | 112 | 103 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 148 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 195 | 0 | 0 | 197 | 0 | 149 | 0 | 90 | 34 | 147 | 140 | 109 | 90 | 105 | 0 | 283 | 55 | 110 | 70 | 0 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 74 | 55 |  | 714 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 70 | 0 | 0 | 70 | 430 | 224 | 0 | 0 | 0 | 0 | 0 |  | 6339 | 2651 | 8990 | 3052 | 714 | 1173 | 0 | 3086 | 708 | 46 | 0 | 99 | 112 | 0 | 0 | 90.08
24:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 42 | 19 | 41 | 0 | 0 | 0 | 310 | 325 | 221 | 8 | 0 | 5 | 5 | 0 | 25 | 0 | 0 | 52 | 21 | 11 | 25 | 15 | 108 | 109 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 148 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 188 | 0 | 149 | 0 | 90 | 0 | 142 | 140 | 80 | 90 | 105 | 0 | 283 | 54 | 110 | 17 | 0 | 100 | 370 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 23 | 0 | 0 | 35 | 380 | 224 | 0 | 0 | 0 | 0 | 0 |  | 5928 | 2402 | 8330 | 3086 | 714 | 1203 | 0 | 2514 | 659 | 46 | 0 | 0 | 108 | 0 | 0 | 90.08
KWH | 0 | 0 | 0 | 0 | 8181855 | 0 | 0 | 0 | 0 |  | 0 | 7073750 | 0 | 0 | 0 | 848705 | 5059166 | 0 | 0 | 0 | 1652832 | 1841760 | 180963 | 0 | 0 | 0 | 1086840 | 673666 | 1198411 | 364428 | 600000 | 651960 | 763700 | 794500 | 619680 | 0 | 1095000 | 0 | 0 | 0 | 155449 | 0 | 0 | 0 | 0 |  | 498480 | 0 | 174985 | 373200 | 2054400 | 831360 | 448560 | 506880 | 0 | 0 | 0 | 7409100 | 7295000 | 4812000 | 217454 | 0 | 350568 | 143040 | 0 | 646404 | 0 | 398464 | 1198685 | 471492 | 220860 | 550900 | 350380 | 2642880 | 2061120 | 0 | 431064 | 16150 | 715000 | 696376 | 1203600 | 0 | 2935636 | 3551000 | 1239264 | 1896960 | 0 | 0 | 0 | 0 | 214740 | 7079000 | 445320 | 185328 | 58368 | 4932871 | 474981 | 225410 | 4430400 | 201005 | 3355776 | 152280 | 1951680 | 2360160 | 3357163 | 3355000 | 1936800 | 1747200 | 2101772 | 35039 | 6779564 | 889933 | 2422109 | 1964220 | 0 | 1375680 | 8307400 | 2132160 | 363710 | 3954240 | 2453891 | 0 | 436680 | 231177 | 1017600 | 1193040 |  | 17136000 | 0 | 5979744 | 0 | 0 | 0 | 0 | 0 | 116640 | 19584 | 0 | 2217350 | 177496 | 0 | 0 | 0 | 0 | 132677 | 58433 | 919000 | 0 | 143096 | 306574 | 663360 | 227336 | 485520 | 0 | 190386 | 1977163 | 0 | 4864800 | 0 | 0 | 0 | 0 | 0 | 0 | 280859 | 131520 | 4340382 | 0 | 0 | 2208000 | 130891 | 2246112 | 0 | 1959139 | 0 | 39800 | 2181024 | 9480700 | 5194445 | 0 | 0 | 40140 | 605520 | 1515165 |  | 151305624 | 65968856 | 217274480 | 72039203 | 17136000 | 28055784 | 1222175 | 73081506 | 16322663 | 1095000 | 0 | 4195453 | 2642880 | 1483816 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 9081859.05 | 0 | 0 | 0 | 0 |  | 0 | 7710387.5 | 0 | 0 | 0 | 7180044.3 | 5261532.64 | 0 | 0 | 0 | 15073827.84 | 18122918.4 | 1668478.86 | 0 | 0 | 0 | 7933932 | 5207438.18 | 11816332.46 | 273321 | 450000 | 0 | 0 | 0 | 5992305.6 | 0 | 295650 | 0 | 0 | 0 | 1444121.21 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1697354.5 | 3564060 | 17873280 | 6584371.2 | 565185.6 | 1505433.6 | 0 | 0 | 0 | 5482734 | 7295000 | 4427040 | 280515.66 | 0 | 396141.84 | 200256 | 0 | 1105350.84 | 0 | 4024486.4 | 11447441.75 | 598794.84 | 165645 | 964075 | 262785 | 19821600 | 2184787.2 | 0 | 547451.28 | 257431 | 1172600 | 1114201.6 | 2142408 | 0 | 3346625.04 | 3693040 | 2441350.08 | 3623193.6 | 0 | 0 | 0 | 0 | 438069.6 | 7149790 | 333990 | 140849.28 | 992839.68 | 37292504.76 | 8065177.38 | 3768855.2 | 23038080 | 3360803.6 | 33020835.84 | 1780153.2 | 15906192 | 25607736 | 23667999.15 | 3120150 | 17663616 | 16511040 | 18306434.12 | 0 | 51253503.84 | 7751316.43 | 21290338.11 | 19602915.6 | 0 | 9162028.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98703360 | 0 | 6278731.2 | 0 | 0 | 0 | 0 | 0 | 1223553.6 | 205240.32 | 0 | 2505605.5 | 275118.8 | 0 | 0 | 0 | 0 | 1305541.68 | 593679.28 | 8133150 | 0 | 1934657.92 | 2970702.06 | 6427958.4 | 2205159.2 | 932198.4 | 0 | 144122.202 | 11922292.89 | 0 | 26367216 | 0 | 0 | 0 | 0 | 0 | 0 | 421288.5 | 2237155.2 | 5078246.94 | 0 | 0 | 23051520 | 2226455.91 | 21315602.88 | 0 | 15202918.64 | 0 | 439790 | 16117767.36 | 41620273 | 0 | 0 | 0 | 0 | 0 | 0 |  | 555522006.66 | 299839305.882 | 855361312.542 | 63979239.252 | 98703360 | 29130635.54 | 20651286.97 | 499910599.25 | 79909781.89 | 295650 | 0 | 40481785.44 | 19821600 | 2477374.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 40 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 16 | 25 | 30 | 33 | 25 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 70 | 32 | 18 | 3 | 0 | 0 | 0 | 300 | 300 | 205 | 8 | 0 | 5 | 5 | 0 | 17 | 0 | 33 | 43 | 21 | 11 | 25 | 15 | 124 | 67 | 0 | 17 | 2 | 30 | 30 | 45 | 0 | 110 | 159 | 60 | 84 | 0 | 0 | 0 | 0 | 9 | 300 | 14 | 5 | 0 | 278 | 0 | 0 | 186 | 0 | 149 | 20 | 76 | 140 | 137 | 140 | 109 | 90 | 89 | 5 | 280 | 54 | 102 | 114 | 0 | 55 | 392 | 91 | 51 | 162 | 94 | 0 | 17 | 34 | 53 | 37 |  | 712 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 24 | 34 | 14 | 18 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 179 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 300 | 221 | 0 | 0 | 5 | 89 | 111 |  | 9486 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 219 | 0 | 0 | 0 | 93 | 150 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 51 | 70 | 85 | 39 | 18 | 24 | 0 | 0 | 0 | 260 | 300 | 218 | 8 | 0 | 5 | 5 | 0 | 24 | 0 | 31 | 52 | 21 | 11 | 25 | 16 | 128 | 84 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 140 | 159 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 70 | 280 | 300 | 100 | 197 | 100 | 149 | 0 | 90 | 170 | 135 | 140 | 109 | 90 | 105 | 0 | 290 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 72 | 43 |  | 713 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 33 | 12 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 34 | 0 | 99 | 0 | 34 | 40 | 52 | 28 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 83 | 163 | 0 | 0 | 105 | 100 | 94 | 0 | 113 | 0 | 0 | 113 | 440 | 220 | 0 | 0 | 0 | 0 | 116 |  | 10844 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 0 | 0 | 55 | 200 | 0 | 0 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 42 | 20 | 35 | 0 | 0 | 0 | 320 | 310 | 190 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 11 | 25 | 21 | 163 | 125 | 0 | 22 | 0 | 30 | 30 | 50 | 0 | 110 | 160 | 66 | 86 | 0 | 0 | 0 | 0 | 10 | 330 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 140 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 |  | 115 | 55 |  | 733 | 0 | 300 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 91 | 10 | 110 | 0 | 0 | 0 | 34 | 41 | 100 | 0 | 50 | 40 | 52 | 22 | 22 | 0 | 11 | 85 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 180 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 225 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 200 | 0 | 0 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 42 | 20 | 35 | 0 | 0 | 0 | 340 | 330 | 190 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 10 | 25 | 21 | 138 | 140 | 0 | 22 | 1.6 | 30 | 30 | 50 | 0 | 110 | 160 | 66 | 84 | 0 | 0 | 0 | 0 | 10 | 330 | 16 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 140 | 140 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 50 | 162 | 113 | 0 | 17 | 30 | 115 | 55 |  | 733 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 110 | 0 | 0 | 0 | 34 | 40 | 100 | 0 | 43 | 0 | 52 | 22 | 22 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 180 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 225 |  | 50 | 6 | 50 | 120
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 5 | 150 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 24 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 78 | 0 | 16 | 39 | 0 | 0 | 0 | 345 | 320 | 223 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 25 | 15 | 76 | 165 | 0 | 20 | 1 | 30 | 30 | 53 | 0 | 110 | 160 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 5 | 0 | 110 | 0 | 0 | 162 | 0 | 107 | 9 | 90 | 0 | 102 | 140 | 60 | 52 | 0 | 2 | 283 | 54 | 92 | 17 | 0 | 30 | 250 | 91 | 15 | 162 | 68 | 0 | 17 | 10 | 0 | 55 | 0 | 719 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 0 | 105 | 0 | 94 | 0 | 50 | 0 | 1 | 70 | 250 | 165 | 0 | 0 | 1 | 28 | 0 | 0
199
| Minimum Generation |  | 6983 | 5:00
| Highest Generation |  | 10844 | 19:00
| Day Peak Generation |  | 9486 | 12:00
| Evening Peak Generation |  | 10844 | 19:00
| HVDC Max Flow |  | 716 | 2:00
| HVDC EvPeak Flow |  | 713 | 19:00
| Load factor L.F |  | 83.48%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-04
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9486 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6980 | MW
Evening Peak Generation : |  | 10844 | MW Hour : | 19:00 | Available Max Generation : |  | 12360 | MW
E.P. Demand (at gen end) : |  | 10844 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 10844 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2360 | MW
Total Gen. (MKWH) : |  | 217.2745 | System Load Factor : | 83.48% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -258 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-04
Actual : | 90.05 | Ft.(MSL) , | Rule curve : | 92.52 | Ft.( MSL )
Gas Consumed : | Total = | 761.8 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 93109874.792
: |  | Coal : | 79909781.89 | Oil : | 561043671.66 | Total : | 734063328.342
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3577.133 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1213.7348 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1086.9871 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 982.0145 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 887.5261 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 716.1953 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 403.9207 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 184.4926 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 552.3489 |  |  | 0 | 0%
Total | 0 |  | 9604.3531 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Meghnaghat Summit 305 MW CCPP
6) Raozan unit- 1,2
7) Sirajganj Unit 1,2
8) Siddhirganj 210 MW .
9) Siddhirganj GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) B.Baria-Narshingdi 132 kV Ckt-2 was under shut down from 08:42 to 17:58 for A/M.
b) Comilla(N) 132/33 kV T-3 & T-4 transformers tripped at 08:40 showing O/C relay & LT Bus coupler | [5 empty] | About 50 MW power interruption occurred under
Y-phase flashing and were switched on at 12:24 & 09:17 respectively. | [5 empty] | Camilla(N) S/S area from 08:40 to 12:24.
c) Shahjibazar 330 MW GT-1 was synchronized at 10:14 and
d) Mymensingh-Bhaluka 132 kV Ckt-1 was under shut down from 09:55 to 13:37 for C/M.
e) Bhaluka 132 kV Bus-A was under shut down from 10:04 to 13:01 for C/M.
f) Khulna(S)-Satkhira 132 kV Ckt-1 was switched on at 09:43.
g) Tongi 132/33 kV T-1 transformer was under shut down from 09:48 to 16:40 for C/M.
h) Shariatpur 132/33 kV T-1 transformer & 33 kV Bus-1 were under shut down from 08:25 to 13:06 for C/M.
i) Khulna(C) 132 kV Bus-1 was under shut down from 09:02 to 16:42 for C/M.
j) Sirajganj-Baghabari 132 kV Ckt-1 tripped at 12:18 due to trip Ckt fault at Sirajganj end and
was switched on at 13:10.
k) Jashore-Noapara 132 kV ckt-1 was switched on at 12:25.
l) Natore-Ishurdi 132 kV ckt-1 was under shut down from 13:23 to 13:39 for C/M.
m) Daudkandi 132/33 kV T-1 transformer was under shut down from 11:16 to 12:10 for C/M.
n) Daudkandi 132/33 kV T-2 transformer was under shut down from 12:14 to 13:26 for C/M.
o) Shahjibazar 330 MW GT-2 was shut down at 10:14 due to gas shortage.
p) Sholoshahar 132/33 kV T-1 transformer was charged at 15:35 for the first time.
q) Sholoshahar 132/33 kV T-2 transformer was charged at 15:53 for the first time.
R) Comilla(N)-Comilla(S) 132 kV Ckt-1 was switched on at 17:04 for the first time.
s) Comilla(N)-Comilla(S) 132 kV Ckt-2 was switched on at 17:15 for the first time.
t) Sirajganj 132/33 kV T-4 transformer was switched on at 16:40.
u) Jashore 132 kV Bus coupler CB was switched on at 15:59.
v) Ullon-Dhanmondi 132 kV Ckt-3 was switched on at 16:17.
w) Ullon-Dhanmondi 132 kV Ckt-1 was under shut down from 17:15 for R/H maintenance at 919 isolator
at Ullon end and was switched on at 21:27.
x) Rajshahi(O) 132 kV Bus & 132/33 kV transformers were under shut down from 06:40(04/3/2022) to | [5 empty] | About 60 MW power interruption occurred under
11:46 for C/M. | [5 empty] | Rajshahi(O) S/S area from 06:40(04/3/2022 to 11:46.
y) Khulshi 132 kV Bus & 132/33 kV transformer were shut down at 06:44(04/3/2022) for A/M. | [5 empty] | About 60 MW power interruption occurred under
Khulshi S/S area from 06:40(04/3/2022 to till now.
z) Chapainawabganj 132 kV Bus & 132/33 kV transformer were under shut down from 06:44(04/3/2022) to | [5 empty] | About 35 MW power interruption occurred under
12:30 for D/W. | [5 empty] | Chapainawabganj S/S area since 06:40(04/3/2022 to 12:30.
aa) Uttara 3rd phase 132/33 kv T-2 transformer tripped at 05:03(04/3/2022) showing E/F relay and was
switched on at 07:39.
ab) Sylhet 132 kV Bus section-3 & 4 were shut down at 07:58(04/3/2022) for C/M.
ac) Jhenaidah(N) 230 kV Bus 1 & 2 were shut down at 07:42(04/3/2022) for protection test.
ad) Sylhet-Chattak 132 kV Ckt-2 was shut down at 07:29(04/3/2022) for C/M.
ae) Sylhet-Sylhet CCPP 132 kV Ckt was shut down at 06:40(04/3/2022) for C/M.
af) Sylhet 132/33 kV T-4 transformer was shut down at 07:47(04/3/2022) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 8181855
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7073750 | GT-2 S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 848705
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 23 | 180963 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 364428
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 219 | 5059166 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1652832 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 1086840 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1841760
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 673666
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1198411
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1251960 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 763700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 794500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 619680 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 4932871 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 474981
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 225410
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 201005
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3355776
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1747200 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2132160
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3954240
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 231177
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 43 | 1193040
| Dhaka area Total |  |  |  | 5696 | 2841 | 50040076
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 155449
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 152280
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 831360 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1095000 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2101772
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 174985 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 70 | 373200
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1951680 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 448560
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 506880
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 2054400 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35039
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 290 | 6779564 | Engine problem
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 889933
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2422109
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1375680
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 115 | 2453891
| Chattogram area Total |  |  |  | 2382 | 1222 | 23801782
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 4812000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7409100 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7295000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 350568 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 143040 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 24 | 646404 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 3357163 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 398464 | Engine problem
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 170 | 2360160 | Engine problem
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 471492
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 220860
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2642880
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 550900 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1198685
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 16 | 350380 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 70 | 58368 | Low demand
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1964220
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 436680 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 72 | 1017600 | Engine problem
| Cumilla Area Total |  |  |  | 2899 | 1682 | 35901418
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 84 | 2061120 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 431064
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 16150
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 197 | 4430400 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 109 | 1936800 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 363710
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 498480
| Mymensingh Area Total |  |  |  | 622 | 428 | 9737724
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 696376 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 2935636 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 159 | 3551000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1203600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 185328
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1239264
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1896960
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 445320 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7079000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 140 | 3355000 | Gas shortage, ST under Maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 214740
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8307400
| Sylhet Area Total |  |  |  | 2377 | 1443 | 31824624
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 713 | 17136000
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 116640
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 12 | 19584 | High voltage
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 215 | 5979744 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 83 | 131520
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2208000
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 605520
| Khulna Area Total |  |  |  | 2229 | 1161 | 26197008
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 9 | 177496 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2217350 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 280859 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 440 | 9480700 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5194445
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 771 | 17350850
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 132677 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 58433 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 143096 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 306574 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 163 | 4340382 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 227336 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 485520
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 190386 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 663360
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 919000
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 100 | 130891 | Low demand
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2246112 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2181024
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 40140
| Rajshahi Area Total |  |  |  | 2129 | 787 | 12064931
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1977163
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4864800 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1959139
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39800
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 116 | 1515165 | On test
| Rangpur Area Total |  |  |  | 605 | 509 | 10356067
| Total |  |  |  | 20985 | 10844 | 217274480
| Eastern Grid Total |  |  |  | 13976 | 7616 | 151305624
| Western Grid Total |  |  |  | 7009 | 3228 | 65968856
| National Grid Total |  |  |  | 20985 | 10844 | 217274480
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-03
(a) ENTIRE EASTERN GRID : |  | 7163 | MW | (b) ENTIRE WESTERN GRID : |  | 3242 | MW
i) Dhaka area |  | 3847 | MW | i) Khulna area |  | 1203 | MW
ii) Chittagong area |  | 1173 | MW | ii) Rajshahi area |  | 1078 | MW
iii) Comilla area |  | 858 | MW | iii) Barisal area |  | 258 | MW
iv) Mymensingh area |  | 921 | MW | iv) Rangpur area |  | 703 | MW
v) Sylhet area |  | 364 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10405 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 107 | 12:00 | Valuka | 108 | 9:00 | Central S/S | 66 | 19:00
Munsiganj | 70 | 21:00 | Tangail | 179 | 19:00 | Noapara | 38 | 19:00
Sonargaon | 67 | 12:00 | Mymensing | 197 | 12:00 | Jessore | 97 | 19:00
Bhulta | 192 | 16:00 | Kishoreganj | 110 | 19:30 | Benapol | 42 | 18:30
Madanganj | 39 | 18:30 | Netrokona | 122 | 18:30 | Jhenida(Old) | 90 | 19:00
Rahim steel | 16 | 18:00 | Jamalpur | 133 | 8:00 | Bottail | 100 | 19:00
Ghorasal | 68 | 19:00 | Sherpur | 124 | 8:00 | G.K Project | 41 | 18:30
Narsingdi | 141 | 20:00 | Srimongal | 35 | 19:00 | Faridpur | 96 | 19:00
Haripur(SBU) | 117 | 19:30 | Shahjibazar | 81 | 21:00 | Rajbari | 46 | 19:00
Sreenagar | 29 | 20:00 | Fenchuganj | 30 | 18:00 | Madaripur | 70 | 21:00
Shyampur | 176 | 18:00 | Kulawara | 28 | 18:30 | Sariatpur | 44 | 19:30
Shitalakhya | 97 | 12:00 | Sylhet | 108 | 19:00 | Gopalganj | 72 | 19:00
Matuail | 60 | 10:00 | Chatak | 15 | 18:00 | Bagerhat | 80 | 18:30
Char Saidpur | 37 | 18:30 | Sunamganj | 34 | 19:00 | Mongla | 38 | 20:00
Ullon | 26 | 14:00 | Biani Bazar | 38 | 18:30 | Satkhira | 85 | 19:00
Hasnabad | 63 | 13:00 | Comilla (S) | 131 | 18:30 | Gallamari | 43 | 19:00
Magbazar | 90 | 15:00 | Comilla(N) | 93 | 19:00 | Magura | 42 | 19:00
Maniknagar | 60 | 13:00 | Chandpur | 32 | 21:00 | Norail | 35 | 19:00
Bangabhaban | 2 | 1:00 | Feni | 90 | 18:30 | Chuadanga | 69 | 19:00
Motijheel | 32 | 11:00 | Chowmuhani | 150 | 18:30 | Barisal(N) | 40 | 18:30
Narinda | 44 | 13:00 | Ashuganj | 31 | 19:00 | Barisal (S) | 71 | 21:00
Kazla | 74 | 13:00 | Daudkandi | 90 | 14:00 | Patuakhali | 63 | 19:00
Dhanmondi | 146 | 13:00 | B.Baria | 110 | 20:00 | Bhandaria | 38 | 19:30
Lalbag | 79 | 13:00 | Ramganj | 52 | 18:30 | Borguna | 12 | 19:00
Madartek | 58 | 22:00 | Chaddagram | 33 | 19:00 | Borhan Uddin | 42 | 19:30
Dhaka University | 26 | 12:00 | PHP | 10 | 14:00 | Ishurdi | 55 | 19:00
Aftabnagar | 24 | 18:00 | Kochua | 44 | 18:30 | Ruppur Paromanobik | 4 | 15:00
Fatullah | 56 | 11:00 | Madunaghat | 37 | 18:00 | Natore | 106 | 19:00
Nawabganj | 33 | 20:00 | Hathazari | 69 | 19:00 | Bogra | 125 | 19:00
Keraniganj | 62 | 19:00 | Khulshi | 168 | 12:00 | Naogaon | 104 | 13:00
Banani | 32 | 15:00 | Halishahar | 70 | 14:00 | Rajshahi | 92 | 19:00
Mirpur | 98 | 18:30 | Baraulia | 93 | 11:00 | Rajshahi New | 34 | 19:00
Kalyanpur | 69 | 12:00 | Sikalbaha | 19 | 14:00 | C.Nawabganj | 57 | 10:00
Gulshan | 86 | 13:00 | Dohazari | 62 | #N/A | Amnura | 47 | 19:00
Uttara | 52 | 18:30 | Cox'sbazar | 104 | 18:30 | Pabna | 75 | 18:30
Uttara New | 25 | 14:00 | Chandraghona | 22 | 18:00 | Shahjadpur | 84 | 8:00
Kamrangirchar | 63 | 12:00 | Kaptai | 3 | 19:00 | Serajganj | 82 | 8:00
Savar | 146 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 84 | 9:00
Bhasantec | 114 | 14:00 | Bakulia | 100 | 19:00 | Joypurhat | 52 | 8:00
Agargaon | 63 | 13:00 | Julda | 22 | 11:00 | Sherpur(Bogura) | 54 | 19:00
Satmosjid | 76 | 19:30 | TK chemical | 21 | 18:00 | Mohastangor | 56 | 19:30
Old Tongi | 112 | 18:00 | Modern Steel | 0 | 1:00 | Bhangura | 28 | 7:00
Kabirpur | 247 | 15:00 | Shahmirpur | 41 | 18:30 | Rangpur | 105 | 18:30
Manikgonj | 69 | 20:00 | Khagrachhari | 26 | 19:00 | Lalmonirhat | 37 | 8:00
Joydevpur | 165 | 18:30 | Matarbari | 29 | 18:30 | Saidpur | 97 | 9:00
New Tongi | 73 | 15:00 | Baroiar Hat | 38 | 18:30 | Purbasadipur | 97 | 9:00
Kodda | 230 | 15:00 | Rangamati | 10 | 18:30 | Thakurgaon | 69 | 19:00
Dhamrai | 84 | 9:00 | Agrabad | 62 | 18:30 | Palashbari | 100 | 8:00
Rajendrapur | 92 | 19:00 | Rampur | 5 | 18:30 | Barapukuria | 52 | 12:00
Bashundara | 104 | 18:00 | Abul Khair 230 | 11 | 16:00 | Panchagar | 48 | 19:00
Purbachal | 13 | 15:00 | BSRM | 161 | 7:00 | Joldhaka | 52 | 19:00
Tongi Millgate | 38 | 12:00 | GPH Ispat | 101 | 19:30 | Kurigram | 55 | 18:30
Bashundhara Cement |  |  | Goalpara | 19 | 20:00 | Mithapukur | 26 | 18:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 413 | 2:00 | 404 | 19:30 | Kaliakoir | 397 | 0.20833 | 378 | 0.5
| Bheramara | 400 | 2:00 | 394 | 7:00 | Bhulta | 406 | 0.083333 | 388 | 0.5
| Ashuganj(N) | 407 | 5:00 | 389 | 16:00 | Gopalganj | 413 | 0.625 | 402 | 0.83333
| Payra | 420 | 1:00 | 413 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 235 | 10:00 | Hathazari | 241 | 3:00 | 233 | 9:00
| Ishurdi | 242 | 5:00 | 229 | 8:00 | Megnaghat | 239 | 6:00 | 229 | 14:00
| Ashuganj | 243 | 6:00 | 233 | 12:00 | Fenchuganj | 244 | 1:00 | 238 | 11:00
| Serajganj | 239 | 1:00 | 228 | 8:00 | Siddhirganj | 235 | 1:00 | 224 | 10:00
| Baghabari | 239 | 1:00 | 230 | 7:00 | Maniknagar | 233 | 1:00 | 222 | 12:00
| Barapukuria | 236 | 22:00 | 223 | 7:00 | Agargaon | 234 | 4:00 | 222 | 12:00
| Bogra | 237 | 1:00 | 222 | 8:00 | Barisal | 243 | 9:00 | 238 | 19:30
| Rajshahi | 240 | 21:00 | 225 | 8:00 | Bhola 225 MW | 246 | 4:00 | 243 | 19:00
| Khulna South | 245 | 5:00 | 228 | 12:00 | AKSML | 241 | 9:00 | 235 | 5:00
| Rampura | 232 | 4:00 | 223 | 16:00 | BSRM | 240 | 3:00 | 232 | 10:00
| Haripur | 231 | 1:00 | 222 | 12:00 | Bibiyana | 245 | 6:00 | 237 | 16:00
| Hasnabad | 233 | 3:00 | 220 | 16:00 | Bhulta | 235 | 2:00 | 224 | 12:00
| Shyampur | 232 | 1:00 | 221 | 12:00 | Ashuganj (S) | 239 | 5:00 | 230 | 12:00
| Aminbazar | 235 | 1:00 | 224 | 2:00 | Kaliakoir | 232 | 1:00 | 221 | 12:00
| Tongi | 232 | 21:00 | 220 | 15:00 | GPH | 241 | 20:00 | 234 | 10:00
| Comilla (N) | 236 | 6:00 | 230 | 11:00 | Jhenaidah | 241 | 5:00 | 226 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 1:00 | 126 | 12:00 | PHP | 138 | 9:00 | 134 | 1:00
| Munsiganj | 135 | 22:00 | 127 | 12:00 | Kachua | 140 | 9:00 | 134 | 1:00
| Sonargaon | 133 | 1:00 | 126 | 12:00 | Madanhat | 140 | 1:00 | 138 | 10:00
| Bhulta | 128 | 8:00 | 121 | 12:00 | Hathazari | 142 | 22:00 | 137 | 9:00
| Madanganj | 134 | 22:00 | 126 | 12:00 | Khulshi | 139 | 9:00 | 133 | 11:00
| Rahim steel | 132 | 1:00 | 126 | 12:00 | Halishahar | 140 | 22:00 | 134 | 14:00
| Ghorasal | 141 | 1:00 | 136 | 16:00 | Baraulia | 142 | 7:00 | 137 | 1:00
| Narsingdi | 136 | 5:00 | 126 | 11:00 | Sikalbaha | 140 | 6:00 | 137 | 10:00
| Haripur(SBU) | 133 | 1:00 | 126 | 12:00 | Dohazari | 137 | 7:00 | 130 | 14:00
| Sreenagar | 137 | 2:00 | 128 | 12:00 | Cox'sbazar | 130 | 8:00 | 122 | 18:30
| Shyampur | 133 | 20:00 | 125 | 12:00 | Chandraghona | 141 | 9:00 | 135 | 14:00
| Shitalakhya | 134 | 8:00 | 127 | 12:00 | Kaptai | 142 | 18:00 | 137 | 1:00
| Matuail | 133 | 1:00 | 126 | 12:00 | A. Khaer Stl. | 138 | 3:00 | 135 | 20:00
| Char Saidpur | 137 | 22:00 | 127 | 15:00 | Bakulia | 140 | 8:00 | 135 | 16:00
| Ullon | 132 | 1:00 | 124 | 12:00 | Julda | 140 | 13:00 | 135 | 16:00
| Hasnabad | 134 | 1:00 | 126 | 13:00 | TK Chemical | 140 | 7:00 | 136 | 11:00
| Magbazar | 133 | 4:00 | 124 | 12:00 | Modern Steel | 140 | 8:00 | 133 | 14:00
| Maniknagar | 137 | 6:00 | 129 | 12:00 | Shahmirpur | 140 | 8:00 | 134 | 14:00
| Bangabhaban | 137 | 6:00 | 129 | 12:00 | Khagrachhari | 141 | 21:00 | 135 | 15:00
| Motijheel | 137 | 6:00 | 129 | 12:00 | Matarbari | 132 | 4:00 | 125 | 18:30
| Narinda | 137 | 6:00 | 129 | 12:00 | Baroiar Hat | 138 | 8:00 | 135 | 1:00
| Kazla | 137 | 6:00 | 129 | 12:00 | Rangamati | 141 | 14:00 | 135 | 15:00
| Dhanmondi | 133 | 5:00 | 125 | 12:00 | Agrabad | 140 | 7:00 | 135 | 11:00
| Lalbag | 137 | 6:00 | 128 | 12:00 | Rampur | 139 | 20:00 | 135 | 16:00
| Madartek | 132 | 4:00 | 123 | 12:00 | Goalpara S/S | 139 | 4:00 | 131 | 12:00
| Dhaka University | 132 | 4:00 | 124 | 12:00 | Khulna Central S/S | 139 | 5:00 | 130 | 8:00
| Aftabnagar | 132 | 1:00 | 123 | 12:00 | Noapara | 138 | 3:00 | 129 | 12:00
| Fatullah | 133 | 6:00 | 125 | 12:00 | Jessore | 135 | 1:00 | 126 | 8:00
| Nawabganj | 137 | 5:00 | 128 | 12:00 | Benapol | 137 | 4:00 | 126 | 8:00
| Keraniganj | 136 | 1:00 | 128 | 16:00 | Jhenida(Old) | 137 | 2:00 | 129 | 8:00
| Banani | 132 | 1:00 | 120 | 19:30 | Bottail | 139 | 4:00 | 131 | 8:00
| Mirpur | 130 | 1:00 | 125 | 12:00 | G.K Project | 142 | 4:00 | 135 | 9:00
| Kalyanpur | 133 | 1:00 | 125 | 12:00 | Faridpur | 137 | 9:00 | 135 | 6:00
| Gulshan | 132 | 4:00 | 123 | 16:00 | Rajbari | 139 | 3:00 | 132 | 8:00
| Uttara | 138 | 1:00 | 132 | 12:00 | Madaripur | 142 | 4:00 | 138 | 18:00
| Uttara New | 138 | 6:00 | 132 | 12:00 | Shariyatpur S/S | 142 | 5:00 | 137 | 15:00
| Kamrangirchar | 136 | 1:00 | 128 | 12:00 | Gopalganj | 142 | 3:00 | 137 | 18:30
| Savar | 132 | 3:00 | 125 | 12:00 | Bagerhat | 137 | 2:00 | 129 | 13:00
| Bhasantec | 138 | 4:00 | 130 | 12:00 | Mongla | 136 | 1:00 | 130 | 12:00
| Agargaon | 139 | 4:00 | 131 | 12:00 | Satkhira | 135 | 4:00 | 126 | 8:00
| Satmosjid | 138 | 1:00 | 131 | 12:00 | Gallamari | 142 | 6:00 | 135 | 18:30
| Old Tongi | 139 | 21:00 | 132 | 15:00 | Magura | 140 | 2:00 | 128 | 8:00
| Kabirpur | 138 | 1:00 | 128 | 11:00 | Narail | 137 | 3:00 | 128 | 8:00
| Manikgonj | 135 | 1:00 | 126 | 12:00 | Chuadanga | 137 | 4:00 | 125 | 12:00
| Joydevpur | 141 | 1:00 | 134 | 16:00 | Barisal(N) | 141 | 3:00 | 138 | 18:30
| New Tongi | 140 | 4:00 | 131 | 16:00 | Barisal (S) | 142 | 4:00 | 137 | 18:30
| Kodda | 139 | 1:00 | 132 | 16:00 | Patuakhali(S) | 139 | 1:00 | 134 | 20:00
| Dhamrai | 140 | 1:00 | 132 | 12:00 | Bhandaria | 142 | 6:00 | 135 | 21:00
| Rajendrapur | 138 | 1:00 | 130 | 17:00 | Borguna | 142 | 6:00 | 137 | 19:30
| Bashundara | 139 | 1:00 | 131 | 16:00 | Jhenaidah(New) | 138 | 4:00 | 129 | 8:00
| Purbachal | 132 | 5:00 | 124 | 16:00 | Ishurdi | 140 | 4:00 | 133 | 8:00
| Tongi Millgate | 138 | 7:00 | 129 | 16:00 | Ruppur Paromanobik | 138 | 1:00 | 132 | 8:00
| Bashundhara Cement |  |  |  |  | Natore | 139 | 1:00 | 130 | 8:00
| Valuka | 128 | 1:00 | 117 | 8:00 | Bogra | 140 | 1:00 | 131 | 7:00
| Tangail | 134 | 1:00 | 125 | 17:00 | Noagaon | 134 | 20:00 | 119 | 8:00
| Mymensing | 131 | 1:00 | 119 | 18:30 | Rajshahi | 137 | 3:00 | 129 | 8:00
| Kishorganj | 133 | 4:00 | 124 | 19:00 | Rajshahi New | 137 | 5:00 | 128 | 7:00
| Netrokona | 130 | 1:00 | 115 | 18:30 | C.Nawabganj | 135 | 19:00 | 125 | 8:00
| Jamalpur | 139 | 22:00 | 130 | 8:00 | Amnura | 137 | 19:30 | 125 | 8:00
| Sherpur | 138 | 23:00 | 127 | 8:00 | Pabna | 139 | 1:00 | 131 | 8:00
| Srimongal | 140 | 1:00 | 136 | 12:00 | Shahjadpur | 143 | 1:00 | 133 | 8:00
| Shahjibazar | 137 | 6:00 | 133 | 12:00 | Serajganj | 138 | 1:00 | 128 | 8:00
| Fenchuganj | 141 | 6:00 | 135 | 11:00 | Niyamatpur | 133 | 1:00 | 118 | 8:00
| Khulawara | 139 | 1:00 | 135 | 12:00 | Joypurhat | 135 | 1:00 | 118 | 8:00
| Sylhet | 137 | 4:00 | 127 | 14:00 | Sherpur(Bogura) | 139 | 1:00 | 129 | 8:00
| Chatak | 136 | 4:00 | 125 | 10:00 | Mohastangor | 137 | 1:00 | 127 | 8:00
| Sunamganj | 136 | 5:00 | 124 | 10:00 | Bhangura | 140 | 1:00 | 130 | 8:00
| Biani Bazar | 138 | 5:00 | 128 | 10:00 | Rangpur | 137 | 2:00 | 118 | 8:00
| Comilla(s) | 130 | 1:00 | 126 | 18:30 | Lalmonirhat | 132 | 15:00 | 122 | 8:00
| Comilla(n) | 139 | 6:00 | 132 | 12:00 | Saidpur | 135 | 16:00 | 119 | 8:00
| Chandpur | 140 | 9:00 | 132 | 1:00 | Purbasadipur | 136 | 15:00 | 114 | 8:00
| Feni | 139 | 9:00 | 134 | 5:00 | Thakurgaon | 138 | 15:00 | 117 | 7:00
| Chowmuhani | 136 | 22:00 | 130 | 2:00 | Palashbari | 135 | 5:00 | 122 | 8:00
| Ashuganj | 140 | 1:00 | 136 | 12:00 | Barapukuria | 135 | 14:00 | 123 | 7:00
| Daudkandi | 139 | 12:00 | 128 | 16:00 | Panchagar | 138 | 14:00 | 112 | 8:00
| B.Baria | 136 | 1:00 | 131 | 12:00 | Joldhaka | 133 | 15:00 | 118 | 8:00
| Ramganj | 139 | 9:00 | 129 | 1:00 | Kurigram | 133 | 4:00 | 120 | 8:00
| Chaddagram | 140 | 21:00 | 135 | 11:00 | Mithapukur | 136 | 15:00 | 123 | 7:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 52 | 5928 | 2402 | 8330 |  |  |  | QF-LDC-11
0:30 | 77 | 5715 | 2410.5 | 8125.5 | Date: | 2022-03-03
1:00 | 102 | 5502 | 2419 | 7921
1:30 | 99 | 5398 | 2350 | 7748
2:00 | 96 | 5294 | 2281 | 7575
2:30 | 104 | 5113.5 | 2253.5 | 7367 | [5 empty] | Gen. at Eve. Peak | 10844 | 10844 MW (19:00 )
3:00 | 112 | 4933 | 2226 | 7159 | [6 empty] | 19:00
3:30 | 117 | 4918.5 | 2195 | 7113.5 | [5 empty] | Gen. at Day Peak | 9486 | 9486 MW (12:00 )
4:00 | 122 | 4904 | 2164 | 7068 | [6 empty] | 12:00
4:30 | 116 | 4868.5 | 2157 | 7025.5 | [5 empty] | Highest Generation | 10844
5:00 | 110 | 4833 | 2150 | 6983 | [6 empty] | 19:00
5:30 | 88 | 4958 | 2204.5 | 7162.5
6:00 | 66 | 5083 | 2259 | 7342
6:30 | 145 | 5282.5 | 2357.5 | 7640
7:00 | 224 | 5482 | 2456 | 7938
7:30 | 241 | 5726 | 2560 | 8286
8:00 | 258 | 5970 | 2664 | 8634
8:30 | 218 | 6143.5 | 2682.5 | 8826
9:00 | 178 | 6317 | 2701 | 9018
9:30 | 100 | 6369 | 2693.5 | 9062.5
10:00 | 22 | 6421 | 2686 | 9107
10:30 | 16 | 6467.5 | 2727.5 | 9195
11:00 | 10 | 6514 | 2769 | 9283
11:30 | 21 | 6592.5 | 2792 | 9384.5
12:00 | 32 | 6671 | 2815 | 9486
12:30 | 48 | 6788.5 | 2828.5 | 9617
13:00 | 64 | 6906 | 2842 | 9748
13:30 | 91 | 6783 | 2828.5 | 9611.5
14:00 | 118 | 6660 | 2815 | 9475
14:30 | 156 | 6667 | 2815 | 9482
15:00 | 194 | 6674 | 2815 | 9489
15:30 | 241 | 6584 | 2803.5 | 9387.5
16:00 | 288 | 6494 | 2792 | 9286
16:30 | 266 | 6499.5 | 2736 | 9235.5
17:00 | 244 | 6505 | 2680 | 9185
17:30 | 220 | 6639.5 | 2751 | 9390.5
18:00 | 196 | 6774 | 2822 | 9596
18:30 | 185 | 7195 | 3025 | 10220
19:00 | 174 | 7616 | 3228 | 10844
19:30 | 208 | 7528 | 3130 | 10658
20:00 | 182 | 7337 | 3102 | 10439 |  |  |  | Executive Engineer
20:30 | 144 | 7229 | 3113.5 | 10342.5 |  |  |  | Network Operation Division
21:00 | 106 | 7121 | 3125 | 10246
21:30 | 74 | 6916.5 | 3029.5 | 9946
22:00 | 42 | 6712 | 2934 | 9646 |  |  |  |  | Page 6 of 7
22:30 | 26 | 6525.5 | 2792.5 | 9318
23:00 | 10 | 6339 | 2651 | 8990
23:30 | 31 | 6133.5 | 2526.5 | 8660
24:00 | 52 | 5928 | 2402 | 8330
10844 MW (19:00 )
9486 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-03 |  | Energy |  | 217274480
[13 empty] | 2022-03-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3086 | 714 | 1203 | 0 | 2514 | 659 | 46 | 0 | 0 | 108 | 0 | 0
0:30 | 3016.5 | 713.5 | 1180 | 0 | 2415.5 | 652 | 46 | 0 | 0 | 102 | 0 | 0 | Date: | 2022-03-03
1:00 | 2947 | 713 | 1157 | 0 | 2317 | 645 | 46 | 0 | 0 | 96 | 0 | 0
1:30 | 2942 | 714.5 | 1155.5 | 0 | 2152 | 645 | 46 | 0 | 0 | 93 | 0 | 0 | [8 empty] | Total Energy | 217.2745 | Total Energy Gen 217.274 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 217.274 MKWHr
2:00 | 2937 | 716 | 1154 | 0 | 1987 | 645 | 46 | 0 | 0 | 90 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2892.5 | 716 | 1143 | 0 | 1866.5 | 615 | 46 | 0 | 0 | 88 | 0 | 0 | [8 empty] | Energy Requirement | 217.2745
3:00 | 2848 | 716 | 1132 | 0 | 1746 | 585 | 46 | 0 | 0 | 86 | 0 | 0
3:30 | 2846.5 | 692.5 | 1130.5 | 0 | 1727.5 | 585.5 | 46 | 0 | 0 | 85 | 0 | 0 | [6 empty] | Shortage
4:00 | 2845 | 669 | 1129 | 0 | 1709 | 586 | 46 | 0 | 0 | 84 | 0 | 0
4:30 | 2868.5 | 668.5 | 1117 | 0 | 1660.5 | 580 | 46 | 0 | 0 | 85 | 0 | 0
5:00 | 2892 | 668 | 1105 | 0 | 1612 | 574 | 46 | 0 | 0 | 86 | 0 | 0
5:30 | 2937.5 | 692 | 1148 | 0 | 1673.5 | 578.5 | 46 | 0 | 0 | 87 | 0 | 0
6:00 | 2983 | 716 | 1191 | 0 | 1735 | 583 | 46 | 0 | 0 | 88 | 0 | 0
6:30 | 3010 | 715.5 | 1209 | 0 | 1981 | 582.5 | 46 | 0 | 0 | 88 | 8 | 0 |  |  |  |  | Coal
7:00 | 3037 | 715 | 1227 | 0 | 2227 | 582 | 46 | 0 | 0 | 88 | 16 | 0
7:30 | 2978.5 | 715.5 | 1199 | 0 | 2592 | 603 | 46 | 0 | 16 | 91 | 45 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2920 | 716 | 1171 | 0 | 2957 | 624 | 46 | 0 | 32 | 94 | 74 | 0
8:30 | 2918 | 715.5 | 1143.5 | 0 | 3079 | 614 | 46 | 0 | 107.5 | 98 | 104.5 | 0
9:00 | 2916 | 715 | 1116 | 0 | 3201 | 604 | 46 | 0 | 183 | 102 | 135 | 0
9:30 | 2902.5 | 714.5 | 1095 | 0 | 3250.5 | 584 | 46 | 0 | 209 | 106 | 155 | 0
10:00 | 2889 | 714 | 1074 | 0 | 3300 | 564 | 46 | 0 | 235 | 110 | 175 | 0
10:30 | 2931.5 | 713 | 1103.5 | 0 | 3288.5 | 563.5 | 46 | 0 | 245.5 | 116 | 187.5 | 0
11:00 | 2974 | 712 | 1133 | 0 | 3277 | 563 | 46 | 0 | 256 | 122 | 200 | 0
11:30 | 2989.5 | 712 | 1136 | 0 | 3338 | 571.5 | 46 | 0 | 262.5 | 123 | 206 | 0
12:00 | 3005 | 712 | 1139 | 0 | 3399 | 580 | 46 | 0 | 269 | 124 | 212 | 0
12:30 | 2966 | 712 | 1143.5 | 51 | 3501 | 600 | 46 | 0 | 271 | 118 | 208.5 | 0
13:00 | 2927 | 712 | 1148 | 102 | 3603 | 620 | 46 | 0 | 273 | 112 | 205 | 0
13:30 | 2927 | 712 | 1148 | 102 | 3603 | 620 | 46 | 0 | 273 | 112 | 205 | 0
14:00 | 2927 | 712 | 1148 | 102 | 3603 | 620 | 46 | 0 | 273 | 112 | 205 | 0
14:30 | 2939.5 | 711.5 | 1148.5 | 51 | 3550 | 620.5 | 46 | 0 | 258.5 | 118 | 175 | 0
15:00 | 2952 | 711 | 1149 | 0 | 3497 | 621 | 46 | 0 | 244 | 124 | 145 | 0
15:30 | 2964.5 | 710 | 1139 | 0 | 3434.5 | 620.5 | 46 | 0 | 231 | 123 | 119 | 0
16:00 | 2977 | 709 | 1129 | 0 | 3372 | 620 | 46 | 0 | 218 | 122 | 93 | 0
16:30 | 2982 | 709.5 | 1136 | 0 | 3341.5 | 619.5 | 46 | 0 | 219 | 121 | 63.5 | 0
17:00 | 2982 | 710 | 1143 | 0 | 3311 | 619 | 46 | 0 | 220 | 120 | 34 | 0
17:30 | 2981.5 | 710 | 1142 | 43 | 3373.5 | 619.5 | 46 | 0 | 334 | 124 | 17 | 0
18:00 | 2981 | 710 | 1141 | 86 | 3436 | 620 | 46 | 0 | 448 | 128 | 0 | 0
18:30 | 2993 | 711.5 | 1176.5 | 419.5 | 3612.5 | 670 | 46 | 0 | 463 | 128 | 0 | 0
19:00 | 3005 | 713 | 1212 | 753 | 3789 | 720 | 46 | 0 | 478 | 128 | 0 | 0
19:30 | 3017 | 714 | 1177 | 500 | 3868 | 741 | 46 | 0 | 465 | 130 | 0 | 0
20:00 | 3032 | 713 | 1175 | 233 | 3877 | 761 | 46 | 0 | 478 | 124 | 0 | 0
20:30 | 3047.5 | 713.5 | 1175.5 | 116.5 | 3874.5 | 771.5 | 46 | 0 | 473.5 | 124 | 0 | 0
21:00 | 3063 | 714 | 1176 | 0 | 3872 | 782 | 46 | 0 | 469 | 124 | 0 | 0
21:30 | 3064.5 | 714 | 1158 | 0 | 3756 | 767.5 | 46 | 0 | 320 | 120 | 0 | 0
22:00 | 3066 | 714 | 1140 | 0 | 3640 | 753 | 46 | 0 | 171 | 116 | 0 | 0
22:30 | 3059 | 714 | 1156.5 | 0 | 3363 | 730.5 | 46 | 0 | 135 | 114 | 0 | 0
23:00 | 3052 | 714 | 1173 | 0 | 3086 | 708 | 46 | 0 | 99 | 112 | 0 | 0
23:30 | 3069 | 714 | 1188 | 0 | 2800 | 683.5 | 46 | 0 | 49.5 | 110 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.2° C
24:00 | 3086 | 714 | 1203 | 0 | 2514 | 659 | 46 | 0 | 0 | 108 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 217.274 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 217.274 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1095000
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 0 | 18 | 8 | 8 | 8 | 8 | 9 |  | 25 | 25 | 25 | 25 |  |  | 0 | 155449
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 10 | 18 | 19 | 20 | 20 | 20 | 20 | 15 | 10 | 4 | [9 empty] | 152280
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 51 |  |  |  | 174985
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 68 | 68 | 68 | 34 | 34 | 38 | 68 | 71 | 85 | 85 | 89 | 93 | 68 | 72 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2101772
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 70 | [6 empty] | 58368
14 | Titas 50 MW Peaking PP | [8 empty] | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 31 | 31 | 31 |  | 31 | 31 | 32 | 32 |  |  | 0 | 398464
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 200 | 200 | 200 | 200 | 200 | 235 | 228 | 228 | 228 | 180 | 223 | 213 | 190 | 180 | 214 | 215 | 218 | 222 |  | 219 | 218 | 217 | 217 | 212 | 212 | 209 | 5059166
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 45 | 15 | 15 | 15 | 15 | 30 | 200 | 268 | 278 | 280 | 278 | 280 | 278 | 278 | 280 | 278 | 280 |  | 280 | 280 | 280 | 280 | 288 | 195 | 45 | 4932871
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8181855
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 350568
33 | Ashuganj 225 MW CCPP | 168 | 176 | 186 | 187 | 190 | 192 | 162 | 150 | 159 | 210 | 220 | 205 | 205 | 215 | 210 | 215 | 217 | 218 |  | 218 | 219 | 219 | 221 | 225 | 222 | 221 | 4812000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 355 | 300 | 275 | 285 | 280 | 300 | 275 | 280 | 280 | 280 | 280 | 280 |  | 300 | 295 | 300 | 300 | 300 | 305 | 325 | 7295000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 360 | 330 | 280 | 285 | 280 | 300 | 280 | 260 | 260 | 260 | 260 | 260 |  | 260 | 270 | 280 | 280 | 280 | 290 | 310 | 7409100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143040
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7073750
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 90 | 100 | 100 | 110 | 104 | 112 | 109 | 93 | 93 | 67 | 67 | 67 | 65 | 65 | 66 | 82 | 84 | 83 |  | 84 | 84 | 84 | 101 | 101 | 103 | 109 | 2061120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 19 | 32 | 43 | 50 | 51 | 50 | 47 | 36 | 23 | 9 | 0 | [8 empty] | 363710
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 696376
46 | Shajibazar 330 MW CCPP | 148 | 147 | 147 | 148 | 146 | 147 | 148 | 147 | 137 | 140 | 159 | 159 | 158 | 158 | 159 | 160 | 159 | 158 |  | 159 | 157 | 158 | 159 | 158 | 148 | 148 | 3551000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 40 | 40 | 60 | 60 | 40 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 40 | 60 | 1239264
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 40 | 40 | 40 | 84 | 84 | 84 | 82 | 84 | 84 | 84 | 86 | 84 | 84 | 81 | 86 | 86 |  | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 1896960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 214740
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 185328
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 51 | 48 | 48 | 48 | 48 | 45 | 45 | 45 | 45 | 49 | 51 | 50 | 48 | 49 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1203600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 8 | 14 | 16 | 16 | 22 | 22 | 22 | 22 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 445320
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 260 | 280 | 300 | 280 | 295 | 310 | 290 | 295 | 290 | 295 | 300 | 300 | 290 | 300 | 285 | 290 | 280 |  | 300 | 270 | 275 | 285 | 265 | 270 | 300 | 7079000
| Bibiyana South 400 MW | 360 | 330 | 220 | 200 | 230 | 250 | 240 | 280 | 379 | 380 | 400 | 392 | 398 | 350 | 395 | 397 | 395 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 370 | 8307400
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 17 | 17 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1198411
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 19 | 18 | 18 | 18 | 18 | 19 | 19 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 498480
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 448560
61 | Narshingdi 22 MW PP (Doreen) |  |  |  |  | 22 | 22 | 22 | 22 | 19 | 16 | 16 | 16 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 364428
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 431064
63 | Impoprt (Tripura) | 96 | 90 | 86 | 84 | 86 | 88 | 88 | 94 | 102 | 110 | 122 | 124 | 112 | 122 | 124 | 122 | 120 | 128 |  | 128 | 130 | 124 | 124 | 116 | 112 | 108 | 2642880
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 41 | 41 | 41 | 37 | 10 | 2 | 2 | 2 | 3 | 6 | 2 | 2 | 2 | 5 | 6 |  | 24 | 19 | 14 | 33 | 37 | 41 | 41 | 506880
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 18 | 18 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 471492
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220860
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 10 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 550900
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  | 8 | 15 | 15 | 15 | 14 | 14 | 14 | 10 |  | 16 | 19 | 19 | 19 | 19 | 19 | 15 | 350380
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 9 | 9 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 24 | 30 | 30 | 30 | 30 | 30 | 31 | 651960
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 763700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 794500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 70 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 70 | 70 | 80 |  | 114 | 114 | 114 | 114 | 114 | 70 | 17 | 1964220
| Chowmuhani 113 MW | [25 empty] | 0 | 0
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3954240
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 13 | 32 | 51 | 51 | 51 | 50 | 50 | 50 | 25 | 25 | 26 |  | 51 | 51 | 51 | 51 |  |  | 0 | 619680
79 | Kodda 150MW PP | [7 empty] | 32 | 150 | 150 | 150 | 150 | 150 | 150 | 115 | 82 | 82 | 150 |  | 150 | 150 | 150 | 150 | 32 |  | 0 | 1841760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 43 | 46 | 52 | 52 | 52 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 53 | 52 | 1198685
| Gazipur 100 MW PP | 90 | 40 | 17 | 17 | 17 | 17 | 19 | 52 | 73 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 80 | 90 |  | 90 | 100 | 90 | 90 | 90 | 90 | 90 | 1747200
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 35039
| Jodiac Power | [7 empty] | 15 | 41 | 54 | 54 | 54 | 54 | 54 | 54 | 51 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 55 | 54 | 889933
| Karnaphuli Power Ltd. | 68 | 68 | 68 | 68 | 68 | 80 | 108 | 110 | 110 | 110 | 110 | 102 | 102 | 97 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 102 | 110 | 110 | 110 | 2422109
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 22 | 22 | 22 | [14 empty] | 4 |  | 23 | 23 | 22 | 22 | 22 |  | 0 | 180963
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 91 | 91 | 40 | 35 | 35 | 49 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2132160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 20 | 60 | 50 | 10 | 10 | 10 | 10 |  | 70 | 70 | 70 | 50 |  |  | 0 | 373200
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 24 | 24 | 24 | 24 | 24 | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 646404
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 7 | 7 | 7 | 7 | 40 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 24 | 1652832
95 | Patenga 50MW PP (Baraka) | 19 | 25 | 25 | 25 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 37 | 38 | 37 | 37 | 37 | 37 |  | 39 | 42 | 42 | 42 | 42 | 42 | 42 | 831360
96 | Chattogram 108 MW PP (ECPV) | 97 | 92 | 90 | 90 | 92 | 90 | 92 | 91 | 79 | 84 | 80 | 70 | 72 | 77 | 70 | 70 | 66 | 73 |  | 85 | 88 | 90 | 92 | 96 | 103 | 102 | 2054400
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 30 | 55 | 55 | 40 | 40 | 47 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 40 | 0 | 848705
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 5 | 17 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 17 | 17 | 44 |  | 55 | 55 | 55 | 55 | 17 |  | 0 | 673666
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 140 | 140 | 140 | 110 | 110 | 110 | 110 | 2935636
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 16150
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 |  | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 1086840
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 52 |  |  |  |  | 36 |  | 300 | 240 | 63 | 0 |  |  | 0 | 474981
105 | Bramhangoan 100 MW PP (Aggreko) | [12 empty] | 25 |  |  |  |  | 25 |  | 100 | 100 | 100 | 0 |  |  | 0 | 225410
106 | Mymensingh 200 MW PP (United) | 190 | 200 | 160 | 160 | 120 | 139 | 190 | 191 | 189 | 199 | 199 | 186 | 196 | 197 | 194 | 193 | 193 | 194 |  | 197 | 197 | 197 | 197 | 197 | 197 | 188 | 4430400
112 | Aurahati 100MW PP (Aggreko) | [12 empty] | 25 |  |  |  |  | 25 |  | 100 | 100 | 70 | 0 |  |  | 0 | 201005
114 | Kodda 149 MW PP Unit-1 (Summit) | 126 | 113 | 90 | 90 | 90 | 95 | 133 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3355776
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 60 | 60 | 68 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1951680
116 | Chandpur 200MW (Desh energy) | [6 empty] | 3 | 17 | 42 | 100 | 100 | 140 | 200 | 200 | 200 | 155 | 136 | 137 |  | 170 | 200 | 200 | 200 | 155 | 34 | 0 | 2360160
117 | Ashuganj 150MW PP (Midland) | 147 | 135 | 135 | 133 | 140 | 142 | 143 | 137 | 147 | 133 | 130 | 137 | 143 | 140 | 132 | 130 | 135 | 138 |  | 135 | 140 | 138 | 145 | 150 | 147 | 142 | 3357163
118 | Bibiyana-III 400 MW CCPP | 140 | 139 | 140 | 140 | 140 | 140 | 139 | 139 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3355000
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 8 | 32 | 113 | 115 | 115 | 115 | 109 | 109 | 109 | 99 | 109 | 85 | 108 |  | 109 | 109 | 109 | 109 | 109 | 109 | 80 | 1936800
| Anwara 300 MW PP (United) | 294 | 290 | 298 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 280 | 270 | 283 | 283 | 283 | 283 | 283 |  | 290 | 290 | 290 | 300 | 300 | 283 | 283 | 6779564
| Juldah unit-2 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 50 | 20 | 20 | 20 | 55 | 100 | 70 | 62 | 70 | 70 | 38 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1375680
| Anlima Energy Ltd. | 113 | 90 | 68 | 68 | 68 | 68 | 80 | 113 | 113 | 87 | 87 | 94 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2453891
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 |  | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 436680
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 11 | 20 | 28 | 31 | 34 | 32 | 29 | 23 | 14 | 4 | 0 | [8 empty] | 231177
| Chandpur 115(Doreen) | [6 empty] | 3 | 51 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 54 | 54 | 71 |  | 72 | 72 | 72 | 72 | 74 | 74 | 0 | 1017600
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 47 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 27 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 43 | 55 | 55 | 55 | 55 | 55 | 55 | 1193040
120 | Eastern Zone Total | 5502 | 5294 | 4933 | 4904 | 4833 | 5083 | 5482 | 5970 | 6317 | 6421 | 6514 | 6671 | 6906 | 6660 | 6674 | 6494 | 6505 | 6774 |  | 7616 | 7528 | 7337 | 7121 | 6712 | 6339 | 5928 | 151305624
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [12 empty] | 4 | 4 | 4 | 6 | 8 | 27 |  | 33 | 29 | 29 | 8 |  |  |  | 116640
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 35 | 35 | 35 | 35 | 35 | 49 | 90 | 94 | 94 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2208000
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 29 | 55 | 71 | 82 | 89 | 85 | 75 | 59 | 37 | 13 | [9 empty] | 605520
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 210 | 217 | 220 | 200 | 200 | 200 | 225 | 225 | 214 | 175 | 222 | 221 | 221 | 218 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 200 | 224 | 224 | 5194445
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 280859
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 91 | 91 | 91 | 91 | 92 | 92 | 92 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2217350
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 7 | 7 | 8 |  | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 177496
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 83 | 50 |  |  |  |  | 0 | 131520
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 12 |  | 12 | [6 empty] | 19584
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 713 | 716 | 716 | 669 | 668 | 716 | 715 | 716 | 715 | 714 | 712 | 712 | 712 | 712 | 711 | 709 | 710 | 710 |  | 713 | 714 | 713 | 714 | 714 | 714 | 714 | 17136000
147 | Bheramara 410 MW CCPP | 245 | 250 | 260 | 265 | 265 | 270 | 275 | 270 | 260 | 250 | 240 | 230 | 225 | 225 | 220 | 220 | 220 | 215 |  | 215 | 215 | 215 | 225 | 230 | 240 | 245 | 5979744
148 | Payra 1320 MW | 360 | 360 | 300 | 300 | 290 | 300 | 300 | 340 | 320 | 280 | 280 | 300 | 340 | 340 | 340 | 340 | 340 | 340 |  | 440 | 460 | 480 | 500 | 470 | 430 | 380 | 9480700
149
150 | Barapukuria TPP Unit-1 | 86 | 85 | 85 | 86 | 84 | 83 | 82 | 84 | 85 | 84 | 83 | 80 | 80 | 79 | 81 | 80 | 80 | 80 |  | 80 | 81 | 81 | 82 | 83 | 78 | 79 | 1977163
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4864800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 34 |  | 34 | 34 | 34 | 34 |  |  |  | 132677
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [8 empty] | 40140
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 166 | 165 | 165 | 165 | 165 | 165 | 165 | 199 | 205 | 189 | 180 | 179 | 175 | 170 | 168 | 165 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 4340382
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [21 empty] | 13 | 26 | 40 |  |  | 58433
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 485520
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190386
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 34 | 50 | 50 | 50 |  |  | 0 | 143096
167 | Katakhali 50 MW Peaking PP | [9 empty] | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 40 |  | 40 | 41 | 41 | 40 |  |  |  | 306574
168 | Santahar 50 MW Peaking PP | [11 empty] | 14 | 15 | 15 | 21 | 27 | 27 | 28 |  | 28 | 30 | 29 | 29 |  |  |  | 227336
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 52 | 52 | 52 | 52 | 52 | 24 | 0 | 663360
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 44 | 49 | 48 | 48 | 48 | 48 | 48 | 48 | 75 |  | 99 | 99 | 99 | 99 | 99 | 99 | 0 | 919000
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 100 | 10 |  |  |  |  | 0 | 130891
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | 70 | 70 | 70 | 83 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2246112
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 35 | 35 | 35 | 35 | 35 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 100 |  | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 2181024
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 48 | 9 |  |  |  | 34 | 100 | 113 | 110 | 113 | 113 | 113 | 109 | 112 | 112 | 112 | 70 | 90 |  | 113 | 113 | 113 | 113 | 113 | 70 | 23 | 1959139
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 6 | 6 | 6 | 4 | 3 | 2 | 0 | [8 empty] | 39800
178 | Energypac Power Venture Thakurgaon Ltd. | [7 empty] | 16 | 60 | 78 | 91 | 111 | 110 | 99 | 117 | 117 | 117 | 117 |  | 116 | 116 | 117 | 117 | 117 |  | 0 | 1515165
178