## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-05 | Saturday
|  |  | Date (day): | 2022-03-05 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12041.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12720 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-04 | 2022-03-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 340 | 340 | 340
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 20 | 45 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 22 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 91 | 95 | 95 | 115 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 203 | 153 | 200 | 200 | 135 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 49 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 42 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 23 | 25 | 25
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 20 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 168 | 265 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 124 | 125 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 65 | 84 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 100 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 1845 | 2188 | 2913 | 2983 | 1306 | 979
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 24
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 42 | 42 | 42 |  | 8 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 |  | 184 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 43 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 30 | 42 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 60 | 85 | 100 | 100 |  | 8 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 283 | 283 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 92 | 92 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 46 | 92 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 68 | 109 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 799 | 1066 | 1290 | 1279 | 180 | 914
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 213 | 182 | 190 | 190 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 280 | 310 | 335 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 305 | 310 | 335 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 29 | 5 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 25 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 98 | 97 | 140 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 33 | 33 | 33 |  | 19 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 3 | 45 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 110 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 50 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 51 | 88 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 13 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 5 | 70 | 115 | 115 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1351 | 1462 | 1861 | 2068 | 621 | 229
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 148 | 208 | 140 | 210
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 168 | 185 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 68 | 103 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 475 | 538 | 548.6 | 567 | 0 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 160 | 160 | 160 | 170 |  | Gas shortage
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 48 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 89 | 86 | 89
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 24 | 21 | 24
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 270 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 140 | 140 | 140 | 140 | 260 |  | Gas shortage
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 384 | 395 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1363 | 1377 | 1438 | 1444 | 734 | 200
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 718 | 717 | 731 | 731
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 3 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 410 | 360 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1283 | 1235 | 1396 | 1746 | 0 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 7 | 8 | 10 | 10 |  |  | Engine problem
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 79 | 91 | 90 | 91 | 103 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 16 | 11 | 11 | 84 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 230 | 260 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 152 | 190 | 225 | 225
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 479 | 565 | 1116 | 1217 | 187 | 0
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 34 | 34 |  | 18 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 40 | 41 |  | 30 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 25 | 43 | 50
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 40 |  | 10 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 183 | 200 | 220
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 22 | 22 |  | 28 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 0 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 24 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 90 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 100 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 428 | 672 | 956 | 1018 | 600 | 500
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 82 | 85
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 75 | 104 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 36 | 120 | 0 |  |  | On test
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 81 | 340 | 523 | 398 | 74 | 125
|  | Total |  |  |  |  | 22066 | 20985 | 8104 | 9443 | 12041.6 | 12720 | 3702 | 3038
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7879.1511 | 9181 | 11707.5008 | 12367.0783
| A. |  | 2022-03-04 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 9443 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6980 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9443 | MW
| 3 | Day peak Generation : |  |  | 8104 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9181 | MW
| 4 | Evening peak Generation : |  |  | 9443 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 195.1694 | MKWHr | By Solar | 1.3348 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 103.3128 | MKWHr |  | By Oil: | 57.0221 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.9081 | MKWHr |  | By Hydro: | 1.0627 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3702 | MW | Dhaka | 3097 | 3097 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3038 | MW | Chittagong | 1040 | 1040 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6740 | MW | Khulna | 1092 | 1092 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 792.26 | MMCFD |  |  | Rajshahi | 992 | 992 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 99205995.968 | ii) Oil : | Taka | 377385589.98 | Comilla | 785 | 785 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 62514839.62 | Total | Taka | 539106425.568 | Mymensingh | 906 | 906 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.144 | MKWHr. | Sylhet | 346 | 346 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -260 | MW (E to W) at | 19:00 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -264 | MW at | 13:00 | hrs | Rangpur | 686 | 686 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.4° C |  |  | Total | 9181 | 9181 |  | 0
| B. |  | 2022-03-05 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 32.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12720 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9300 | MW
| 4 | Reserve(Generation end) |  |  |  | 2220 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 217.0156 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6823 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2182 | MKWHr. | ii) HVDC Flow at Peak Time |  | 717 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3107 | MKWHr. | iii) Maximum HVDC Flow : |  | 720 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.05 |  | (b) Today: | 89.93 |  | (c) Rule Curve: |  | 92.36
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 38 | 19 | 41 | 0 | 0 | 0 | 280 | 295 | 225 | 8 | 0 | 5 | 5 | 0 | 25 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 106 | 110 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 158 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 11 | 0 | 0 | 0 | 0 | 198 | 0 | 149 | 0 | 90 | 0 | 143 | 140 | 8 | 52 | 105 | 0 | 283 | 54 | 110 | 0 | 0 | 100 | 370 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 350 | 224 | 0 | 0 | 0 | 0 | 0 |  | 5688 | 2323 | 8011 | 3046 | 714 | 1203 | 0 | 2267 | 629 | 46 | 0 | 0 | 106 | 0 | 0 | 90.07
2:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 92 | 0 | 19 | 42 | 0 | 0 | 0 | 310 | 320 | 223 | 8 | 0 | 5 | 5 | 0 | 25 | 0 | 0 | 8 | 22 | 11 | 25 | 15 | 104 | 110 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 159 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 11 | 0 | 0 | 0 | 0 | 198 | 0 | 74 | 0 | 90 | 0 | 137 | 140 | 0 | 0 | 68 | 0 | 283 | 54 | 110 | 0 | 0 | 20 | 320 | 96 | 0 | 162 | 115 | 0 | 17 | 0 | 0 | 55 |  | 714 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 0 | 70 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 330 | 225 | 0 | 0 | 0 | 0 | 0 |  | 5326 | 2280 | 7606 | 3053 | 714 | 1205 | 0 | 1874 | 610 | 46 | 0 | 0 | 104 | 0 | 0 | 90.07
3:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 0 | 19 | 42 | 0 | 0 | 0 | 310 | 320 | 224 | 8 | 0 | 5 | 5 | 0 | 25 | 0 | 0 | 0 | 22 | 8 | 25 | 15 | 100 | 110 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 160 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 305 | 21 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 34 | 0 | 90 | 0 | 135 | 140 | 0 | 0 | 34 | 0 | 283 | 54 | 110 | 0 | 0 | 0 | 310 | 92 | 0 | 147 | 115 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 166 | 0 | 0 | 17 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 310 | 225 | 0 | 0 | 0 | 0 | 0 |  | 5059 | 2246 | 7305 | 3046 | 716 | 1209 | 0 | 1599 | 589 | 46 | 0 | 0 | 100 | 0 | 0 | 90.06
4:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 0 | 19 | 42 | 0 | 0 | 0 | 310 | 325 | 223 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 15 | 96 | 110 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 160 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 34 | 0 | 90 | 0 | 130 | 140 | 0 | 0 | 0 | 0 | 283 | 54 | 110 | 0 | 0 | 0 | 250 | 91 | 0 | 158 | 68 | 0 | 17 | 0 | 0 | 55 |  | 669 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 171 | 0 | 0 | 17 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 300 | 225 | 0 | 0 | 0 | 0 | 0 |  | 4913 | 2183 | 7096 | 2998 | 669 | 1229 | 0 | 1479 | 579 | 46 | 0 | 0 | 96 | 0 | 0 | 90.06
5:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 0 | 19 | 42 | 0 | 0 | 0 | 290 | 310 | 223 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 15 | 96 | 110 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 159 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 305 | 21 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 34 | 0 | 90 | 0 | 95 | 140 | 0 | 0 | 0 | 0 | 283 | 54 | 95 | 0 | 0 | 0 | 250 | 91 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 55 |  | 668 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 0 | 17 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 300 | 204 | 0 | 0 | 0 | 0 | 0 |  | 4817 | 2163 | 6980 | 2957 | 668 | 1213 | 0 | 1421 | 579 | 46 | 0 | 0 | 96 | 0 | 0 | 90.05
6:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 45 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 90 | 0 | 19 | 42 | 0 | 0 | 0 | 280 | 290 | 224 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 5 | 22 | 8 | 25 | 15 | 92 | 110 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 159 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 320 | 21 | 5 | 0 | 0 | 0 | 0 | 125 | 0 | 36 | 0 | 90 | 0 | 102 | 140 | 5 | 19 | 0 | 0 | 283 | 54 | 92 | 0 | 0 | 14 | 280 | 91 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 55 |  | 718 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 0 | 24 | 0 | 94 | 0 | 0 | 0 | 0 | 25 | 300 | 204 | 0 | 0 | 0 | 0 | 0 |  | 4951 | 2238 | 7189 | 2956 | 718 | 1228 | 0 | 1572 | 577 | 46 | 0 | 0 | 92 | 0 | 0 | 90.05
7:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 88 | 0 | 0 | 39 | 0 | 0 | 0 | 345 | 335 | 226 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 46 | 22 | 8 | 25 | 15 | 82 | 143 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 160 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 285 | 21 | 5 | 0 | 70 | 0 | 0 | 150 | 0 | 98 | 3 | 90 | 0 | 100 | 140 | 30 | 52 | 0 | 0 | 283 | 54 | 92 | 0 | 0 | 30 | 250 | 91 | 4 | 162 | 68 | 0 | 17 | 2 | 0 | 55 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 0 | 87 | 0 | 94 | 0 | 22 | 0 | 0 | 50 | 260 | 162 | 0 | 0 | 0 | 6 | 0 |  | 5215 | 2255 | 7470 | 2963 | 719 | 1148 | 0 | 1960 | 537 | 46 | 0 | 0 | 82 | 15 | 0 | 90.04
8:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 5 | 150 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 24 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 78 | 0 | 16 | 39 | 0 | 0 | 0 | 345 | 320 | 223 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 25 | 15 | 76 | 165 | 0 | 20 | 1 | 30 | 30 | 53 | 0 | 110 | 160 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 5 | 0 | 110 | 0 | 0 | 162 | 0 | 107 | 9 | 90 | 0 | 102 | 140 | 60 | 52 | 0 | 2 | 283 | 54 | 92 | 17 | 0 | 30 | 250 | 91 | 15 | 162 | 68 | 0 | 17 | 10 | 0 | 55 |  | 719 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 0 | 105 | 0 | 94 | 0 | 50 | 0 | 1 | 70 | 250 | 165 | 0 | 0 | 1 | 28 | 0 |  | 5368 | 2349 | 7717 | 2974 | 719 | 1146 | 0 | 2161 | 528 | 46 | 0 | 0 | 76 | 67 | 0 | 90.04
9:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 15 | 150 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 10 | 25 | 24 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 78 | 0 | 16 | 39 | 0 | 0 | 0 | 310 | 305 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 25 | 15 | 80 | 163 | 0 | 20 | 1 | 30 | 30 | 53 | 0 | 110 | 161 | 40 | 84 | 0 | 0 | 0 | 0 | 10 | 295 | 21 | 5 | 0 | 145 | 0 | 0 | 180 | 0 | 105 | 14 | 90 | 0 | 102 | 140 | 56 | 52 | 0 | 0 | 283 | 54 | 92 | 17 | 0 | 30 | 345 | 91 | 27 | 162 | 68 | 0 | 17 | 20 | 0 | 55 |  | 719 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 76 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 0 | 105 | 0 | 94 | 0 | 50 | 0 | 3 | 70 | 240 | 132 | 0 | 0 | 3 | 53 | 0 |  | 5481 | 2326 | 7807 | 2981 | 719 | 1126 | 0 | 2218 | 516 | 46 | 0 | 0 | 80 | 121 | 0 | 90.03
10:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 15 | 150 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 24 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 72 | 0 | 16 | 21 | 0 | 0 | 0 | 280 | 305 | 185 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 25 | 15 | 92 | 153 | 0 | 20 | 2 | 30 | 30 | 53 | 0 | 110 | 159 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 21 | 5 | 0 | 145 | 0 | 0 | 180 | 0 | 104 | 19 | 76 | 0 | 102 | 140 | 56 | 52 | 0 | 4 | 283 | 54 | 92 | 17 | 0 | 30 | 370 | 91 | 39 | 162 | 68 | 0 | 17 | 28 | 0 | 55 |  | 719 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 54 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 0 | 105 | 0 | 94 | 0 | 50 | 0 | 4 | 70 | 230 | 138 | 0 | 0 | 4 | 72 | 0 |  | 5458 | 2319 | 7777 | 2978 | 719 | 1090 | 0 | 2197 | 483 | 46 | 0 | 0 | 92 | 172 | 0 | 90.03
11:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 15 | 150 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 15 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 0 | 19 | 20 | 0 | 0 | 0 | 260 | 310 | 186 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 5 | 25 | 15 | 96 | 152 | 0 | 17 | 2 | 30 | 30 | 50 | 0 | 110 | 157 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 270 | 21 | 5 | 0 | 145 | 0 | 0 | 178 | 0 | 101 | 0 | 76 | 0 | 100 | 140 | 56 | 52 | 0 | 5 | 283 | 54 | 92 | 17 | 0 | 30 | 395 | 91 | 47 | 162 | 68 | 0 | 0 | 31 | 0 | 55 |  | 719 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 0 | 105 | 0 | 94 | 0 | 50 | 0 | 5 | 70 | 230 | 138 | 0 | 0 | 5 | 85 | 0 |  | 5449 | 2301 | 7750 | 3017 | 719 | 1085 | 0 | 2178 | 429 | 46 | 0 | 0 | 96 | 180 | 0 | 90.02
12:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 20 | 203 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 17 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 60 | 0 | 19 | 30 | 0 | 0 | 0 | 345 | 335 | 213 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 20 | 5 | 25 | 15 | 102 | 148 | 0 | 20 | 2 | 30 | 30 | 50 | 0 | 110 | 157 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 5 | 0 | 168 | 0 | 0 | 168 | 0 | 124 | 20 | 76 | 3 | 98 | 140 | 68 | 65 | 0 | 5 | 283 | 54 | 92 | 51 | 0 | 46 | 384 | 91 | 47 | 162 | 68 | 0 | 13 | 29 | 5 | 55 |  | 718 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 200 | 0 | 0 | 105 | 0 | 94 | 0 | 75 | 0 | 6 | 100 | 230 | 152 | 0 | 0 | 5 | 90 | 0 |  | 5833 | 2271 | 8104 | 3296 | 718 | 1100 | 0 | 2408 | 230 | 46 | 0 | 0 | 102 | 204 | 0 | 90.02
13:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 32 | 180 | 0 | 0 | 0 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 14 | 25 | 33 | 11 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 18 | 60 | 12 | 19 | 30 | 0 | 0 | 0 | 290 | 280 | 185 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 20 | 5 | 25 | 15 | 106 | 146 | 0 | 20 | 2 | 30 | 30 | 50 | 0 | 110 | 158 | 60 | 50 | 0 | 0 | 0 | 0 | 10 | 295 | 21 | 5 | 0 | 238 | 0 | 0 | 170 | 0 | 134 | 20 | 90 | 56 | 96 | 140 | 101 | 90 | 0 | 5 | 283 | 54 | 88 | 114 | 0 | 80 | 330 | 91 | 49 | 162 | 93 | 0 | 17 | 30 | 51 | 55 |  | 719 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 206 | 0 | 0 | 105 | 0 | 94 | 0 | 97 | 0 | 5 | 50 | 250 | 172 | 0 | 0 | 5 | 84 | 76 |  | 6138 | 2400 | 8538 | 3061 | 719 | 1099 | 0 | 3001 | 285 | 35 | 0 | 32 | 106 | 200 | 0 | 90.01
14:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 176 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 10 | 25 | 33 | 8 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 60 | 37 | 19 | 31 | 0 | 0 | 0 | 260 | 270 | 184 | 8 | 0 | 5 | 20 | 0 | 51 | 0 | 0 | 52 | 20 | 5 | 25 | 15 | 100 | 149 | 0 | 17 | 2 | 30 | 30 | 50 | 0 | 110 | 158 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 260 | 21 | 5 | 0 | 195 | 0 | 0 | 169 | 0 | 116 | 20 | 90 | 34 | 92 | 140 | 64 | 34 | 0 | 4 | 230 | 54 | 80 | 17 | 0 | 20 | 340 | 55 | 43 | 108 | 68 | 0 | 17 | 29 | 17 | 55 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 0 | 105 | 0 | 94 | 0 | 45 | 0 | 5 | 50 | 240 | 176 | 0 | 0 | 4 | 77 | 31 |  | 5459 | 2211 | 7670 | 2928 | 719 | 1120 | 0 | 2233 | 335 | 35 | 0 | 16 | 100 | 184 | 0 | 90.01
15:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 178 | 0 | 34 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 10 | 25 | 33 | 8 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 71 | 42 | 19 | 31 | 0 | 0 | 0 | 260 | 275 | 183 | 8 | 0 | 5 | 25 | 0 | 51 | 0 | 0 | 52 | 20 | 5 | 25 | 15 | 92 | 155 | 0 | 17 | 1 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 5 | 0 | 195 | 0 | 0 | 193 | 0 | 97 | 16 | 90 | 17 | 93 | 140 | 64 | 34 | 0 | 3 | 230 | 54 | 85 | 17 | 0 | 20 | 340 | 53 | 35 | 108 | 68 | 0 | 17 | 23 | 17 | 55 |  | 720 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 0 | 105 | 0 | 94 | 0 | 34 | 0 | 4 | 50 | 240 | 140 | 0 | 0 | 3 | 0 | 18 |  | 5512 | 2164 | 7676 | 2979 | 720 | 1108 | 0 | 2217 | 424 | 35 | 0 | 16 | 92 | 85 | 0 | 90
16:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 168 | 0 | 35 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 10 | 25 | 25 | 8 | 0 | 46 | 35 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 73 | 42 | 19 | 27 | 0 | 0 | 0 | 260 | 275 | 186 | 8 | 0 | 5 | 25 | 0 | 51 | 0 | 0 | 25 | 20 | 11 | 25 | 15 | 90 | 155 | 0 | 17 | 1 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 5 | 0 | 145 | 0 | 0 | 192 | 0 | 81 | 0 | 76 | 17 | 92 | 140 | 45 | 34 | 0 | 2 | 230 | 54 | 86 | 17 | 0 | 20 | 340 | 53 | 23 | 108 | 68 | 0 | 17 | 15 | 17 | 55 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 0 | 105 | 0 | 94 | 0 | 34 | 0 | 3 | 50 | 240 | 140 | 0 | 0 | 2 | 0 | 18 |  | 5344 | 2208 | 7552 | 2971 | 719 | 1104 | 0 | 2054 | 438 | 81 | 0 | 49 | 90 | 46 | 0 | 90
17:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 150 | 0 | 66 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 17 | 25 | 25 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 72 | 42 | 19 | 42 | 0 | 0 | 0 | 265 | 290 | 191 | 8 | 0 | 5 | 25 | 0 | 51 | 0 | 0 | 25 | 20 | 11 | 25 | 15 | 94 | 156 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 145 | 0 | 0 | 192 | 0 | 60 | 5 | 90 | 17 | 85 | 140 | 45 | 34 | 0 | 1 | 230 | 54 | 91 | 17 | 0 | 20 | 340 | 53 | 7 | 108 | 68 | 0 | 17 | 5 | 17 | 55 |  | 717 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 79 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 0 | 105 | 0 | 94 | 0 | 34 | 0 | 2 | 35 | 230 | 140 | 0 | 0 | 1 | 0 | 18 |  | 5357 | 2192 | 7549 | 3020 | 717 | 1131 | 0 | 2029 | 430 | 46 | 0 | 61 | 94 | 21 | 0 | 89.99
18:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 154 | 0 | 66 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 17 | 23 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 81 | 42 | 19 | 42 | 0 | 0 | 0 | 270 | 320 | 198 | 8 | 0 | 15 | 25 | 0 | 51 | 0 | 33 | 25 | 20 | 11 | 25 | 13 | 102 | 161 | 0 | 17 | 0 | 30 | 30 | 22 | 0 | 110 | 159 | 61 | 30 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 195 | 0 | 0 | 191 | 0 | 60 | 0 | 40 | 18 | 92 | 140 | 50 | 34 | 0 | 0 | 260 | 54 | 92 | 50 | 0 | 25 | 360 | 57 | 0 | 109 | 71 | 0 | 17 | 0 | 21 | 55 |  | 717 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 79 | 7 | 0 | 0 | 0 | 0 | 34 | 4 | 66 | 0 | 0 | 16 | 8 | 31 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 160 | 0 | 0 | 105 | 0 | 94 | 0 | 80 | 0 | 0 | 60 | 240 | 143 | 0 | 0 | 0 | 0 | 18 |  | 5512 | 2435 | 7947 | 3155 | 717 | 1049 | 0 | 2234 | 440 | 46 | 0 | 204 | 102 | 0 | 0 | 89.99
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 45 | 153 | 0 | 91 | 0 | 93 | 49 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 17 | 23 | 33 | 20 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 85 | 42 | 19 | 42 | 0 | 0 | 0 | 280 | 305 | 182 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 33 | 50 | 21 | 11 | 25 | 15 | 110 | 208 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 265 | 0 | 0 | 185 | 0 | 125 | 0 | 90 | 45 | 97 | 140 | 103 | 84 | 43 | 0 | 283 | 54 | 92 | 88 | 0 | 92 | 395 | 100 | 0 | 162 | 109 | 0 | 17 | 0 | 70 | 55 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 34 | 4 | 90 | 0 | 25 | 37 | 52 | 32 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 183 | 0 | 0 | 105 | 0 | 94 | 0 | 104 | 0 | 0 | 113 | 260 | 190 | 0 | 0 | 0 | 0 | 36 |  | 6631 | 2812 | 9443 | 3361 | 717 | 1167 | 0 | 3249 | 460 | 46 | 0 | 333 | 110 | 0 | 0 | 89.97
19:30 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 55 | 155 | 0 | 95 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 23 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 87 | 42 | 19 | 42 | 0 | 0 | 0 | 285 | 310 | 189 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 15 | 106 | 208 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 290 | 0 | 0 | 185 | 0 | 135 | 0 | 90 | 17 | 100 | 140 | 103 | 102 | 51 | 0 | 283 | 54 | 92 | 88 | 8 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 35 | 55 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 220 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 360 | 200 | 0 | 0 | 0 | 0 | 36 |  | 6527 | 2843 | 9370 | 3439 | 717 | 1209 | 0 | 3186 | 560 | 46 | 0 | 107 | 106 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 155 | 0 | 95 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 30 | 23 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 87 | 42 | 19 | 42 | 0 | 0 | 0 | 280 | 310 | 187 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 15 | 106 | 209 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 159 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 290 | 0 | 0 | 185 | 0 | 132 | 0 | 90 | 17 | 107 | 140 | 103 | 90 | 51 | 0 | 283 | 54 | 92 | 88 | 5 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 35 | 55 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 221 | 0 | 0 | 105 | 0 | 99 | 0 | 113 | 0 | 0 | 113 | 350 | 200 | 0 | 0 | 0 | 0 | 0 |  | 6428 | 2792 | 9220 | 3433 | 717 | 1195 | 0 | 3064 | 550 | 46 | 0 | 109 | 106 | 0 | 0 | 89.98
21:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 30 | 155 | 0 | 95 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 22 | 23 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 92 | 42 | 19 | 42 | 0 | 0 | 0 | 280 | 305 | 186 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 15 | 110 | 208 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 161 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 290 | 0 | 0 | 177 | 0 | 138 | 0 | 90 | 17 | 140 | 140 | 103 | 90 | 51 | 0 | 283 | 54 | 92 | 88 | 8 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 35 | 55 |  | 716 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 222 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 390 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6478 | 2854 | 9332 | 3421 | 716 | 1234 | 0 | 3117 | 589 | 46 | 0 | 99 | 110 | 0 | 0 | 89.97
22:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 15 | 153 | 0 | 60 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 23 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 94 | 42 | 19 | 41 | 0 | 0 | 0 | 280 | 295 | 184 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 15 | 110 | 210 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 260 | 0 | 0 | 177 | 0 | 149 | 0 | 90 | 0 | 148 | 140 | 103 | 90 | 51 | 0 | 283 | 54 | 80 | 17 | 8 | 100 | 400 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 0 | 55 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 370 | 225 | 0 | 0 | 0 | 0 | 0 |  | 6202 | 2812 | 9014 | 3379 | 717 | 1222 | 0 | 2881 | 569 | 46 | 0 | 90 | 110 | 0 | 0 | 89.97
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 15 | 154 | 0 | 62 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 23 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 109 | 18 | 19 | 42 | 0 | 0 | 0 | 300 | 305 | 193 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 100 | 210 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 159 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 177 | 0 | 149 | 0 | 90 | 0 | 145 | 140 | 64 | 90 | 51 | 0 | 283 | 54 | 93 | 17 | 8 | 100 | 385 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 220 | 0 | 0 | 53 | 0 | 113 | 0 | 49 | 0 | 0 | 50 | 310 | 204 | 0 | 0 | 0 | 0 | 0 |  | 6037 | 2461 | 8498 | 3376 | 716 | 1202 | 0 | 2549 | 509 | 46 | 0 | 0 | 100 | 0 | 0 | 89.96
24:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 154 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 102 | 18 | 19 | 42 | 0 | 0 | 0 | 280 | 295 | 182 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 98 | 213 | 0 | 20 | 0 | 30 | 30 | 53 | 0 | 110 | 159 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 285 | 22 | 11 | 0 | 45 | 0 | 0 | 186 | 0 | 149 | 0 | 90 | 0 | 140 | 140 | 24 | 90 | 51 | 0 | 283 | 54 | 96 | 0 | 0 | 100 | 360 | 104 | 0 | 162 | 115 | 0 | 17 | 0 | 0 | 55 |  | 716 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 192 | 0 | 0 | 0 | 0 | 113 | 0 | 33 | 0 | 0 | 10 | 280 | 200 | 0 | 0 | 0 | 0 | 0 |  | 5745 | 2283 | 8028 | 3265 | 716 | 1203 | 0 | 2220 | 480 | 46 | 0 | 0 | 98 | 0 | 0 | 89.96
KWH | 0 | 0 | 0 | 0 | 8135891 | 0 | 0 | 0 | 0 |  | 0 | 7066750 | 0 | 0 | 0 | 457874 | 4234511 | 0 | 644000 | 0 | 716544 | 144960 | 34059 | 0 | 0 | 0 | 1304280 | 281359 | 1043602 | 419724 | 600000 | 558720 | 622600 | 811400 | 88320 | 0 | 946740 | 116000 | 0 | 0 | 50545 | 0 | 0 | 0 | 0 |  | 531840 | 0 | 51303 | 88920 | 2004480 | 479520 | 421008 | 912000 | 0 | 0 | 0 | 7352200 | 7467000 | 4829000 | 217454 | 0 | 312624 | 360480 | 0 | 1138824 | 0 | 45072 | 974246 | 492480 | 199620 | 606500 | 382910 | 2310720 | 3622080 | 0 | 430740 | 15200 | 716000 | 698808 | 1215600 | 0 | 2920581 | 3789000 | 1279584 | 1992960 | 0 | 0 | 0 | 0 | 250020 | 7162000 | 514032 | 162480 | 0 | 3515235 | 0 | 0 | 4068000 | 0 | 2442960 | 131625 | 2000640 | 310080 | 2679709 | 3358000 | 1281600 | 1285800 | 601345 | 32160 | 6493527 | 1349673 | 2282426 | 721620 | 33600 | 1220160 | 8264100 | 2125440 | 336590 | 3677760 | 2161582 | 0 | 435600 | 214589 | 359040 | 1365480 |  | 17218181 | 0 | 7234560 | 0 | 0 | 0 | 0 | 0 | 6720 | 13824 | 0 | 2097777 | 156585 | 0 | 0 | 0 | 0 | 54166 | 10672 | 457928 | 0 | 20694 | 38501 | 293616 | 54655 | 248880 | 0 | 149454 | 843054 | 0 | 4335800 | 0 | 0 | 0 | 0 | 0 | 0 | 331083 | 0 | 4511118 | 0 | 0 | 2198880 | 0 | 2371104 | 0 | 1159200 | 0 | 39154 | 1388640 | 7729200 | 4421645 | 0 | 0 | 37740 | 527760 | 245263 |  | 136973506 | 58195854 | 195169360 | 74917921 | 17218181 | 28394862 | 0 | 56144263 | 12908054 | 1062740 | 0 | 877801 | 2310720 | 1334818 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 9030839.01 | 0 | 0 | 0 | 0 |  | 0 | 7702757.5 | 0 | 0 | 0 | 3873614.04 | 4403891.44 | 0 | 1114120 | 0 | 6534881.28 | 1426406.4 | 314023.98 | 0 | 0 | 0 | 9521244 | 2174905.07 | 10289915.72 | 314793 | 450000 | 0 | 0 | 0 | 854054.4 | 0 | 255619.8 | 31320 | 0 | 0 | 469563.05 | 0 | 0 | 0 | 0 |  | 0 | 0 | 497639.1 | 849186 | 17438976 | 3797798.4 | 530470.08 | 2708640 | 0 | 0 | 0 | 5440628 | 7467000 | 4442680 | 280515.66 | 0 | 353265.12 | 504672 | 0 | 1947389.04 | 0 | 455227.2 | 9304049.3 | 625449.6 | 149715 | 1061375 | 287182.5 | 17330400 | 3839404.8 | 0 | 547039.8 | 242288 | 1174240 | 1118092.8 | 2163768 | 0 | 3329462.34 | 3940560 | 2520780.48 | 3806553.6 | 0 | 0 | 0 | 0 | 510040.8 | 7233620 | 385524 | 123484.8 | 0 | 26575176.6 | 0 | 0 | 21153600 | 0 | 24038726.4 | 1538696.25 | 16305216 | 3364368 | 18891948.45 | 3122940 | 11688192 | 12150810 | 5237714.95 | 0 | 49091064.12 | 11755651.83 | 20062524.54 | 7201767.6 | 287952 | 8126265.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99176722.56 | 0 | 7596288 | 0 | 0 | 0 | 0 | 0 | 70492.8 | 144875.52 | 0 | 2370488.01 | 242706.75 | 0 | 0 | 0 | 0 | 532993.44 | 108427.52 | 4052662.8 | 0 | 279782.88 | 373074.69 | 2845139.04 | 530153.5 | 477849.6 | 0 | 113136.678 | 5083615.62 | 0 | 23500036 | 0 | 0 | 0 | 0 | 0 | 0 | 496624.5 | 0 | 5278008.06 | 0 | 0 | 22956307.2 | 0 | 22501776.96 | 0 | 8995392 | 0 | 432651.7 | 10262049.6 | 33931188 | 0 | 0 | 0 | 0 | 0 | 0 |  | 405761680.45 | 252352443.428 | 658114123.878 | 67801396.178 | 99176722.56 | 31404599.79 | 0 | 369193637.01 | 62514839.62 | 286939.8 | 0 | 8191952.97 | 17330400 | 2213635.95 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 20 | 203 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 17 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 60 | 0 | 19 | 30 | 0 | 0 | 0 | 345 | 335 | 213 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 52 | 20 | 5 | 25 | 15 | 102 | 148 | 0 | 20 | 2 | 30 | 30 | 50 | 0 | 110 | 157 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 5 | 0 | 168 | 0 | 0 | 168 | 0 | 124 | 20 | 76 | 3 | 98 | 140 | 68 | 65 | 0 | 5 | 283 | 54 | 92 | 51 | 0 | 46 | 384 | 91 | 47 | 162 | 68 | 0 | 13 | 29 | 5 | 55 |  | 718 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 200 | 0 | 0 | 105 | 0 | 94 | 0 | 75 | 0 | 6 | 100 | 230 | 152 | 0 | 0 | 5 | 90 | 0 |  | 8104 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 45 | 153 | 0 | 91 | 0 | 93 | 49 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 17 | 23 | 33 | 20 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 10 | 85 | 42 | 19 | 42 | 0 | 0 | 0 | 280 | 305 | 182 | 8 | 0 | 29 | 25 | 0 | 51 | 0 | 33 | 50 | 21 | 11 | 25 | 15 | 110 | 208 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 265 | 0 | 0 | 185 | 0 | 125 | 0 | 90 | 45 | 97 | 140 | 103 | 84 | 43 | 0 | 283 | 54 | 92 | 88 | 0 | 92 | 395 | 100 | 0 | 162 | 109 | 0 | 17 | 0 | 70 | 55 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 34 | 4 | 90 | 0 | 25 | 37 | 52 | 32 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 183 | 0 | 0 | 105 | 0 | 94 | 0 | 104 | 0 | 0 | 113 | 260 | 190 | 0 | 0 | 0 | 0 | 36 |  | 9443 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 0 | 0 | 55 | 200 | 0 | 95 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 42 | 19 | 25 | 0 | 0 | 0 | 335 | 335 | 190 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 11 | 25 | 15 | 163 | 210 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 330 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 140 | 140 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 |  | 115 | 55 |  | 731 | 0 | 410 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 91 | 10 | 110 | 0 | 0 | 0 | 34 | 41 | 100 | 0 | 50 | 40 | 52 | 22 | 22 | 0 | 11 | 85 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 225 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 55 | 200 | 0 | 95 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 42 | 19 | 10 | 0 | 0 | 0 | 310 | 310 | 190 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 11 | 25 | 15 | 138 | 140 | 0 | 20 | 1.6 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 330 | 21 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 140 | 140 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 50 | 162 | 113 | 0 | 17 | 30 | 115 | 55 |  | 731 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 110 | 0 | 0 | 0 | 34 | 40 | 100 | 0 | 43 | 0 | 52 | 22 | 22 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 200 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 225 |  | 50 | 6 | 50 | 120
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 193 | 0 | 57 | 0 | 84 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 20 | 33 | 4 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 108 | 0 | 19 | 7 | 0 | 0 | 0 | 335 | 310 | 170 | 8 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 15 | 96 | 215 | 0 | 20 | 1 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 19 | 5 | 0 | 195 | 0 | 0 | 160 | 0 | 129 | 7 | 60 | 25 | 103 | 140 | 80 | 70 | 17 | 2 | 283 | 54 | 68 | 114 | 0 | 0 | 260 | 104 | 15 | 144 | 17 | 0 | 17 | 11 | 25 | 55 | 0 | 716 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 181 | 0 | 0 | 105 | 0 | 113 | 0 | 112 | 0 | 1 | 113 | 270 | 175 | 0 | 0 | 1 | 28 | 42 | 0
199
| Minimum Generation |  | 6980 | 5:00
| Highest Generation |  | 9443 | 19:00
| Day Peak Generation |  | 8104 | 12:00
| Evening Peak Generation |  | 9443 | 19:00
| HVDC Max Flow |  | 720 | 15:00
| HVDC EvPeak Flow |  | 717 | 19:00
| Load factor L.F |  | 86.12%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-05
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8104 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6823 | MW
Evening Peak Generation : |  | 9443 | MW Hour : | 19:00 | Available Max Generation : |  | 12720 | MW
E.P. Demand (at gen end) : |  | 9443 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 9443 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2220 | MW
Total Gen. (MKWH) : |  | 195.1694 | System Load Factor : | 86.12% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -264 | MW at | 13:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-05
Actual : | 89.93 | Ft.(MSL) , | Rule curve : | 92.36 | Ft.( MSL )
Gas Consumed : | Total = | 792.26 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 99205995.968
: |  | Coal : | 62514839.62 | Oil : | 377385589.98 | Total : | 539106425.568
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3801.3649 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1291.6118 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1157.052 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1045.4268 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 944.7742 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 762.3966 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 427.6622 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 196.3328 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 587.9916 |  |  | 0 | 0%
Total | 0 |  | 10214.6129 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Meghnaghat Summit 305 MW CCPP
6) Raozan unit- 1,2
7) Sirajganj Unit 1,2
8) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ishwardi 132/33 kV T-1 transformer was under shut down from 08:22 to 16:35 for C/M.
b) Siddhirganj 132/33 kV T-2 transformer was shut down at 08:24 for A/M.
c) After testing Barapukuria Unit-1 was shutdown at 10:48.
d) Barapukuria unit-3 tripped at 11:24 due to turbine temperature high and was switched on at 12:55.
e) Shahjibazar-B.Baria 132 kV Ckt-2 tripped at 12:24 from Shahjibazar end showing Dist. and was
switched on at 12:44.
f) Kaptai unit-2 tripped at 12:10 due to AVR problem.
g) Shahjibazar 86 MW tripped at 12:29 due to voltage fluctuation.
h) Kachua 132/33 kV T-1 transformer was under shut down from 12:00 to 14:49 for C/M.
i) Gopalganj(N)-Faridpur 132 kV Ckt-1&2 were under shut down from 08:50 to 18:05 for D/W.
j) Ghorashal GIS-AIS 230 kV Ckt-2 tripped at 12:38 from both ends showing Dist. B at GIS end & CB problem
at AIS end and was switched on at 15:48.
k) Madaripur-Gopalganj 132 kV Ckt-1&2 were under shut down from 08:50 to 18:13 for D/W.
l) Mongla 132 kV Bus was under shut down from 15:04 to 16:47 for C/M.
m) After Gas clearance Siddhirganj peaking GT-1 was synchronized at 14:56.
n) Cumilla(N) 230/132 kV T-02 transformer tripped at 06:30(05/03/2022) showing protection trip.
o) Sylhet 132 kV Bus-3&4 were shutdown at 07:08(05/03/2022) due to C/M.
p) Bogura-Barapukuria 230 kV Ckt-2 was shutdown at 07:13(05/03/2022) due to D/W.
q) Faridpur 132/33 T-2 transformer along with 33 kV Bus-2 was shutdown at 07:10(05/03/2022) due to C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 8135891
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7066750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 45 | 457874 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 22 | 34059 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 419724
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 91 | 644000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 153 | 4234511 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 716544 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1304280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 49 | 144960 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 281359
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1043602
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 1158720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 622600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 20 | 88320 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 265 | 3515235
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 125 | 2442960 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 84 | 1285800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 100 | 2125440
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3677760
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 214589
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1365480
| Dhaka area Total |  |  |  | 5696 | 2188 | 41791858
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 50545 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 131625
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 479520 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1062740 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 43 | 601345 | Low demand
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 51303 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 88920 | Low demand
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2000640 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 421008
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 912000
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 2004480 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32160
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 283 | 6493527 | Engine problem
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1349673
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 92 | 2282426 | Engine problem
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 92 | 1220160 | Low demand
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 109 | 2161582
| Chattogram area Total |  |  |  | 2382 | 1066 | 21343654
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4829000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7352200 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7467000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 312624 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 25 | 360480 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1138824
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 97 | 2679709 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 45072 | Engine problem
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 45 | 310080 | Low demand
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 492480
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 199620
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2310720
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 606500 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 50 | 974246
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 382910 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 721620 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 33600 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 435600 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 70 | 359040 | Engine problem
| Cumilla Area Total |  |  |  | 2899 | 1462 | 31228779
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 208 | 3622080
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 430740
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15200
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 185 | 4068000 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 103 | 1281600 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 336590
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 531840
| Mymensingh Area Total |  |  |  | 622 | 538 | 10286050
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 698808 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2920581 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3789000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 1215600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 162480
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1279584
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 1992960
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 514032
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7162000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 140 | 3358000 | Gas shortage, ST under Maint.
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250020
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 395 | 8264100
| Sylhet Area Total |  |  |  | 2377 | 1377 | 32323165
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 717 | 17218181
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 6720 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 3 | 13824 | Low demand
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 7234560
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2198880
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 527760
| Khulna Area Total |  |  |  | 2229 | 1235 | 27199925
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 8 | 156585 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2097777 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 16 | 331083 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 260 | 7729200 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 190 | 4421645
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 565 | 14736290
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 54166 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 10672 | Low demand
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 20694 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 38501 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 4511118 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 54655 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 248880 | Engine problem
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 149454 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 293616
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 457928 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2371104 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1388640
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37740
| Rajshahi Area Total |  |  |  | 2129 | 672 | 9637168
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 843054
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4335800 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 104 | 1159200
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39154
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 36 | 245263 | On test
| Rangpur Area Total |  |  |  | 605 | 340 | 6622471
| Total |  |  |  | 20985 | 9443 | 195169360
| Eastern Grid Total |  |  |  | 13976 | 6631 | 136973506
| Western Grid Total |  |  |  | 7009 | 2812 | 58195854
| National Grid Total |  |  |  | 20985 | 9443 | 195169360
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-04
(a) ENTIRE EASTERN GRID : |  | 6174 | MW | (b) ENTIRE WESTERN GRID : |  | 3007 | MW
i) Dhaka area |  | 3097 | MW | i) Khulna area |  | 1092 | MW
ii) Chittagong area |  | 1040 | MW | ii) Rajshahi area |  | 992 | MW
iii) Comilla area |  | 785 | MW | iii) Barisal area |  | 237 | MW
iv) Mymensingh area |  | 906 | MW | iv) Rangpur area |  | 686 | MW
v) Sylhet area |  | 346 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9181 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 82 | 1:00 | Valuka | 88 | 9:00 | Central S/S | 57 | 19:00
Munsiganj | 64 | 21:00 | Tangail | 187 | 8:00 | Noapara | 32 | 18:30
Sonargaon | 62 | 1:00 | Mymensing | 190 | 19:00 | Jessore | 89 | 19:00
Bhulta | 166 | 21:00 | Kishoreganj | 110 | 19:00 | Benapol | 42 | 18:30
Madanganj | 31 | 1:00 | Netrokona | 120 | 9:00 | Jhenida(Old) | 80 | 19:00
Rahim steel | 15 | 9:00 | Jamalpur | 131 | 8:00 | Bottail | 81 | 19:00
Ghorasal | 54 | 19:00 | Sherpur | 126 | 8:00 | G.K Project | 38 | 19:00
Narsingdi | 132 | 20:00 | Srimongal | 33 | 18:30 | Faridpur | 85 | 19:00
Haripur(SBU) | 88 | 1:00 | Shahjibazar | 85 | 18:30 | Rajbari | 44 | 19:00
Sreenagar | 28 | 13:00 | Fenchuganj | 28 | 18:30 | Madaripur | 67 | 21:00
Shyampur | 164 | 3:00 | Kulawara | 26 | 18:30 | Sariatpur | 44 | 21:00
Shitalakhya | 73 | 11:00 | Sylhet | 93 | 18:30 | Gopalganj | 69 | 19:00
Matuail | 51 | 1:00 | Chatak | 15 | 18:30 | Bagerhat | 78 | 19:00
Char Saidpur | 26 | 7:00 | Sunamganj | 33 | 18:30 | Mongla | 36 | 1:00
Ullon | 28 | 21:00 | Biani Bazar | 37 | 18:30 | Satkhira | 81 | 19:00
Hasnabad | 58 | 11:00 | Comilla (S) | 112 | 18:30 | Gallamari | 42 | 13:00
Magbazar | 69 | 12:00 | Comilla(N) | 89 | 21:00 | Magura | 42 | 19:00
Maniknagar | 46 | 12:00 | Chandpur | 48 | 18:30 | Norail | 34 | 19:00
Bangabhaban | 3 | 12:00 | Feni | 86 | 19:00 | Chuadanga | 66 | 19:00
Motijheel | 19 | 12:00 | Chowmuhani | 136 | 20:00 | Barisal(N) | 35 | 19:00
Narinda | 32 | 11:00 | Ashuganj | 26 | 1:00 | Barisal (S) | 66 | 19:00
Kazla | 63 | 19:30 | Daudkandi | 84 | 19:30 | Patuakhali | 61 | 21:00
Dhanmondi | 104 | 19:00 | B.Baria | 110 | 19:00 | Bhandaria | 37 | 21:00
Lalbag | 59 | 1:00 | Ramganj | 52 | 19:00 | Borguna | 12 | 19:00
Madartek | 57 | 13:00 | Chaddagram | 33 | 18:30 | Borhan Uddin | 42 | 21:00
Dhaka University | 13 | 11:00 | PHP | 10 | 10:00 | Ishurdi | 47 | 1:00
Aftabnagar | 22 | 18:30 | Kochua | 36 | 18:30 | Ruppur Paromanobik | 3 | 9:00
Fatullah | 48 | 1:00 | Madunaghat | 34 | 19:00 | Natore | 103 | 19:00
Nawabganj | 33 | 21:00 | Hathazari | 68 | 18:30 | Bogra | 113 | 19:30
Keraniganj | 42 | 1:00 | Khulshi | 131 | 22:00 | Naogaon | 98 | 8:00
Banani | 28 | 18:30 | Halishahar | 59.5 | 18:30 | Rajshahi | 86 | 19:00
Mirpur | 88 | 13:00 | Baraulia | 93 | 2:00 | Rajshahi New | 48 | 13:00
Kalyanpur | 69 | 13:00 | Sikalbaha | 20 | 18:00 | C.Nawabganj | 48 | 19:30
Gulshan | 64 | 18:30 | Dohazari | 62 | 19:00 | Amnura | 49 | 20:00
Uttara | 60 | 13:00 | Cox'sbazar | 98 | 19:00 | Pabna | 65 | 19:00
Uttara New | 18 | 1:00 | Chandraghona | 22 | 18:30 | Shahjadpur | 80 | 8:00
Kamrangirchar | 51 | 1:00 | Kaptai | 4 | 18:30 | Serajganj | 72 | 19:00
Savar | 111 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 95 | 9:00
Bhasantec | 100 | 19:00 | Bakulia | 78 | 19:00 | Joypurhat | 51 | 9:00
Agargaon | 54 | 13:00 | Julda | 20 | 11:00 | Sherpur(Bogura) | 48 | 8:00
Satmosjid | 71 | 13:00 | TK chemical | 21 | 18:30 | Mohastangor | 56 | 19:00
Old Tongi | 87 | 11:00 | Modern Steel | 0 | 1:00 | Bhangura | 28 | 8:00
Kabirpur | 169 | 1:00 | Shahmirpur | 23 | 1:00 | Rangpur | 101 | 19:00
Manikgonj | 59 | 19:30 | Khagrachhari | 20 | 18:30 | Lalmonirhat | 36 | 8:00
Joydevpur | 116 | 12:00 | Matarbari | 29 | 18:30 | Saidpur | 74 | 9:00
New Tongi | 53 | 12:00 | Baroiar Hat | 31 | 18:30 | Purbasadipur | 95 | 18:30
Kodda | 160 | 10:00 | Rangamati | 10 | 18:30 | Thakurgaon | 68 | 19:00
Dhamrai | 68 | 19:00 | Agrabad | 48 | 18:30 | Palashbari | 100 | 19:00
Rajendrapur | 70 | 18:30 | Rampur | 5 | 18:30 | Barapukuria | 49 | 9:00
Bashundara | 90 | 18:00 | Abul Khair 230 | 121 | 12:00 | Panchagar | 46 | 19:00
Purbachal | 12 | 12:00 | BSRM | 162 | 10:00 | Joldhaka | 52 | 19:00
Tongi Millgate | 28 | 11:00 | GPH Ispat | 102 | 6:00 | Kurigram | 52 | 19:00
Bashundhara Cement |  |  | Goalpara | 18 | 13:00 | Mithapukur | 27 | 8:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 6:00 | 406 | 4:00 | Kaliakoir | 395 | 0.375 | 391 | 0.5
| Bheramara | 401 | 13:00 | 393 | 13:00 | Bhulta | 410 | 0.25 | 398 | 0.5
| Ashuganj(N) | 410 | 13:00 | 397 | 12:00 | Gopalganj | 417 | 0.625 | 406 | 0.875
| Payra | 421 | 13:00 | 416 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 18:00 | 236 | 1:00 | Hathazari | 243 | 6:00 | 231 | 12:00
| Ishurdi | 241 | 6:00 | 229 | 12:00 | Megnaghat | 240 | 24:00 | 234 | 1:00
| Ashuganj | 244 | 13:00 | 236 | 12:00 | Fenchuganj | 245 | 6:00 | 240 | 11:00
| Serajganj | 238 | 18:00 | 227 | 12:00 | Siddhirganj | 237 | 13:00 | 230 | 12:00
| Baghabari | 238 | 3:00 | 226 | 11:00 | Maniknagar | 235 | 13:00 | 228 | 12:00
| Barapukuria | 234 | 22:00 | 219 | 12:00 | Agargaon | 236 | 16:00 | 228 | 12:00
| Bogra | 236 | 18:00 | 219 | 12:00 | Barisal | 245 | 19:00 | 240 | 21:00
| Rajshahi | 238 | 4:00 | 225 | 12:00 | Bhola 225 MW | 246 | 3:00 | 241 | 9:00
| Khulna South | 244 | 6:00 | 233 | 8:00 | AKSML | 244 | 19:00 | 228 | 12:00
| Rampura | 235 | 19:30 | 228 | 12:00 | BSRM | 241 | 6:00 | 230 | 12:00
| Haripur | 234 | 18:30 | 227 | 12:00 | Bibiyana | 244 | 19:00 | 238 | 11:00
| Hasnabad | 235 | 19:00 | 230 | 11:00 | Bhulta | 238 | 6:00 | 228 | 12:00
| Shyampur | 235 | 13:00 | 228 | 12:00 | Ashuganj (S) | 327 | 19:30 | 232 | 12:00
| Aminbazar | 236 | 1:00 | 231 | 2:00 | Kaliakoir | 231 | 9:00 | 228 | 1:00
| Tongi | 237 | 5:00 | 230 | 7:00 | GPH | 242 | 13:00 | 230 | 12:00
| Comilla (N) | 237 | 13:00 | 230 | 11:00 | Jhenaidah | 240 | 16:00 | 229 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 6:00 | 131 | 2:00 | PHP | 139 | 13:00 | 132 | 2:00
| Munsiganj | 137 | 18:30 | 131 | 1:00 | Kachua | 140 | 13:00 | 131 | 3:00
| Sonargaon | 136 | 18:30 | 131 | 14:00 | Madanhat | 141 | 8:00 | 134 | 11:00
| Bhulta | 130 | 18:00 | 126 | 1:00 | Hathazari | 142 | 5:00 | 137 | 12:00
| Madanganj | 136 | 13:00 | 130 | 12:00 | Khulshi | 139 | 18:00 |  | 7:00
| Rahim steel | 135 | 18:30 | 131 | 1:00 | Halishahar | 142 | 19:00 | 132 | 12:00
| Ghorasal | 142 | 18:00 | 138 | 1:00 | Baraulia | 142 | 5:00 | 134 | 12:00
| Narsingdi | 136 | 14:00 | 132 | 1:00 | Sikalbaha | 142 | 18:00 | 137 | 13:00
| Haripur(SBU) | 135 | 18:30 | 131 | 1:00 | Dohazari | 138 | 6:00 | 129 | 12:00
| Sreenagar | 137 | 18:30 | 132 | 12:00 | Cox'sbazar | 130 | 9:00 | 122 | 12:00
| Shyampur | 134 | 13:00 | 129 | 12:00 | Chandraghona | 142 | 6:00 | 134 | 12:00
| Shitalakhya | 137 | 13:00 | 131 | 1:00 | Kaptai | 140 | 1:00 | 140 | 1:00
| Matuail | 135 | 6:00 | 131 | 2:00 | A. Khaer Stl. | 141 | 4:00 | 136 | 12:00
| Char Saidpur | 136 | 18:30 | 131 | 1:00 | Bakulia | 141 | 8:00 | 135 | 12:00
| Ullon | 132 | 5:00 | 128 | 12:00 | Julda | 141 | 6:00 | 134 | 12:00
| Hasnabad | 136 | 19:00 | 130 | 11:00 | TK Chemical | 142 | 1:00 | 136 | 19:30
| Magbazar | 132 | 4:00 | 127 | 12:00 | Modern Steel | 141 | 6:00 | 133 | 12:00
| Maniknagar | 138 | 5:00 | 133 | 12:00 | Shahmirpur | 140 | 9:00 | 137 | 5:00
| Bangabhaban | 138 | 5:00 | 133 | 12:00 | Khagrachhari | 141 | 21:00 | 135 | 18:00
| Motijheel | 138 | 5:00 | 133 | 12:00 | Matarbari | 132 | 8:00 | 125 | 12:00
| Narinda | 138 | 5:00 | 133 | 12:00 | Baroiar Hat | 139 | 3:00 | 132 | 22:00
| Kazla | 138 | 5:00 | 133 | 12:00 | Rangamati | 142 | 6:00 | 134 | 12:00
| Dhanmondi | 135 | 13:00 | 131 | 11:00 | Agrabad | 141 | 6:00 | 133 | 12:00
| Lalbag | 138 | 13:00 | 133 | 12:00 | Rampur | 139 | 1:00 | 136 | 6:00
| Madartek | 132 | 13:00 | 127 | 12:00 | Goalpara S/S | 139 | 5:00 | 133 | 12:00
| Dhaka University | 132 | 7:00 | 127 | 12:00 | Khulna Central S/S | 138 | 5:00 | 132 | 8:00
| Aftabnagar | 132 | 7:00 | 128 | 12:00 | Noapara | 138 | 6:00 | 131 | 8:00
| Fatullah | 134 | 13:00 | 130 | 1:00 | Jessore | 136 | 2:00 | 128 | 12:00
| Nawabganj | 138 | 19:00 | 133 | 12:00 | Benapol | 136 | 6:00 | 127 | 12:00
| Keraniganj | 138 | 13:00 | 133 | 12:00 | Jhenida(Old) | 138 | 6:00 | 124 | 12:00
| Banani | 132 | 5:00 | 128 | 11:00 | Bottail | 139 | 6:00 | 131 | 12:00
| Mirpur | 130 | 5:00 | 128 | 12:00 | G.K Project | 142 | 6:00 | 136 | 12:00
| Kalyanpur | 134 | 6:00 | 130 | 11:00 | Faridpur | 140 | 18:30 | 129 | 12:00
| Gulshan | 132 | 6:00 | 127 | 12:00 | Rajbari | 139 | 6:00 | 128 | 12:00
| Uttara | 139 | 18:00 | 134 | 2:00 | Madaripur | 144 | 9:00 | 139 | 1:00
| Uttara New | 139 | 13:00 | 134 | 1:00 | Shariyatpur S/S | 143 | 7:00 | 139 | 20:00
| Kamrangirchar | 137 | 6:00 | 133 | 12:00 | Gopalganj | 142 | 4:00 | 139 | 7:00
| Savar | 134 | 13:00 | 130 | 3:00 | Bagerhat | 137 | 6:00 | 132 | 12:00
| Bhasantec | 139 | 6:00 | 135 | 12:00 | Mongla | 137 | 18:00 | 132 | 8:00
| Agargaon | 140 | 13:00 | 135 | 12:00 | Satkhira | 136 | 18:00 | 136 | 18:00
| Satmosjid | 139 | 6:00 | 134 | 12:00 | Gallamari | 142 | 6:00 | 133 | 12:00
| Old Tongi | 140 | 13:00 | 136 | 11:00 | Magura | 138 | 18:00 | 126 | 8:00
| Kabirpur | 137 | 13:00 | 132 | 12:00 | Narail | 138 | 4:00 | 123 | 12:00
| Manikgonj | 134 | 13:00 | 130 | 12:00 | Chuadanga | 136 | 5:00 | 121 | 12:00
| Joydevpur | 141 | 18:30 | 135 | 12:00 | Barisal(N) | 143 | 16:00 | 140 | 1:00
| New Tongi | 140 | 13:00 | 135 | 4:00 | Barisal (S) | 141 | 3:00 | 139 | 12:00
| Kodda | 141 | 13:00 | 132 | 1:00 | Patuakhali(S) | 140 | 9:00 | 136 | 21:00
| Dhamrai | 141 | 13:00 | 136 | 12:00 | Bhandaria | 141 | 5:00 | 137 | 20:00
| Rajendrapur | 139 | 19:00 | 130 | 3:00 | Borguna | 142 | 5:00 | 138 | 21:00
| Bashundara | 139 | 18:00 | 134 | 2:00 | Jhenaidah(New) | 138 | 6:00 | 133 | 19:30
| Purbachal | 133 | 7:00 | 129 | 12:00 | Ishurdi | 139 | 4:00 | 133 | 12:00
| Tongi Millgate | 138 | 7:00 | 134 | 16:00 | Ruppur Paromanobik | 139 | 5:00 | 130 | 9:00
| Bashundhara Cement |  |  |  |  | Natore | 138 | 3:00 | 129 | 12:00
| Valuka | 132 | 0:00 | 118 | 8:00 | Bogra | 140 | 22:00 | 128 | 12:00
| Tangail | 136 | 0:00 | 130 | 12:00 | Noagaon | 133 | 3:00 | 122 | 8:00
| Mymensing | 134 | 0:00 | 121 | 9:00 | Rajshahi | 137 | 19:00 | 128 | 12:00
| Kishorganj | 135 | 0:00 | 125 | 7:00 | Rajshahi New | 137 | 19:00 | 127 | 12:00
| Netrokona | 132 | 0:00 | 117 | 9:00 | C.Nawabganj | 136 | 22:00 | 130 | 13:00
| Jamalpur | 140 | 22:00 | 129 | 9:00 | Amnura | 137 | 19:00 | 124 | 12:00
| Sherpur | 138 | 22:00 | 124 | 7:00 | Pabna | 139 | 24:00 | 132 | 12:00
| Srimongal | 140 | 4:00 | 137 | 7:00 | Shahjadpur | 143 | 1:00 | 134 | 12:00
| Shahjibazar | 138 | 4:00 | 135 | 12:00 | Serajganj | 138 | 4:00 | 128 | 12:00
| Fenchuganj | 140 | 6:00 | 136 | 18:00 | Niyamatpur | 132 | 3:00 | 117 | 12:00
| Khulawara | 140 | 6:00 | 137 | 18:00 | Joypurhat | 135 | 5:00 | 120 | 8:00
| Sylhet | 135 | 3:00 | 131 | 12:00 | Sherpur(Bogura) | 139 | 8:00 | 129 | 12:00
| Chatak | 137 | 7:00 | 133 | 12:00 | Mohastangor | 138 | 18:00 | 124 | 12:00
| Sunamganj | 135 | 8:00 | 128 | 18:30 | Bhangura | 139 | 1:00 | 131 | 12:00
| Biani Bazar | 136 | 7:00 | 131 | 12:00 | Rangpur | 134 | 5:00 | 118 | 12:00
| Comilla(s) | 130 | 3:00 | 125 | 18:30 | Lalmonirhat | 133 | 23:00 | 117 | 12:00
| Comilla(n) | 139 | 9:00 | 135 | 11:00 | Saidpur | 134 | 23:00 | 117 | 8:00
| Chandpur | 140 | 13:00 | 129 | 22:00 | Purbasadipur | 133 | 13:00 | 115 | 12:00
| Feni | 138 | 13:00 | 131 | 2:00 | Thakurgaon | 133 | 13:00 | 111 | 8:00
| Chowmuhani | 135 | 13:00 | 129 | 18:00 | Palashbari | 134 | 18:00 | 120 | 12:00
| Ashuganj | 141 | 14:00 | 139 | 8:00 | Barapukuria | 133 | 18:00 | 119 | 12:00
| Daudkandi | 137 | 13:00 | 132 | 12:00 | Panchagar | 136 | 13:00 | 114 | 8:00
| B.Baria | 137 | 5:00 | 133 | 12:00 | Joldhaka | 131 | 4:00 | 115 | 8:00
| Ramganj | 137 | 13:00 | 128 | 22:00 | Kurigram | 132 | 13:00 | 115 | 8:00
| Chaddagram | 139 | 13:00 | 134 | 1:00 | Mithapukur | 136 | 14:00 | 124 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 98 | 5745 | 2283 | 8028 |  |  |  | QF-LDC-11
0:30 | 54 | 5716.5 | 2303 | 8019.5 | Date: | 2022-03-04
1:00 | 10 | 5688 | 2323 | 8011
1:30 | 42 | 5507 | 2301.5 | 7808.5
2:00 | 74 | 5326 | 2280 | 7606
2:30 | 98 | 5192.5 | 2263 | 7455.5 | [5 empty] | Gen. at Eve. Peak | 9443 | 9443 MW (19:00 )
3:00 | 122 | 5059 | 2246 | 7305 | [6 empty] | 19:00
3:30 | 130 | 4986 | 2214.5 | 7200.5 | [5 empty] | Gen. at Day Peak | 8104 | 8104 MW (12:00 )
4:00 | 138 | 4913 | 2183 | 7096 | [6 empty] | 12:00
4:30 | 138 | 4865 | 2173 | 7038 | [5 empty] | Highest Generation | 9443
5:00 | 138 | 4817 | 2163 | 6980 | [6 empty] | 19:00
5:30 | 119 | 4884 | 2200.5 | 7084.5
6:00 | 100 | 4951 | 2238 | 7189
6:30 | 126 | 5083 | 2246.5 | 7329.5
7:00 | 152 | 5215 | 2255 | 7470
7:30 | 191 | 5291.5 | 2302 | 7593.5
8:00 | 230 | 5368 | 2349 | 7717
8:30 | 186 | 5424.5 | 2337.5 | 7762
9:00 | 142 | 5481 | 2326 | 7807
9:30 | 79 | 5469.5 | 2322.5 | 7792
10:00 | 16 | 5458 | 2319 | 7777
10:30 | 15 | 5453.5 | 2310 | 7763.5
11:00 | 14 | 5449 | 2301 | 7750
11:30 | 92 | 5641 | 2286 | 7927
12:00 | 170 | 5833 | 2271 | 8104
12:30 | 217 | 5985.5 | 2335.5 | 8321
13:00 | 264 | 6138 | 2400 | 8538
13:30 | 140 | 5798.5 | 2305.5 | 8104
14:00 | 16 | 5459 | 2211 | 7670
14:30 | 29 | 5485.5 | 2187.5 | 7673
15:00 | 42 | 5512 | 2164 | 7676
15:30 | 79 | 5428 | 2186 | 7614
16:00 | 116 | 5344 | 2208 | 7552
16:30 | 113 | 5350.5 | 2200 | 7550.5
17:00 | 110 | 5357 | 2192 | 7549
17:30 | 111 | 5434.5 | 2313.5 | 7748
18:00 | 112 | 5512 | 2435 | 7947
18:30 | 186 | 6071.5 | 2623.5 | 8695
19:00 | 260 | 6631 | 2812 | 9443
19:30 | 212 | 6527 | 2843 | 9370
20:00 | 200 | 6428 | 2792 | 9220 |  |  |  | Executive Engineer
20:30 | 163 | 6453 | 2823 | 9276 |  |  |  | Network Operation Division
21:00 | 126 | 6478 | 2854 | 9332
21:30 | 71 | 6340 | 2833 | 9173
22:00 | 16 | 6202 | 2812 | 9014 |  |  |  |  | Page 6 of 7
22:30 | 51 | 6119.5 | 2636.5 | 8756
23:00 | 86 | 6037 | 2461 | 8498
23:30 | 92 | 5891 | 2372 | 8263
24:00 | 98 | 5745 | 2283 | 8028
9443 MW (19:00 )
8104 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-04 |  | Energy |  | 195169360
[13 empty] | 2022-03-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3265 | 716 | 1203 | 0 | 2220 | 480 | 46 | 0 | 0 | 98 | 0 | 0
0:30 | 3155.5 | 715 | 1203 | 0 | 2243.5 | 554.5 | 46 | 0 | 0 | 102 | 0 | 0 | Date: | 2022-03-04
1:00 | 3046 | 714 | 1203 | 0 | 2267 | 629 | 46 | 0 | 0 | 106 | 0 | 0
1:30 | 3049.5 | 714 | 1204 | 0 | 2070.5 | 619.5 | 46 | 0 | 0 | 105 | 0 | 0 | [8 empty] | Total Energy | 195.1694 | Total Energy Gen 195.169 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 195.169 MKWHr
2:00 | 3053 | 714 | 1205 | 0 | 1874 | 610 | 46 | 0 | 0 | 104 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3049.5 | 715 | 1207 | 0 | 1736.5 | 599.5 | 46 | 0 | 0 | 102 | 0 | 0 | [8 empty] | Energy Requirement | 195.1694
3:00 | 3046 | 716 | 1209 | 0 | 1599 | 589 | 46 | 0 | 0 | 100 | 0 | 0
3:30 | 3022 | 692.5 | 1219 | 0 | 1539 | 584 | 46 | 0 | 0 | 98 | 0 | 0 | [6 empty] | Shortage
4:00 | 2998 | 669 | 1229 | 0 | 1479 | 579 | 46 | 0 | 0 | 96 | 0 | 0
4:30 | 2977.5 | 668.5 | 1221 | 0 | 1450 | 579 | 46 | 0 | 0 | 96 | 0 | 0
5:00 | 2957 | 668 | 1213 | 0 | 1421 | 579 | 46 | 0 | 0 | 96 | 0 | 0
5:30 | 2956.5 | 693 | 1220.5 | 0 | 1496.5 | 578 | 46 | 0 | 0 | 94 | 0 | 0
6:00 | 2956 | 718 | 1228 | 0 | 1572 | 577 | 46 | 0 | 0 | 92 | 0 | 0
6:30 | 2959.5 | 718.5 | 1188 | 0 | 1766 | 557 | 46 | 0 | 0 | 87 | 7.5 | 0 |  |  |  |  | Coal
7:00 | 2963 | 719 | 1148 | 0 | 1960 | 537 | 46 | 0 | 0 | 82 | 15 | 0
7:30 | 2968.5 | 719 | 1147 | 0 | 2060.5 | 532.5 | 46 | 0 | 0 | 79 | 41 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2974 | 719 | 1146 | 0 | 2161 | 528 | 46 | 0 | 0 | 76 | 67 | 0
8:30 | 2977.5 | 719 | 1136 | 0 | 2189.5 | 522 | 46 | 0 | 0 | 78 | 94 | 0
9:00 | 2981 | 719 | 1126 | 0 | 2218 | 516 | 46 | 0 | 0 | 80 | 121 | 0
9:30 | 2979.5 | 719 | 1108 | 0 | 2207.5 | 499.5 | 46 | 0 | 0 | 86 | 146.5 | 0
10:00 | 2978 | 719 | 1090 | 0 | 2197 | 483 | 46 | 0 | 0 | 92 | 172 | 0
10:30 | 2997.5 | 719 | 1087.5 | 0 | 2187.5 | 456 | 46 | 0 | 0 | 94 | 176 | 0
11:00 | 3017 | 719 | 1085 | 0 | 2178 | 429 | 46 | 0 | 0 | 96 | 180 | 0
11:30 | 3156.5 | 718.5 | 1092.5 | 0 | 2293 | 329.5 | 46 | 0 | 0 | 99 | 192 | 0
12:00 | 3296 | 718 | 1100 | 0 | 2408 | 230 | 46 | 0 | 0 | 102 | 204 | 0
12:30 | 3178.5 | 718.5 | 1099.5 | 0 | 2704.5 | 257.5 | 40.5 | 0 | 16 | 104 | 202 | 0
13:00 | 3061 | 719 | 1099 | 0 | 3001 | 285 | 35 | 0 | 32 | 106 | 200 | 0
13:30 | 3061 | 719 | 1099 | 0 | 3001 | 285 | 35 | 0 | 32 | 106 | 200 | 0
14:00 | 3061 | 719 | 1099 | 0 | 3001 | 285 | 35 | 0 | 32 | 106 | 200 | 0
14:30 | 3020 | 719.5 | 1103.5 | 0 | 2609 | 354.5 | 35 | 0 | 24 | 99 | 142.5 | 0
15:00 | 2979 | 720 | 1108 | 0 | 2217 | 424 | 35 | 0 | 16 | 92 | 85 | 0
15:30 | 2975 | 719.5 | 1106 | 0 | 2135.5 | 431 | 58 | 0 | 32.5 | 91 | 65.5 | 0
16:00 | 2971 | 719 | 1104 | 0 | 2054 | 438 | 81 | 0 | 49 | 90 | 46 | 0
16:30 | 3020 | 718 | 1117.5 | 0 | 2041.5 | 434 | 63.5 | 0 | 55 | 92 | 33.5 | 0
17:00 | 3020 | 717 | 1131 | 0 | 2029 | 430 | 46 | 0 | 61 | 94 | 21 | 0
17:30 | 3087.5 | 717 | 1090 | 0 | 2131.5 | 435 | 46 | 0 | 132.5 | 98 | 10.5 | 0
18:00 | 3155 | 717 | 1049 | 0 | 2234 | 440 | 46 | 0 | 204 | 102 | 0 | 0
18:30 | 3258 | 717 | 1108 | 0 | 2741.5 | 450 | 46 | 0 | 268.5 | 106 | 0 | 0
19:00 | 3361 | 717 | 1167 | 0 | 3249 | 460 | 46 | 0 | 333 | 110 | 0 | 0
19:30 | 3439 | 717 | 1209 | 0 | 3186 | 560 | 46 | 0 | 107 | 106 | 0 | 0
20:00 | 3433 | 717 | 1195 | 0 | 3064 | 550 | 46 | 0 | 109 | 106 | 0 | 0
20:30 | 3427 | 716.5 | 1214.5 | 0 | 3090.5 | 569.5 | 46 | 0 | 104 | 108 | 0 | 0
21:00 | 3421 | 716 | 1234 | 0 | 3117 | 589 | 46 | 0 | 99 | 110 | 0 | 0
21:30 | 3400 | 716.5 | 1228 | 0 | 2999 | 579 | 46 | 0 | 94.5 | 110 | 0 | 0
22:00 | 3379 | 717 | 1222 | 0 | 2881 | 569 | 46 | 0 | 90 | 110 | 0 | 0
22:30 | 3377.5 | 716.5 | 1212 | 0 | 2715 | 539 | 46 | 0 | 45 | 105 | 0 | 0
23:00 | 3376 | 716 | 1202 | 0 | 2549 | 509 | 46 | 0 | 0 | 100 | 0 | 0
23:30 | 3320.5 | 716 | 1202.5 | 0 | 2384.5 | 494.5 | 46 | 0 | 0 | 99 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.4° C
24:00 | 3265 | 716 | 1203 | 0 | 2220 | 480 | 46 | 0 | 0 | 98 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 195.169 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 195.169 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 0 |  |  | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 946740
2 | Karnaphuli Hydro PP Unit-4 & 5 | [12 empty] | 35 | 35 | 35 | 35 | 0 | [9 empty] | 116000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 0 | 8 | 8 | 8 | 8 | 8 |  | 8 | [5 empty] | 0 | 50545
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 14 | 19 |  | 20 | 20 | 20 | 16 |  | 5 | [9 empty] | 131625
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | [5 empty] | 0 | 51303
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 68 | 34 | [16 empty] | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 601345
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 33 |  | 33 | [5 empty] | 0 | 45072
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [14 empty] | 34 | 35 | 66 | 66 |  | 91 | 95 | 95 | 95 | 60 | 62 | 57 | 644000
17 | Siddhirganj 335 MW CCPP | 206 | 203 | 191 | 204 | 205 | 203 | 150 | 150 | 150 | 150 | 150 | 203 | 180 | 176 | 178 | 168 | 150 | 154 |  | 153 | 155 | 155 | 155 | 153 | 154 | 154 | 4234511
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 70 | 110 | 145 | 145 | 145 | 168 | 238 | 195 | 195 | 145 | 145 | 195 |  | 265 | 290 | 290 | 290 | 260 | 145 | 45 | 3515235
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 310 | 300 | 8135891
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 312624
33 | Ashuganj 225 MW CCPP | 225 | 223 | 224 | 223 | 223 | 224 | 226 | 223 | 183 | 185 | 186 | 213 | 185 | 184 | 183 | 186 | 191 | 198 |  | 182 | 189 | 187 | 186 | 184 | 193 | 182 | 4829000
34 | Ashuganj 450 MW CCPP(South) | 295 | 320 | 320 | 325 | 310 | 290 | 335 | 320 | 305 | 305 | 310 | 335 | 280 | 270 | 275 | 275 | 290 | 320 |  | 305 | 310 | 310 | 305 | 295 | 305 | 295 | 7467000
| Ashuganj 450 MW CCPP(North) | 280 | 310 | 310 | 310 | 290 | 280 | 345 | 345 | 310 | 280 | 260 | 345 | 290 | 260 | 260 | 260 | 265 | 270 |  | 280 | 285 | 280 | 280 | 280 | 300 | 280 | 7352200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 360480
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7066750
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 110 | 110 | 110 | 110 | 110 | 110 | 143 | 165 | 163 | 153 | 152 | 148 | 146 | 149 | 155 | 155 | 156 | 161 |  | 208 | 208 | 209 | 208 | 210 | 210 | 213 | 3622080
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 15 | 27 | 39 | 47 | 47 | 49 | 43 | 35 | 23 | 7 | 0 | [8 empty] | 336590
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 698808
46 | Shajibazar 330 MW CCPP | 158 | 159 | 160 | 160 | 159 | 159 | 160 | 160 | 161 | 159 | 157 | 157 | 158 | 158 | 160 | 160 | 160 | 159 |  | 160 | 160 | 159 | 161 | 160 | 159 | 159 | 3789000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 61 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1279584
48 | Shahjibazar 86MW PP (Shahjibazar) | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 86 | 84 | 86 | 50 | 86 | 86 | 86 | 89 | 30 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 1992960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250020
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 8 | 8 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 162480
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 22 |  | 48 | 48 | 48 | 48 | 53 | 53 | 53 | 1215600
56 | Shahjahanulla 25 MW PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 514032
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 305 | 300 | 305 | 320 | 285 | 280 | 295 | 270 | 270 | 280 | 295 | 260 | 280 | 280 | 290 | 290 |  | 270 | 300 | 280 | 300 | 280 | 280 | 285 | 7162000
| Bibiyana South 400 MW | 370 | 320 | 310 | 250 | 250 | 280 | 250 | 250 | 345 | 370 | 395 | 384 | 330 | 340 | 340 | 340 | 340 | 360 |  | 395 | 400 | 400 | 400 | 400 | 385 | 360 | 8264100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 |  |  |  | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1043602
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531840
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 |  | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 421008
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 419724
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 17 | 17 | 17 | 17 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 430740
63 | Impoprt (Tripura) | 106 | 104 | 100 | 96 | 96 | 92 | 82 | 76 | 80 | 92 | 96 | 102 | 106 | 100 | 92 | 90 | 94 | 102 |  | 110 | 106 | 106 | 110 | 110 | 100 | 98 | 2310720
64 | Malancha, Ctg. EPZ (United) | 41 | 42 | 42 | 42 | 42 | 42 | 39 | 39 | 39 | 21 | 20 | 30 | 30 | 31 | 31 | 27 | 42 | 42 |  | 42 | 42 | 42 | 42 | 41 | 42 | 42 | 912000
65 | Feni 22MW PP (Doreen) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 492480
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 199620
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 606500
68 | Cumilla 25 MW PP (Summit) | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 382910
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 24 | 24 | 24 | 15 | 17 | 14 | 10 | 10 | 10 | 17 | 17 |  | 17 | 30 | 30 | 22 | 30 | 30 | 30 | 558720
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 622600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [7 empty] | 17 | 17 | 17 | 17 | 51 | 114 | 17 | 17 | 17 | 17 | 50 |  | 88 | 88 | 88 | 88 | 17 | 17 | 0 | 721620
| Chowmuhani 113 MW | [20 empty] | 8 | 5 | 8 | 8 | 8 | 0 | 33600
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 147 | 158 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 108 | 108 | 108 | 108 | 109 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3677760
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [12 empty] | 11 | 8 | 8 | 8 | 8 | 8 |  | 20 | [5 empty] | 0 | 88320
79 | Kodda 150MW PP | [12 empty] | 32 | 16 | 16 | 16 | 16 | 16 |  | 49 | [5 empty] | 0 | 144960
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 8 |  |  |  | 5 | 46 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 25 |  | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 974246
| Gazipur 100 MW PP | 52 |  |  |  |  | 19 | 52 | 52 | 52 | 52 | 52 | 65 | 90 | 34 | 34 | 34 | 34 | 34 |  | 84 | 102 | 90 | 90 | 90 | 90 | 90 | 1285800
| Kaptai 7 MW Solar PP | [7 empty] | 2 |  | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 32160
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1349673
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 95 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 88 | 80 | 85 | 86 | 91 | 92 |  | 92 | 92 | 92 | 92 | 80 | 93 | 96 | 2282426
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 22 | [5 empty] | 0 | 34059
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 96 | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 55 | 53 | 53 | 53 | 57 |  | 100 | 104 | 104 | 104 | 104 | 104 | 104 | 2125440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 18 | 10 | 10 | 10 | 10 | 10 |  | 10 | [5 empty] | 0 | 88920
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 25 | 25 | 25 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1138824
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 16 | 16 | 16 | 16 | 40 | 93 | 32 | 32 | 32 | 32 | 64 |  | 93 | 74 | 58 | 58 | 32 | 32 | 0 | 716544
95 | Patenga 50MW PP (Baraka) | 38 | [11 empty] | 12 | 37 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 18 | 18 | 479520
96 | Chattogram 108 MW PP (ECPV) | 102 | 92 | 96 | 102 | 90 | 90 | 88 | 78 | 78 | 72 | 77 | 60 | 60 | 60 | 71 | 73 | 72 | 81 |  | 85 | 87 | 87 | 92 | 94 | 109 | 102 | 2004480
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 5 | 15 | 15 | 15 | 20 | 32 | 30 | 30 | 30 | 30 | 30 |  | 45 | 55 | 30 | 30 | 15 | 15 | 0 | 457874
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 55 | 17 | 17 | 17 | 17 | 17 |  | 55 | 55 | 35 | 35 | 0 |  | 0 | 281359
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2920581
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 15200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1304280
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 198 | 198 | 150 | 100 | 100 | 125 | 150 | 162 | 180 | 180 | 178 | 168 | 170 | 169 | 193 | 192 | 192 | 191 |  | 185 | 185 | 185 | 177 | 177 | 177 | 186 | 4068000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 74 | 34 | 34 | 34 | 36 | 98 | 107 | 105 | 104 | 101 | 124 | 134 | 116 | 97 | 81 | 60 | 60 |  | 125 | 135 | 132 | 138 | 149 | 149 | 149 | 2442960
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 76 | 76 | 76 | 90 | 90 | 90 | 76 | 90 | 40 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2000640
116 | Chandpur 200MW (Desh energy) | [11 empty] | 3 | 56 | 34 | 17 | 17 | 17 | 18 |  | 45 | 17 | 17 | 17 | 0 |  | 0 | 310080
117 | Ashuganj 150MW PP (Midland) | 143 | 137 | 135 | 130 | 95 | 102 | 100 | 102 | 102 | 102 | 100 | 98 | 96 | 92 | 93 | 92 | 85 | 92 |  | 97 | 100 | 107 | 140 | 148 | 145 | 140 | 2679709
118 | Bibiyana-III 400 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3358000
| Jamalpur 115 MW PP (United) | 8 |  |  |  |  | 5 | 30 | 60 | 56 | 56 | 56 | 68 | 101 | 64 | 64 | 45 | 45 | 50 |  | 103 | 103 | 103 | 103 | 103 | 64 | 24 | 1281600
| Anwara 300 MW PP (United) | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 230 | 230 | 230 | 230 | 260 |  | 283 | 283 | 283 | 283 | 283 | 283 | 283 | 6493527
| Juldah unit-2 (Acorn) | 100 | 20 |  |  |  | 14 | 30 | 30 | 30 | 30 | 30 | 46 | 80 | 20 | 20 | 20 | 20 | 25 |  | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 1220160
| Anlima Energy Ltd. | 115 | 115 | 115 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 93 | 68 | 68 | 68 | 68 | 71 |  | 109 | 115 | 115 | 115 | 115 | 115 | 115 | 2161582
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 13 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 435600
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 10 | 20 | 28 | 31 | 29 | 30 | 29 | 23 | 15 | 5 | [9 empty] | 214589
| Chandpur 115(Doreen) | [11 empty] | 5 | 51 | 17 | 17 | 17 | 17 | 21 |  | 70 | 35 | 35 | 35 | 0 |  | 0 | 359040
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1365480
120 | Eastern Zone Total | 5688 | 5326 | 5059 | 4913 | 4817 | 4951 | 5215 | 5368 | 5481 | 5458 | 5449 | 5833 | 6138 | 5459 | 5512 | 5344 | 5357 | 5512 |  | 6631 | 6527 | 6428 | 6478 | 6202 | 6037 | 5745 | 136973506
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 4 | [8 empty] | 6720
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 70 | 17 | 17 | 17 | 24 | 87 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 53 | 0 | 2198880
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 28 | 53 | 72 | 85 | 90 | 84 | 77 | [12 empty] | 527760
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 225 | 225 | 225 | 204 | 204 | 162 | 165 | 132 | 138 | 138 | 152 | 172 | 176 | 140 | 140 | 140 | 143 |  | 190 | 200 | 200 | 220 | 225 | 204 | 200 | 4421645
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 16 | 18 | 23 | 22 | 22 | 22 | 22 | 331083
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 79 | 79 | 79 | 79 | 57 | 79 | 79 | 79 | 79 | 79 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2097777
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 7 | 7 | 7 | 6 | 6 | 5 | 7 |  | 8 | 8 | 9 | 9 | 8 | 8 | 8 | 156585
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 3 | 8 | 10 |  |  |  |  | 13824
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 714 | 714 | 716 | 669 | 668 | 718 | 719 | 719 | 719 | 719 | 719 | 718 | 719 | 719 | 720 | 719 | 717 | 717 |  | 717 | 717 | 717 | 716 | 717 | 716 | 716 | 17218181
147 | Bheramara 410 MW CCPP | 255 | 265 | 300 | 290 | 290 | 285 | 300 | 305 | 310 | 310 | 330 | 370 | 370 | 300 | 300 | 300 | 300 | 350 |  | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 7234560
148 | Payra 1320 MW | 350 | 330 | 310 | 300 | 300 | 300 | 260 | 250 | 240 | 230 | 230 | 230 | 250 | 240 | 240 | 240 | 230 | 240 |  | 260 | 360 | 350 | 390 | 370 | 310 | 280 | 7729200
149
150 | Barapukuria TPP Unit-1 | 79 | 80 | 79 | 79 | 79 | 77 | 77 | 78 | 76 | 54 | [16 empty] | 843054
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 |  | 35 | 95 | 184 | 198 | 200 | 200 |  | 200 | 200 | 200 | 199 | 199 | 199 | 200 | 4335800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 34 |  | 34 | [6 empty] | 54166
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 37740
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 163 | 163 | 166 | 171 | 173 | 173 | 140 | 140 | 140 | 140 | 140 | 200 | 206 | 160 | 160 | 160 | 160 | 160 |  | 183 | 220 | 221 | 222 | 220 | 220 | 192 | 4511118
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 4 |  | 4 | [6 empty] | 10672
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [14 empty] | 0 | 248880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 149454
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 25 | [5 empty] | 0 | 20694
167 | Katakhali 50 MW Peaking PP | [17 empty] | 16 |  | 37 | [6 empty] | 38501
168 | Santahar 50 MW Peaking PP | [17 empty] | 31 |  | 32 | [6 empty] | 54655
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 8 | 8 | 8 | 8 | 24 | 52 | 8 | 8 | 8 | 8 | 8 |  | 52 | 43 | 24 | 24 | 8 | 8 | 0 | 293616
170 | Chapainawabganj 100 MW Peaking PP | [15 empty] | 33 | 41 | 66 |  | 90 | 99 | 99 | 99 | 90 | 0 | 0 | 457928
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 99 | 113 | 113 | 113 | 113 | 2371104
172 | Confidence Power Bogura Unit-1 113 MW | [5 empty] | 25 | 50 | 70 | 70 | 70 | 70 | 100 | 50 | 50 | 50 | 50 | 35 | 60 |  | 113 | 113 | 113 | 113 | 113 | 50 | 10 | 1388640
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 22 | 50 | 50 | 50 | 50 | 75 | 97 | 45 | 34 | 34 | 34 | 80 |  | 104 | 113 | 113 | 113 | 113 | 49 | 33 | 1159200
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 6 | 5 | 5 | 4 | 3 | 2 | 0 | [8 empty] | 39154
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 76 | 31 | 18 | 18 | 18 | 18 |  | 36 | 36 |  |  |  |  | 0 | 245263
178