## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-06-20 | Thursday
|  | Date (day): | 2019-06-20 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13340 | MW |  |  | (b) At Evening Peak Hour : |  | 15226 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-06-19 | 2019-06-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 65 | 65 | 65 |  | 20
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 190 | 200 | 200
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 320 | 255 | 255 |  | 110 | ST under maint.
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 63 | 63 | 70 | 70 |  |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 106 | 108 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 347 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 26 | 55 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 335 | 338 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 15 | 55 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 188 | 260 | 335 | 335
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 10 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 5 | 50 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 213 | 180 | 20 | 20 |  |  | ST Blowing
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 70 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 13 | 48 | 49 | 49
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 80 | 125 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 67 | 70 | 70 | 70 |  | 38 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 53 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 35 | 0 | 50 | 50
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 5 | 114 | 100 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300 |  |  | low demand
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100 |  |  | low demand
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100 |  |  | low demand
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 110 | 149 | 149 | 149
37 | Gazipur 100 MW |  | HFO | RPCL | 100 MW | 105 | 105 | 106 | 106 | 100 | 100
| Dhaka area Total |  |  |  |  | 6039 | 5803 | 2667 | 3551 | 3919 | 4619 | 640 | 360
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 5 | 100 | 100 | 80 |  | Gas Shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 13 | 8 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 12.5 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 47 | 46 | 46
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 38 | 40 | 40 |  | 190 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 204 | 210 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 90 | 135 | 135
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 33 | 32 | 32 |  | 19 | Engine problem
47 | Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
48 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 70 | 85 | 85
49 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
50 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 10 | 100 | 100
51 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
52 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 30 | 6 | 25
53 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 38 | 32 | 100 | 100 |  | 8
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 5.8 | 0 | 3 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 304 | 304 | 300 | 300
| Chattogram area Total |  |  |  |  | 1866 | 1786 | 1238.3 | 1180 | 1615 | 1626 | 140 | 257
54 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 200 | 221 | 221
56 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
57 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 360 | 360
58 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 |  | 45 | Gas Line problem.
59 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 53 | 55 | 55
60 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
61 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 16 | 16 | 16 | 179 |  | Gas shortage
62 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 40 | 40 | 40 | 40 |  | 11 | Engine problem
63 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 133 | 0 | 150 |  |  | low demand
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50 |  |  | low demand
66 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 100 | 100
67 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 160 | 200 | 200 | 200
68 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
69 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 158 | 152 | 136 | 181
70 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
72 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 20 | 20
73 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1608 | 1743 | 1731 | 2176 | 525 | 56
74 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 140 | 140 | 144 | 144 | 58 |  | GT-1 Under maint.
75 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 21 | 21
76 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 84 | 85 | 87 | 87
77 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
78 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 81 | 180 | 100 | 200
79 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 94 | 93 | 100 | 100 |  | 15
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 422.1 | 520 | 454 | 552 | 58 | 0
80 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 54 | 56 | 60 | 60
81 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 57 | 57 | 58 | 58
82 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
83 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 20 | 251 | 300 | 330 |  | 150
84 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 50 | 50
85 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 49 | 50 | 50
86 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 59 | 66 | 66 |  |  | FGMO
88 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 80 | 86 | 86
89 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 45 | 45 | 45
90 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 110 | 120 | 130 | 130
91 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 19 | 19
92 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 47 | 45 | 45
93 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25
94 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 265 | 300 | 341 | 341
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 291 | 288 | 285 | 285 |  |  | On test
95 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1324 | 1542 | 1744 | 1774 | 0 | 150
96 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 28 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 932 | 925 | 945 | 945
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
97 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 99 | 115 | 115
98 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 0 | 38
99 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 120 | 225
100 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 0 | 80
101 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint. |  | 20/06/2019
102 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
104 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
105 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 70 | 87 | 105 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1281 | 1576 | 1430 | 1785 | 0 | 410
106 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
107 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 26
108 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 27 | 37 | 33 | 33
109 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 172 | 172 | 172 | 190
110 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 97 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 296 | 429 | 410 | 454 | 0 | 0
111 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
112 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
113 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 27 | 0 | 35
114 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 6 | 33 | 6 | 50
115 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 8 | 32 | 43
116 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 44 | 44
117 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 196 | 169 | 214 | 214 |  |  | FGMO
118 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 160 | 220 | 220 |  |  | FGMO
119 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 181 | 220 | 220
120 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 420 | 408 | 414 | 414
121 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 28
122 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
123 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 11 | 12 | 12
124 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
125 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 50 | 50 | 52 | 52
126 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 68 | 93 | 95 | 95
127 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
128 | Confidence Bogura-2 (CPBL) |  | HFO | IPP | 113 MW | 113 | 113 | 108 | 108 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1335 | 1458 | 1702 | 1870 | 0 | 100
129 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 63 | 62 | 62
130 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 249 | 240 | 250 | 250 | 24
131 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
132 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 18
| Confidence Rangpur |  | HFO | IPP | 113 MW | 0 | 0 | 25 | 20 | 23 | 23
| Rangpur Area Total |  |  |  |  | 564 | 484 | 337 | 356 | 335 | 370 | 24 | 85
| Total |  |  |  |  | 18539 | 17996 | 10508.4 | 12355 | 13340 | 15226 | 1387 | 1418
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10027.8459 | 11790 | 12729.9555 | 14529.7078
A. |  | 2019-06-19 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 12398 | MW at | 24:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9067.2 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12355 | MW
3 | Day peak Generation : |  |  | 10508.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11790 | MW
4 | Evening peak Generation : |  |  | 12355 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 261.5326 | MKWHr | By Solar | 0.1571 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 160.6212 | MKWHr |  | By Oil: | 66.5586 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 7.5357 | MKWHr |  | By Hydro: | 0.79998 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1387 | MW | Dhaka | 4337 | 4337 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1418 | MW | Chittagong | 1031 | 1031 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2805 | MW | Khulna | 1533 | 1533 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1401.94 | MMCFD |  |  | Rajshahi | 1262 | 1262 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 108922299.49 | ii) Oil : | Taka | 451532176.85 | Comilla | 1096 | 1096 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 32436996.3 | Total | Taka | 592891472.64 | Mymensingh | 929 | 929 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.6555 | MKWHr. | Sylhet | 500 | 500 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -340 | MW (E to W) at | 21:00 | hrs | Barisal | 351 | 351 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -340 | MW at | 21:00 | hrs | Rangpur | 751 | 751 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.6° C |  |  | Total | 11790 | 11790 |  | 0
B. |  | 2019-06-20 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 36.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15226 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | 2526 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 267.9032 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8883.8 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2793 | MKWHr. | ii) HVDC Flow at Peak Time |  | 925 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5808 | MKWHr. | iii) Maximum HVDC Flow : |  | 933 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.42 |  | (b) Today: | 75.42 |  | (c) Rule Curve: |  | 80.76
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-06-19
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 150 | 0 | 350 | 107 | 50 | 328 | 354 | 0 | 0 | 400 | 260 | 0 | 30 | 0 | 200 | 0 | 0 | 0 | 0 | 16 | 130 | 0 | 71 | 0 | 26 | 54 | 55 | 55 | 22 | 25 | 24 | 25 | 33 | 49 | 0 | 36 | 0 | 100 | 120 | 17 | 204 | 0 | 0 | 0 | 0 | 25 | 0 | 34 | 40 | 44 | 47 | 21 | 30 | 100 | 0 | 0 | 330 | 330 | 215 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 146 | 145 | 85 | 21 | 0 | 54 | 57 | 50 | 49 | 130 | 197 | 40 | 82 | 46 | 112 | 0 | 46 | 10 | 275 | 15 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 133 | 0 | 100 | 200 | 0 | 294 | 95 | 106 | 0 | 0 | 304 |  | 933 | 0 | 0 | 0 | 99 | 10 | 0 | 0 | 32 | 25 | 40 | 171 | 38 | 110 | 0 | 0 | 60 | 43 | 0 | 93 | 6 | 43 | 44 | 51 | 27 | 22 | 13 | 11 | 0 | 63 | 249 | 0 | 0 | 182 | 0 | 178 | 0 | 98 | 99 | 205 | 0 | 414 | 70 | 0 | 108 | 88 | 23 |  | 7888 | 3648 | 11536 | 4548 | 933 | 2330 | 2793 | 312 | 36 | 438 | 146 | 0 | 0 | 75.32
2:00 | 35 | 0 | 150 | 0 | 350 | 107 | 50 | 330 | 304 | 0 | 0 | 400 | 265 | 0 | 30 | 0 | 200 | 0 | 0 | 0 | 0 | 16 | 98 | 0 | 71 | 0 | 7 | 54 | 35 | 35 | 22 | 25 | 24 | 25 | 33 | 49 | 0 | 35 | 0 | 100 | 120 | 17 | 204 | 0 | 16 | 0 | 0 | 25 | 0 | 17 | 10 | 44 | 41 | 21 | 30 | 100 | 0 | 0 | 330 | 330 | 216 | 16 | 95 | 0 | 55 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 148 | 144 | 85 | 21 | 0 | 54 | 57 | 50 | 50 | 130 | 197 | 53 | 82 | 44 | 112 | 0 | 46 | 10 | 280 | 15 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 102 | 0 | 100 | 200 | 0 | 293 | 96 | 106 | 0 | 0 | 304 |  | 929 | 0 | 0 | 0 | 74 | 20 | 0 | 0 | 32 | 0 | 40 | 171 | 37 | 110 | 0 | 0 | 60 | 35 | 0 | 93 | 6 | 43 | 44 | 51 | 27 | 22 | 13 | 11 | 0 | 63 | 249 | 0 | 0 | 187 | 0 | 183 | 0 | 97 | 70 | 202 | 0 | 370 | 70 | 0 | 108 | 88 | 23 |  | 7699 | 3528 | 11227 | 4580 | 929 | 2238 | 2619 | 312 | 35 | 366 | 148 | 0 | 0 | 75.34
3:00 | 35 | 0 | 150 | 0 | 350 | 106 | 50 | 338 | 304 | 0 | 0 | 400 | 260 | 0 | 15 | 0 | 200 | 0 | 0 | 0 | 0 | 7 | 64 | 0 | 72 | 0 | 6 | 54 | 18 | 17 | 22 | 25 | 20 | 25 | 33 | 24 | 0 | 34 | 0 | 100 | 120 | 17 | 205 | 0 | 120 | 0 | 0 | 25 | 0 | 17 | 10 | 16 | 47 | 21 | 30 | 100 | 0 | 0 | 330 | 330 | 216 | 16 | 95 | 0 | 55 | 5 | 40 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 140 | 145 | 85 | 21 | 0 | 55 | 57 | 50 | 50 | 130 | 197 | 63 | 82 | 45 | 114 | 0 | 46 | 10 | 290 | 15 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 34 | 0 | 100 | 200 | 0 | 293 | 96 | 106 | 0 | 0 | 304 |  | 930 | 0 | 0 | 0 | 66 | 30 | 0 | 0 | 32 | 0 | 40 | 172 | 33 | 80 | 0 | 0 | 60 | 0 | 0 | 93 | 6 | 43 | 43 | 51 | 27 | 22 | 13 | 11 | 0 | 63 | 249 | 0 | 0 | 193 | 0 | 188 | 0 | 97 | 50 | 202 | 0 | 370 | 70 | 0 | 108 | 88 | 23 |  | 7566 | 3453 | 11019 | 4715 | 930 | 2244 | 2338 | 312 | 34 | 306 | 140 | 0 | 0 | 75.36
4:00 | 35 | 0 | 150 | 0 | 350 | 106 | 50 | 328 | 304 | 0 | 0 | 400 | 255 | 0 | 15 | 0 | 170 | 0 | 0 | 0 | 0 | 7 | 48 | 0 | 72 | 0 | 6 | 54 | 18 | 17 | 22 | 25 | 20 | 25 | 33 | 24 | 0 | 34 | 0 | 100 | 120 | 17 | 205 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 10 | 12 | 47 | 21 | 39 | 100 | 0 | 0 | 330 | 310 | 215 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 142 | 147 | 85 | 21 | 0 | 55 | 57 | 50 | 50 | 130 | 198 | 63 | 82 | 45 | 111 | 0 | 46 | 10 | 275 | 23 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 15 | 0 | 100 | 160 | 0 | 298 | 96 | 106 | 0 | 0 | 304 |  | 930 | 0 | 0 | 0 | 66 | 60 | 0 | 0 | 32 | 0 | 40 | 172 | 32 | 80 | 0 | 0 | 60 | 0 | 0 | 38 | 6 | 43 | 0 | 46 | 27 | 22 | 13 | 11 | 0 | 64 | 249 | 0 | 0 | 193 | 0 | 188 | 0 | 97 | 0 | 202 | 0 | 370 | 70 | 0 | 108 | 88 | 23 |  | 7435 | 3330 | 10765 | 4682 | 930 | 2237 | 2222 | 313 | 34 | 205 | 142 | 0 | 0 | 75.38
5:00 | 35 | 0 | 150 | 0 | 330 | 106 | 50 | 329 | 304 | 0 | 0 | 370 | 250 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 72 | 0 | 6 | 54 | 18 | 17 | 22 | 25 | 20 | 25 | 33 | 24 | 0 | 34 | 0 | 100 | 120 | 17 | 205 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 10 | 12 | 46 | 21 | 39 | 100 | 0 | 0 | 300 | 310 | 184 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 114 | 147 | 85 | 21 | 0 | 55 | 57 | 50 | 50 | 130 | 195 | 50 | 82 | 45 | 112 | 0 | 46 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 15 | 0 | 100 | 160 | 0 | 250 | 96 | 106 | 0 | 0 | 296 |  | 930 | 0 | 0 | 0 | 16 | 105 | 0 | 0 | 0 | 0 | 40 | 172 | 32 | 32 | 0 | 0 | 60 | 0 | 0 | 38 | 6 | 43 | 0 | 25 | 27 | 22 | 13 | 11 | 0 | 64 | 249 | 0 | 0 | 186 | 0 | 181 | 0 | 97 | 0 | 196 | 0 | 370 | 70 | 0 | 108 | 88 | 24 |  | 7194 | 3205 | 10399 | 4520 | 930 | 2202 | 2068 | 313 | 34 | 218 | 114 | 0 | 0 | 75.4
6:00 | 35 | 0 | 150 | 0 | 300 | 107 | 50 | 327 | 274 | 0 | 0 | 340 | 270 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 6 | 54 | 18 | 17 | 22 | 25 | 20 | 25 | 33 | 24 | 0 | 34 | 0 | 100 | 120 | 8 | 205 | 0 | 90 | 0 | 0 | 33 | 0 | 0 | 10 | 12 | 40 | 21 | 38 | 100 | 0 | 0 | 270 | 280 | 184 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 106 | 147 | 85 | 21 | 0.2 | 56 | 57 | 53 | 50 | 100 | 195 | 42 | 83 | 45 | 110 | 0 | 46 | 9 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 15 | 0 | 70 | 95 | 0 | 250 | 96 | 106 | 0 | 0.4 | 298 |  | 930 | 0 | 0 | 0 | 16 | 115 | 0 | 0 | 0 | 0 | 0 | 172 | 27 | 0 | 0 | 0 | 60 | 0 | 0 | 38 | 6 | 0 | 0 | 8 | 0 | 22 | 13 | 8 | 0 | 65 | 249 | 0 | 0 | 162 | 0 | 159 | 0 | 97 | 0 | 183 | 0 | 300 | 22 | 0 | 108 | 72 | 20 |  | 6623.6 | 2852 | 9475.6 | 4267 | 930 | 2030 | 1625 | 314 | 34 | 169 | 106 | 0.6 | 0 | 75.42
7:00 | 35 | 0 | 150 | 0 | 270 | 54 | 50 | 330 | 275 | 0 | 0 | 340 | 275 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 18 | 17 | 19 | 25 | 19 | 25 | 33 | 24 | 0 | 38 | 0 | 100 | 120 | 8 | 205 | 0 | 90 | 0 | 0 | 33 | 0 | 0 | 10 | 0 | 13 | 21 | 29 | 100 | 0 | 0 | 270 | 280 | 186 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 106 | 145 | 85 | 22 | 0.5 | 56 | 57 | 50 | 50 | 100 | 195 | 49 | 80 | 45 | 72 | 0 | 12 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0.5 | 70 | 17 | 0 | 250 | 96 | 106 | 0 | 1.2 | 298 |  | 930 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 27 | 0 | 0 | 0 | 60 | 0 | 0 | 38 | 6 | 8 | 0 | 0 | 0 | 22 | 13 | 8 | 0 | 64 | 249 | 0 | 0 | 160 | 0 | 157 | 0 | 97 | 0 | 172 | 0 | 300 | 17 | 0 | 108 | 53 | 20 |  | 6266.2 | 2801 | 9067.2 | 4189 | 930 | 1950 | 1381 | 313 | 38 | 158 | 106 | 2.2 | 0 | 75.44
8:00 | 35 | 0 | 150 | 0 | 270 | 54 | 50 | 331 | 302 | 0 | 0 | 380 | 283 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 18 | 17 | 19 | 25 | 19 | 25 | 33 | 24 | 0 | 38 | 0 | 100 | 120 | 8 | 204 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 10 | 0 | 24 | 21 | 12 | 100 | 0 | 0 | 270 | 280 | 198 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 122 | 141 | 85 | 21 | 0.9 | 57 | 57 | 50 | 50 | 100 | 194 | 61 | 80 | 45 | 85 | 0 | 12 | 9 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 6 | 20 | 17 | 0 | 250 | 96 | 106 | 0 | 3.5 | 291 |  | 930 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 38 | 6 | 8 | 0 | 0 | 0 | 22 | 13 | 8 | 0 | 64 | 249 | 0 | 0 | 161 | 0 | 159 | 0 | 97 | 0 | 178 | 0 | 300 | 17 | 0 | 108 | 54 | 20 |  | 6336.4 | 2802 | 9138.4 | 4229 | 930 | 1995 | 1343 | 313 | 38 | 158 | 122 | 10.4 | 0 | 75.46
9:00 | 35 | 0 | 150 | 0 | 300 | 54 | 50 | 365 | 304 | 0 | 0 | 400 | 250 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 60 | 0 | 6 | 54 | 36 | 35 | 19 | 25 | 22 | 25 | 33 | 27 | 0 | 38 | 0 | 100 | 120 | 8 | 205 | 0 | 132 | 0 | 0 | 32 | 0 | 0 | 10 | 0 | 26 | 21 | 3 | 100 | 0 | 0 | 300 | 300 | 200 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 138 | 141 | 85 | 21 | 1.4 | 56 | 57 | 50 | 50 | 130 | 196 | 61 | 80 | 45 | 117 | 0 | 12 | 9 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 7 | 4.5 | 50 | 17 | 0 | 250 | 95 | 106 | 0 | 4.1 | 304 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 38 | 6 | 8 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 63 | 249 | 0 | 0 | 193 | 0 | 192 | 0 | 96 | 0 | 178 | 0 | 350 | 17 | 0 | 108 | 54 | 20 |  | 6782 | 2916 | 9698 | 4517 | 932 | 2106 | 1487 | 312 | 38 | 158 | 138 | 10 | 0 | 75.15
10:00 | 35 | 0 | 150 | 0 | 300 | 77 | 50 | 364 | 305 | 0 | 0 | 400 | 215 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 69 | 0 | 6 | 54 | 36 | 35 | 19 | 25 | 22 | 25 | 33 | 0 | 0 | 40 | 0 | 100 | 120 | 8 | 207 | 0 | 132 | 0 | 0 | 33 | 0 | 0 | 10 | 0 | 41 | 21 | 2 | 100 | 0 | 0 | 330 | 300 | 206 | 16 | 100 | 0 | 54 | 5 | 40 | 0 | 0 | 7 | 21 | 8 | 25 | 20 | 140 | 140 | 85 | 20 | 1.9 | 56 | 57 | 53 | 47 | 130 | 193 | 59 | 80 | 44 | 118 | 0 | 37 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 31 | 6.1 | 100 | 38 | 0 | 250 | 94 | 106 | 0 | 3.3 | 304 |  | 933 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 68 | 6 | 8 | 0 | 0 | 0 | 18 | 10 | 8 | 0 | 63 | 249 | 0 | 0 | 203 | 0 | 201 | 0 | 97 | 0 | 191 | 0 | 405 | 17 | 0 | 108 | 58 | 23 |  | 6941.3 | 3039 | 9980.3 | 4593 | 933 | 2205 | 1558 | 312 | 40 | 188 | 140 | 11.3 | 0 | 75.48
11:00 | 35 | 0 | 150 | 0 | 0 | 100 | 63 | 345 | 310 | 0 | 0 | 430 | 200 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 69 | 0 | 12 | 54 | 36 | 35 | 19 | 25 | 22 | 16 | 33 | 15 | 0 | 39 | 0 | 100 | 120 | 8 | 206 | 0 | 137 | 0 | 0 | 33 | 0 | 0 | 10 | 0 | 45 | 21 | 2 | 100 | 0 | 0 | 360 | 270 | 205 | 16 | 50 | 0 | 50 | 5 | 40 | 0 | 0 | 46 | 19 | 8 | 33 | 20 | 152 | 137 | 84 | 21 | 2 | 55 | 58 | 50 | 50 | 163 | 208 | 59 | 82 | 44 | 125 | 0 | 44 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 43 | 14.3 | 100 | 70 | 1 | 285 | 94 | 106 | 0 | 4.7 | 303 |  | 932 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 68 | 6 | 8 | 0 | 25 | 0 | 18 | 10 | 8 | 0 | 63 | 249 | 0 | 0 | 195 | 0 | 201 | 0 | 97 | 0 | 181 | 0 | 400 | 17 | 0 | 108 | 71 | 23 |  | 6915 | 3093 | 10008 | 4295 | 932 | 2309 | 1744 | 312 | 39 | 204 | 152 | 21 | 0 | 75.49
12:00 | 35 | 0 | 150 | 0 | 0 | 102 | 63 | 351 | 335 | 26 | 0 | 430 | 188 | 15 | 0 | 10 | 213 | 0 | 0 | 0 | 0 | 64 | 80 | 5 | 67 | 0 | 13 | 54 | 55 | 35 | 19 | 25 | 27 | 16 | 33 | 35 | 0 | 38 | 0 | 100 | 120 | 13 | 205 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 70 | 38 | 45 | 21 | 4 | 100 | 0 | 0 | 360 | 300 | 183 | 16 | 50 | 0 | 51 | 5 | 40 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 158 | 140 | 84 | 21 | 2.1 | 54 | 57 | 53 | 50 | 163 | 20 | 59 | 78 | 43 | 110 | 0 | 44 | 10 | 265 | 16 | 11 | 0 | 5 | 0 | 0 | 81 | 0 | 110 | 12.5 | 100 | 160 | 50 | 291 | 94 | 106 | 0 | 5.8 | 304 |  | 932 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 68 | 6 | 8 | 0 | 50 | 0 | 18 | 8 | 8 | 0 | 63 | 249 | 0 | 0 | 196 | 0 | 194 | 0 | 97 | 0 | 196 | 0 | 420 | 70 | 0 | 108 | 70 | 25 |  | 7259.4 | 3249 | 10508.4 | 4121 | 932 | 2322 | 2337 | 312 | 38 | 268 | 158 | 20.4 | 0 | 0
13:00 | 35 | 0 | 188 | 0 | 0 | 100 | 63 | 329 | 305 | 26 | 0 | 430 | 224 | 88 | 0 | 30 | 150 | 0 | 0 | 0 | 0 | 100 | 125 | 40 | 67 | 0 | 13 | 54 | 36 | 35 | 19 | 25 | 30 | 25 | 33 | 42 | 0 | 38 | 0 | 100 | 120 | 19 | 204 | 0 | 130 | 0 | 0 | 33 | 0 | 0 | 70 | 82 | 45 | 21 | 8 | 100 | 0 | 0 | 330 | 360 | 184 | 16 | 50 | 0 | 50 | 5 | 40 | 0 | 0 | 52 | 19 | 8 | 33 | 20 | 166 | 142 | 84 | 21 | 1.6 | 54 | 57 | 53 | 49 | 130 | 100 | 40 | 78 | 43 | 95 | 0 | 45 | 9 | 260 | 16 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 149 | 19.3 | 100 | 195 | 130 | 291 | 94 | 106 | 0 | 2.8 | 304 |  | 932 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 28 | 0 | 0 | 0 | 50 | 8 | 0 | 68 | 6 | 8 | 0 | 49 | 0 | 18 | 8 | 8 | 0 | 63 | 249 | 0 | 0 | 181 | 0 | 180 | 0 | 97 | 0 | 184 | 0 | 375 | 105 | 0 | 108 | 70 | 23 |  | 7709.7 | 3199 | 10908.7 | 4115 | 932 | 2210 | 2791 | 312 | 38 | 321 | 166 | 23.7 | 0 | 75.19
14:00 | 40 | 0 | 190 | 0 | 75 | 102 | 50 | 345 | 274 | 55 | 0 | 400 | 250 | 99 | 0 | 30 | 160 | 0 | 0 | 0 | 0 | 100 | 127 | 54 | 67 | 0 | 13 | 54 | 37 | 35 | 19 | 25 | 30 | 25 | 33 | 49 | 0 | 38 | 0 | 95 | 120 | 25 | 203 | 0 | 100 | 0 | 0 | 33 | 0 | 0 | 70 | 83 | 46 | 21 | 5 | 100 | 0 | 0 | 300 | 350 | 194 | 16 | 50 | 0 | 50 | 5 | 40 | 0 | 0 | 52 | 21 | 8 | 33 | 20 | 170 | 139 | 76 | 21 | 1.8 | 56 | 57 | 53 | 49 | 100 | 102 | 59 | 80 | 43 | 110 | 0 | 45 | 9 | 260 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 149 | 17.2 | 100 | 200 | 130 | 260 | 93 | 106 | 0 | 5.9 | 304 |  | 933 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 27 | 0 | 0 | 0 | 50 | 8 | 0 | 68 | 6 | 8 | 0 | 49 | 0 | 18 | 8 | 8 | 0 | 63 | 249 | 0 | 0 | 191 | 0 | 190 | 0 | 97 | 0 | 182 | 0 | 340 | 70 | 0 | 108 | 71 | 23 |  | 7761.9 | 3148 | 10909.9 | 4189 | 933 | 2071 | 2849 | 312 | 38 | 323 | 170 | 24.9 | 0 | 75.2
15:00 | 65 | 0 | 190 | 0 | 96 | 101 | 50 | 365 | 339 | 80 | 0 | 450 | 201 | 100 | 5 | 55 | 210 | 0 | 0 | 0 | 0 | 100 | 127 | 72 | 59 | 0 | 13 | 54 | 37 | 35 | 19 | 25 | 28 | 25 | 33 | 48 | 0 | 38 | 0 | 95 | 120 | 25 | 203 | 0 | 104 | 0 | 0 | 33 | 0 | 0 | 40 | 82 | 46 | 21 | 5 | 100 | 0 | 0 | 300 | 340 | 205 | 16 | 51 | 0 | 50 | 5 | 40 | 0 | 0 | 52 | 21 | 8 | 33 | 20 | 174 | 135 | 76 | 21 | 1.3 | 56 | 57 | 50 | 49 | 130 | 105 | 58 | 79 | 43 | 96 | 0 | 42 | 10 | 305 | 24 | 11 | 0 | 22 | 0 | 0 | 125 | 0 | 149 | 10.7 | 90 | 200 | 133 | 261 | 93 | 106 | 0 | 1.7 | 304 |  | 932 | 0 | 0 | 0 | 73 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 27 | 48 | 0 | 0 | 50 | 8 | 0 | 68 | 6 | 8 | 0 | 52 | 0 | 17 | 8 | 8 | 0 | 67 | 249 | 0 | 0 | 196 | 0 | 198 | 0 | 96 | 0 | 196 | 0 | 380 | 70 | 0 | 108 | 70 | 23 |  | 8052.7 | 3290 | 11342.7 | 4321 | 932 | 2292 | 2933 | 316 | 38 | 323 | 174 | 13.7 | 0 | 75.21
16:00 | 65 | 0 | 190 | 0 | 180 | 103 | 62 | 344 | 338 | 80 | 0 | 450 | 200 | 100 | 15 | 55 | 213 | 0 | 0 | 0 | 4 | 100 | 127 | 72 | 67 | 0 | 13 | 35 | 36 | 35 | 19 | 25 | 28 | 25 | 33 | 48 | 0 | 38 | 0 | 95 | 120 | 25 | 203 | 0 | 103 | 0 | 0 | 33 | 0 | 0 | 40 | 84 | 46 | 21 | 6 | 100 | 0 | 0 | 360 | 230 | 184 | 16 | 51 | 0 | 51 | 5 | 40 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 176 | 138 | 76 | 21 | 0.9 | 58 | 57 | 50 | 49 | 163 | 107 | 59 | 79 | 44 | 84 | 0 | 43 | 10 | 310 | 24 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 149 | 9.8 | 100 | 200 | 137 | 261 | 92 | 106 | 0 | 2.2 | 304 |  | 921 | 0 | 0 | 0 | 99 | 120 | 0 | 0 | 0 | 18 | 40 | 172 | 26 | 48 | 0 | 0 | 50 | 8 | 0 | 68 | 6 | 8 | 0 | 49 | 0 | 17 | 8 | 8 | 0 | 65 | 249 | 0 | 0 | 192 | 0 | 190 | 0 | 95 | 0 | 208 | 0 | 408 | 70 | 0 | 108 | 70 | 24 |  | 8159.9 | 3345 | 11504.9 | 4308 | 921 | 2373 | 3021 | 314 | 38 | 341 | 176 | 12.9 | 0 | 75.22
17:00 | 65 | 0 | 190 | 0 | 180 | 103 | 62 | 329 | 338 | 74 | 0 | 450 | 270 | 50 | 15 | 55 | 213 | 0 | 0 | 0 | 7 | 40 | 98 | 45 | 66 | 0 | 13 | 40 | 35 | 35 | 0 | 25 | 28 | 25 | 33 | 49 | 0 | 38 | 0 | 95 | 120 | 25 | 205 | 0 | 100 | 0 | 0 | 33 | 0 | 0 | 10 | 89 | 47 | 18 | 9 | 100 | 0 | 0 | 360 | 360 | 183 | 16 | 50 | 0 | 51 | 5 | 40 | 0 | 0 | 52 | 21 | 5 | 33 | 20 | 168 | 142 | 84 | 21 | 0.5 | 56 | 57 | 53 | 49 | 130 | 107 | 40 | 79 | 43 | 94 | 0 | 44 | 10 | 290 | 16 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 132 | 1.6 | 100 | 200 | 137 | 261 | 93 | 106 | 0 | 0.4 | 304 |  | 922 | 0 | 0 | 0 | 82 | 120 | 0 | 0 | 0 | 30 | 8 | 172 | 25 | 16 | 0 | 0 | 50 | 8 | 0 | 68 | 6 | 8 | 0 | 8 | 0 | 18 | 9 | 8 | 0 | 65 | 249 | 0 | 0 | 183 | 0 | 180 | 0 | 95 | 0 | 194 | 0 | 370 | 35 | 0 | 108 | 76 | 23 |  | 7992.5 | 3136 | 11128.5 | 4350 | 922 | 2289 | 2721 | 314 | 38 | 324 | 168 | 2.5 | 0 | 75.23
18:00 | 65 | 0 | 190 | 0 | 180 | 103 | 62 | 331 | 277 | 55 | 0 | 370 | 262 | 9 | 15 | 30 | 130 | 0 | 0 | 0 | 7 | 40 | 95 | 13 | 66 | 0 | 13 | 35 | 36 | 17 | 0 | 25 | 28 | 33 | 33 | 49 | 0 | 38 | 0 | 95 | 120 | 25 | 204 | 0 | 100 | 0 | 0 | 33 | 0 | 0 | 10 | 95 | 47 | 18 | 7 | 100 | 0 | 0 | 320 | 160 | 184 | 16 | 50 | 0 | 20 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 158 | 139 | 84 | 21 | 0.5 | 56 | 57 | 13 | 20 | 130 | 195 | 59 | 40 | 20 | 84 | 0 | 20 | 10 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 90 | 1.5 | 100 | 160 | 138 | 220 | 93 | 106 | 0 | 0 | 304 |  | 922 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 10 | 33 | 8 | 172 | 25 | 16 | 0 | 0 | 55 | 9 | 7 | 68 | 12 | 8 | 0 | 8 | 0 | 22 | 10 | 8 | 0 | 64 | 249 | 0 | 0 | 182 | 0 | 178 | 0 | 64 | 0 | 185 | 0 | 300 | 17 | 0 | 108 | 79 | 9 |  | 7169 | 2997 | 10166 | 4094 | 922 | 1854 | 2443 | 313 | 38 | 342 | 158 | 2 | 0 | 75.24
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 65 | 0 | 191 | 0 | 210 | 103 | 63 | 340 | 309 | 55 | 0 | 400 | 295 | 9 | 15 | 30 | 180 | 0 | 0 | 0 | 7 | 72 | 110 | 13 | 70 | 0 | 13 | 35 | 35 | 30 | 19 | 25 | 28 | 33 | 33 | 49 | 0 | 38 | 0 | 95 | 120 | 0 | 204 | 0 | 145 | 0 | 0 | 33 | 85 | 58 | 10 | 97 | 47 | 21 | 12 | 100 | 0 | 0 | 360 | 220 | 206 | 16 | 52 | 0 | 20 | 5 | 40 | 0 | 50 | 52 | 22 | 8 | 33 | 19 | 188 | 137 | 84 | 22 | 0 | 56 | 57 | 13 | 20 | 100 | 236 | 59 | 40 | 20 | 123 | 0 | 20 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 125 | 0 | 90 | 0 | 100 | 160 | 139 | 222 | 93 | 106 | 0 | 0 | 304 |  | 923 | 30 | 0 | 0 | 90 | 120 | 0 | 0 | 24 | 38 | 40 | 172 | 32 | 110 | 12 | 0 | 55 | 50 | 22 | 81 | 33 | 8 | 41 | 8 | 28 | 22 | 11 | 8 | 0 | 64 | 249 | 16 | 16 | 162 | 0 | 154 | 0 | 70 | 30 | 176 | 0 | 350 | 100 | 0 | 108 | 88 | 7 |  | 7899 | 3548 | 11447 | 4403 | 923 | 1966 | 2835 | 313 | 38 | 781 | 188 | 0 | 0 | 75.25
19:30 | 65 | 0 | 190 | 0 | 280 | 103 | 63 | 330 | 308 | 55 | 0 | 450 | 275 | 30 | 15 | 30 | 180 | 0 | 0 | 0 | 15 | 72 | 127 | 50 | 70 | 0 | 13 | 54 | 35 | 55 | 19 | 25 | 28 | 33 | 33 | 49 | 0 | 38 | 0 | 95 | 120 | 0 | 170 | 0 | 90 | 0 | 0 | 33 | 77 | 68 | 10 | 55 | 37 | 21 | 21 | 100 | 0 | 0 | 360 | 250 | 184 | 16 | 50 | 0 | 20 | 5 | 40 | 0 | 50 | 52 | 22 | 8 | 33 | 19 | 172 | 140 | 85 | 21 | 0 | 56 | 57 | 39 | 49 | 100 | 254 | 61 | 79 | 20 | 114 | 0 | 47 | 10 | 300 | 16 | 11 | 0 | 90 | 0 | 0 | 187 | 0 | 149 | 0 | 100 | 200 | 132 | 287 | 93 | 106 | 0 | 0 | 304 |  | 922 | 30 | 0 | 0 | 99 | 120 | 0 | 0 | 30 | 46 | 40 | 172 | 39 | 110 | 12 | 0 | 55 | 50 | 27 | 85 | 33 | 8 | 44 | 41 | 28 | 22 | 11 | 11 | 0 | 64 | 249 | 16 | 16 | 171 | 0 | 168 | 0 | 95 | 100 | 176 | 0 | 400 | 105 | 0 | 108 | 88 | 7 |  | 8375 | 3798 | 12173 | 4475 | 922 | 2237 | 3190 | 313 | 38 | 826 | 172 | 0 | 0 | 0
20:00 | 65 | 0 | 190 | 0 | 280 | 103 | 63 | 339 | 308 | 55 | 0 | 450 | 260 | 55 | 15 | 45 | 180 | 0 | 0 | 0 | 45 | 72 | 125 | 50 | 71 | 0 | 23 | 54 | 36 | 55 | 22 | 25 | 28 | 33 | 33 | 42 | 0 | 38 | 0 | 95 | 120 | 0 | 170 | 0 | 90 | 0 | 0 | 33 | 77 | 68 | 10 | 31 | 47 | 21 | 25 | 100 | 0 | 0 | 360 | 250 | 183 | 16 | 50 | 0 | 20 | 5 | 40 | 0 | 50 | 52 | 22 | 8 | 33 | 19 | 158 | 141 | 85 | 21 | 0 | 56 | 57 | 53 | 49 | 100 | 249 | 61 | 81 | 45 | 110 | 0 | 42 | 10 | 300 | 16 | 11 | 0 | 96 | 0 | 0 | 180 | 0 | 139 | 0 | 100 | 200 | 132 | 289 | 93 | 106 | 0 | 0 | 304 |  | 924 | 28 | 0 | 0 | 99 | 120 | 0 | 0 | 34 | 55 | 40 | 171 | 37 | 110 | 12 | 0 | 55 | 50 | 27 | 90 | 33 | 8 | 47 | 42 | 28 | 22 | 11 | 11 | 0 | 64 | 249 | 17 | 16 | 163 | 0 | 160 | 0 | 96 | 100 | 178 | 0 | 415 | 105 | 0 | 108 | 87 | 14 |  | 8439 | 3826 | 12265 | 4465 | 924 | 2291 | 3232 | 313 | 38 | 844 | 158 | 0 | 0 | 75.26
21:00 | 65 | 0 | 190 | 0 | 320 | 106 | 63 | 347 | 338 | 55 | 0 | 450 | 260 | 55 | 0 | 55 | 180 | 0 | 0 | 0 | 50 | 70 | 125 | 50 | 70 | 0 | 48 | 54 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 38 | 0 | 5 | 120 | 8 | 204 | 0 | 90 | 0 | 0 | 33 | 70 | 68 | 10 | 32 | 47 | 21 | 30 | 100 | 0 | 0 | 360 | 300 | 200 | 16 | 50 | 0 | 53 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 152 | 140 | 85 | 22 | 0 | 56 | 57 | 53 | 49 | 100 | 251 | 59 | 80 | 45 | 120 | 0 | 47 | 10 | 300 | 16 | 11 | 0 | 114 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 133 | 288 | 93 | 106 | 0 | 0 | 304 |  | 925 | 28 | 0 | 0 | 99 | 120 | 0 | 0 | 32 | 40 | 40 | 172 | 37 | 110 | 12 | 0 | 55 | 50 | 27 | 93 | 33 | 8 | 44 | 50 | 28 | 22 | 11 | 11 | 0 | 63 | 240 | 17 | 16 | 169 | 0 | 160 | 0 | 98 | 100 | 181 | 0 | 408 | 105 | 0 | 108 | 87 | 20 |  | 8536 | 3819 | 12355 | 4543 | 925 | 2361 | 3263 | 303 | 38 | 770 | 152 | 0 | 0 | 75.27
22:00 | 65 | 0 | 190 | 0 | 320 | 106 | 63 | 347 | 347 | 13 | 0 | 450 | 160 | 55 | 0 | 55 | 180 | 0 | 0 | 0 | 50 | 70 | 125 | 10 | 72 | 0 | 48 | 54 | 35 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 38 | 0 | 100 | 120 | 25 | 203 | 0 | 90 | 0 | 0 | 30 | 77 | 68 | 10 | 32 | 47 | 21 | 37 | 100 | 0 | 0 | 360 | 300 | 195 | 16 | 50 | 0 | 53 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 158 | 140 | 85 | 22 | 0 | 56 | 57 | 53 | 49 | 100 | 251 | 60 | 80 | 45 | 120 | 0 | 46 | 10 | 310 | 24 | 11 | 0 | 70 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 133 | 288 | 93 | 106 | 0 | 0 | 304 |  | 924 | 28 | 0 | 0 | 115 | 120 | 0 | 0 | 31 | 35 | 40 | 172 | 38 | 110 | 12 | 0 | 55 | 50 | 27 | 93 | 6 | 24 | 46 | 50 | 28 | 22 | 10 | 11 | 0 | 66 | 240 | 17 | 16 | 170 | 0 | 159 | 0 | 98 | 100 | 182 | 0 | 408 | 105 | 0 | 108 | 87 | 19 |  | 8464 | 3822 | 12286 | 4644 | 924 | 2386 | 3057 | 306 | 38 | 773 | 158 | 0 | 0 | 75.28
23:00 | 65 | 0 | 190 | 0 | 320 | 104 | 64 | 352 | 347 | 13 | 0 | 450 | 160 | 55 | 0 | 55 | 217 | 0 | 0 | 0 | 50 | 70 | 125 | 10 | 72 | 0 | 14 | 54 | 35 | 55 | 22 | 25 | 30 | 33 | 33 | 2 | 0 | 38 | 0 | 100 | 120 | 25 | 206 | 0 | 114 | 0 | 0 | 32 | 67 | 68 | 10 | 31 | 47 | 21 | 38 | 100 | 0 | 0 | 360 | 330 | 206 | 16 | 50 | 0 | 52 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 160 | 142 | 85 | 22 | 0 | 56 | 57 | 53 | 49 | 100 | 256 | 61 | 80 | 45 | 122 | 0 | 47 | 10 | 320 | 24 | 11 | 0 | 45 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 140 | 286 | 94 | 106 | 0 | 0 | 304 |  | 925 | 30 | 0 | 0 | 115 | 120 | 0 | 0 | 31 | 35 | 40 | 172 | 39 | 110 | 12 | 0 | 60 | 50 | 27 | 93 | 6 | 42 | 43 | 50 | 28 | 22 | 11 | 11 | 0 | 63 | 239 | 16 | 16 | 172 | 0 | 163 | 0 | 98 | 100 | 182 | 0 | 414 | 70 | 0 | 107 | 106 | 19 |  | 8536 | 3837 | 12373 | 4773 | 925 | 2404 | 3010 | 302 | 38 | 761 | 160 | 0 | 0 | 75.29
24:00 | 65 | 0 | 190 | 0 | 320 | 104 | 64 | 346 | 352 | 13 | 0 | 450 | 185 | 55 | 0 | 55 | 217 | 0 | 0 | 0 | 50 | 70 | 125 | 10 | 73 | 0 | 6 | 54 | 35 | 55 | 22 | 25 | 30 | 33 | 33 | 44 | 0 | 37 | 0 | 100 | 120 | 25 | 204 | 0 | 111 | 0 | 0 | 33 | 67 | 68 | 10 | 32 | 47 | 21 | 41 | 100 | 0 | 0 | 360 | 330 | 181 | 16 | 50 | 0 | 54 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 150 | 141 | 85 | 22 | 0 | 56 | 57 | 50 | 49 | 163 | 254 | 50 | 80 | 45 | 109 | 0 | 47 | 10 | 310 | 24 | 11 | 0 | 45 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 140 | 294 | 93 | 106 | 0 | 0 | 304 |  | 924 | 28 | 0 | 0 | 115 | 120 | 0 | 0 | 31 | 24 | 40 | 172 | 38 | 110 | 12 | 0 | 60 | 50 | 27 | 90 | 6 | 42 | 43 | 50 | 28 | 22 | 10 | 11 | 0 | 63 | 239 | 17 | 17 | 169 | 0 | 160 | 0 | 96 | 100 | 182 | 0 | 416 | 70 | 0 | 108 | 105 | 11 |  | 8592 | 3806 | 12398 | 4713 | 924 | 2462 | 3063 | 302 | 37 | 747 | 150 | 0 | 0 | 75.3
KWH | 1102000 | 0 | 4164000 | 0 | 5945454 | 2240409 | 1378272 | 8290300 | 7414000 | 544600 | 0 | 9498500 | 5835142 | 777600 | 223464 | 575520 | 4364147 | 0 | 0 | 0 | 309120 | 1108944 | 1902240 | 491832 | 1419840 | 0 | 352032 | 1201320 | 796520 | 882000 | 429264 | 600000 | 580500 | 624000 | 828600 | 816192 | 0 | 799980 | 0 | 2300000 | 3000000 | 401079 | 4796114 | 0 | 2362467 | 0 | 0 | 767040 | 386760 | 440698 | 524760 | 1012800 | 1028160 | 485856 | 478560 | 2471500 | 0 | 0 | 8192100 | 7274500 | 4797000 | 434909 | 1725610 | 0 | 1215360 | 120000 | 959200 | 0 | 87656 | 898090 | 495720 | 183060 | 796300 | 457080 | 3580800 | 3320400 | 2010240 | 461736 | 12950 | 1322000 | 1364520 | 1146600 | 1157328 | 3191375 | 4136000 | 1333056 | 1852800 | 983880 | 2558140 | 0 | 912540 | 229320 | 7120700 | 475776 | 256896 | 0 | 659890 | 0 | 0 | 3273600 | 0 | 2177280 | 107190 | 223584 | 3661440 | 1669382 | 6525000 | 2229600 | 2535600 | 0 | 36960 | 7293927 |  | 22279272 | 163500 | 0 | 0 | 1350720 | 2614080 | 0 | 0 | 290400 | 317312 | 676125 | 4204225 | 717664 | 1008960 | 69099 | 0 | 1345000 | 412768 | 157621 | 1424440 | 236820 | 446683 | 384100 | 755520 | 295290 | 484800 | 247932 | 221220 | 0 | 1515490 | 6020200 | 92000 | 93000 | 4609127 | 0 | 4449091 | 0 | 2256226 | 803520 | 4742173 | 0 | 8990909 | 1460160 | 0 | 2589216 | 1859760 | 539520 |  | 181408681 | 80123943 | 261532624 | 107589932 | 22279272 | 53031284 | 57427602 | 7535690 | 799980 | 9130964 | 3580800 | 157100 | 0
Fuel Cost | 947720 | 0 | 3581040 | 0 | 3805090.56 | 1814731.29 | 1295575.68 | 5057083 | 4522540 | 5233606 | 0 | 6363995 | 88635806.98 | 4883328 | 1492739.52 | 3516427.2 | 2836695.55 | 0 | 0 | 0 | 1932000 | 7307940.96 | 18394660.8 | 3132969.84 | 8504841.6 | 0 | 2348053.44 | 8565411.6 | 4978250 | 5530140 | 321948 | 450000 | 0 | 0 | 0 | 7721176.32 | 0 | 0 | 0 | 2530000 | 3300000 | 3798218.13 | 3165435.24 | 0 | 2716837.05 | 0 | 0 | 6742281.6 | 4165405.2 | 4287991.54 | 3248264.4 | 6542688 | 6724166.4 | 412977.6 | 0 | 2249065 | 0 | 0 | 5079102 | 5019405 | 3357900 | 300087.21 | 1656585.6 | 0 | 1045209.6 | 110400 | 786544 | 0 | 950191.04 | 6663827.8 | 381704.4 | 137295 | 613151 | 342810 | 24492672 | 2490300 | 18474105.6 | 355536.72 | 0 | 1374880 | 1419100.8 | 1100736 | 1041595.2 | 2489272.5 | 2895200 | 1519683.84 | 1982496 | 1082268 | 2916279.6 | 0 | 848662.2 | 213267.6 | 4557248 | 356832 | 195240.96 | 0 | 4790801.4 | 0 | 0 | 23406240 | 0 | 0 | 0 | 0 | 34197849.6 | 15592027.88 | 5676750 | 0 | 0 | 0 | 0 | 0 |  | 113624287.2 | 4766025 | 0 | 0 | 11197468.8 | 42034406.4 | 0 | 0 | 3269904 | 3737935.36 | 5327865 | 2900915.25 | 710487.36 | 7466304 | 2327254.32 | 0 | 1412250 | 4726193.6 | 1689697.12 | 12762982.4 | 2048493 | 3975478.7 | 4090665 | 7494758.4 | 3475563.3 | 533280 | 233056.08 | 167463.54 | 0 | 9199024.3 | 23237972 | 2965160 | 2489610 | 3134206.36 | 0 | 3114363.7 | 0 | 0 | 13925001.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 432970360.05 | 298038071.79 | 731008431.84 | 77890847.77 | 113624287.2 | 31031451.72 | 335398531.77 | 32436996.3 | 0 | 116133645.08 | 24492672 | 0 | 0
Yesterday Day Peak | 35 | 0 | 150 | 0 | 0 | 102 | 63 | 351 | 335 | 26 | 0 | 430 | 188 | 15 | 0 | 10 | 213 | 0 | 0 | 0 | 0 | 64 | 80 | 5 | 67 | 0 | 13 | 54 | 55 | 35 | 19 | 25 | 27 | 16 | 33 | 35 | 0 | 38 | 0 | 100 | 120 | 13 | 205 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 70 | 38 | 45 | 21 | 4 | 100 | 0 | 0 | 360 | 300 | 183 | 16 | 50 | 0 | 51 | 5 | 40 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 158 | 140 | 84 | 21 | 2.1 | 54 | 57 | 53 | 50 | 163 | 20 | 59 | 78 | 43 | 110 | 0 | 44 | 10 | 265 | 16 | 11 | 0 | 5 | 0 | 0 | 81 | 0 | 110 | 12.5 | 100 | 160 | 50 | 291 | 94 | 106 | 0 | 5.8 | 304 |  | 932 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 68 | 6 | 8 | 0 | 50 | 0 | 18 | 8 | 8 | 0 | 63 | 249 | 0 | 0 | 196 | 0 | 194 | 0 | 97 | 0 | 196 | 0 | 420 | 70 | 0 | 108 | 70 | 25 |  | 10508.4 | DayPeak
Yesterday Evening Peak | 65 | 0 | 190 | 0 | 320 | 106 | 63 | 347 | 338 | 55 | 0 | 450 | 260 | 55 | 0 | 55 | 180 | 0 | 0 | 0 | 50 | 70 | 125 | 50 | 70 | 0 | 48 | 54 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 38 | 0 | 5 | 120 | 8 | 204 | 0 | 90 | 0 | 0 | 33 | 70 | 68 | 10 | 32 | 47 | 21 | 30 | 100 | 0 | 0 | 360 | 300 | 200 | 16 | 50 | 0 | 53 | 5 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 152 | 140 | 85 | 22 | 0 | 56 | 57 | 53 | 49 | 100 | 251 | 59 | 80 | 45 | 120 | 0 | 47 | 10 | 300 | 16 | 11 | 0 | 114 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 133 | 288 | 93 | 106 | 0 | 0 | 304 |  | 925 | 28 | 0 | 0 | 99 | 120 | 0 | 0 | 32 | 40 | 40 | 172 | 37 | 110 | 12 | 0 | 55 | 50 | 27 | 93 | 33 | 8 | 44 | 50 | 28 | 22 | 11 | 11 | 0 | 63 | 240 | 17 | 16 | 169 | 0 | 160 | 0 | 98 | 100 | 181 | 0 | 408 | 105 | 0 | 108 | 87 | 20 |  | 12355 | EvPeak
Forecast for Evening | 65 | 0 | 200 | 0 | 255 | 108 | 70 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 20 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 120 | 25 | 225 | 0 | 135 | 0 | 0 | 32 | 85 | 68 | 100 | 100 | 46 | 20 | 25 | 100 | 0 | 0 | 360 | 360 | 221 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 181 | 144 | 87 | 21 | 0 | 60 | 58 | 50 | 50 | 163 | 330 | 66 | 86 | 45 | 130 | 19 | 45 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 100 | 100 | 105 |  | 300 |  | 945 | 32 | 0 | 0 | 115 | 225 | 0 | 0 | 38 | 80 | 40 | 190 | 33 | 110 | 26 | 0 | 60 | 50 | 35 | 95 | 50 | 43 | 44 | 52 | 28 | 22 | 12 | 11 | 0 | 62 | 250 | 17 | 18 | 214 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 105 | 23
Forecast for Day | 65 | 0 | 200 | 0 | 255 | 108 | 70 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 20 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 40 | 0 | 100 | 120 | 25 | 210 | 0 | 135 | 0 | 0 | 32 | 85 | 68 | 100 | 100 | 46 | 20 | 6 | 100 | 0 | 0 | 360 | 360 | 221 | 16 | 100 | 0 | 55 | 5 | 40 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 136 | 144 | 87 | 21 | 2 | 60 | 58 | 50 | 50 | 163 | 300 | 66 | 86 | 45 | 130 | 19 | 45 | 10 | 341 | 25 | 11 | 0 | 100 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 0 | 285 | 100 | 100 | 105 | 3 | 300 |  | 945 | 0 | 0 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 33 | 110 | 0 | 0 | 60 | 0 | 0 | 95 | 6 | 32 | 44 | 52 | 0 | 22 | 12 | 11 | 0 | 62 | 250 | 0 | 0 | 214 | 0 | 220 | 0 | 95 | 0 | 220 | 0 | 414 | 105 | 0 | 100 | 105 | 23
Generation at 08:00(Today) | 65 | 0 | 190 | 0 | 60 | 104 | 66 | 280 | 282 | 0 | 0 | 400 | 270 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 35 | 53 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 36 | 0 | 100 | 120 | 0 | 205 | 0 | 110 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 25 | 21 | 10 | 100 | 0 | 0 | 280 | 280 | 185 | 16 | 30 | 0 | 57 | 5 | 5 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 126 | 147 | 85 | 22 | 0.3 | 56 | 57 | 5 | 5 | 100 | 155 | 61 | 10 | 5 | 122 | 0 | 47 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 4.9 | 70 | 105 | 0 | 250 | 94 | 71 | 0 | 1.6 | 220 | 0 | 932 | 0 | 0 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 25 | 16 | 0 | 0 | 60 | 0 | 0 | 90 | 6 | 8 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 63 | 240 | 0 | 0 | 156 | 0 | 148 | 0 | 96 | 0 | 164 | 0 | 300 | 72 | 0 | 17 | 106 | 6 | 0
199
| Minimum Generation |  | 9067.2 | 7:00
| Highest Generation |  | 12398 | 24:00
| Day Peak Generation |  | 10508.4 | 12:00
| Evening Peak Generation |  | 12355 | 21:00
| HVDC Max Flow |  | 933 | 1:00
| HVDC EvPeak Flow |  | 925 | 21:00
| Load factor L.F |  | 87.89%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-06-20
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-06-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10508.4 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8883.8 | MW
Evening Peak Generation : |  | 12355 | MW Hour : | 21:00 | Available Max Generation : |  | 15226 | MW
E.P. Demand (at gen end) : |  | 12355 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 12398 | MW Hour : | 24:00 | Reserve(Generation end) |  | 2526 | MW
Total Gen. (MKWH) : |  | 261.5326 | System Load Factor : | 87.89% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -340 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-06-20
Actual : | 75.42 | Ft.(MSL) , | Rule curve : | 80.76 | Ft.( MSL )
Gas Consumed : | Total = | 1401.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 108922299.49
|  | Coal : | 32436996.3 | Oil : | 451532176.85 | Total : | 592891472.64
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4504.9529 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1535.9717 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1376.8993 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1244.4001 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1124.4055 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 907.3656 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 502.1575 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 233.4847 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 699.8303 |  |  | 0 | 0%
Total | 0 |  | 12129.4675 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1, | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-7 ST
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal # 3,5
|  |  |  | 4) Bheramara 410 MW. | 10) Shahjibazar 330 MW GT-2
5) Siddhirganj ST
6) Ashuganj #4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ghorasal Unit-7 CCPP tripped at 10:46 due to tripping of GBC and GT & ST were synchronized at 13:15 & 14:54
respectively and ST was shut down at 05:18(20/06/2019) for maintenance.
b) Bibiyana-Shahjibazar 132 kV Ckt-2 was under shut down from 08:35 to 17:15 for D/W.
c) Cumilla(N)-Daudkandi 132 kV Ckt-1 tripped at 11:34 from both ends showing O/C, Dist a-phase at Cumilla(N) end
& Dist a-phase at Daudkandi end and was switched on at 11:46.
d) Kabirpur-Kaliakoir 132 kV Ckt-2 was switched on at 12:34.
e) Kabirpur 132/33 kV T3 transformer and associated 33 kV bus were under shut down from 10:22 to 11:38 due |  |  |  |  | About 40 MW power interruption occurred under Kabirpur S/S
to changing 33 kV bus of 33 kV EPZ PBS feeder. |  |  |  |  | area from 10:22 to 11:38.
f) Bogura-Mohasthangar 132 kV Ckt-1 tripped at 10:02 from both side showing Dist ABC at Bogura end |  |  |  |  | About 20 MW power interruption occurred under Palashbari S/S
and Dist AB at Mohasthangar end and was switched on at 14:20. |  |  |  |  | area from 14:02 to 14:20.
g) Palasbari-Mahasthangar 132 kV Ckt-2 tripped at 14:33 form both ends showing Dist Z1 A-phase and |  |  |  |  | About 30 MW power interruption occurred under Palashbari S/S
was switched on at 14:51. |  |  |  |  | area from 14:33 to 14:51.
h) Bashundhara-Tongi 132 kV Ckt-2 tripped at 14:33 from both ends due to B-phase LA burst at Bashundhara end
and was switched on at 21:29.
i) Bashundhara-Tongi 132 kV Ckt-1 tripped at 14:33 from both ends due to B-phase LA burst at Bashundhara end |  |  |  |  | About 55 MW power interruption occurred under Bashundhara S/S
and was switched on at 14:45. |  |  |  |  | area from 14:33 to 14:45.
j) Ramganj 132/33 kV T1 transformer was shut down at 07:10(20/06/2019) for red hot maintenance at 132 kV
Y-phase CT terminal and was switched on at 10:39.
k) Bogura 132/33 kV T3 transformer was under shut down from 07:50 to 08:51(20/06/2019) for red hot maintenance
at 132 kV B-phase CT terminal.
l) Shahjibazar 330 MW CCPP GT-2 was shut down at 07:43(20/06/2019) for combine mode of operation.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-06-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 65 | 1102000 | Gas shortage
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 190 | 4164000 | Gas shortage
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 5945454 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 63 | 1378272
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 106 | 2240409
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 8290300 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 55 | 544600 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 338 | 7414000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 9498500
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 55 | 777600 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 5835142 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 223464 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 575520
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 50 | 491832 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 429264
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 309120 | Low demand
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 180 | 4364147 | Low demand
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 70 | 1108944 | Low demand
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 48 | 352032
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1201320
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 1902240 | Engine problem
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 35 | 796520
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 882000
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 70 | 1419840 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1180500 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 624000
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 828600
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 0 | 816192 | Reserve
31 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 114 | 659890 | Low demand
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 149 | 2177280
37 | Gazipur 100 MW |  | RPCL | 100 MW | 105 | 106 | 2535600
| Dhaka area Total |  |  |  | 5803 | 3551 | 70068582
38 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 5 | 2300000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage
39 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 8 | 401079 | Machine problem
40 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 107190
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 47 | 1028160
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 38 | 799980 | Low water level
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4796114 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 90 | 2362467 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 33 | 767040 | Engine problem
47 | Baraka Sikalbaha PL |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
48 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 70 | 386760
49 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 440698
50 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 524760 | Line O/L
51 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 223584
52 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 485856
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 478560
53 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 32 | 1012800 | Line O/L
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 36960
| Anwara United |  | United Group | 300 MW | 0 | 304 | 7293927 | on test
| Chattogram area Total |  |  |  | 1786 | 1180 | 26445935
54 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2471500
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 200 | 4797000 | FGMO
56 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8192100
57 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7274500 | Frequency control
58 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas Line maint.
59 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 53 | 1215360
60 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Engine problem
61 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 16 | 434909 | Gas shortage
62 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 40 | 959200
63 | Midland 150MW |  | IPP | 23*7.015 | 150 | 133 | 1669382 | Engine problem
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 87656 | Reserve
66 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1725610
67 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 3661440
68 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 495720
69 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 183060
** | Tripura |  | Imported power | 0 | 160 | 152 | 3580800
70 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 796300
71 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 898090
72 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 457080 | Engine problem
73 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1743 | 39019707
74 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 140 | 3320400 | GT-1 Under maint
75 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 461736
76 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 85 | 2010240 | Engine problem
77 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12950
78 | United Mymensingh PPL |  | IPP | 200 | 200 | 180 | 3273600
79 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 93 | 2229600 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 520 | 11308526
80 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 1322000
81 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1364520
82 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3191375 | Frequency control
83 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 251 | 4136000 | FGMO
84 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1146600
85 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 49 | 1157328
86 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 256896
87 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 59 | 1333056 | FGMO
88 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 80 | 1852800
89 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 983880
90 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 120 | 2558140 | FGMO
91 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
92 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 912540
93 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 16 | 475776
94 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 300 | 7120700 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 288 | 6525000 | On test
95 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 229320
| Sylhet Area Total |  |  |  | 1549 | 1542 | 34565931
96 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 28 | 163500
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 925 | 22279272
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
97 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1350720 | Engine problem
98 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 32 | 290400
99 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 2614080 | Low demand
100 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 40 | 317312 | Low demand
101 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
102 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 676125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
103 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 100 | 803520
104 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1460160
105 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 87 | 1859760
| Khulna Area Total |  |  |  | 2314 | 1576 | 31814849
106 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1008960
107 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 12 | 69099 | Low demand
108 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 37 | 717664
109 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 172 | 4204225 | FGMO
110 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 98 | 2256226
| Barisal Area Total |  |  |  | 462 | 429 | 8256174
111 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 55 | 1345000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
112 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 412768
113 | Bera Peaking |  | PDB | 9*8.29 | 71 | 27 | 157621
114 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 33 | 236820 | Engine problem
115 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 446683
116 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 384100
117 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 169 | 4609127 | FGMO
118 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 160 | 4449091 | FGMO
119 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 181 | 4742173 | FGMO
120 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 408 | 8990909
121 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 28 | 295290
122 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 484800
123 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 247932
124 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 221220
125 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 755520
126 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 93 | 1424440
127 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
128 | Confidence Bogura-2 (CPBL) |  | IPP | 113 MW | 113 | 108 | 2589216
| Rajshahi Area Total |  |  |  | 2070 | 1458 | 31792710
129 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 63 | 1515490
130 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 240 | 6020200
131 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 92000
132 | Saidpur GT |  | PDB | 1*20 | 20 | 16 | 93000
| Confidence Rangpur |  | IPP | 113 MW | 0 | 20 | 539520
| Rangpur Area Total |  |  |  | 484 | 356 | 8260210
| Total |  |  |  | 17996 | 12355 | 261532624
| Eastern Grid Total |  |  |  | 12666 | 8536 | 181408681
| Western Grid Total |  |  |  | 5330 | 3819 | 80123943
| National Grid Total |  |  |  | 17996 | 12355 | 261532624
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-06-19
| (a) ENTIRE EASTERN GRID : |  | 7893 | MW | (b) ENTIRE WESTERN GRID : |  | 3897 | MW
| i) Dhaka area |  | 4337 | MW | i) Khulna area |  | 1533 | MW
| ii) Chittagong area |  | 1031 | MW | ii) Rajshahi area |  | 1262 | MW
| iii) Comilla area |  | 1096 | MW | iii) Barisal area |  | 351 | MW
| iv) Mymensingh area |  | 929 | MW | iv) Rangpur area |  | 751 | MW
| v) Sylhet area |  | 500 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11790 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 128 | 1200 | Jamalpur | 136 | 2200 | Jessore | 120 | 2000
2 | Munsiganj | 118 | 2000 | Sherpur | 112 | 1930 | Jhenida | 118 | 1930
3 | Sonargaon | 66 | 2100 | Srimongal | 43 | 2200 | Bottail | 138 | 2000
4 | Shyampur | 180 | 1100 | Shahjibazar | 128 | 2100 | G.K Project | 55 | 2100
5 | Bhulta | 203 | 2100 | Fenchuganj | 56 | 2100 | Faridpur | 176 | 2000
6 | Madanganj | 52 | 900 | Kulawara | 45 | 2100 | Madaripur | 125 | 2100
7 | Shitalakhya | 114 | 1500 | Sylhet | 156 | 1930 | Gopalganj | 97 | 2100
8 | Rahim steel | 20 | 1200 | Chatak | 32 | 1900 | Bagerhat | 89 | 2000
9 | Matuail | 95 | 1600 | Sunamganj | 39 | 2100 | Mongla | 40 | 1900
10 | Ghorasal | 88 | 2000 | Biani Bazar | 52 | 1930 | Satkhira | 112 | 2200
11 | Narsingdi | 134 | 100 | Comilla (S) | 188 | 1900 | Gallamari | 56 | 1300
12 | Haripur (SBU) | 100 | 1000 | Comilla(N) | 141 | 2200 | Magura | 56 | 2000
13 | Ullon | 96 | 1700 | Chandpur | 107 | 2100 | Chuadanga | 84 | 2100
14 | Hasnabad | 233 | 2100 | Feni | 134 | 1900 | Barisal | 120 | 1930
15 | Magbazar | 153 | 1700 | Chowmuhani | 166 | 1900 | Patuakhali | 109 | 2200
16 | Maniknagar | 118 | 1900 | Ashuganj | 58 | 2300 | Bhandaria | 54 | 1930
17 | Bangabhaban | 38 | 1300 | Daudkandi | 136 | 2200 | Barisal (N) | 42 | 2000
18 | Narinda | 96 | 1600 | B.Baria | 149 | 2100 | Sariatpur | 39 | 1930
19 | Dhanmondi | 189 | 1600 | Ramganj | 96 | 2400 | Benapol | 43 | 2200
20 | Lalbag | 78 | 1700 | Madunaghat | 65 | 1400 | Borhan Uddin | 36 | 2100
21 | Madartek | 53 | 2100 | Hathazari | 94 | 2100 | Ishurdi | 61 | 1930
22 | Mirpur | 120 | 1900 | Khulshi | 212 | 1200 | Ruppur Paromanobik | 2 | 800
23 | Kalyanpur | 129 | 1900 | Halishahar | 152 | 1500 | Natore | 126 | 1930
24 | Gulshan | 176 | 1300 | Baraulia | 159 | 1600 | Bogra | 256 | 2100
25 | Uttara | 96 | 2000 | Sikalbaha | 31 | 2100 | Noagaon | 122 | 2000
26 | Uttara New | 19 | 2100 | Dohazari | 78 | 1700 | Rajshahi | 164 | 2000
27 | Kamrangirchar | 73 | 1300 | Cox'sbazar | 99 | 1900 | C.Nawabganj | 82 | 2100
28 | Savar | 151 | 1100 | Chandraghona | 24 | 100 | Amnura | 35 | 100
29 | Bhasantec | 183 | 1600 | Kaptai | 5 | 2000 | Pabna | 131 | 2000
30 | Agargaon | 70 | 1300 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 99 | 2100
31 | Satmosjid | 115 | 1930 | Bakulia | 109 | 1200 | Serajganj | 106 | 1930
32 | Tongi | 165 | 1100 | Julda | 18 | 100 | Niyamatpur | 62 | 2100
33 | Kabirpur | 230 | 1500 | TK chemical | 4 | 1000 | Joypurhat | 49 | 100
34 | Basundhara | 128 | 1600 | Modern Steel | 14 | 1000 | Mohastangor | 15 | 1930
35 | Manikganj | 98 | 2000 | Shahmirpur | 31 | 400 | Rangpur | 145 | 2100
36 | Joydevpur | 236 | 2100 | Khagrachhari | 20 | 2000 | Lalmonirhat | 94 | 2000
37 | New Tongi | 109 | 1600 | Matarbari | 26 | 1930 | Saidpur | 113 | 2000
38 | Korda | 265 | 1930 | Baroiar Hat | 38 | 1900 | Purbasadipur | 107 | 2100
39 | Dhamrai | 60 | 2100 | Rangamati | 12 | 1930 | Thakurgaon | 76 | 2100
40 | Valuka | 102 | 1500 | Abul Khair 230 | 142 | 1700 | Palashbari | 118 | 2000
41 | Tangail | 188 | 2000 | BSRM | 106 | 1500 | Barapukuria | 49 | 2100
42 | Mymensing | 232 | 2000 | Goalpara | 29 | 2100 | Panchagar | 40 | 1930
43 | Kishorganj | 110 | 2000 | Central (S) | 96 | 2300 | Joldhaka | 20 | 2000
44 | Netrokona | 101 | 2100 | Noapara | 108 | 2200
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-06-19
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 393 | 5:00 | 382 | 19:00 | Kaliakoir | 372 | 6:00 | 356
2 | Bheramara | 396 | 6:00 | 383 | 15:00 | Bhulta | 387 | 5:00 | 370
3 | Ashuganj(N) | 391 | 2:00 | 377 | 11:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 11:00
1 | Ghorasal | 230 | 1:00 | 224 | 10:00 | Hathazari | 223 | 20:00 | 220
2 | Ishurdi | 237 | 18:30 | 223 | 21:00 | Megnaghat | 226 | 1:00 | 215
3 | Ashuganj | 236 | 5:00 | 228 | 11:00 | Fenchuganj | 237 | 5:00 | 230
4 | Serajganj | 234 | 8:00 | 227 | 21:00 | Siddhirganj | 226 | 5:00 | 214
5 | Baghabari | 230 | 9:00 | 224 | 21:00 | Maniknagar | 222 | 1:00 | 212
6 | Barapukuria | 233 | 6:00 | 220 | 22:00 | Old Airport | 222 | 6:00 | 210
7 | Bogra | 226 | 18:00 | 212 | 22:00 | Barisal | 231 | 1:00 | 222
8 | Khulna South | 231 | 18:30 | 222 | 21:00 | AKSML | 220 | 1:00 | 215
9 | Rampura | 224 | 3:00 | 214 | 11:00 | BSRM | 223 | 6:00 | 218
10 | Haripur | 221 | 3:00 | 213 | 11:00 | Bibiyana | 235 | 6:00 | 227
11 | Hasnabad | 222 | 4:00 | 210 | 11:00 | Bhulta | 225 | 4:00 | 214
12 | Aminbazar | 222 | 3:00 | 212 | 10:00 | Ashuganj (S) | 234 | 4:00 | 227
13 | Tongi | 225 | 5:00 | 214 | 9:00 | Kaliakoir | 226 | 5:00 | 215
14 | Comilla (N) | 230 | 2:00 | 222 | 11:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 129 | 400 | 122 | 1100 | Hathazari | 132 | 1400 | 128
2 | Munsiganj | 132 | 100 | 123 | 1000 | Khulshi | 132 | 1930 | 125
3 | Megnaghat | 129 | 2000 | 123 | 1000 | Halishahar | 135 | 1930 | 129
4 | Shyampur | 130 | 600 | 123 | 1000 | Baraulia | 132 | 500 | 127
5 | Bhulta | 124 | 1930 | 117 | 1100 | Sikalbaha | 136 | 1930 | 130
6 | Madanganj | 129 | 300 | 120 | 1100 | Dohazari | 136 | 1930 | 128
7 | Shitalakhya | 134 | 2000 | 123 | 1100 | Cox'sbazar | 128 | 1930 | 119
8 | Rahim steal | 129 | 100 | 123 | 1100 | Chandraghona | 134 | 1930 | 129
9 | Matuail | 129 | 400 | 121 | 1100 | Kaptai | 132 | 100 | 129
10 | Ghorasal | 137 | 1800 | 132 | 800 | A. Khaer Stl. | 130 | 1830 | 125
11 | Narsinghdi | 134 | 500 | 116 | 1100 | Bakulia | 134 | 1900 | 128
12 | Haripur (SBU) | 130 | 500 | 126 | 900 | Julda | 134 | 1800 | 129
13 | Ullon | 136 | 600 | 125 | 1100 | TK Chemical | 137 | 1900 | 130
14 | Hasnabad | 131 | 600 | 125 | 1000 | Modern Steel | 135 | 1900 | 129
15 | Magbazar | 135 | 600 | 123 | 1100 | Shahmirpur | 134 | 100 | 129
16 | Maniknagar | 135 | 600 | 128 | 1100 | Khagrachhari | 133 | 1800 | 128
17 | Bangabhaban | 135 | 600 | 128 | 1100 | Matarbari | 130 | 1800 | 122
18 | Narinda | 135 | 600 | 128 | 1100 | Baroiar Hat | 130 | 1300 | 122
19 | Dhanmondi | 135 | 600 | 128 | 1100 | Rangamati | 133 | 1800 | 128
20 | Lalbag | 131 | 600 | 120 | 1100 | Goalpara | 138 | 1700 | 133
21 | Madartek | 136 | 600 | 124 | 1100 | Central s/s | 137 | 1900 | 131
22 | Mirpur | 137 | 500 | 127 | 1100 | Noapara | 132 | 1900 | 127
23 | Kalyanpur | 138 | 200 | 130 | 1100 | Jessore | 126 | 300 | 117
24 | Gulshan | 134 | 300 | 124 | 1100 | Jhenida | 126 | 1830 | 112
25 | Uttara | 134 | 300 | 125 | 1100 | Bottail | 132 | 1800 | 120
26 | Uttara New | 136 | 100 | 124 | 1000 | G.K.Project | 140 | 1830 | 130
27 | Kamrangirchar | 138 | 100 | 120 | 1100 | Faridpur | 130 | 600 | 120
28 | Savar | 135 | 400 | 126 | 1100 | Madaripur | 134 | 1830 | 123
29 | Bhasantec | 137 | 400 | 127 | 1100 | Gopalganj | 144 | 2000 | 125
30 | Agargaon | 139 | 600 | 129 | 1100 | Bagerhat | 136 | 600 | 127
31 | Satmosjid | 138 | 500 | 128 | 1000 | Mongla | 132 | 500 | 125
32 | Tongi | 134 | 2000 | 127 | 900 | Satkhira | 134 | 1830 | 127
33 | Kabirpur | 133 | 700 | 125 | 1900 | Gallamari | 136 | 600 | 132
34 | Basundhara | 130 | 1300 | 122 | 1000 | Magura | 124 | 700 | 106
35 | Manikganj | 137 | 500 | 130 | 1300 | Chuadanga | 120 | 600 | 101
36 | Joydevpur | 139 | 600 | 128 | 1100 | Barisal | 135 | 500 | 129
37 | New Tongi | 133 | 2000 | 124 | 1000 | Patuakhali | 135 | 600 | 125
38 | Kodda | 140 | 1300 | 120 | 1000 | Bhandaria | 133 | 300 | 127
39 | Dhamrai | 134 | 500 | 125 | 1900 | Barisal (N) | 137 | 400 | 130
40 | Valuka | 125 | 1800 | 115 | 1900 | Sariatpur | 134 | 600 | 119
41 | Tangail | 135 | 500 | 122 | 1900 | Benapol | 127 | 1800 | 116
42 | Mymensing | 129 | 600 | 116 | 2200 | Ishurdi | 138 | 1800 | 129
43 | Kishorganj | 130 | 400 | 120 | 1900 | Ruppur Paromanobik | 138 | 1800 | 128
44 | Netrokona | 130 | 500 | 116 | 2200 | Natore | 134 | 1830 | 124
45 | Jamalpur | 136 | 300 | 128 | 1900 | Bogra | 133 | 1800 | 123
46 | Sherpur | 136 | 1200 | 126 | 2200 | Noagaon | 128 | 600 | 116
47 | Srimongal | 137 | 600 | 131 | 1900 | Rajshahi | 130 | 1800 | 118
48 | Shahjibazar | 135 | 700 | 129 | 2000 | C.Nawabganj | 127 | 1800 | 117
49 | Fenchuganj | 136 | 600 | 130 | 1900 | Amnura | 133 | 1830 | 120
50 | Khulawara | 134 | 500 | 130 | 1900 | Pabna | 136 | 1800 | 125
51 | Sylhet | 135 | 500 | 130 | 2000 | Shahjadpur | 140 | 500 | 132
52 | Chatak | 134 | 600 | 127 | 1900 | Serajganj | 134 | 1900 | 126
53 | Sunamganj | 133 | 700 | 125 | 1900 | Niyamatpur | 128 | 1800 | 109
54 | Biani Bazar | 134 | 500 | 127 | 1930 | Joypurhat | 129 | 600 | 114
55 | Comilla(s) | 124 | 500 | 119 | 1900 | Mohastangor | 132 | 600 | 119
56 | Comilla(n) | 135 | 700 | 132 | 900 | Rangpur | 127 | 600 | 111
57 | Chandpur | 137 | 1200 | 127 | 700 | Lalmonirhat | 120 | 600 | 105
58 | Feni | 129 | 1800 | 123 | 900 | Saidpur | 128 | 600 | 109
59 | Chowmuhani | 128 | 1200 | 116 | 2400 | Purbasadipur | 128 | 700 | 110
60 | Ashuganj | 136 | 600 | 130 | 1700 | Thakurgaon | 123 | 600 | 102
61 | Daudkandi | 128 | 700 | 123 | 900 | Palashbari | 128 | 1830 | 116
62 | B.Baria | 133 | 600 | 125 | 2100 | Barapukuria | 133 | 600 | 121

## L-Curve
Date | 2019-06-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 300 | 8592 | 3806 | 12398 |  |  |  | QF-LDC-12
0:30 | 260 | 8240 | 3727 | 11967 | Date: | 2019-06-19
1:00 | 220 | 7888 | 3648 | 11536
1:30 | 240 | 7793.5 | 3588 | 11381.5
2:00 | 260 | 7699 | 3528 | 11227
2:30 | 260 | 7632.5 | 3490.5 | 11123 | [5 empty] | Gen. at Eve. Peak | 12355 | 12355 MW (21:00 )
3:00 | 260 | 7566 | 3453 | 11019 | [6 empty] | 21:00
3:30 | 250 | 7500.5 | 3391.5 | 10892 | [5 empty] | Gen. at Day Peak | 10508.4 | 10508.4 MW (12:00 )
4:00 | 240 | 7435 | 3330 | 10765 | [6 empty] | 12:00
4:30 | 220 | 7314.5 | 3267.5 | 10582 | [5 empty] | Highest Generation | 12398
5:00 | 200 | 7194 | 3205 | 10399 | [6 empty] | 24:00
5:30 | 200 | 6908.8 | 3028.5 | 9937.3
6:00 | 200 | 6623.6 | 2852 | 9475.6
6:30 | 155 | 6444.9 | 2826.5 | 9271.4
7:00 | 110 | 6266.2 | 2801 | 9067.2
7:30 | 90 | 6301.3 | 2801.5 | 9102.8
8:00 | 70 | 6336.4 | 2802 | 9138.4
8:30 | 150 | 6559.2 | 2859 | 9418.2
9:00 | 230 | 6782 | 2916 | 9698
9:30 | 225 | 6861.65 | 2977.5 | 9839.15
10:00 | 220 | 6941.3 | 3039 | 9980.3
10:30 | 230 | 6928.15 | 3066 | 9994.15
11:00 | 240 | 6915 | 3093 | 10008
11:30 | 215 | 7087.2 | 3171 | 10258.2
12:00 | 190 | 7259.4 | 3249 | 10508.4
12:30 | 115 | 7484.55 | 3224 | 10708.55
13:00 | 40 | 7709.7 | 3199 | 10908.7
13:30 | 70 | 7735.8 | 3173.5 | 10909.3
14:00 | 100 | 7761.9 | 3148 | 10909.9
14:30 | 60 | 7907.3 | 3219 | 11126.3
15:00 | 20 | 8052.7 | 3290 | 11342.7
15:30 | 20 | 8106.3 | 3317.5 | 11423.8
16:00 | 20 | 8159.9 | 3345 | 11504.9
16:30 | 30 | 8076.2 | 3240.5 | 11316.7
17:00 | 40 | 7992.5 | 3136 | 11128.5
17:30 | 70 | 7580.75 | 3066.5 | 10647.25
18:00 | 100 | 7169 | 2997 | 10166
18:30 | 95 | 7534 | 3272.5 | 10806.5
19:00 | 90 | 7899 | 3548 | 11447
19:30 | 280 | 8375 | 3798 | 12173
20:00 | 280 | 8439 | 3826 | 12265 |  |  |  | Executive Engineer
20:30 | 310 | 8487.5 | 3822.5 | 12310 |  |  |  | Network Operation Division
21:00 | 340 | 8536 | 3819 | 12355
21:30 | 330 | 8500 | 3820.5 | 12320.5
22:00 | 320 | 8464 | 3822 | 12286 |  |  |  |  | Page 6 of 7
22:30 | 315 | 8500 | 3829.5 | 12329.5
23:00 | 310 | 8536 | 3837 | 12373
23:30 | 305 | 8564 | 3821.5 | 12385.5
24:00 | 300 | 8592 | 3806 | 12398
12355 MW (21:00 )
10508.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-06-19 |  | Energy | 261532624
[10 empty] | 2019-06-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4713 | 924 | 2462 | 3063 | 302 | 37 | 747 | 0 | 150
0:30 | 4630.5 | 928.5 | 2396 | 2928 | 307 | 36.5 | 592.5 | 0 | 148 | Date: | 2019-06-19
1:00 | 4548 | 933 | 2330 | 2793 | 312 | 36 | 438 | 0 | 146
1:30 | 4564 | 931 | 2284 | 2706 | 312 | 35.5 | 402 | 0 | 147 | [7 empty] | Total Energy | 261.5326 | Total Energy Gen 261.533 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.533 MKWHr
2:00 | 4580 | 929 | 2238 | 2619 | 312 | 35 | 366 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 4647.5 | 929.5 | 2241 | 2478.5 | 312 | 34.5 | 336 | 0 | 144 | [7 empty] | Energy Requirement | 261.5326
3:00 | 4715 | 930 | 2244 | 2338 | 312 | 34 | 306 | 0 | 140
3:30 | 4698.5 | 930 | 2240.5 | 2280 | 312.5 | 34 | 255.5 | 0 | 141 | [6 empty] | Shortage
4:00 | 4682 | 930 | 2237 | 2222 | 313 | 34 | 205 | 0 | 142
4:30 | 4601 | 930 | 2219.5 | 2145 | 313 | 34 | 211.5 | 0 | 128
5:00 | 4520 | 930 | 2202 | 2068 | 313 | 34 | 218 | 0 | 114
5:30 | 4393.5 | 930 | 2116 | 1846.5 | 313.5 | 34 | 193.5 | 0 | 110
6:00 | 4267 | 930 | 2030 | 1625 | 314 | 34 | 169 | 0 | 106
6:30 | 4228 | 930 | 1990 | 1503 | 313.5 | 36 | 163.5 | 0 | 106 |  |  |  |  | Coal
7:00 | 4189 | 930 | 1950 | 1381 | 313 | 38 | 158 | 0 | 106
7:30 | 4209 | 930 | 1972.5 | 1362 | 313 | 38 | 158 | 0 | 114 |  |  |  | Oil |  |  |  | ,
8:00 | 4229 | 930 | 1995 | 1343 | 313 | 38 | 158 | 0 | 122
8:30 | 4373 | 931 | 2050.5 | 1415 | 312.5 | 38 | 158 | 0 | 130
9:00 | 4517 | 932 | 2106 | 1487 | 312 | 38 | 158 | 0 | 138
9:30 | 4555 | 932.5 | 2155.5 | 1522.5 | 312 | 39 | 173 | 0 | 139
10:00 | 4593 | 933 | 2205 | 1558 | 312 | 40 | 188 | 0 | 140
10:30 | 4444 | 932.5 | 2257 | 1651 | 312 | 39.5 | 196 | 0 | 146
11:00 | 4295 | 932 | 2309 | 1744 | 312 | 39 | 204 | 0 | 152
11:30 | 4208 | 932 | 2315.5 | 2040.5 | 312 | 38.5 | 236 | 0 | 155
12:00 | 4121 | 932 | 2322 | 2337 | 312 | 38 | 268 | 0 | 158
12:30 | 4118 | 932 | 2266 | 2564 | 312 | 38 | 294.5 | 0 | 162
13:00 | 4115 | 932 | 2210 | 2791 | 312 | 38 | 321 | 0 | 166
13:30 | 4115 | 932 | 2210 | 2791 | 312 | 38 | 321 | 0 | 166
14:00 | 4115 | 932 | 2210 | 2791 | 312 | 38 | 321 | 0 | 166
14:30 | 4218 | 932 | 2251 | 2862 | 314 | 38 | 322 | 0 | 170
15:00 | 4321 | 932 | 2292 | 2933 | 316 | 38 | 323 | 0 | 174
15:30 | 4314.5 | 926.5 | 2332.5 | 2977 | 315 | 38 | 332 | 0 | 175
16:00 | 4308 | 921 | 2373 | 3021 | 314 | 38 | 341 | 0 | 176
16:30 | 4329 | 921.5 | 2331 | 2871 | 314 | 38 | 332.5 | 0 | 172
17:00 | 4350 | 922 | 2289 | 2721 | 314 | 38 | 324 | 0 | 168
17:30 | 4222 | 922 | 2071.5 | 2582 | 313.5 | 38 | 333 | 0 | 163
18:00 | 4094 | 922 | 1854 | 2443 | 313 | 38 | 342 | 0 | 158
18:30 | 4248.5 | 922.5 | 1910 | 2639 | 313 | 38 | 561.5 | 0 | 173
19:00 | 4403 | 923 | 1966 | 2835 | 313 | 38 | 781 | 0 | 188
19:30 | 4475 | 922 | 2237 | 3190 | 313 | 38 | 826 | 0 | 172
20:00 | 4465 | 924 | 2291 | 3232 | 313 | 38 | 844 | 0 | 158
20:30 | 4504 | 924.5 | 2326 | 3247.5 | 308 | 38 | 807 | 0 | 155
21:00 | 4543 | 925 | 2361 | 3263 | 303 | 38 | 770 | 0 | 152
21:30 | 4593.5 | 924.5 | 2373.5 | 3160 | 304.5 | 38 | 771.5 | 0 | 155
22:00 | 4644 | 924 | 2386 | 3057 | 306 | 38 | 773 | 0 | 158
22:30 | 4708.5 | 924.5 | 2395 | 3033.5 | 304 | 38 | 767 | 0 | 159
23:00 | 4773 | 925 | 2404 | 3010 | 302 | 38 | 761 | 0 | 160
23:30 | 4743 | 924.5 | 2433 | 3036.5 | 302 | 37.5 | 754 | 0 | 155 | Max Temp. in Dhaka |  | 36.6° C
24:00 | 4713 | 924 | 2462 | 3063 | 302 | 37 | 747 | 0 | 150
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 261.533 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.533 MKWHr
Note on W13: Author:

## Generation
2019-06-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 36 | 35 | 34 | 34 | 34 | 34 | 38 | 38 | 38 | 40 | 39 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 799980
2 | Kaptai Unit-4 & 5 | [26 empty] | 0
3 | Chattogram ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 5 | 100 | 100 | 100 | 2300000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW (RPCL) | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 13 | 19 | 25 | 25 | 25 | 25 | 25 |  | 0 |  | 0 | 8 | 25 | 25 | 25 | 401079
| Teknaf Solartech 20MW | [5 empty] | 0 | 0.5 | 6 | 4.5 | 6.1 | 14.3 | 12.5 | 19.3 | 17.2 | 10.7 | 9.8 | 1.6 | 1.5 |  | 0 | [6 empty] | 107190
6 | Sikalbaha 225MW (Gas) | 204 | 204 | 205 | 205 | 205 | 205 | 205 | 204 | 205 | 207 | 206 | 205 | 204 | 203 | 203 | 203 | 205 | 204 |  | 204 | 170 | 170 | 204 | 203 | 206 | 204 | 4796114
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 0 | 16 | 120 | 130 | 130 | 90 | 90 | 90 | 132 | 132 | 137 | 130 | 130 | 100 | 104 | 103 | 100 | 100 |  | 145 | 90 | 90 | 90 | 90 | 114 | 111 | 2362467
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 34 | 17 | 17 | 0 | [15 empty] | 58 | 68 | 68 | 68 | 68 | 68 | 68 | 440698
12 | Hathazari peaking | [19 empty] | 85 | 77 | 77 | 70 | 77 | 67 | 67 | 386760
Baraka Sikalbaha PL
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [19 empty] | 50 | 50 | 50 | 0 |  |  |  | 87656
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 200 | 200 | 200 | 170 | 170 | 120 | 120 | 120 | 150 | 180 | 214 | 213 | 150 | 160 | 210 | 213 | 213 | 130 |  | 180 | 180 | 180 | 180 | 180 | 217 | 217 | 4364147
18 | Summit Gazipur -2 | [10 empty] | 0 | 5 | 15 | 15 | 22 | 45 | 45 | 45 |  | 45 | 90 | 96 | 114 | 70 | 45 | 45 | 659890
19 | Ashuganj 195MW Modular | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 434909
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1102000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 188 | 190 | 190 | 190 | 190 | 190 |  | 191 | 190 | 190 | 190 | 190 | 190 | 190 | 4164000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 350 | 350 | 350 | 350 | 330 | 300 | 270 | 270 | 300 | 300 | 0 |  |  | 75 | 96 | 180 | 180 | 180 |  | 210 | 280 | 280 | 320 | 320 | 320 | 320 | 5945454
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2471500
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK
33 | Ashuganj CCPP 225 MW | 215 | 216 | 216 | 215 | 184 | 184 | 186 | 198 | 200 | 206 | 205 | 183 | 184 | 194 | 205 | 184 | 183 | 184 |  | 206 | 184 | 183 | 200 | 195 | 206 | 181 | 4797000
34 | Ashuganj CCPP(South) | 330 | 330 | 330 | 310 | 310 | 280 | 280 | 280 | 300 | 300 | 270 | 300 | 360 | 350 | 340 | 230 | 360 | 160 |  | 220 | 250 | 250 | 300 | 300 | 330 | 330 | 7274500
| Ashuganj CCPP(North) | 330 | 330 | 330 | 330 | 300 | 270 | 270 | 270 | 300 | 330 | 360 | 360 | 330 | 300 | 300 | 360 | 360 | 320 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8192100
35 | Ashuganj (Precision) 55MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 50 | 51 | 50 | 50 | 50 | 51 | 51 | 20 |  | 20 | 20 | 20 | 53 | 53 | 52 | 54 | 1215360
36 | Chandpur CCPP | 100 | 95 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 51 | 51 | 50 | 50 |  | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 1725610
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 328 | 330 | 338 | 328 | 329 | 327 | 330 | 331 | 365 | 364 | 345 | 351 | 329 | 345 | 365 | 344 | 329 | 331 |  | 340 | 330 | 339 | 347 | 347 | 352 | 346 | 8290300
40 | Meghnaghat CCPP 450MW | 400 | 400 | 400 | 400 | 370 | 340 | 340 | 380 | 400 | 400 | 430 | 430 | 430 | 400 | 450 | 450 | 450 | 370 |  | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 9498500
41 | Haripur Power CCPP 360MW | 354 | 304 | 304 | 304 | 304 | 274 | 275 | 302 | 304 | 305 | 310 | 335 | 305 | 274 | 339 | 338 | 338 | 277 |  | 309 | 308 | 308 | 338 | 347 | 347 | 352 | 7414000
42 | Mymensingh RPCL 210MW | 145 | 144 | 145 | 147 | 147 | 147 | 145 | 141 | 141 | 140 | 137 | 140 | 142 | 139 | 135 | 138 | 142 | 139 |  | 137 | 140 | 141 | 140 | 140 | 142 | 141 | 3320400
43 | Haripur NEPC 110MW | [10 empty] | 0 | 26 | 26 | 55 | 80 | 80 | 74 | 55 |  | 55 | 55 | 55 | 55 | 13 | 13 | 13 | 544600
44 | Fenchugonj CCPP-1 | 54 | 54 | 55 | 55 | 55 | 56 | 56 | 57 | 56 | 56 | 55 | 54 | 54 | 56 | 56 | 58 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1322000
45 | Fenchugonj CCPP-2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 58 | 57 | 57 | 57 | 57 | 57 | 57 | 57 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1364520
46 | Shajibazar 330 MW | 197 | 197 | 197 | 198 | 195 | 195 | 195 | 194 | 196 | 193 | 208 | 20 | 100 | 102 | 105 | 107 | 107 | 195 |  | 236 | 254 | 249 | 251 | 251 | 256 | 254 | 4136000
47 | Shahjibazar GT: Unit- 8, 9 | 40 | 53 | 63 | 63 | 50 | 42 | 49 | 61 | 61 | 59 | 59 | 59 | 40 | 59 | 58 | 59 | 40 | 59 |  | 59 | 61 | 61 | 59 | 60 | 61 | 50 | 1333056
48 | Shahjibazar 86MW | 82 | 82 | 82 | 82 | 82 | 83 | 80 | 80 | 80 | 80 | 82 | 78 | 78 | 80 | 79 | 79 | 79 | 40 |  | 40 | 79 | 81 | 80 | 80 | 80 | 80 | 1852800
49 | Shahjibazar (EPL) 50MW | 46 | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 43 | 43 | 43 | 43 | 44 | 43 | 20 |  | 20 | 20 | 45 | 45 | 45 | 45 | 45 | 983880
50 | Sylhet GT 150 MW | 112 | 112 | 114 | 111 | 112 | 110 | 72 | 85 | 117 | 118 | 125 | 110 | 95 | 110 | 96 | 84 | 94 | 84 |  | 123 | 114 | 110 | 120 | 120 | 122 | 109 | 2558140
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 46 | 12 | 12 | 12 | 37 | 44 | 44 | 45 | 45 | 42 | 43 | 44 | 20 |  | 20 | 47 | 42 | 47 | 46 | 47 | 47 | 912540
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 9 | 9 | 9 | 9 | 10 | 9 | 9 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 229320
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256896
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 53 | 50 | 50 | 50 | 53 | 50 | 53 | 53 | 53 | 50 | 50 | 53 | 13 |  | 13 | 39 | 53 | 53 | 53 | 53 | 50 | 1146600
56 | Shahjahanulla 25 MW | 15 | 15 | 15 | 23 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 16 | 24 |  | 24 | 16 | 16 | 16 | 24 | 24 | 24 | 475776
57 | Summit Bibiana- 2 | 275 | 280 | 290 | 275 | 270 | 260 | 280 | 285 | 300 | 300 | 300 | 265 | 260 | 260 | 305 | 310 | 290 | 280 |  | 290 | 300 | 300 | 300 | 310 | 320 | 310 | 7120700
58 | Southern 55MW | 55 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 |  | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 882000
59 | Sikalbaha (Energis) | 25 | 25 | 25 | 32 | 32 | 33 | 33 | 32 | 32 | 33 | 33 | 32 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 30 | 32 | 33 | 767040
60 | Barabkunda (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 485856
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 |  | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 429264
62 | Tangail (Doreen) 22MW | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 21 | 21 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 21 | 21 | 22 | 22 | 22 | 22 | 461736
63 | Tripura | 146 | 148 | 140 | 142 | 114 | 106 | 106 | 122 | 138 | 140 | 152 | 158 | 166 | 170 | 174 | 176 | 168 | 158 |  | 188 | 172 | 158 | 152 | 158 | 160 | 150 | 3580800
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 39 | 39 | 38 | 29 | 12 | 3 | 2 | 2 | 4 | 8 | 5 | 5 | 6 | 9 | 7 |  | 12 | 21 | 25 | 30 | 37 | 38 | 41 | 478560
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 19 | 19 | 19 | 21 | 21 | 18 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495720
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 8 | 8 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 183060
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 796300
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 457080
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 20 | 20 | 20 | 20 | 19 | 19 | 22 | 22 | 22 | 27 | 30 | 30 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 30 | 30 | 30 | 580500
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 624000
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 828600
73 | Ghorashal (Regent) | 107 | 107 | 106 | 106 | 106 | 107 | 54 | 54 | 54 | 77 | 100 | 102 | 100 | 102 | 101 | 103 | 103 | 103 |  | 103 | 103 | 103 | 106 | 106 | 104 | 104 | 2240409
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | [15 empty] | 4 | 7 | 7 |  | 7 | 15 | 45 | 50 | 50 | 50 | 50 | 309120
78 | Gazipur (RPCL) | 49 | 49 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 0 | 15 | 35 | 42 | 49 | 48 | 48 | 49 | 49 |  | 49 | 49 | 42 | 0 | 0 | 2 | 44 | 816192
79 | Kodda 149MW | 130 | 98 | 64 | 48 | 48 | 16 | 0 |  |  | 0 | 16 | 80 | 125 | 127 | 127 | 127 | 98 | 95 |  | 110 | 127 | 125 | 125 | 125 | 125 | 125 | 1902240
80 | Jamalpur 95MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 84 | 76 | 76 | 76 | 84 | 84 |  | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 2010240
81 | Lakdhanvi 52 MW | 52 | 52 | 8 | 8 | 8 | 8 | 0 |  | 0 | 7 | 46 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 898090
| Gazipur 100 MW | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 2535600
| Kaptai Solar |  |  |  |  | 0 | 0.4 | 1.2 | 3.5 | 4.1 | 3.3 | 4.7 | 5.8 | 2.8 | 5.9 | 1.7 | 2.2 | 0.4 | 0 | [8 empty] | 36960
82 | Madanganj 102MW | 30 | 30 | 15 | 15 | 0 | [9 empty] | 5 | 15 | 15 | 15 |  | 15 | 15 | 15 | 0 |  |  |  | 223464
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [10 empty] | 0 | 5 | 40 | 54 | 72 | 72 | 45 | 13 |  | 13 | 50 | 50 | 50 | 10 | 10 | 10 | 491832
86 | Meghnaghat CCPP(Summit) | 260 | 265 | 260 | 255 | 250 | 270 | 275 | 283 | 250 | 215 | 200 | 188 | 224 | 250 | 201 | 200 | 270 | 262 |  | 295 | 275 | 260 | 260 | 160 | 160 | 185 | 5835142
87 | Meghnaghat (IEL) | 0 | [9 empty] | 0 | 15 | 88 | 99 | 100 | 100 | 50 | 9 |  | 9 | 30 | 55 | 55 | 55 | 55 | 55 | 777600
88 | Ghorashal 78MW (MAX) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 63 | 63 | 63 | 50 | 50 | 62 | 62 | 62 |  | 63 | 63 | 63 | 63 | 63 | 64 | 64 | 1378272
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 70 | 70 | 40 | 40 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 524760
92 | Fenchuganj (EPL) 44MW | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 49 | 49 | 49 | 49 | 49 | 20 |  | 20 | 49 | 49 | 49 | 49 | 49 | 49 | 1157328
93 | Ashuganj (Midland) 51MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 959200
94 | Gagnagar (Orion) | 16 | 16 | 7 | 7 | 0 |  |  |  | 16 | 16 | 32 | 64 | 100 | 100 | 100 | 100 | 40 | 40 |  | 72 | 72 | 72 | 70 | 70 | 70 | 70 | 1108944
95 | Patenga 50MW | 47 | 41 | 47 | 47 | 46 | 40 | 13 | 24 | 26 | 41 | 45 | 45 | 45 | 46 | 46 | 46 | 47 | 47 |  | 47 | 37 | 47 | 47 | 47 | 47 | 47 | 1028160
96 | Chattogram ECPV 108 MW | 44 | 44 | 16 | 12 | 12 | 12 | 0 |  |  |  | 0 | 38 | 82 | 83 | 82 | 84 | 89 | 95 |  | 97 | 55 | 31 | 32 | 32 | 31 | 32 | 1012800
97 | Katpotti 51 MW | 26 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 23 | 48 | 48 | 14 | 6 | 352032
98 | Bosila 108MW | 71 | 71 | 72 | 72 | 72 | 8 | 8 | 8 | 60 | 69 | 69 | 67 | 67 | 67 | 59 | 67 | 66 | 66 |  | 70 | 70 | 71 | 70 | 72 | 72 | 73 | 1419840
99 | Madanganj-55 MW | [10 empty] | 0 | 10 | 30 | 30 | 55 | 55 | 55 | 30 |  | 30 | 30 | 45 | 55 | 55 | 55 | 55 | 575520
100 | Northern 55 MW | 55 | 35 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 36 | 55 | 36 | 37 | 37 | 36 | 35 | 36 |  | 35 | 35 | 36 | 35 | 35 | 35 | 35 | 796520
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 130 | 100 | 130 | 163 | 130 | 130 |  | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 3191375
102 | Sarishabari (Solar) |  |  |  |  | 0 | 0.2 | 0.5 | 0.9 | 1.4 | 1.9 | 2 | 2.1 | 1.6 | 1.8 | 1.3 | 0.9 | 0.5 | 0.5 |  | 0 | [6 empty] | 12950
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 40 | 35 |  | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 1201320
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 192 | 192 | 192 | 192 | 192 | 100 | 50 | 50 | 50 | 50 | 50 | 81 | 100 | 100 | 125 | 150 | 100 | 100 |  | 125 | 187 | 180 | 180 | 180 | 180 | 180 | 3273600
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 133 | 102 | 34 | 15 | 15 | 15 | 0 |  | 7 | 31 | 43 | 110 | 149 | 149 | 149 | 149 | 132 | 90 |  | 90 | 149 | 139 | 149 | 149 | 149 | 149 | 2177280
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 20 | 50 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 223584
116 | Chandpur Desh 200MW | 200 | 200 | 200 | 160 | 160 | 95 | 17 | 17 | 17 | 38 | 70 | 160 | 195 | 200 | 200 | 200 | 200 | 160 |  | 160 | 200 | 200 | 200 | 200 | 200 | 200 | 3661440
117 | Midland 150MW | [9 empty] | 0 | 1 | 50 | 130 | 130 | 133 | 137 | 137 | 138 |  | 139 | 132 | 132 | 133 | 133 | 140 | 140 | 1669382
118 | Bibiyana-3 285 MW | 294 | 293 | 293 | 298 | 250 | 250 | 250 | 250 | 250 | 250 | 285 | 291 | 291 | 260 | 261 | 261 | 261 | 220 |  | 222 | 287 | 289 | 288 | 288 | 286 | 294 | 6525000
| United Jamalpur PPL | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 95 | 94 | 94 | 94 | 94 | 93 | 93 | 92 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 94 | 93 | 2229600
| Anwara United | 304 | 304 | 304 | 304 | 296 | 298 | 298 | 291 | 304 | 304 | 303 | 304 | 304 | 304 | 304 | 304 | 304 | 304 |  | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 7293927
120 | Eastern Zone Total | 7888 | 7699 | 7566 | 7435 | 7194 | 6623.6 | 6266.2 | 6336.4 | 6782 | 6941.3 | 6915 | 7259.4 | 7709.7 | 7761.9 | 8052.7 | 8159.9 | 7992.5 | 7169 |  | 7899 | 8375 | 8439 | 8536 | 8464 | 8536 | 8592 | 181408681
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 99 | 74 | 66 | 66 | 16 | 16 | 0 |  |  |  | 0 | 49 | 49 | 49 | 73 | 99 | 82 | 49 |  | 90 | 99 | 99 | 99 | 115 | 115 | 115 | 1350720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 32 | 32 | 32 | 32 | 0 | [12 empty] | 10 |  | 24 | 30 | 34 | 32 | 31 | 31 | 31 | 290400
| Khulna CCPP 225MW | 10 | 20 | 30 | 60 | 105 | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2614080
129 | Labon Chora 105 MW | 70 | 70 | 70 | 70 | 70 | 22 | 17 | 17 | 17 | 17 | 17 | 70 | 105 | 70 | 70 | 70 | 35 | 17 |  | 100 | 105 | 105 | 105 | 105 | 70 | 70 | 1460160
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 80 | 80 | 32 | 0 | [8 empty] | 48 | 48 | 16 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1008960
136 | Barisal GT: Unit-1, 2 | [19 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 69099
137 | Bhola Aggreko 95MW | 98 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 97 | 97 | 97 | 97 | 97 | 96 | 95 | 95 | 64 |  | 70 | 95 | 96 | 98 | 98 | 98 | 96 | 2256226
| Bhola CCPP 194MW | 171 | 171 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 |  | 172 | 172 | 171 | 172 | 172 | 172 | 172 | 4204225
140 | Bhola (Venture) 33MW | 38 | 37 | 33 | 32 | 32 | 27 | 27 | 18 | 24 | 26 | 26 | 27 | 28 | 27 | 27 | 26 | 25 | 25 |  | 32 | 39 | 37 | 37 | 38 | 39 | 38 | 717664
141 | Bangla Trak Noapara | 99 | 70 | 50 | 0 | [15 empty] | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 803520
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 0 |  |  |  | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 676125
143 | Gopalganj Peaking | 25 | 0 | [13 empty] | 18 | 30 | 33 |  | 38 | 46 | 55 | 40 | 35 | 35 | 24 | 317312
144 | Bheramara GT-1,2,3 | [19 empty] | 30 | 30 | 28 | 28 | 28 | 30 | 28 | 163500
145 | Madhumati Power Plant | 88 | 88 | 88 | 88 | 88 | 72 | 53 | 54 | 54 | 58 | 71 | 70 | 70 | 71 | 70 | 70 | 76 | 79 |  | 88 | 88 | 87 | 87 | 87 | 106 | 105 | 1859760
146 | Bheramara HVDC | 933 | 929 | 930 | 930 | 930 | 930 | 930 | 930 | 932 | 933 | 932 | 932 | 932 | 933 | 932 | 921 | 922 | 922 |  | 923 | 922 | 924 | 925 | 924 | 925 | 924 | 22279272
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 63 | 63 | 63 | 64 | 64 | 65 | 64 | 64 | 63 | 63 | 63 | 63 | 63 | 63 | 67 | 65 | 65 | 64 |  | 64 | 64 | 64 | 63 | 66 | 63 | 63 | 1515490
152 | Barapukuria Unit-3 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 |  | 249 | 249 | 249 | 240 | 240 | 239 | 239 | 6020200
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 50 | 50 | 50 | 50 | 50 | 55 |  | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 1345000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 43 | 35 | 0 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 9 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 412768
157 | Sirajgonj Unit-1 225MW (Gas) | 182 | 187 | 193 | 193 | 186 | 162 | 160 | 161 | 193 | 203 | 195 | 196 | 181 | 191 | 196 | 192 | 183 | 182 |  | 162 | 171 | 163 | 169 | 170 | 172 | 169 | 4609127
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 178 | 183 | 188 | 188 | 181 | 159 | 157 | 159 | 192 | 201 | 201 | 194 | 180 | 190 | 198 | 190 | 180 | 178 |  | 154 | 168 | 160 | 160 | 159 | 163 | 160 | 4449091
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 205 | 202 | 202 | 202 | 196 | 183 | 172 | 178 | 178 | 191 | 181 | 196 | 184 | 182 | 196 | 208 | 194 | 185 |  | 176 | 176 | 178 | 181 | 182 | 182 | 182 | 4742173
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 414 | 370 | 370 | 370 | 370 | 300 | 300 | 300 | 350 | 405 | 400 | 420 | 375 | 340 | 380 | 408 | 370 | 300 |  | 350 | 400 | 415 | 408 | 408 | 414 | 416 | 8990909
161 | Bera Peaking | 0 | [16 empty] | 7 |  | 22 | 27 | 27 | 27 | 27 | 27 | 27 | 157621
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 18 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 484800
163 | Bogra (EPL) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 11 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 9 | 10 |  | 11 | 11 | 11 | 11 | 10 | 11 | 10 | 247932
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 221220
165 | Amnura 50MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 |  | 33 | 33 | 33 | 33 | 6 | 6 | 6 | 236820
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 24 | 42 | 42 | 446683
167 | Katakhali Peaking | 44 | 44 | 43 | 0 | [15 empty] | 41 | 44 | 47 | 44 | 46 | 43 | 43 | 384100
168 | Santahar Peaking | 27 | 27 | 27 | 27 | 27 | 0 | [13 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 295290
169 | Rajlanka 52 MW | 51 | 51 | 51 | 46 | 25 | 8 |  |  |  | 0 | 25 | 50 | 49 | 49 | 52 | 49 | 8 | 8 |  | 8 | 41 | 42 | 50 | 50 | 50 | 50 | 755520
170 | Chapainawabganj-100 MW | 93 | 93 | 93 | 38 | 38 | 38 | 38 | 38 | 38 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 81 | 85 | 90 | 93 | 93 | 93 | 90 | 1424440
171 | Paramount Baghabari
172 | Confidence Bogura-2 (CPBL) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 107 | 108 | 2589216
173 | Rangpur GT | 0 | [18 empty] | 16 | 16 | 17 | 17 | 17 | 16 | 17 | 92000
175 | Saidpur GT | 0 | [18 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 93000
176 | Confidence Rangpur | 23 | 23 | 23 | 23 | 24 | 20 | 20 | 20 | 20 | 23 | 23 | 25 | 23 | 23 | 23 | 24 | 23 | 9 |  | 7 | 7 | 14 | 20 | 19 | 19 | 11 | 539520
177
178
178 | Western Zone Total | 3648 | 3528 | 3453 | 3330 | 3205 | 2852 | 2801 | 2802 | 2916 | 3039 | 3093 | 3249 | 3199 | 3148 | 3290 | 3345 | 3136 | 2997 | 0 | 3548 | 3798 | 3826 | 3819 | 3822 | 3837 | 3806 | 80123943