## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-07 | Monday
|  |  | Date (day): | 2022-03-07 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12883.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13494 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-06 | 2022-03-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 340 | 340 | 340
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 45 | 97 | 108 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 25 | 280 | 280 | 280 | 55 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 94 | 95 | 95 | 115 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 148 | 157 | 200 | 200 | 135 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 84 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 110 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 49 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 28 | 30 | 30 |  |  | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 34 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 277 | 291 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 25 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 137 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 88 | 84 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2333 | 2857 | 3306 | 3376 | 1026 | 979
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 6 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 42 | 42 | 42 |  | 8 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 |  | 184 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 40 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 19 | 19 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 10 | 10 | 10
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 91 | 96 | 100 | 100 |  | 8 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 265 | 276 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 79 | 90 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 115 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1066 | 1167 | 1290 | 1265 | 180 | 914
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 190 | 200 | 200 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 320 | 310 | 335 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 315 | 330 | 335 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 147 | 175 | 68 | 68 | 127 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 98 | 115 | 140 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 33 | 32 | 33 | 33 |  | 19 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 92 | 154 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 130 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 15 | 15
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 72 | 72 | 115 | 115 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1683 | 1844 | 1975 | 2138 | 561 | 229
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 189 | 200 | 210 | 210
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 175 | 173 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 98 | 108 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 556 | 523 | 618.6 | 567 | 0 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 160 | 160 | 160 | 170 |  | Gas shortage
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 51 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 89 | 86 | 89
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 24 | 21 | 24
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 80 | 240 | 240 | 240 | 160 |  | Gas shortage
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 343 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1282 | 1507 | 1538 | 1544 | 634 | 200
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 719 | 719 | 733 | 733
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 5 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 380 | 410 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1283 | 1249 | 1448 | 1748 | 0 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 7 | 9 | 10 | 10 |  |  | Engine problem
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 92 | 90 | 91 | 103 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 22 | 22 | 22 | 22 | 73 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 240 | 380 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 223 | 225 | 225
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 581 | 726 | 1127 | 1228 | 176 | 0
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 100 | 100 | 100 | 100 | 0
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 34 | 34 |  | 18 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 25 | 35 | 40 | 41 |  | 30 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 50 | 50
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 31 | 0 | 40 |  | 10 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 5 | 200 | 200 | 220 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 178 | 200 | 220
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 22 | 22 |  | 28 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 0 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 56 | 97 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 658 | 839 | 1260 | 1315 | 500 | 500
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 112 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 98 | 0 | 0 | 0 |  |  | On test
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 415 | 312 | 321 | 313 | 74 | 125
|  | Total |  |  |  |  | 22066 | 20985 | 9857 | 11024 | 12883.6 | 13494 | 3151 | 3038
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9446.5897 | 10565 | 12347.1729 | 12932.158
| A. |  | 2022-03-06 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 11024 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7301 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11024 | MW
| 3 | Day peak Generation : |  |  | 9857 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10565 | MW
| 4 | Evening peak Generation : |  |  | 11024 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 223.8822 | MKWHr | By Solar | 1.4299 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 116.6739 | MKWHr |  | By Oil: | 71.5126 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.142 | MKWHr |  | By Hydro: | 1.1094 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3151 | MW | Dhaka | 3837 | 3837 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3038 | MW | Chittagong | 1151 | 1151 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6189 | MW | Khulna | 1229 | 1229 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 922.08 | MMCFD |  |  | Rajshahi | 1128 | 1128 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 116819173.07 | ii) Oil : | Taka | 498721060.14 | Comilla | 884 | 884 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 62707523 | Total | Taka | 678247756.21 | Mymensingh | 957 | 957 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.0155 | MKWHr. | Sylhet | 385 | 385 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -374 | MW (E to W) at | 19:00 | hrs | Barisal | 274 | 274 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -374 | MW at | 19:00 | hrs | Rangpur | 720 | 720 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.6° C |  |  | Total | 10565 | 10565 |  | 0
| B. |  | 2022-03-07 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13494 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
| 4 | Reserve(Generation end) |  |  |  | 1994 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 233.5491 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7432 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3811 | MKWHr. | ii) HVDC Flow at Peak Time |  | 719 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6333 | MKWHr. | iii) Maximum HVDC Flow : |  | 719 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.81 |  | (b) Today: | 89.66 |  | (c) Rule Curve: |  | 92.04
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 164 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 40 | 0 | 0 | 0 | 310 | 305 | 181 | 26 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 11 | 25 | 15 | 102 | 215 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 110 | 159 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 11 | 0 | 95 | 0 | 0 | 187 | 0 | 149 | 0 | 90 | 0 | 80 | 79 | 24 | 70 | 105 | 0 | 270 | 54 | 110 | 0 | 0 | 50 | 355 | 97 | 0 | 144 | 115 | 0 | 17 | 0 | 0 | 55 |  | 719 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 220 | 0 | 0 | 70 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 360 | 203 | 0 | 0 | 0 | 0 | 0 |  | 5772 | 2586 | 8358 | 3417 | 719 | 1192 | 0 | 2322 | 560 | 46 | 0 | 0 | 102 | 0 | 0 | 89.83
2:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 165 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 40 | 0 | 0 | 0 | 310 | 305 | 184 | 26 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 22 | 11 | 25 | 15 | 100 | 215 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 110 | 159 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 21 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 109 | 0 | 90 | 0 | 97 | 79 | 0 | 34 | 68 | 0 | 282 | 54 | 110 | 0 | 0 | 10 | 355 | 88 | 0 | 144 | 115 | 0 | 17 | 0 | 0 | 55 |  | 719 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 220 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 350 | 223 | 0 | 0 | 0 | 0 | 0 |  | 5411 | 2458 | 7869 | 3423 | 719 | 1203 | 0 | 1828 | 550 | 46 | 0 | 0 | 100 | 0 | 0 | 89.83
3:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 40 | 0 | 0 | 0 | 310 | 305 | 182 | 26 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 22 | 11 | 25 | 15 | 98 | 215 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 101 | 0 | 90 | 0 | 100 | 80 | 0 | 0 | 34 | 0 | 264 | 54 | 110 | 0 | 0 | 10 | 310 | 70 | 0 | 108 | 115 | 0 | 17 | 0 | 0 | 55 |  | 719 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 220 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 310 | 223 | 0 | 0 | 0 | 0 | 0 |  | 5232 | 2387 | 7619 | 3350 | 719 | 1214 | 0 | 1683 | 509 | 46 | 0 | 0 | 98 | 0 | 0 | 89.82
4:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 165 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 40 | 0 | 0 | 0 | 310 | 305 | 181 | 26 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 22 | 11 | 25 | 15 | 94 | 215 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 285 | 21 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 106 | 0 | 90 | 0 | 100 | 80 | 0 | 0 | 17 | 0 | 265 | 54 | 110 | 0 | 0 | 10 | 250 | 70 | 0 | 108 | 115 | 0 | 17 | 0 | 0 | 55 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 220 | 0 | 0 | 35 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 290 | 224 | 0 | 0 | 0 | 0 | 0 |  | 5154 | 2306 | 7460 | 3242 | 719 | 1220 | 0 | 1649 | 490 | 46 | 0 | 0 | 94 | 0 | 0 | 89.82
5:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 167 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 40 | 0 | 0 | 0 | 280 | 295 | 181 | 26 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 22 | 11 | 25 | 15 | 92 | 215 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 275 | 21 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 106 | 0 | 90 | 0 | 100 | 80 | 0 | 0 | 17 | 0 | 265 | 54 | 110 | 0 | 0 | 10 | 200 | 70 | 0 | 108 | 95 | 0 | 17 | 0 | 0 | 35 |  | 718 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 6 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 220 | 0 | 0 | 35 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 280 | 214 | 0 | 0 | 0 | 0 | 0 |  | 5017 | 2284 | 7301 | 3157 | 718 | 1199 | 0 | 1609 | 480 | 46 | 0 | 0 | 92 | 0 | 0 | 89.81
6:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 173 | 0 | 96 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 42 | 0 | 0 | 0 | 295 | 335 | 202 | 26 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 24 | 22 | 11 | 25 | 15 | 92 | 215 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 161 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 310 | 21 | 8 | 0 | 2 | 0 | 0 | 160 | 0 | 105 | 0 | 70 | 5 | 100 | 80 | 6 | 9 | 17 | 0 | 265 | 54 | 110 | 3 | 0 | 40 | 200 | 70 | 0 | 121 | 87 | 0 | 17 | 0 | 5 | 46 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 206 | 0 | 0 | 40 | 0 | 103 | 0 | 44 | 0 | 0 | 35 | 280 | 223 | 0 | 0 | 0 | 0 | 0 |  | 5226 | 2381 | 7607 | 3226 | 719 | 1246 | 0 | 1798 | 480 | 46 | 0 | 0 | 92 | 0 | 0 | 89.81
7:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 20 | 194 | 0 | 96 | 0 | 58 | 48 | 0 | 0 | 0 | 0 | 54 | 26 | 50 | 22 | 25 | 30 | 25 | 33 | 9 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 99 | 42 | 18 | 38 | 0 | 0 | 0 | 270 | 305 | 186 | 26 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 34 | 22 | 11 | 25 | 15 | 92 | 216 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 310 | 21 | 8 | 0 | 68 | 0 | 0 | 170 | 0 | 114 | 1 | 70 | 30 | 100 | 80 | 58 | 49 | 17 | 0 | 248 | 54 | 110 | 85 | 0 | 40 | 205 | 77 | 4 | 144 | 87 | 0 | 17 | 3 | 31 | 55 |  | 719 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 207 | 0 | 0 | 88 | 0 | 113 | 0 | 54 | 0 | 0 | 100 | 280 | 223 | 0 | 0 | 0 | 7 | 56 |  | 5698 | 2605 | 8303 | 3202 | 719 | 1242 | 0 | 2459 | 480 | 46 | 0 | 48 | 92 | 15 | 0 | 89.8
8:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 0 | 0 | 0 | 45 | 184 | 0 | 95 | 0 | 76 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 30 | 30 | 17 | 25 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 6 | 0 | 0 | 0 | 280 | 330 | 194 | 0 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 25 | 15 | 98 | 216 | 0 | 20 | 1 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 8 | 0 | 270 | 0 | 0 | 170 | 0 | 149 | 4 | 70 | 80 | 100 | 80 | 105 | 90 | 17 | 2 | 246 | 54 | 110 | 114 | 0 | 40 | 240 | 88 | 18 | 144 | 87 | 0 | 12 | 11 | 52 | 0 |  | 719 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 186 | 0 | 0 | 105 | 0 | 113 | 0 | 105 | 0 | 1 | 113 | 270 | 223 | 0 | 0 | 1 | 26 | 54 |  | 6164 | 2700 | 8864 | 3237 | 719 | 1154 | 0 | 3028 | 470 | 46 | 0 | 48 | 98 | 64 | 0 | 89.8
9:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 12 | 0 | 0 | 55 | 154 | 0 | 95 | 0 | 93 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 30 | 30 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 99 | 42 | 18 | 2 | 0 | 0 | 0 | 345 | 315 | 195 | 55 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 49 | 20 | 8 | 25 | 15 | 100 | 210 | 0 | 20 | 2 | 30 | 30 | 48 | 0 | 110 | 161 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 21 | 5 | 0 | 290 | 0 | 0 | 180 | 0 | 149 | 10 | 82 | 85 | 100 | 80 | 109 | 90 | 22 | 3 | 246 | 54 | 110 | 114 | 0 | 40 | 320 | 87 | 31 | 144 | 95 | 0 | 17 | 20 | 56 | 45 |  | 718 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 197 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 3 | 113 | 240 | 223 | 0 | 0 | 3 | 48 | 54 |  | 6484 | 2724 | 9208 | 3327 | 718 | 1221 | 0 | 3185 | 439 | 46 | 0 | 52 | 100 | 120 | 0 | 89.79
10:00 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 |  | 0 | 300 | 12 | 0 | 0 | 40 | 160 | 0 | 95 | 0 | 93 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 30 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 18 | 2 | 0 | 0 | 0 | 315 | 310 | 160 | 73 | 0 | 26 | 5 | 0 | 43 | 0 | 0 | 43 | 20 | 11 | 23 | 15 | 102 | 206 | 0 | 20 | 2 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 5 | 0 | 290 | 0 | 0 | 178 | 0 | 149 | 19 | 90 | 85 | 98 | 80 | 99 | 90 | 53 | 4 | 246 | 54 | 110 | 114 | 0 | 40 | 350 | 90 | 42 | 144 | 114 | 0 | 17 | 25 | 72 | 55 |  | 719 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 4 | 32 | 0 | 0 | 12 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 193 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 240 | 221 | 0 | 0 | 4 | 72 | 54 |  | 6565 | 2780 | 9345 | 3285 | 719 | 1239 | 0 | 3246 | 440 | 46 | 0 | 96 | 102 | 172 | 0 | 89.79
11:00 | 0 | 0 | 0 | 0 | 340 | 15 | 0 | 0 | 0 |  | 0 | 300 | 12 | 0 | 0 | 40 | 159 | 0 | 95 | 0 | 93 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 24 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 92 | 42 | 20 | 2 | 0 | 0 | 0 | 310 | 305 | 192 | 102 | 0 | 26 | 5 | 0 | 43 | 0 | 17 | 52 | 20 | 11 | 20 | 17 | 106 | 201 | 0 | 20 | 2 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 9 | 300 | 21 | 5 | 0 | 290 | 0 | 0 | 177 | 0 | 140 | 15 | 90 | 85 | 98 | 80 | 98 | 90 | 86 | 5 | 265 | 54 | 110 | 114 | 0 | 46 | 343 | 88 | 49 | 144 | 115 | 0 | 17 | 32 | 72 | 55 |  | 719 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 7 | 56 | 0 | 0 | 21 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 194 | 0 | 0 | 105 | 0 | 105 | 0 | 113 | 0 | 5 | 95 | 240 | 221 | 0 | 0 | 5 | 85 | 54 |  | 6676 | 2825 | 9501 | 3293 | 719 | 1282 | 0 | 3268 | 440 | 46 | 0 | 149 | 106 | 198 | 0 | 89.78
12:00 | 0 | 0 | 0 | 0 | 340 | 45 | 0 | 0 | 0 |  | 0 | 300 | 25 | 0 | 0 | 55 | 148 | 0 | 95 | 0 | 93 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 30 | 33 | 33 | 34 | 0 | 46 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 60 | 91 | 0 | 20 | 2 | 0 | 0 | 0 | 310 | 305 | 186 | 147 | 0 | 26 | 5 | 0 | 43 | 0 | 33 | 52 | 20 | 11 | 16 | 18 | 118 | 189 | 0 | 20 | 2 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 9 | 300 | 21 | 5 | 0 | 277 | 0 | 0 | 175 | 0 | 137 | 18 | 90 | 92 | 98 | 80 | 98 | 90 | 105 | 5 | 265 | 54 | 110 | 114 | 0 | 79 | 343 | 88 | 50 | 144 | 115 | 0 | 17 | 32 | 72 | 55 |  | 719 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 25 | 56 | 0 | 0 | 24 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 199 | 0 | 0 | 105 | 0 | 94 | 0 | 112 | 0 | 6 | 95 | 240 | 221 | 0 | 0 | 5 | 89 | 98 |  | 6920 | 2937 | 9857 | 3322 | 719 | 1370 | 0 | 3388 | 439 | 46 | 0 | 248 | 118 | 207 | 0 | 89.78
13:00 | 0 | 0 | 0 | 0 | 340 | 57 | 0 | 0 | 0 |  | 0 | 300 | 100 | 0 | 0 | 55 | 155 | 0 | 92 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 86 | 97 | 9 | 20 | 7 | 0 | 0 | 0 | 310 | 305 | 183 | 175 | 0 | 29 | 5 | 0 | 43 | 0 | 31 | 43 | 20 | 11 | 25 | 18 | 120 | 175 | 0 | 20 | 2 | 30 | 30 | 49 | 0 | 110 | 161 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 275 | 21 | 5 | 0 | 282 | 0 | 0 | 175 | 0 | 135 | 15 | 90 | 120 | 97 | 80 | 99 | 90 | 105 | 5 | 265 | 39 | 110 | 114 | 0 | 88 | 300 | 87 | 49 | 162 | 115 | 0 | 17 | 32 | 72 | 55 |  | 719 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 100 | 0 | 0 | 33 | 56 | 0 | 0 | 24 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 206 | 0 | 0 | 105 | 0 | 94 | 0 | 110 | 0 | 5 | 105 | 240 | 221 | 0 | 0 | 5 | 86 | 115 |  | 7116 | 2985 | 10101 | 3315 | 719 | 1471 | 0 | 3497 | 440 | 46 | 0 | 294 | 120 | 199 | 0 | 89.77
14:00 | 0 | 0 | 0 | 0 | 340 | 56 | 0 | 0 | 0 |  | 0 | 300 | 120 | 0 | 0 | 40 | 145 | 0 | 92 | 0 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 28 | 28 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 97 | 38 | 20 | 5 | 0 | 0 | 0 | 305 | 305 | 188 | 177 | 0 | 29 | 5 | 0 | 43 | 0 | 32 | 52 | 19 | 11 | 25 | 18 | 122 | 175 | 0 | 20 | 2 | 30 | 30 | 45 | 0 | 110 | 160 | 40 | 87 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 5 | 0 | 245 | 0 | 0 | 174 | 0 | 135 | 16 | 90 | 34 | 93 | 197 | 99 | 90 | 105 | 4 | 265 | 52 | 107 | 77 | 0 | 88 | 250 | 87 | 42 | 162 | 114 | 0 | 17 | 28 | 71 | 55 |  | 719 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 8 | 0 | 0 | 100 | 0 | 0 | 38 | 56 | 0 | 0 | 24 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 164 | 0 | 0 | 105 | 0 | 94 | 0 | 70 | 0 | 5 | 113 | 240 | 183 | 0 | 0 | 5 | 77 | 17 |  | 6771 | 2698 | 9469 | 3272 | 719 | 1451 | 0 | 3058 | 440 | 46 | 0 | 182 | 122 | 179 | 0 | 89.77
15:00 | 0 | 0 | 0 | 0 | 340 | 54 | 0 | 0 | 0 |  | 0 | 300 | 120 | 0 | 0 | 36 | 154 | 0 | 92 | 0 | 93 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 29 | 28 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 97 | 40 | 20 | 2 | 0 | 0 | 0 | 325 | 320 | 195 | 177 | 0 | 26 | 5 | 0 | 43 | 0 | 32 | 43 | 19 | 8 | 25 | 18 | 122 | 187 | 0 | 20 | 1 | 30 | 30 | 50 | 0 | 110 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 305 | 21 | 5 | 0 | 245 | 0 | 0 | 165 | 0 | 144 | 15 | 90 | 34 | 92 | 240 | 89 | 90 | 98 | 3 | 263 | 54 | 106 | 114 | 0 | 76 | 300 | 87 | 33 | 162 | 114 | 0 | 17 | 22 | 72 | 55 |  | 719 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 8 | 0 | 0 | 90 | 0 | 0 | 34 | 56 | 0 | 0 | 24 | 34 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 189 | 0 | 0 | 105 | 0 | 94 | 0 | 95 | 0 | 4 | 95 | 260 | 184 | 0 | 0 | 4 | 58 | 17 |  | 6936 | 2742 | 9678 | 3456 | 719 | 1479 | 0 | 3078 | 460 | 46 | 0 | 178 | 122 | 140 | 0 | 89.76
16:00 | 0 | 0 | 0 | 0 | 340 | 84 | 0 | 0 | 0 |  | 0 | 300 | 130 | 0 | 0 | 55 | 157 | 0 | 92 | 0 | 48 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 29 | 28 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 97 | 15 | 18 | 2 | 0 | 0 | 0 | 310 | 305 | 182 | 177 | 0 | 26 | 5 | 0 | 43 | 0 | 32 | 43 | 19 | 8 | 25 | 18 | 114 | 191 | 0 | 20 | 1 | 30 | 30 | 48 | 0 | 110 | 158 | 40 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 8 | 0 | 245 | 0 | 0 | 155 | 0 | 135 | 9 | 90 | 17 | 93 | 240 | 35 | 70 | 104 | 2 | 262 | 54 | 108 | 114 | 0 | 50 | 300 | 87 | 22 | 162 | 114 | 0 | 17 | 14 | 72 | 55 |  | 718 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 92 | 6 | 0 | 0 | 90 | 0 | 0 | 34 | 56 | 0 | 0 | 24 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 188 | 0 | 0 | 105 | 0 | 94 | 0 | 109 | 0 | 3 | 50 | 260 | 180 | 0 | 0 | 2 | 37 | 18 |  | 6705 | 2702 | 9407 | 3400 | 718 | 1506 | 0 | 2907 | 460 | 46 | 0 | 166 | 114 | 90 | 0 | 89.76
17:00 | 0 | 0 | 0 | 0 | 340 | 98 | 0 | 0 | 0 |  | 0 | 300 | 230 | 0 | 0 | 55 | 155 | 0 | 90 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 29 | 28 | 33 | 32 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 95 | 18 | 19 | 5 | 0 | 0 | 0 | 310 | 305 | 185 | 70 | 0 | 29 | 5 | 0 | 43 | 0 | 32 | 52 | 19 | 8 | 25 | 14 | 108 | 203 | 0 | 20 | 0 | 30 | 30 | 48 | 0 | 110 | 160 | 40 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 8 | 0 | 245 | 0 | 0 | 165 | 0 | 136 | 4 | 90 | 17 | 93 | 240 | 35 | 70 | 105 | 1 | 283 | 54 | 110 | 114 | 0 | 50 | 300 | 58 | 7 | 162 | 115 | 0 | 17 | 6 | 72 | 55 |  | 718 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 92 | 7 | 0 | 0 | 90 | 0 | 0 | 34 | 56 | 0 | 0 | 30 | 52 | 26 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 3 | 0 | 22 | 0 | 191 | 0 | 0 | 105 | 0 | 94 | 0 | 112 | 0 | 2 | 50 | 260 | 161 | 0 | 0 | 0 | 13 | 18 |  | 6710 | 2698 | 9408 | 3420 | 718 | 1488 | 0 | 2937 | 460 | 46 | 0 | 198 | 108 | 33 | 0 | 89.75
18:00 | 0 | 0 | 0 | 0 | 340 | 97 | 0 | 0 | 0 |  | 0 | 300 | 260 | 0 | 0 | 55 | 158 | 0 | 37 | 0 | 74 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 28 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 92 | 36 | 19 | 2 | 0 | 0 | 0 | 270 | 280 | 122 | 118 | 0 | 29 | 5 | 0 | 51 | 0 | 32 | 52 | 19 | 8 | 25 | 14 | 120 | 199 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 110 | 160 | 40 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 23 | 8 | 0 | 282 | 0 | 0 | 174 | 0 | 141 | 0 | 90 | 32 | 93 | 240 | 54 | 90 | 105 | 0 | 278 | 54 | 110 | 114 | 0 | 55 | 401 | 54 | 0 | 162 | 113 | 0 | 17 | 0 | 72 | 55 |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 92 | 8 | 0 | 0 | 90 | 0 | 34 | 34 | 90 | 0 | 0 | 31 | 52 | 29 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 173 | 0 | 0 | 105 | 0 | 107 | 0 | 112 | 0 | 0 | 95 | 270 | 163 | 0 | 0 | 0 | 0 | 0 |  | 7000 | 2768 | 9768 | 3277 | 719 | 1577 | 0 | 3207 | 470 | 46 | 0 | 352 | 120 | 0 | 0 | 89.75
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 340 | 97 | 0 | 0 | 0 |  | 0 | 300 | 280 | 0 | 0 | 55 | 157 | 0 | 94 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 28 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 40 | 96 | 42 | 19 | 10 | 0 | 0 | 0 | 320 | 315 | 190 | 175 | 0 | 29 | 5 | 0 | 51 | 0 | 32 | 52 | 19 | 8 | 25 | 21 | 130 | 200 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 291 | 0 | 100 | 173 | 25 | 149 | 0 | 90 | 154 | 115 | 240 | 108 | 90 | 105 | 0 | 276 | 54 | 110 | 114 | 0 | 90 | 400 | 84 | 0 | 162 | 113 | 0 | 17 | 0 | 72 | 55 |  | 719 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 92 | 9 | 0 | 0 | 100 | 0 | 34 | 35 | 97 | 0 | 43 | 31 | 52 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 0 | 178 | 0 | 0 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 380 | 223 | 0 | 0 | 0 | 0 | 0 |  | 7898 | 3126 | 11024 | 3601 | 719 | 1727 | 125 | 3591 | 580 | 46 | 0 | 505 | 130 | 0 | 0 | 89.73
19:30 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 250 | 0 | 0 | 55 | 158 | 0 | 92 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 28 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 40 | 98 | 42 | 19 | 9 | 0 | 0 | 0 | 310 | 305 | 184 | 175 | 0 | 29 | 5 | 0 | 51 | 0 | 32 | 52 | 19 | 8 | 25 | 21 | 126 | 203 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 291 | 0 | 0 | 173 | 0 | 149 | 0 | 90 | 184 | 150 | 240 | 108 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 88 | 0 | 162 | 113 | 0 | 17 | 0 | 72 | 55 |  | 718 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 39 | 15 | 0 | 91 | 9 | 0 | 0 | 100 | 0 | 34 | 35 | 98 | 0 | 50 | 37 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 4 | 0 | 22 | 0 | 185 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 220 | 0 | 0 | 0 | 0 | 0 |  | 7818 | 3193 | 11011 | 3591 | 718 | 1696 | 0 | 3713 | 600 | 46 | 0 | 521 | 126 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 340 | 106 | 0 | 0 | 0 |  | 0 | 300 | 250 | 0 | 0 | 55 | 157 | 0 | 92 | 0 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 28 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 17 | 10 | 98 | 42 | 19 | 18 | 0 | 0 | 0 | 310 | 305 | 184 | 175 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 122 | 200 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 159 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 293 | 0 | 0 | 183 | 0 | 149 | 0 | 90 | 182 | 140 | 240 | 109 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 90 | 0 | 162 | 113 | 0 | 17 | 0 | 72 | 55 |  | 719 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 91 | 9 | 0 | 0 | 100 | 0 | 34 | 25 | 98 | 0 | 50 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 4 | 0 | 22 | 0 | 185 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 217 | 0 | 0 | 0 | 0 | 0 |  | 7550 | 3179 | 10729 | 3585 | 719 | 1705 | 0 | 3643 | 610 | 46 | 0 | 299 | 122 | 0 | 0 | 89.74
21:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 256 | 0 | 0 | 55 | 155 | 0 | 95 | 0 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 30 | 28 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 19 | 29 | 0 | 0 | 0 | 310 | 305 | 185 | 175 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 122 | 203 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 293 | 0 | 0 | 184 | 0 | 149 | 0 | 90 | 85 | 150 | 240 | 109 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 72 | 55 |  | 718 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 9 | 0 | 0 | 100 | 0 | 34 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 185 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 225 | 0 | 0 | 0 | 0 | 0 |  | 7439 | 3003 | 10442 | 3595 | 718 | 1737 | 0 | 3466 | 610 | 46 | 0 | 148 | 122 | 0 | 0 | 89.73
22:00 | 0 | 0 | 0 | 0 | 340 | 106 | 0 | 0 | 0 |  | 0 | 300 | 241 | 0 | 0 | 15 | 152 | 0 | 95 | 0 | 93 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 28 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 19 | 35 | 0 | 0 | 0 | 310 | 305 | 184 | 182 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 110 | 203 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 195 | 0 | 0 | 175 | 0 | 149 | 0 | 90 | 0 | 150 | 240 | 109 | 90 | 105 | 0 | 300 | 54 | 110 | 70 | 0 | 70 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 718 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 9 | 0 | 0 | 90 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 185 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 203 | 0 | 0 | 0 | 0 | 0 |  | 7011 | 2945 | 9956 | 3598 | 718 | 1716 | 0 | 3044 | 610 | 46 | 0 | 114 | 110 | 0 | 0 | 89.73
23:00 | 0 | 0 | 0 | 0 | 340 | 106 | 0 | 0 | 0 |  | 0 | 300 | 274 | 0 | 0 | 0 | 154 | 0 | 95 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 42 | 19 | 39 | 0 | 0 | 0 | 310 | 305 | 184 | 185 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 108 | 205 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 23 | 11 | 0 | 15 | 0 | 0 | 175 | 0 | 149 | 0 | 90 | 0 | 150 | 240 | 35 | 90 | 105 | 0 | 300 | 54 | 110 | 34 | 0 | 70 | 400 | 104 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 718 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 26 | 0 | 22 | 0 | 184 | 0 | 0 | 105 | 0 | 113 | 0 | 49 | 0 | 0 | 50 | 400 | 225 | 0 | 0 | 0 | 0 | 0 |  | 6623 | 2706 | 9329 | 3611 | 718 | 1763 | 0 | 2483 | 600 | 46 | 0 | 0 | 108 | 0 | 0 | 89.72
24:00 | 0 | 0 | 0 | 0 | 340 | 106 | 0 | 0 | 0 |  | 0 | 300 | 257 | 0 | 0 | 0 | 155 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 18 | 19 | 40 | 0 | 0 | 0 | 310 | 305 | 169 | 150 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 100 | 205 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 110 | 161 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 22 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 117 | 0 | 90 | 0 | 150 | 240 | 8 | 35 | 51 | 0 | 300 | 54 | 110 | 0 | 0 | 30 | 400 | 75 | 0 | 162 | 112 | 0 | 17 | 0 | 19 | 55 |  | 718 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 38 | 0 | 22 | 0 | 184 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 50 | 360 | 223 | 0 | 0 | 0 | 0 | 0 |  | 6178 | 2584 | 8762 | 3609 | 718 | 1710 | 0 | 2019 | 560 | 46 | 0 | 0 | 100 | 0 | 0 | 89.72
KWH | 0 | 0 | 0 | 0 | 8217291 | 1032909 | 0 | 0 | 0 |  | 0 | 7077000 | 2401367 | 0 | 0 | 799469 | 3988620 | 0 | 2332000 | 0 | 1330704 | 891360 | 0 | 0 | 0 | 0 | 1271520 | 620706 | 1030729 | 365904 | 600000 | 681840 | 746280 | 802400 | 465120 | 0 | 1109400 | 0 | 0 | 0 | 155215 | 0 | 0 | 0 | 0 |  | 530400 | 0 | 88179 | 284880 | 2339520 | 912960 | 417936 | 492480 | 0 | 0 | 0 | 7737100 | 7550000 | 4497000 | 2425454 | 0 | 652752 | 142560 | 0 | 1158198 | 0 | 283688 | 1082270 | 476208 | 228060 | 592100 | 434920 | 2633280 | 4774080 | 0 | 450576 | 15450 | 716000 | 690400 | 1185000 | 0 | 2914936 | 3789000 | 1375104 | 2128320 | 0 | 0 | 0 | 0 | 245340 | 7056000 | 526560 | 190368 | 0 | 4496289 | 0 | 90688 | 4053600 | 22192 | 3245900 | 124605 | 2076480 | 1289280 | 2602763 | 3573000 | 1606800 | 1680000 | 1870945 | 35279 | 6455891 | 1330240 | 2673007 | 1800060 | 0 | 1396800 | 7591600 | 2064000 | 346770 | 3625920 | 2645836 | 0 | 437760 | 225475 | 1052160 | 1300680 |  | 17381090 | 0 | 8657568 | 0 | 0 | 0 | 0 | 0 | 82080 | 9472 | 0 | 2211103 | 184352 | 0 | 0 | 2359000 | 0 | 123376 | 300527 | 857120 | 0 | 83154 | 250848 | 721440 | 109737 | 141120 | 0 | 173100 | 0 | 0 | 4868100 | 0 | 0 | 0 | 0 | 161491 | 0 | 521983 | 0 | 4961118 | 0 | 0 | 2260960 | 0 | 2563584 | 0 | 1829068 | 0 | 40068 | 1869504 | 8273900 | 5046409 | 0 | 0 | 38160 | 604080 | 547740 |  | 156650933 | 67231252 | 223882185 | 82520479 | 17381090 | 34153428 | 112880 | 68403354 | 13142000 | 1109400 | 0 | 2996387 | 2633280 | 1429887 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 9121193.01 | 1363439.88 | 0 | 0 | 0 |  | 0 | 7713930 | 2665517.37 | 0 | 0 | 6763507.74 | 4148164.8 | 0 | 4034360 | 0 | 12136020.48 | 8770982.4 | 0 | 0 | 0 | 0 | 9282096 | 4798057.38 | 10162987.94 | 274428 | 450000 | 0 | 0 | 0 | 4497710.4 | 0 | 299538 | 0 | 0 | 0 | 1441947.35 | 0 | 0 | 0 | 0 |  | 0 | 0 | 855336.3 | 2720604 | 20353824 | 7230643.2 | 526599.36 | 1462665.6 | 0 | 0 | 0 | 5725454 | 7550000 | 4137240 | 3128835.66 | 0 | 737609.76 | 199584 | 0 | 1980518.58 | 0 | 2865248.8 | 10335678.5 | 604784.16 | 171045 | 1036175 | 326190 | 19749600 | 5060524.8 | 0 | 572231.52 | 246273 | 1174240 | 1104640 | 2109300 | 0 | 3323027.04 | 3940560 | 2708954.88 | 4065091.2 | 0 | 0 | 0 | 0 | 500493.6 | 7126560 | 394920 | 144679.68 | 0 | 33991944.84 | 0 | 1516303.36 | 21078720 | 371050.24 | 31939656 | 1456632.45 | 16923312 | 13988688 | 18349479.15 | 3322890 | 14654016 | 15876000 | 16295930.95 | 0 | 48806535.96 | 11586390.4 | 23495731.53 | 17964598.8 | 0 | 9302688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100115078.4 | 0 | 9090446.4 | 0 | 0 | 0 | 0 | 0 | 861019.2 | 99266.56 | 0 | 2498546.39 | 285745.6 | 0 | 0 | 4835950 | 0 | 1214019.84 | 3053354.32 | 7585512 | 0 | 1124242.08 | 2430717.12 | 6990753.6 | 1064448.9 | 270950.4 | 0 | 131036.7 | 0 | 0 | 26385102 | 0 | 0 | 0 | 0 | 213168.12 | 0 | 782974.5 | 0 | 5804508.06 | 0 | 0 | 23604422.4 | 0 | 24328412.16 | 0 | 14193567.68 | 0 | 442751.4 | 13815634.56 | 36322421 | 0 | 0 | 0 | 0 | 0 | 0 |  | 513013580.07 | 287544049.39 | 800557629.46 | 79840539.64 | 100115078.4 | 36978633.43 | 1887353.6 | 468033801.1 | 62707523 | 299538 | 0 | 28799905.44 | 19749600 | 2145656.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 340 | 45 | 0 | 0 | 0 |  | 0 | 300 | 25 | 0 | 0 | 55 | 148 | 0 | 95 | 0 | 93 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 30 | 33 | 33 | 34 | 0 | 46 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 60 | 91 | 0 | 20 | 2 | 0 | 0 | 0 | 310 | 305 | 186 | 147 | 0 | 26 | 5 | 0 | 43 | 0 | 33 | 52 | 20 | 11 | 16 | 18 | 118 | 189 | 0 | 20 | 2 | 30 | 30 | 48 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 9 | 300 | 21 | 5 | 0 | 277 | 0 | 0 | 175 | 0 | 137 | 18 | 90 | 92 | 98 | 80 | 98 | 90 | 105 | 5 | 265 | 54 | 110 | 114 | 0 | 79 | 343 | 88 | 50 | 144 | 115 | 0 | 17 | 32 | 72 | 55 |  | 719 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 100 | 0 | 0 | 25 | 56 | 0 | 0 | 24 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 199 | 0 | 0 | 105 | 0 | 94 | 0 | 112 | 0 | 6 | 95 | 240 | 221 | 0 | 0 | 5 | 89 | 98 |  | 9857 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 340 | 97 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 0 | 0 | 55 | 157 | 0 | 94 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 28 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 40 | 96 | 42 | 19 | 10 | 0 | 0 | 0 | 320 | 315 | 190 | 175 | 0 | 29 | 5 | 0 | 51 | 0 | 32 | 52 | 19 | 8 | 25 | 21 | 130 | 200 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 291 | 0 | 100 | 173 | 25 | 149 | 0 | 90 | 154 | 115 | 240 | 108 | 90 | 105 | 0 | 276 | 54 | 110 | 114 | 0 | 90 | 400 | 84 | 0 | 162 | 113 | 0 | 17 | 0 | 72 | 55 |  | 719 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 92 | 9 | 0 | 0 | 100 | 0 | 34 | 35 | 97 | 0 | 43 | 31 | 52 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 0 | 178 | 0 | 0 | 105 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 380 | 223 | 0 | 0 | 0 | 0 | 0 |  | 11024 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 340 | 108 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 0 | 0 | 55 | 200 | 0 | 95 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 42 | 19 | 10 | 0 | 0 | 0 | 335 | 335 | 200 | 68 | 0 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 11 | 25 | 15 | 163 | 210 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 330 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 140 | 240 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 104 | 0 | 162 | 113 | 0 | 17 |  | 115 | 55 |  | 733 | 0 | 410 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 91 | 10 | 110 | 0 | 100 | 0 | 34 | 41 | 100 | 0 | 50 | 40 | 52 | 22 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 225 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 108 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 0 | 0 | 55 | 200 | 0 | 95 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 42 | 19 | 10 | 0 | 0 | 0 | 310 | 330 | 200 | 68 | 0 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 11 | 25 | 15 | 138 | 210 | 0 | 20 | 1.6 | 30 | 30 | 50 | 0 | 110 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 330 | 21 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 140 | 240 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 104 | 50 | 162 | 113 | 0 | 17 | 30 | 115 | 55 |  | 733 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 110 | 0 | 100 | 0 | 34 | 40 | 100 | 0 | 50 | 0 | 52 | 22 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 100 | 200 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 225 |  | 50 | 6 | 50 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 330 | 106 | 0 | 0 | 0 | 0 | 0 | 300 | 250 | 0 | 0 | 17 | 154 | 0 | 60 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 54 | 30 | 35 | 0 | 25 | 9 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 87 | 6 | 19 | 10 | 0 | 0 | 0 | 280 | 295 | 181 | 68 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 0 | 216 | 0 | 20 | 1 | 30 | 30 | 51 | 0 | 110 | 160 | 20 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 8 | 0 | 142 | 0 | 0 | 188 | 0 | 107 | 5 | 80 | 32 | 133 | 240 | 66 | 71 | 26 | 1 | 300 | 54 | 110 | 52 | 0 | 10 | 375 | 82 | 18 | 144 | 51 | 0 | 17 | 11 | 34 | 36 | 0 | 720 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 192 | 0 | 22 | 0 | 180 | 0 | 0 | 32 | 0 | 110 | 0 | 113 | 0 | 2 | 95 | 250 | 150 | 0 | 0 | 1 | 27 | 0 | 0
199
| Minimum Generation |  | 7301 | 5:00
| Highest Generation |  | 11024 | 19:00
| Day Peak Generation |  | 9857 | 12:00
| Evening Peak Generation |  | 11024 | 19:00
| HVDC Max Flow |  | 719 | 1:00
| HVDC EvPeak Flow |  | 719 | 19:00
| Load factor L.F |  | 84.62%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-07
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9857 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 7432 | MW
Evening Peak Generation : |  | 11024 | MW Hour : | 19:00 | Available Max Generation : |  | 13494 | MW
E.P. Demand (at gen end) : |  | 11024 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11024 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1994 | MW
Total Gen. (MKWH) : |  | 223.8822 | System Load Factor : | 84.62% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -374 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-07
Actual : | 89.66 | Ft.(MSL) , | Rule curve : | 92.04 | Ft.( MSL )
Gas Consumed : | Total = | 922.08 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 116819173.07
: |  | Coal : | 62707523 | Oil : | 498721060.14 | Total : | 678247756.21
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4101.1562 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1395.7309 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1250.7266 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1130.2072 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1021.3132 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 824.1664 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 459.4039 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 212.1628 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 635.6449 |  |  | 0 | 0%
Total | 0 |  | 11030.512 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Raozan unit- 1,2
6) Sirajganj Unit 1,2
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Summit Meghnaghat CCPP GT-2 was synchronized at 08:04.
b) Summit Meghnaghat CCPP ST was synchronized at 12:09.
c) Ashuganj 230 kV Bus-1 was under shut down from 10:01 to 17:10 for C/M.
d) Shahjibazar-Ashuganj 132 kV Ckt-2 was under shut down from 08:29 to 16:51 for A/M.
e) Siddhirganj 230 kV bus-1 was under shut down from 08:55 to 13:43 for A/M.
f) Kallyanpur 132/33 kV T-2 transformer was shut down at 08:54 for A/M.
g) Kallyanpur 132 kV main Bus was shut down at 08:58 for A/M.
h) Kabirpur-Tongi 132 kV Ckt-1 was under shut down from 09:37 to 19:42 for C/M.
i) Tongi 132/33 kV T-2 transformer was under shut down from 09:42 to 16:53 for A/M.
j) Kabirpur 132/33 kV T-3 transformer was under shut down from 09:47 to 22:38 for C/M.
k) Nawabganj 132/33 kV T-2 transformer was under shut down from 09:29 to 17:45 for A/M.
l) Ashuganj-Ashuganj(S) 230 kV Ckt-2 was under shut down from 10:12 to 14:57 for C/M.
m) Madanganj-Char Saidpur 132 kV Ckt-1 was under shut down from 10:50 to 14:57 for C/M.
n) Tongi-Tongi P/P 132 kV Ckt was under shut down from 11:37 to 17:40 for A/M.
o) Sylhet-Fenchuganj P/P 132 kV Ckt was switched on at 13:23.
p) Sylhet-Chatak 132 kV Ckt-1 was switched on at 13:27.
q) Faridpur 132/33 kV T-2 transformer was under shut down from 10:04 to 11:08 for C/M.
r) Faridpur 132/33 kV T-1 transformer was under shut down from 11:11 to 11:33 for C/M.
s) Jhenaidah 132/33 kV T-1 transformer was under shut down from 12:09 to 18:09 for C/M.
t) Ashuganj-Cumilla(N) 230 kV Ckt-1 was under shut down from 15:01 to 17:10 for C/M.
u) Kabirpur-Manikganj 132 kV Ckt-1 was under shut down from 15:29 to 18:40 for C/M.
v) Kulaura-Fenchuganj 132 kV Ckt-1 was under shut down from 18:32 to 21:12 for C/M.
w) Chandpur 132/33 kV T-1 transformer was under shut down from 15:15 to 17:06 for C/M.
x) Sirajganj unit-2 GT was synchronized at 16:23.
y) Summit Meghnaghat CCPP GT-1 was synchronized at 15:40.
z) Sirajganj unit-2 ST was synchronized at 22:21.
aa) Shahjibazar GT-8 was shut down 02:08(06-03-2022) due to under maintenance.
ab) Khulna© 132/33 kV T3 transformer was shut down at 07:07(07-03-2022) for C/M. | [5 empty] | About 05 MW power interruption occurred under
Khulna© S/S Area from 07:07(07-03-2022) to till.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 8217291
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 1032909 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7077000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 2401367 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 799469
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 365904
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 94 | 2332000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 157 | 3988620 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 84 | 1330704 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1271520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 891360
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 620706
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1030729
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1281840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 746280 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 802400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 51 | 465120 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 291 | 4496289 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 90688
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 22192
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3245900
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1680000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 84 | 2064000 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3625920
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 225475
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1300680
| Dhaka area Total |  |  |  | 5696 | 2857 | 51406363
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 155215
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 124605
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 912960 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1109400 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1870945
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 88179 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 40 | 284880 | Engine problem
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 2076480 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 417936
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 492480
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 2339520 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35279
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 276 | 6455891 | Engine problem
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1330240
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2673007
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1396800
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2645836
| Chattogram area Total |  |  |  | 2382 | 1167 | 24409653
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 190 | 4497000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7737100 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7550000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 652752 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 142560 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 175 | 2425454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1158198
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 115 | 2602763 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 283688 | Engine problem
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 154 | 1289280 | Engine problem
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 476208
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 228060
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 2633280
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 592100 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1082270
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 434920 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1800060
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 437760 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 72 | 1052160 | Engine problem
| Cumilla Area Total |  |  |  | 2899 | 1844 | 37075613
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 200 | 4774080
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 450576
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15450
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 173 | 4053600 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 108 | 1606800 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 346770
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 530400
| Mymensingh Area Total |  |  |  | 622 | 523 | 11777676
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 690400 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2914936 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3789000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 1185000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 190368
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1375104
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2128320
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 526560
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7056000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 240 | 3573000 | Gas booster problem
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245340
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 7591600
| Sylhet Area Total |  |  |  | 2377 | 1507 | 31981628
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 719 | 17381090
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 82080
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 5 | 9472
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 380 | 8657568
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2260960
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 604080
| Khulna Area Total |  |  |  | 2229 | 1249 | 28995250
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 9 | 184352 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 92 | 2211103 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 521983 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 380 | 8273900 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 223 | 5046409
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 726 | 16237747
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 100 | 2359000
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 123376 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 300527 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 83154
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 250848 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 5 | 161491 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 178 | 4961118
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 109737 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 141120 | Engine problem
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 173100 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 721440
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 857120 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2563584
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1869504
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38160
| Rajshahi Area Total |  |  |  | 2129 | 839 | 14713279
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4868100 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 1829068
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40068
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 547740 | On test
| Rangpur Area Total |  |  |  | 605 | 312 | 7284976
| Total |  |  |  | 20985 | 11024 | 223882185
| Eastern Grid Total |  |  |  | 13976 | 7898 | 156650933
| Western Grid Total |  |  |  | 7009 | 3126 | 67231252
| National Grid Total |  |  |  | 20985 | 11024 | 223882185
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-06
(a) ENTIRE EASTERN GRID : |  | 7214 | MW | (b) ENTIRE WESTERN GRID : |  | 3351 | MW
i) Dhaka area |  | 3837 | MW | i) Khulna area |  | 1229 | MW
ii) Chittagong area |  | 1151 | MW | ii) Rajshahi area |  | 1128 | MW
iii) Comilla area |  | 884 | MW | iii) Barisal area |  | 274 | MW
iv) Mymensingh area |  | 957 | MW | iv) Rangpur area |  | 720 | MW
v) Sylhet area |  | 385 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10565 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 19:00 | Valuka | 112 | 18:30 | Central S/S | 76 | 19:00
Munsiganj | 74 | 15:00 | Tangail | 179 | 7:00 | Noapara | 40 | 19:30
Sonargaon | 76 | 22:00 | Mymensing | 189 | 13:00 | Jessore | 97 | 19:00
Bhulta | 194 | 19:30 | Kishoreganj | 118 | 20:00 | Benapol | 46 | 19:00
Madanganj | 36 | 13:00 | Netrokona | 122 | 19:30 | Jhenida(Old) | 90 | 19:30
Rahim steel | 26 | 17:00 | Jamalpur | 129 | 8:00 | Bottail | 104 | 19:00
Ghorasal | 71 | 18:30 | Sherpur | 134 | 19:00 | G.K Project | 43 | 19:00
Narsingdi | 142 | 20:00 | Srimongal | 38 | 18:30 | Faridpur | 101 | 19:30
Haripur(SBU) | 98 | 9:00 | Shahjibazar | 92 | 18:30 | Rajbari | 44 | 18:30
Sreenagar | 23 | 12:00 | Fenchuganj | 31 | 18:00 | Madaripur | 70 | 19:00
Shyampur | 184 | 12:00 | Kulawara | 28 | 18:30 | Sariatpur | 44 | 20:00
Shitalakhya | 97 | 12:00 | Sylhet | 111 | 19:00 | Gopalganj | 72 | 19:00
Matuail | 60 | 10:00 | Chatak | 15 | 18:30 | Bagerhat | 83 | 18:30
Char Saidpur | 41 | 10:00 | Sunamganj | 34 | 18:30 | Mongla | 44 | 9:00
Ullon | 27 | 20:00 | Biani Bazar | 42 | 18:30 | Satkhira | 89 | 19:30
Hasnabad | 69 | 16:00 | Comilla (S) | 134 | 18:30 | Gallamari | 34 | 19:00
Magbazar | 92 | 14:00 | Comilla(N) | 89 | 19:30 | Magura | 44 | 19:00
Maniknagar | 63 | 13:00 | Chandpur | 49 | 21:00 | Norail | 36 | 19:00
Bangabhaban | 8 | 10:00 | Feni | 90 | 18:00 | Chuadanga | 73 | 19:00
Motijheel | 26 | 13:00 | Chowmuhani | 156 | 19:00 | Barisal(N) | 38 | 19:00
Narinda | 44 | 13:00 | Ashuganj | 29 | 23:00 | Barisal (S) | 79 | 19:00
Kazla | 75 | 12:00 | Daudkandi | 84 | 18:30 | Patuakhali | 66 | 21:00
Dhanmondi | 153 | 13:00 | B.Baria | 120 | 19:00 | Bhandaria | 38 | 19:00
Lalbag | 82 | 13:00 | Ramganj | 54 | 18:30 | Borguna | 14 | 18:30
Madartek | 58 | 21:00 | Chaddagram | 34 | 19:30 | Borhan Uddin | 43 | 20:00
Dhaka University | 28 | 12:00 | PHP | 10 | 6:00 | Ishurdi | 54 | 19:00
Aftabnagar | 24 | 13:00 | Kochua | 44 | 18:30 | Ruppur Paromanobik | 3 | 9:00
Fatullah | 55 | 12:00 | Madunaghat | 38 | 19:00 | Natore | 117 | 19:00
Nawabganj | 34 | 21:00 | Hathazari | 77 | 19:30 | Bogra | 120 | 20:00
Keraniganj | 58 | 18:00 | Khulshi | 147 | 15:00 | Naogaon | 102 | 8:00
Banani | 34 | 14:00 | Halishahar | 79 | 15:00 | Rajshahi | 93 | 20:00
Mirpur | 101 | 19:00 | Baraulia | 99 | 10:00 | Rajshahi New | 35 | 19:30
Kalyanpur | 76 | 18:30 | Sikalbaha | 28 | 18:30 | C.Nawabganj | 50 | 8:00
Gulshan | 86 | 13:00 | Dohazari | 76 | 18:00 | Amnura | 49 | 19:30
Uttara | 67 | 12:00 | Cox'sbazar | 103 | 19:00 | Pabna | 78 | 19:00
Uttara New | 13 | 13:00 | Chandraghona | 24 | 18:30 | Shahjadpur | 84 | 19:00
Kamrangirchar | 62 | 19:00 | Kaptai | 4 | 18:30 | Serajganj | 95 | 19:00
Savar | 149 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 86 | 8:00
Bhasantec | 112 | 18:30 | Bakulia | 105 | 18:30 | Joypurhat | 49 | 7:00
Agargaon | 64 | 13:00 | Julda | 22 | 1:00 | Sherpur(Bogura) | 52 | 18:30
Satmosjid | 79 | 18:30 | TK chemical | 23 | 18:30 | Mohastangor | 56 | 19:00
Old Tongi | 111 | 15:00 | Modern Steel | 0 | 1:00 | Bhangura | 29 | 8:00
Kabirpur | 225 | 15:00 | Shahmirpur | 36 | 18:30 | Rangpur | 111 | 19:00
Manikgonj | 58 | 20:00 | Khagrachhari | 22 | 19:00 | Lalmonirhat | 38 | 18:30
Joydevpur | 165 | 18:30 | Matarbari | 32 | 19:30 | Saidpur | 97 | 9:00
New Tongi | 75 | 12:00 | Baroiar Hat | 37 | 18:30 | Purbasadipur | 98 | 19:00
Kodda | 231 | 15:00 | Rangamati | 10 | 18:30 | Thakurgaon | 69 | 19:00
Dhamrai | 96 | 18:30 | Agrabad | 64 | 18:00 | Palashbari | 100 | 19:00
Rajendrapur | 88 | 21:00 | Rampur | 5 | 22:00 | Barapukuria | 49 | 19:00
Bashundara | 116 | 18:00 | Abul Khair 230 | 141 | 13:00 | Panchagar | 46 | 19:30
Purbachal | 14 | 19:00 | BSRM | 164 | 7:00 | Joldhaka | 54 | 8:00
Tongi Millgate | 40 | 12:00 | GPH Ispat | 95 | 3:00 | Kurigram | 53 | 19:00
Bashundhara Cement |  |  | Goalpara | 20 | 19:30 | Mithapukur | 25 | 19:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 7:00 | 406 | 18:00 | Kaliakoir | 398 | 0.70833 | 382 | 0.45833
| Bheramara | 402 | 8:00 | 394 | 13:00 | Bhulta | 409 | 0.29167 | 391 | 0.45833
| Ashuganj(N) | 412 | 22:00 | 395 | 11:00 | Gopalganj | 413 | 0.625 | 405 | 0.083333
| Payra | 418 | 6:00 | 414 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 238 | 15:00 | Hathazari | 241 | 19:30 | 229 | 14:00
| Ishurdi | 244 | 22:00 | 230 | 8:00 | Megnaghat | 240 | 6:00 | 230 | 11:00
| Ashuganj | 245 | 21:00 | 235 | 11:00 | Fenchuganj | 244 | 22:00 | 238 | 18:30
| Serajganj | 240 | 22:00 | 227 | 7:00 | Siddhirganj | 236 | 6:00 | 226 | 11:00
| Baghabari | 240 | 22:00 | 228 | 8:00 | Maniknagar | 234 | 6:00 | 224 | 11:00
| Barapukuria | 234 | 2:00 | 225 | 8:00 | Agargaon | 234 | 1:00 | 225 | 11:00
| Bogra | 235 | 1:00 | 220 | 8:00 | Barisal | 245 | 20:00 | 239 | 18:30
| Rajshahi | 240 | 17:00 | 226 | 8:00 | Bhola 225 MW | 246 | 4:00 | 239 | 8:00
| Khulna South | 244 | 5:00 | 230 | 19:00 | AKSML | 242 | 20:00 | 232 | 15:00
| Rampura | 234 | 21:00 | 225 | 12:00 | BSRM | 241 | 22:00 | 232 | 14:00
| Haripur | 233 | 4:00 | 224 | 11:00 | Bibiyana | 245 | 4:00 | 237 | 12:00
| Hasnabad | 234 | 7:00 | 223 | 12:00 | Bhulta | 236 | 7:00 | 225 | 11:00
| Shyampur | 233 | 6:00 | 223 | 12:00 | Ashuganj (S) | 243 | 22:00 | 233 | 11:00
| Aminbazar | 235 | 1:00 | 226 | 2:00 | Kaliakoir | 233 | 7:00 | 223 | 11:00
| Tongi | 235 | 20:00 | 222 | 12:00 | GPH | 241 | 1:00 | 233 | 15:00
| Comilla (N) | 237 | 7:00 | 230 | 11:00 | Jhenaidah | 240 | 22:00 | 223 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 6:00 | 128 | 11:00 | PHP | 139 | 13:00 | 131 | 5:00
| Munsiganj | 135 | 7:00 | 129 | 11:00 | Kachua | 140 | 7:00 | 131 | 2:00
| Sonargaon | 135 | 21:00 | 130 | 11:00 | Madanhat | 141 | 22:00 | 134 | 15:00
| Bhulta | 129 | 22:00 | 123 | 16:00 | Hathazari | 142 | 19:30 | 135 | 14:00
| Madanganj | 134 | 7:00 | 129 | 11:00 | Khulshi | 139 | 20:00 | 133 | 15:00
| Rahim steel | 133 | 1:00 | 128 | 11:00 | Halishahar | 141 | 13:00 | 133 | 15:00
| Ghorasal | 142 | 7:00 | 138 | 15:00 | Baraulia | 142 | 6:00 | 135 | 14:00
| Narsingdi | 136 | 4:00 | 128 | 11:00 | Sikalbaha | 140 | 13:00 | 136 | 5:00
| Haripur(SBU) | 133 | 4:00 | 128 | 11:00 | Dohazari | 140 | 18:30 | 131 | 0:00
| Sreenagar | 134 | 1:00 | 129 | 11:00 | Cox'sbazar | 131 | 13:00 | 122 | 18:00
| Shyampur | 133 | 7:00 | 126 | 12:00 | Chandraghona | 141 | 20:00 | 134 | 14:00
| Shitalakhya | 136 | 7:00 | 129 | 11:00 | Kaptai | 140 | 21:00 | 138 | 1:00
| Matuail | 134 | 6:00 | 128 | 11:00 | A. Khaer Stl. | 140 | 5:00 | 134 | 13:00
| Char Saidpur | 136 | 7:00 | 128 | 16:00 | Bakulia | 141 | 5:00 | 135 | 11:00
| Ullon | 132 | 5:00 | 124 | 11:00 | Julda | 141 | 13:00 | 133 | 14:00
| Hasnabad | 135 | 19:30 | 130 | 11:00 | TK Chemical | 140 | 21:00 | 135 | 2:00
| Magbazar | 132 | 4:00 | 125 | 11:00 | Modern Steel | 140 | 19:30 | 135 | 13:00
| Maniknagar | 137 | 7:00 | 130 | 12:00 | Shahmirpur | 141 | 13:00 | 135 | 11:00
| Bangabhaban | 137 | 7:00 | 130 | 12:00 | Khagrachhari | 141 | 21:00 | 134 | 15:00
| Motijheel | 137 | 7:00 | 130 | 12:00 | Matarbari | 131 | 13:00 | 124 | 21:00
| Narinda | 137 | 7:00 | 130 | 12:00 | Baroiar Hat | 139 | 13:00 | 133 | 2:00
| Kazla | 137 | 7:00 | 130 | 12:00 | Rangamati | 140 | 6:00 | 134 | 15:00
| Dhanmondi | 134 | 6:00 | 127 | 11:00 | Agrabad | 139 | 7:00 | 129 | 3:00
| Lalbag | 137 | 7:00 | 129 | 12:00 | Rampur | 139 | 5:00 | 135 | 13:00
| Madartek | 132 | 7:00 | 125 | 11:00 | Goalpara S/S | 140 | 1:00 | 131 | 18:30
| Dhaka University | 132 | 5:00 | 125 | 11:00 | Khulna Central S/S | 138 | 1:00 | 130 | 18:30
| Aftabnagar | 132 | 3:00 | 125 | 11:00 | Noapara | 138 | 4:00 | 128 | 19:00
| Fatullah | 133 | 6:00 | 126 | 12:00 | Jessore | 138 | 2:00 | 127 | 19:00
| Nawabganj | 137 | 7:00 | 130 | 11:00 | Benapol | 138 | 3:00 | 127 | 18:30
| Keraniganj | 137 | 6:00 | 129 | 12:00 | Jhenida(Old) | 137 | 1:00 | 128 | 19:00
| Banani | 133 | 0:00 | 125 | 12:00 | Bottail | 140 | 3:00 | 131 | 19:00
| Mirpur | 130 | 1:00 | 125 | 16:00 | G.K Project | 142 | 4:00 | 137 | 18:30
| Kalyanpur | 133 | 1:00 | 129 | 15:00 | Faridpur | 138 | 1:00 | 135 | 7:00
| Gulshan | 131 | 1:00 | 124 | 11:00 | Rajbari | 138 | 1:00 | 135 | 18:30
| Uttara | 138 | 22:00 | 131 | 10:00 | Madaripur | 143 | 4:00 | 139 | 18:30
| Uttara New | 139 | 6:00 | 132 | 11:00 | Shariyatpur S/S | 142 | 5:00 | 137 | 18:30
| Kamrangirchar | 137 | 3:00 | 130 | 11:00 | Gopalganj | 142 | 17:00 | 138 | 18:30
| Savar | 134 | 6:00 | 126 | 16:00 | Bagerhat | 138 | 2:00 | 125 | 19:00
| Bhasantec | 138 | 7:00 | 131 | 12:00 | Mongla | 137 | 1:00 | 126 | 19:00
| Agargaon | 139 | 5:00 | 132 | 12:00 | Satkhira | 137 | 4:00 | 126 | 19:00
| Satmosjid | 138 | 1:00 | 132 | 12:00 | Gallamari | 140 | 1:00 | 136 | 1:00
| Old Tongi | 139 | 13:00 | 133 | 12:00 | Magura | 141 | 4:00 | 129 | 19:00
| Kabirpur | 136 | 1:00 | 128 | 16:00 | Narail | 137 | 3:00 | 126 | 19:00
| Manikgonj | 133 | 1:00 | 127 | 11:00 | Chuadanga | 136 | 3:00 | 123 | 19:00
| Joydevpur | 141 | 1:00 | 136 | 16:00 | Barisal(N) | 143 | 1:00 | 139 | 18:30
| New Tongi | 139 | 2:00 | 131 | 11:00 | Barisal (S) | 141 | 1:00 | 137 | 18:30
| Kodda | 141 | 6:00 | 130 | 11:00 | Patuakhali(S) | 138 | 1:00 | 135 | 18:30
| Dhamrai | 140 | 1:00 | 133 | 11:00 | Bhandaria | 141 | 5:00 | 136 | 18:30
| Rajendrapur | 138 | 1:00 | 130 | 11:00 | Borguna | 141 | 3:00 | 137 | 18:30
| Bashundara | 139 | 6:00 | 132 | 11:00 | Jhenaidah(New) | 138 | 5:00 | 129 | 19:00
| Purbachal | 133 | 1:00 | 124 | 12:00 | Ishurdi | 139 | 1:00 | 133 | 19:30
| Tongi Millgate | 139 | 7:00 | 132 | 11:00 | Ruppur Paromanobik | 140 | 1:00 | 133 | 18:30
| Bashundhara Cement |  |  |  |  | Natore | 138 | 1:00 | 131 | 8:00
| Valuka | 130 | 1:00 | 114 | 19:00 | Bogra | 138 | 1:00 | 129 | 8:00
| Tangail | 136 | 1:00 | 127 | 17:00 | Noagaon | 133 | 1:00 | 129 | 8:00
| Mymensing | 134 | 1:00 | 120 | 18:30 | Rajshahi | 137 | 17:00 | 129 | 8:00
| Kishorganj | 135 | 4:00 | 125 | 18:30 | Rajshahi New | 137 | 17:00 | 128 | 17:00
| Netrokona | 132 | 1:00 | 116 | 18:30 | C.Nawabganj | 136 | 18:00 | 125 | 8:00
| Jamalpur | 138 | 1:00 | 129 | 16:00 | Amnura | 137 | 17:00 | 125 | 8:00
| Sherpur | 137 | 22:00 | 125 | 17:00 | Pabna | 138 | 1:00 | 131 | 19:00
| Srimongal | 141 | 4:00 | 137 | 11:00 | Shahjadpur | 145 | 3:00 | 136 | 7:00
| Shahjibazar | 140 | 5:00 | 135 | 15:00 | Serajganj | 138 | 1:00 | 128 | 8:00
| Fenchuganj | 140 | 6:00 | 134 | 18:30 | Niyamatpur | 134 | 1:00 | 119 | 8:00
| Khulawara | 140 | 4:00 | 135 | 15:00 | Joypurhat | 136 | 1:00 | 121 | 8:00
| Sylhet | 135 | 1:00 | 128 | 12:00 | Sherpur(Bogura) | 138 | 1:00 | 128 | 8:00
| Chatak | 138 | 4:00 | 127 | 11:00 | Mohastangor | 137 | 1:00 | 126 | 8:00
| Sunamganj | 134 | 4:00 | 124 | 13:00 | Bhangura | 140 | 1:00 | 131 | 8:00
| Biani Bazar | 137 | 3:00 | 129 | 11:00 | Rangpur | 133 | 1:00 | 119 | 8:00
| Comilla(s) | 130 | 1:00 | 126 | 14:00 | Lalmonirhat | 130 | 3:00 | 117 | 8:00
| Comilla(n) | 140 | 7:00 | 136 | 2:00 | Saidpur | 132 | 1:00 | 118 | 18:30
| Chandpur | 142 | 19:00 | 130 | 1:00 | Purbasadipur | 134 | 13:00 | 115 | 14:00
| Feni | 140 | 7:00 | 132 | 23:00 | Thakurgaon | 132 | 12:00 | 112 | 18:30
| Chowmuhani | 135 | 7:00 | 129 | 22:00 | Palashbari | 132 | 1:00 | 124 | 7:00
| Ashuganj | 141 | 6:00 | 139 | 11:00 | Barapukuria | 134 | 2:00 | 125 | 8:00
| Daudkandi | 135 | 5:00 | 131 | 11:00 | Panchagar | 136 | 13:00 | 115 | 18:30
| B.Baria | 137 | 1:00 | 132 | 12:00 | Joldhaka | 130 | 13:00 | 116 | 18:30
| Ramganj | 138 | 7:00 | 128 | 23:00 | Kurigram | 130 | 5:00 | 117 | 18:30
| Chaddagram | 140 | 7:00 | 133 | 1:00 | Mithapukur | 133 | 1:00 | 123 | 8:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 42 | 6178 | 2584 | 8762 |  |  |  | QF-LDC-11
0:30 | 106 | 5975 | 2585 | 8560 | Date: | 2022-03-06
1:00 | 170 | 5772 | 2586 | 8358
1:30 | 192 | 5591.5 | 2522 | 8113.5
2:00 | 214 | 5411 | 2458 | 7869
2:30 | 219 | 5321.5 | 2422.5 | 7744 | [5 empty] | Gen. at Eve. Peak | 11024 | 11024 MW (19:00 )
3:00 | 224 | 5232 | 2387 | 7619 | [6 empty] | 19:00
3:30 | 211 | 5193 | 2346.5 | 7539.5 | [5 empty] | Gen. at Day Peak | 9857 | 9857 MW (12:00 )
4:00 | 198 | 5154 | 2306 | 7460 | [6 empty] | 12:00
4:30 | 195 | 5085.5 | 2295 | 7380.5 | [5 empty] | Highest Generation | 11024
5:00 | 192 | 5017 | 2284 | 7301 | [6 empty] | 19:00
5:30 | 170 | 5121.5 | 2332.5 | 7454
6:00 | 148 | 5226 | 2381 | 7607
6:30 | 219 | 5462 | 2493 | 7955
7:00 | 290 | 5698 | 2605 | 8303
7:30 | 286 | 5931 | 2652.5 | 8583.5
8:00 | 282 | 6164 | 2700 | 8864
8:30 | 188 | 6324 | 2712 | 9036
9:00 | 94 | 6484 | 2724 | 9208
9:30 | 60 | 6524.5 | 2752 | 9276.5
10:00 | 26 | 6565 | 2780 | 9345
10:30 | 56 | 6620.5 | 2802.5 | 9423
11:00 | 86 | 6676 | 2825 | 9501
11:30 | 74 | 6798 | 2881 | 9679
12:00 | 62 | 6920 | 2937 | 9857
12:30 | 64 | 7018 | 2961 | 9979
13:00 | 66 | 7116 | 2985 | 10101
13:30 | 42 | 6943.5 | 2841.5 | 9785
14:00 | 18 | 6771 | 2698 | 9469
14:30 | 64 | 6853.5 | 2720 | 9573.5
15:00 | 110 | 6936 | 2742 | 9678
15:30 | 139 | 6820.5 | 2722 | 9542.5
16:00 | 168 | 6705 | 2702 | 9407
16:30 | 167 | 6707.5 | 2700 | 9407.5
17:00 | 166 | 6710 | 2698 | 9408
17:30 | 106 | 6855 | 2733 | 9588
18:00 | 46 | 7000 | 2768 | 9768
18:30 | 210 | 7449 | 2947 | 10396
19:00 | 374 | 7898 | 3126 | 11024
19:30 | 320 | 7818 | 3193 | 11011
20:00 | 266 | 7550 | 3179 | 10729 |  |  |  | Executive Engineer
20:30 | 271 | 7494.5 | 3091 | 10585.5 |  |  |  | Network Operation Division
21:00 | 276 | 7439 | 3003 | 10442
21:30 | 193 | 7225 | 2974 | 10199
22:00 | 110 | 7011 | 2945 | 9956 |  |  |  |  | Page 6 of 7
22:30 | 73 | 6817 | 2825.5 | 9642.5
23:00 | 36 | 6623 | 2706 | 9329
23:30 | 39 | 6400.5 | 2645 | 9045.5
24:00 | 42 | 6178 | 2584 | 8762
11024 MW (19:00 )
9857 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-06 |  | Energy |  | 223882185
[13 empty] | 2022-03-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3609 | 718 | 1710 | 0 | 2019 | 560 | 46 | 0 | 0 | 100 | 0 | 0
0:30 | 3513 | 718.5 | 1451 | 0 | 2170.5 | 560 | 46 | 0 | 0 | 101 | 0 | 0 | Date: | 2022-03-06
1:00 | 3417 | 719 | 1192 | 0 | 2322 | 560 | 46 | 0 | 0 | 102 | 0 | 0
1:30 | 3420 | 719 | 1197.5 | 0 | 2075 | 555 | 46 | 0 | 0 | 101 | 0 | 0 | [8 empty] | Total Energy | 223.8822 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3423 | 719 | 1203 | 0 | 1828 | 550 | 46 | 0 | 0 | 100 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3386.5 | 719 | 1208.5 | 0 | 1755.5 | 529.5 | 46 | 0 | 0 | 99 | 0 | 0 | [8 empty] | Energy Requirement | 223.8822
3:00 | 3350 | 719 | 1214 | 0 | 1683 | 509 | 46 | 0 | 0 | 98 | 0 | 0
3:30 | 3296 | 719 | 1217 | 0 | 1666 | 499.5 | 46 | 0 | 0 | 96 | 0 | 0 | [6 empty] | Shortage
4:00 | 3242 | 719 | 1220 | 0 | 1649 | 490 | 46 | 0 | 0 | 94 | 0 | 0
4:30 | 3199.5 | 718.5 | 1209.5 | 0 | 1629 | 485 | 46 | 0 | 0 | 93 | 0 | 0
5:00 | 3157 | 718 | 1199 | 0 | 1609 | 480 | 46 | 0 | 0 | 92 | 0 | 0
5:30 | 3191.5 | 718.5 | 1222.5 | 0 | 1703.5 | 480 | 46 | 0 | 0 | 92 | 0 | 0
6:00 | 3226 | 719 | 1246 | 0 | 1798 | 480 | 46 | 0 | 0 | 92 | 0 | 0
6:30 | 3214 | 719 | 1244 | 0 | 2128.5 | 480 | 46 | 0 | 24 | 92 | 7.5 | 0 |  |  |  |  | Coal
7:00 | 3202 | 719 | 1242 | 0 | 2459 | 480 | 46 | 0 | 48 | 92 | 15 | 0
7:30 | 3219.5 | 719 | 1198 | 0 | 2743.5 | 475 | 46 | 0 | 48 | 95 | 39.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3237 | 719 | 1154 | 0 | 3028 | 470 | 46 | 0 | 48 | 98 | 64 | 0
8:30 | 3282 | 718.5 | 1187.5 | 0 | 3106.5 | 454.5 | 46 | 0 | 50 | 99 | 92 | 0
9:00 | 3327 | 718 | 1221 | 0 | 3185 | 439 | 46 | 0 | 52 | 100 | 120 | 0
9:30 | 3306 | 718.5 | 1230 | 0 | 3215.5 | 439.5 | 46 | 0 | 74 | 101 | 146 | 0
10:00 | 3285 | 719 | 1239 | 0 | 3246 | 440 | 46 | 0 | 96 | 102 | 172 | 0
10:30 | 3289 | 719 | 1260.5 | 0 | 3257 | 440 | 46 | 0 | 122.5 | 104 | 185 | 0
11:00 | 3293 | 719 | 1282 | 0 | 3268 | 440 | 46 | 0 | 149 | 106 | 198 | 0
11:30 | 3307.5 | 719 | 1326 | 0 | 3328 | 439.5 | 46 | 0 | 198.5 | 112 | 202.5 | 0
12:00 | 3322 | 719 | 1370 | 0 | 3388 | 439 | 46 | 0 | 248 | 118 | 207 | 0
12:30 | 3318.5 | 719 | 1420.5 | 0 | 3442.5 | 439.5 | 46 | 0 | 271 | 119 | 203 | 0
13:00 | 3315 | 719 | 1471 | 0 | 3497 | 440 | 46 | 0 | 294 | 120 | 199 | 0
13:30 | 3315 | 719 | 1471 | 0 | 3497 | 440 | 46 | 0 | 294 | 120 | 199 | 0
14:00 | 3315 | 719 | 1471 | 0 | 3497 | 440 | 46 | 0 | 294 | 120 | 199 | 0
14:30 | 3385.5 | 719 | 1475 | 0 | 3287.5 | 450 | 46 | 0 | 236 | 121 | 169.5 | 0
15:00 | 3456 | 719 | 1479 | 0 | 3078 | 460 | 46 | 0 | 178 | 122 | 140 | 0
15:30 | 3428 | 718.5 | 1492.5 | 0 | 2992.5 | 460 | 46 | 0 | 172 | 118 | 115 | 0
16:00 | 3400 | 718 | 1506 | 0 | 2907 | 460 | 46 | 0 | 166 | 114 | 90 | 0
16:30 | 3420 | 718 | 1497 | 0 | 2922 | 460 | 46 | 0 | 182 | 111 | 61.5 | 0
17:00 | 3420 | 718 | 1488 | 0 | 2937 | 460 | 46 | 0 | 198 | 108 | 33 | 0
17:30 | 3348.5 | 718.5 | 1532.5 | 0 | 3072 | 465 | 46 | 0 | 275 | 114 | 16.5 | 0
18:00 | 3277 | 719 | 1577 | 0 | 3207 | 470 | 46 | 0 | 352 | 120 | 0 | 0
18:30 | 3439 | 719 | 1652 | 62.5 | 3399 | 525 | 46 | 0 | 428.5 | 125 | 0 | 0
19:00 | 3601 | 719 | 1727 | 125 | 3591 | 580 | 46 | 0 | 505 | 130 | 0 | 0
19:30 | 3591 | 718 | 1696 | 0 | 3713 | 600 | 46 | 0 | 521 | 126 | 0 | 0
20:00 | 3585 | 719 | 1705 | 0 | 3643 | 610 | 46 | 0 | 299 | 122 | 0 | 0
20:30 | 3590 | 718.5 | 1721 | 0 | 3554.5 | 610 | 46 | 0 | 223.5 | 122 | 0 | 0
21:00 | 3595 | 718 | 1737 | 0 | 3466 | 610 | 46 | 0 | 148 | 122 | 0 | 0
21:30 | 3596.5 | 718 | 1726.5 | 0 | 3255 | 610 | 46 | 0 | 131 | 116 | 0 | 0
22:00 | 3598 | 718 | 1716 | 0 | 3044 | 610 | 46 | 0 | 114 | 110 | 0 | 0
22:30 | 3604.5 | 718 | 1739.5 | 0 | 2763.5 | 605 | 46 | 0 | 57 | 109 | 0 | 0
23:00 | 3611 | 718 | 1763 | 0 | 2483 | 600 | 46 | 0 | 0 | 108 | 0 | 0
23:30 | 3610 | 718 | 1736.5 | 0 | 2251 | 580 | 46 | 0 | 0 | 104 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.6° C
24:00 | 3609 | 718 | 1710 | 0 | 2019 | 560 | 46 | 0 | 0 | 100 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1109400
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 6 | 25 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 |  |  |  |  | 155215
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 4 | 10 | 19 | 15 | 18 | 15 | 16 | 15 | 9 | 4 | [9 empty] | 124605
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 17 |  |  |  |  | 88179
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 68 | 34 | 17 | 17 | 17 | 17 | 17 | 22 | 53 | 86 | 105 | 105 | 105 | 98 | 104 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 51 | 1870945
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [10 empty] | 17 | 33 | 31 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | [5 empty] | 283688
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 93 | 95 | 95 | 95 | 96 | 96 | 96 | 95 | 95 | 95 | 95 | 95 | 92 | 92 | 92 | 92 | 90 | 37 |  | 94 | 92 | 92 | 95 | 95 | 95 | 95 | 2332000
17 | Siddhirganj 335 MW CCPP | 164 | 165 | 170 | 165 | 167 | 173 | 194 | 184 | 154 | 160 | 159 | 148 | 155 | 145 | 154 | 157 | 155 | 158 |  | 157 | 158 | 157 | 155 | 152 | 154 | 155 | 3988620
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 |  |  |  |  | 2 | 68 | 270 | 290 | 290 | 290 | 277 | 282 | 245 | 245 | 245 | 245 | 282 |  | 291 | 291 | 293 | 293 | 195 | 15 | 0 | 4496289
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 55 | 73 | 102 | 147 | 175 | 177 | 177 | 177 | 70 | 118 |  | 175 | 175 | 175 | 175 | 182 | 185 | 150 | 2425454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8217291
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 29 | 29 | 26 | 26 | 29 | 29 |  | 29 | 29 | 26 | 29 | 29 | 29 | 29 | 652752
33 | Ashuganj 225 MW CCPP | 181 | 184 | 182 | 181 | 181 | 202 | 186 | 194 | 195 | 160 | 192 | 186 | 183 | 188 | 195 | 182 | 185 | 122 |  | 190 | 184 | 184 | 185 | 184 | 184 | 169 | 4497000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 295 | 335 | 305 | 330 | 315 | 310 | 305 | 305 | 305 | 305 | 320 | 305 | 305 | 280 |  | 315 | 305 | 305 | 305 | 305 | 305 | 305 | 7550000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 280 | 295 | 270 | 280 | 345 | 315 | 310 | 310 | 310 | 305 | 325 | 310 | 310 | 270 |  | 320 | 310 | 310 | 310 | 310 | 310 | 310 | 7737100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7077000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 215 | 215 | 215 | 215 | 215 | 215 | 216 | 216 | 210 | 206 | 201 | 189 | 175 | 175 | 187 | 191 | 203 | 199 |  | 200 | 203 | 200 | 203 | 203 | 205 | 205 | 4774080
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 18 | 31 | 42 | 49 | 50 | 49 | 42 | 33 | 22 | 7 | 0 | [8 empty] | 346770
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 690400
46 | Shajibazar 330 MW CCPP | 159 | 159 | 160 | 158 | 160 | 161 | 160 | 160 | 161 | 160 | 160 | 160 | 161 | 160 | 158 | 158 | 160 | 160 |  | 160 | 160 | 159 | 160 | 160 | 160 | 161 | 3789000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 60 | 40 | 40 | 40 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1375104
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 86 | 86 | 89 | 87 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 2128320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245340
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 190368
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 48 | 48 | 48 | 49 | 45 | 50 | 48 | 48 | 50 |  | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 1185000
56 | Shahjahanulla 25 MW PP | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 23 |  | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 526560
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 280 | 285 | 275 | 310 | 310 | 280 | 290 | 300 | 300 | 300 | 275 | 280 | 305 | 300 | 290 | 270 |  | 295 | 270 | 270 | 280 | 280 | 270 | 270 | 7056000
| Bibiyana South 400 MW | 355 | 355 | 310 | 250 | 200 | 200 | 205 | 240 | 320 | 350 | 343 | 343 | 300 | 250 | 300 | 300 | 300 | 401 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 7591600
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | 17 | 17 | 17 | 17 | 50 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 1030729
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530400
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 417936
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 365904
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 450576
63 | Impoprt (Tripura) | 102 | 100 | 98 | 94 | 92 | 92 | 92 | 98 | 100 | 102 | 106 | 118 | 120 | 122 | 122 | 114 | 108 | 120 |  | 130 | 126 | 122 | 122 | 110 | 108 | 100 | 2633280
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 42 | 38 | 6 | 2 | 2 | 2 | 2 | 7 | 5 | 2 | 2 | 5 | 2 |  | 10 | 9 | 18 | 29 | 35 | 39 | 40 | 492480
65 | Feni 22MW PP (Doreen) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 476208
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 228060
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 23 | 20 | 16 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 592100
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 18 | 18 | 18 | 18 | 18 | 14 | 14 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 434920
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 30 | 30 | 28 | 29 | 29 | 29 | 29 |  | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 681840
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 746280
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 802400
73 | Ghorashal 108MW PP (Regent) | [10 empty] | 15 | 45 | 57 | 56 | 54 | 84 | 98 | 97 |  | 97 | 103 | 106 | 103 | 106 | 106 | 106 | 1032909
| Feni Lanka Power | [5 empty] | 3 | 85 | 114 | 114 | 114 | 114 | 114 | 114 | 77 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 70 | 34 |  | 1800060
| Chowmuhani 113 MW | [26 empty] | 0
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 108 | 108 | 108 | 121 | 144 | 144 | 144 | 144 | 144 | 144 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3625920
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 9 | 25 | 25 | 25 | 25 | 34 | 25 | 25 | 25 | 25 | 32 | 51 |  | 51 | 51 | 8 | 8 | 8 |  |  | 465120
79 | Kodda 150MW PP | [6 empty] | 48 | 48 | 48 | 48 | 48 | 110 | 150 | 32 | 32 | 16 | 16 | 98 |  | 150 | 150 | 16 | 16 | 16 |  |  | 891360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 24 | 24 | 24 | 24 | 24 | 34 | 52 | 49 | 43 | 52 | 52 | 43 | 52 | 43 | 43 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1082270
| Gazipur 100 MW PP | 70 | 34 |  |  |  | 9 | 49 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 35 | 1680000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 35279
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 39 | 52 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1330240
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 107 | 106 | 108 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2673007
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | [8 empty] | 12 | 12 | 12 | 25 | 100 | 120 | 120 | 130 | 230 | 260 |  | 280 | 250 | 250 | 256 | 241 | 274 | 257 | 2401367
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 97 | 88 | 70 | 70 | 70 | 70 | 77 | 88 | 87 | 90 | 88 | 88 | 87 | 87 | 87 | 87 | 58 | 54 |  | 84 | 88 | 90 | 104 | 104 | 104 | 75 | 2064000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 60 | 86 | 10 | 20 | 20 | 20 | 20 |  | 40 | 40 | 10 |  |  |  |  | 284880
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1158198
94 | Gagnagar 102 MW PP (Digital Power) | [5 empty] | 7 | 58 | 76 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 48 | 32 | 74 |  | 84 | 93 | 93 | 93 | 93 | 7 |  | 1330704
95 | Patenga 50MW PP (Baraka) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 9 | 38 | 40 | 15 | 18 | 36 |  | 42 | 42 | 42 | 42 | 42 | 42 | 18 | 912960
96 | Chattogram 108 MW PP (ECPV) | 98 | 98 | 98 | 98 | 98 | 98 | 99 | 98 | 99 | 98 | 92 | 91 | 97 | 97 | 97 | 97 | 95 | 92 |  | 96 | 98 | 98 | 98 | 98 | 98 | 98 | 2339520
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 20 | 45 | 55 | 40 | 40 | 55 | 55 | 40 | 36 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 15 |  |  | 799469
100 | Manikganj 55 MW PP (Northern) | [5 empty] | 17 | 26 | 35 | 35 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 35 |  |  |  | 620706
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2914936
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 15450
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1271520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 100 | [6 empty] | 90688
106 | Mymensingh 200 MW PP (United) | 187 | 150 | 150 | 150 | 150 | 160 | 170 | 170 | 180 | 178 | 177 | 175 | 175 | 174 | 165 | 155 | 165 | 174 |  | 173 | 173 | 183 | 184 | 175 | 175 | 140 | 4053600
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 25 | [6 empty] | 22192
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 109 | 101 | 106 | 106 | 105 | 114 | 149 | 149 | 149 | 140 | 137 | 135 | 135 | 144 | 135 | 136 | 141 |  | 149 | 149 | 149 | 149 | 149 | 149 | 117 | 3245900
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 70 | 82 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2076480
116 | Chandpur 200MW (Desh energy) | [5 empty] | 5 | 30 | 80 | 85 | 85 | 85 | 92 | 120 | 34 | 34 | 17 | 17 | 32 |  | 154 | 184 | 182 | 85 |  |  |  | 1289280
117 | Ashuganj 150MW PP (Midland) | 80 | 97 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 98 | 98 | 97 | 93 | 92 | 93 | 93 | 93 |  | 115 | 150 | 140 | 150 | 150 | 150 | 150 | 2602763
118 | Bibiyana-III 400 MW CCPP | 79 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 197 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 3573000
| Jamalpur 115 MW PP (United) | 24 |  |  |  |  | 6 | 58 | 105 | 109 | 99 | 98 | 98 | 99 | 99 | 89 | 35 | 35 | 54 |  | 108 | 108 | 109 | 109 | 109 | 35 | 8 | 1606800
| Anwara 300 MW PP (United) | 270 | 282 | 264 | 265 | 265 | 265 | 248 | 246 | 246 | 246 | 265 | 265 | 265 | 265 | 263 | 262 | 283 | 278 |  | 276 | 300 | 300 | 300 | 300 | 300 | 300 | 6455891
| Juldah unit-2 (Acorn) | 50 | 10 | 10 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 46 | 79 | 88 | 88 | 76 | 50 | 50 | 55 |  | 90 | 100 | 100 | 100 | 70 | 70 | 30 | 1396800
| Anlima Energy Ltd. | 115 | 115 | 115 | 115 | 95 | 87 | 87 | 87 | 95 | 114 | 115 | 115 | 115 | 114 | 114 | 114 | 115 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 112 | 2645836
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 437760
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 11 | 20 | 25 | 32 | 32 | 32 | 28 | 22 | 14 | 6 | 0 | [8 empty] | 225475
| Chandpur 115(Doreen) | [5 empty] | 5 | 31 | 52 | 56 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 |  |  | 19 | 1052160
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 35 | 46 | 55 |  | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1300680
120 | Eastern Zone Total | 5772 | 5411 | 5232 | 5154 | 5017 | 5226 | 5698 | 6164 | 6484 | 6565 | 6676 | 6920 | 7116 | 6771 | 6936 | 6705 | 6710 | 7000 |  | 7898 | 7818 | 7550 | 7439 | 7011 | 6623 | 6178 | 156650933
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 4 | 4 |  | 40 | 39 | 39 |  |  |  |  | 82080
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 35 | 35 | 35 | 35 | 40 | 88 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 2260960
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 7 | 26 | 48 | 72 | 85 | 89 | 86 | 77 | 58 | 37 | 13 | [9 empty] | 604080
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 203 | 223 | 223 | 224 | 214 | 223 | 223 | 223 | 223 | 221 | 221 | 221 | 221 | 183 | 184 | 180 | 161 | 163 |  | 223 | 220 | 217 | 225 | 203 | 225 | 223 | 5046409
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 521983
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 92 | 92 | 92 | 92 | 92 |  | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 2211103
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 6 | 7 | 8 |  | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 184352
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 5 | 15 | [5 empty] | 9472
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 719 | 719 | 719 | 719 | 718 | 719 | 719 | 719 | 718 | 719 | 719 | 719 | 719 | 719 | 719 | 718 | 718 | 719 |  | 719 | 718 | 719 | 718 | 718 | 718 | 718 | 17381090
147 | Bheramara 410 MW CCPP | 370 | 370 | 340 | 300 | 300 | 300 | 320 | 320 | 320 | 320 | 320 | 370 | 380 | 350 | 350 | 350 | 350 | 300 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 8657568
148 | Payra 1320 MW | 360 | 350 | 310 | 290 | 280 | 280 | 280 | 270 | 240 | 240 | 240 | 240 | 240 | 240 | 260 | 260 | 260 | 270 |  | 380 | 400 | 410 | 410 | 410 | 400 | 360 | 8273900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4868100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 2359000
| Baghabari 50 MW Peaking PP | [17 empty] | 34 |  | 34 | 34 | 34 | 34 |  |  |  | 123376
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 4 | 2 | 0 | 0 | [8 empty] | 38160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [16 empty] | 3 | 8 |  | 5 | 4 | 4 | 8 | 25 | 26 | 38 | 161491
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 220 | 220 | 220 | 220 | 220 | 206 | 207 | 186 | 197 | 193 | 194 | 199 | 206 | 164 | 189 | 188 | 191 | 173 |  | 178 | 185 | 185 | 185 | 185 | 184 | 184 | 4961118
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [8 empty] | 4 | 4 | 7 | 25 | 33 | 38 | 34 | 34 | 34 | 34 |  | 35 | 35 | 25 |  |  |  |  | 300527
162 | Bogra 22 MW PP (GBB) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 141120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 173100
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 43 | 50 | 50 |  |  |  |  | 83154
167 | Katakhali 50 MW Peaking PP | [9 empty] | 12 | 21 | 24 | 24 | 24 | 24 | 24 | 30 | 31 |  | 31 | 37 | 40 |  |  |  |  | 250848
168 | Santahar 50 MW Peaking PP | [16 empty] | 26 | 29 |  | 30 | 30 | 30 |  |  |  |  | 109737
169 | Natore 52 MW PP (Rajlanka) | [5 empty] | 3 | 10 | 36 | 43 | 52 | 52 | 52 | 52 | 8 | 34 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 43 | 8 | 0 | 721440
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 32 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 90 |  | 97 | 98 | 98 | 98 | 98 |  |  | 857120
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 90 | 90 | 103 | 113 | 113 | 113 | 94 | 105 | 94 | 94 | 94 | 94 | 94 | 94 | 107 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2563584
172 | Confidence Power Bogura Unit-1 113 MW | 70 |  |  |  |  | 35 | 100 | 113 | 113 | 113 | 95 | 95 | 105 | 113 | 95 | 50 | 50 | 95 |  | 113 | 113 | 113 | 113 | 113 | 50 | 50 | 1869504
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 |  |  |  |  | 44 | 54 | 105 | 113 | 113 | 113 | 112 | 110 | 70 | 95 | 109 | 112 | 112 |  | 112 | 113 | 113 | 113 | 113 | 49 |  | 1829068
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 6 | 5 | 5 | 4 | 3 | 2 | 0 | [8 empty] | 40068
178 | Energypac Power Venture Thakurgaon Ltd. | [6 empty] | 56 | 54 | 54 | 54 | 54 | 98 | 115 | 17 | 17 | 18 | 18 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547740
178