## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-09 | Wednesday
|  |  | Date (day): | 2022-03-09 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12815.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13480 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-08 | 2022-03-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 340 | 340 | 340
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 103 | 104 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 305 | 305 | 30 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 158 | 225 | 225 | 110 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 29 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 53 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 30 | 30
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 290 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 108 | 304 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 45 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 25 | 99 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 133 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 90 | 90 | 90 |  | 15 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 86 | 76 | 90 | 93 |  | 11 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 37 | 0 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2476 | 2967 | 3232 | 3305 | 963 | 1365
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 7 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 27 | 45 | 42 | 45 |  | 5 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 |  | 184 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 91 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 0 | 19 | 19
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 8 | 10 | 10
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 99 | 105 | 100 | 108
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 102 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1106 | 1244 | 1290 | 1276 | 180 | 903
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 213 | 210 | 225 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 315 | 325 | 335 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 305 | 330 | 335 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 78 | 45 | 45 | 150 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 142 | 138 | 140 | 145
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 32 | 33 | 33 | 33 |  | 19 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 152 | 160 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 148 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 8 | 20 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 8 | 105 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 34 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 0 | 0 | 70 | 115 | 115 | 115 |  |  | On test
|  | Cumilla Area Total |  |  |  |  | 2944 | 2899 | 1789 | 2055 | 1982 | 2151 | 584 | 227
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 173 | 187 | 200 | 200
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 154 | 160 | 190 | 190
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 108 | 108 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 530 | 497 | 598.6 | 547 | 0 | 8
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 41 | 42 | 42 |  | 48 | GT-4 under maint.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 | 53 |  | Gas shortage
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 142 | 140 | 150 | 150 | 180 |  | Gas shortage
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 60 | 60 | 60
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 89 | 89 | 86 | 86
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 23 | 21 | 24
| 102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 330 | 330 |  |  | FGMO
| 103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 240 | 240 | 370 | 400 | 0 |  | Gas shortage
| 104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
| 105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 350 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1415 | 1464 | 1670 | 1703 | 484 | 188
| 106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 720 | 717 | 730 | 730
| 107 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 0 | 40 |  | 14 | Engine problem
| 109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 8 | 0 | 40 |  | 69 | Engine problem
| 111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 410 | 410 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 112 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 70 | 100 | 100
| 113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 94 | 105 | 105 | 105
| 114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 50 | 100
| 115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1225 | 1349 | 1445 | 1745 | 0 | 83
| 116 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 117 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 8 | 9 | 10 | 10 |  |  | Engine problem
| 118 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 91 | 90 | 90 | 92 | 102 |  | Gas shortage
| 119 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 460 | 620 | 620
| 121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 215 | 217 | 225 | 225
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 50 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 625 | 787 | 1116 | 1218 | 186 | 0
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 34 | 34 | 34 | 34 |  | 18 | Engine problem
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 29 | 40 | 40 | 41 |  | 30 | Engine problem
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 32 | 0 | 40 |  | 10 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 202 | 214 | 200 | 200 |  |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 203 | 200 | 220
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 30 | 25 | 30 |  | 20 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 6 | 7 |  | 4 | Engine problem
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 48 | 96 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 120 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 95 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113 |  | 0
| 142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 850 | 1126 | 1161 | 1222 | 380 | 496
| 143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 104 | 113 | 113 | 113
| 148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 311 | 313 | 321 | 313 | 74 | 210
|  | Total |  |  |  |  | 22066 | 20985 | 10327 | 11802 | 12815.6 | 13480 | 2851 | 3480
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9934.9905 | 11354 | 12329.1241 | 12968.3037
| A. |  | 2022-03-08 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 11802 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 7763 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11802 | MW
| 3 | Day peak Generation : |  |  | 10327 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11354 | MW
| 4 | Evening peak Generation : |  |  | 11802 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 232.6287 | MKWHr | By Solar | 1.4593 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 120.325 | MKWHr |  | By Oil: | 75.1845 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.6296 | MKWHr |  | By Hydro: | 1.1045 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2851 | MW | Dhaka | 4173 | 4173 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3480 | MW | Chittagong | 1290 | 1290 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6331 | MW | Khulna | 1313 | 1313 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 897.94 | MMCFD |  |  | Rajshahi | 1181 | 1181 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 118496050.168 | ii) Oil : | Taka | 556183898.77 | Comilla | 928 | 928 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 69204921 | Total | Taka | 743884869.938 | Mymensingh | 995 | 995 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.475 | MKWHr. | Sylhet | 417 | 417 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -86 | MW (E to W) at | 19:00 | hrs | Barisal | 286 | 286 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -192 | MW at | 8:00 | hrs | Rangpur | 771 | 771 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.1° C |  |  | Total | 11354 | 11354 |  | 0
| B. |  | 2022-03-09 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13480 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10400 | MW
| 4 | Reserve(Generation end) |  |  |  | 1480 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 236.5315 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8037 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.4058 | MKWHr. | ii) HVDC Flow at Peak Time |  | 717 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.52 | MKWHr. | iii) Maximum HVDC Flow : |  | 721 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.46 |  | (b) Today: | 89.34 |  | (c) Rule Curve: |  | 91.88
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 0 | 18 | 31 | 0 | 0 | 0 | 270 | 270 | 210 | 120 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 21 | 10 | 25 | 21 | 100 | 210 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 148 | 50 | 89 | 0 | 0 | 0 | 0 | 9 | 280 | 23 | 11 | 0 | 15 | 0 | 0 | 183 | 0 | 149 | 0 | 90 | 0 | 150 | 240 | 8 | 90 | 34 | 0 | 300 | 54 | 110 | 75 | 0 | 10 | 350 | 91 | 0 | 162 | 113 | 0 | 17 | 0 | 72 | 55 |  | 721 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 0 | 187 | 0 | 0 | 70 | 0 | 113 | 0 | 44 | 0 | 0 | 0 | 370 | 224 | 0 | 0 | 0 | 0 | 0 |  | 6149 | 2588 | 8737 | 3474 | 721 | 1562 | 0 | 2265 | 569 | 46 | 0 | 0 | 100 | 0 | 0 | 89.48
2:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 93 | 0 | 18 | 32 | 0 | 0 | 0 | 270 | 270 | 211 | 120 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 25 | 21 | 96 | 210 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 147 | 50 | 89 | 0 | 0 | 0 | 0 | 9 | 285 | 23 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 149 | 0 | 90 | 0 | 150 | 240 | 8 | 17 | 17 | 0 | 300 | 54 | 110 | 70 | 0 | 10 | 330 | 80 | 0 | 162 | 113 | 0 | 17 | 0 | 53 | 55 |  | 721 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 185 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 350 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5923 | 2480 | 8403 | 3450 | 721 | 1564 | 0 | 1977 | 549 | 46 | 0 | 0 | 96 | 0 | 0 | 89.48
3:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 0 | 156 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 105 | 0 | 18 | 40 | 0 | 0 | 0 | 285 | 270 | 208 | 120 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 25 | 21 | 94 | 212 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 146 | 50 | 89 | 0 | 0 | 0 | 0 | 9 | 280 | 23 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 124 | 0 | 50 | 0 | 150 | 240 | 8 | 0 | 17 | 0 | 300 | 54 | 110 | 70 | 0 | 10 | 307 | 53 | 0 | 108 | 17 | 0 | 17 | 0 | 0 | 55 |  | 721 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 185 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 320 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5570 | 2452 | 8022 | 3437 | 721 | 1567 | 0 | 1637 | 520 | 46 | 0 | 0 | 94 | 0 | 0 | 89.47
4:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 104 | 0 | 18 | 40 | 0 | 0 | 0 | 285 | 270 | 203 | 120 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 25 | 21 | 92 | 213 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 140 | 50 | 89 | 0 | 0 | 0 | 0 | 9 | 290 | 21 | 8 | 0 | 15 | 0 | 0 | 100 | 0 | 115 | 0 | 10 | 0 | 150 | 240 | 8 | 0 | 17 | 0 | 300 | 54 | 68 | 52 | 0 | 10 | 238 | 53 | 0 | 108 | 17 | 0 | 17 | 0 | 0 | 55 |  | 720 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 0 | 190 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 320 | 224 | 0 | 0 | 0 | 0 | 0 |  | 5385 | 2465 | 7850 | 3364 | 720 | 1581 | 0 | 1527 | 520 | 46 | 0 | 0 | 92 | 0 | 0 | 89.47
5:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 104 | 0 | 18 | 41 | 0 | 0 | 0 | 285 | 270 | 210 | 120 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 25 | 21 | 92 | 214 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 142 | 50 | 86 | 0 | 0 | 0 | 0 | 9 | 280 | 21 | 8 | 0 | 15 | 0 | 0 | 100 | 0 | 115 | 0 | 10 | 0 | 150 | 240 | 8 | 0 | 17 | 0 | 300 | 54 | 68 | 52 | 0 | 10 | 203 | 53 | 0 | 108 | 17 | 0 | 17 | 0 | 0 | 55 |  | 721 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 0 | 186 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 320 | 182 | 0 | 0 | 0 | 0 | 0 |  | 5348 | 2415 | 7763 | 3331 | 721 | 1527 | 0 | 1527 | 519 | 46 | 0 | 0 | 92 | 0 | 0 | 89.46
6:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 0 | 165 | 0 | 92 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 32 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 104 | 1 | 18 | 42 | 0 | 0 | 0 | 285 | 270 | 209 | 120 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 16 | 21 | 90 | 216 | 0 | 20 | 0 | 30 | 42 | 51 | 0 | 110 | 142 | 50 | 89 | 0 | 0 | 0 | 0 | 9 | 295 | 21 | 8 | 0 | 17 | 0 | 0 | 122 | 0 | 120 | 0 | 10 | 0 | 150 | 240 | 8 | 6 | 17 | 0 | 300 | 54 | 68 | 52 | 0 | 10 | 180 | 62 | 0 | 128 | 17 | 0 | 17 | 0 | 0 | 55 |  | 721 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 191 | 0 | 0 | 35 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 320 | 220 | 0 | 0 | 0 | 0 | 0 |  | 5491 | 2537 | 8028 | 3370 | 721 | 1585 | 0 | 1697 | 519 | 46 | 0 | 0 | 90 | 0 | 0 | 89.46
7:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 12 | 173 | 0 | 94 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 104 | 18 | 18 | 40 | 0 | 0 | 0 | 320 | 305 | 190 | 120 | 0 | 26 | 5 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 25 | 21 | 88 | 215 | 0 | 20 | 0 | 30 | 42 | 48 | 0 | 110 | 142 | 30 | 89 | 0 | 0 | 0 | 0 | 9 | 295 | 21 | 8 | 0 | 74 | 0 | 0 | 136 | 0 | 136 | 2 | 30 | 0 | 143 | 240 | 45 | 24 | 17 | 0 | 300 | 54 | 68 | 70 | 0 | 10 | 175 | 90 | 5 | 144 | 40 | 0 | 17 | 3 | 6 | 41 |  | 720 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 195 | 0 | 11 | 0 | 198 | 0 | 0 | 70 | 0 | 113 | 0 | 54 | 0 | 0 | 80 | 320 | 223 | 0 | 0 | 0 | 6 | 0 |  | 5862 | 2670 | 8532 | 3428 | 720 | 1583 | 0 | 2132 | 519 | 46 | 0 | 0 | 88 | 16 | 0 | 89.45
8:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 31 | 171 | 0 | 92 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 96 | 31 | 16 | 10 | 0 | 0 | 0 | 285 | 270 | 191 | 120 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 25 | 21 | 98 | 214 | 0 | 20 | 1 | 30 | 42 | 48 | 0 | 110 | 141 | 30 | 89 | 0 | 0 | 0 | 0 | 9 | 290 | 21 | 8 | 0 | 163 | 0 | 0 | 148 | 0 | 132 | 8 | 50 | 36 | 142 | 240 | 105 | 50 | 17 | 1 | 300 | 54 | 68 | 70 | 0 | 10 | 230 | 90 | 17 | 144 | 69 | 0 | 17 | 10 | 71 | 38 |  | 720 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 191 | 0 | 11 | 0 | 195 | 0 | 0 | 94 | 0 | 113 | 0 | 90 | 0 | 1 | 95 | 320 | 221 | 0 | 0 | 1 | 28 | 0 |  | 6267 | 2796 | 9063 | 3399 | 720 | 1546 | 0 | 2668 | 519 | 46 | 0 | 0 | 98 | 67 | 0 | 89.45
9:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 162 | 0 | 57 | 0 | 93 | 82 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 30 | 25 | 33 | 36 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 93 | 31 | 16 | 3 | 0 | 0 | 0 | 285 | 270 | 200 | 88 | 0 | 23 | 5 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 25 | 21 | 104 | 203 | 0 | 20 | 2 | 30 | 42 | 47 | 0 | 110 | 141 | 30 | 89 | 0 | 0 | 0 | 0 | 9 | 280 | 21 | 8 | 0 | 250 | 0 | 0 | 158 | 0 | 136 | 14 | 70 | 58 | 140 | 240 | 108 | 74 | 17 | 3 | 300 | 54 | 95 | 70 | 0 | 30 | 350 | 90 | 30 | 144 | 90 | 0 | 17 | 19 | 72 | 38 |  | 720 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 12 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 0 | 183 | 0 | 0 | 94 | 0 | 113 | 0 | 97 | 0 | 2 | 95 | 290 | 216 | 0 | 0 | 3 | 53 | 0 |  | 6663 | 2752 | 9415 | 3405 | 720 | 1491 | 0 | 2934 | 490 | 46 | 0 | 99 | 104 | 126 | 0 | 89.44
10:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 164 | 0 | 59 | 0 | 93 | 82 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 31 | 16 | 2 | 0 | 0 | 0 | 300 | 285 | 218 | 78 | 0 | 23 | 5 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 17 | 21 | 110 | 188 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 143 | 30 | 89 | 0 | 0 | 0 | 0 | 9 | 290 | 21 | 8 | 0 | 270 | 0 | 0 | 157 | 0 | 132 | 18 | 76 | 85 | 140 | 240 | 108 | 90 | 17 | 4 | 300 | 54 | 110 | 73 | 0 | 43 | 350 | 89 | 41 | 144 | 113 | 0 | 17 | 26 | 72 | 37 |  | 721 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 7 | 0 | 0 | 0 | 0 | 0 | 5 | 36 | 0 | 0 | 24 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 156 | 0 | 0 | 94 | 0 | 105 | 0 | 106 | 0 | 3 | 95 | 280 | 221 | 0 | 0 | 4 | 73 | 0 |  | 6847 | 2760 | 9607 | 3376 | 721 | 1485 | 0 | 3071 | 480 | 46 | 0 | 147 | 110 | 171 | 0 | 89.44
11:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 40 | 166 | 0 | 95 | 0 | 93 | 115 | 0 | 0 | 0 | 0 | 35 | 29 | 55 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 31 | 16 | 2 | 0 | 0 | 0 | 285 | 345 | 186 | 78 | 0 | 23 | 5 | 0 | 43 | 0 | 18 | 45 | 18 | 11 | 25 | 21 | 116 | 175 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 140 | 30 | 89 | 0 | 0 | 0 | 0 | 9 | 310 | 21 | 5 | 0 | 280 | 0 | 0 | 155 | 0 | 135 | 20 | 76 | 93 | 140 | 240 | 108 | 90 | 58 | 4 | 300 | 54 | 110 | 114 | 0 | 55 | 350 | 80 | 49 | 144 | 113 | 0 | 17 | 29 | 72 | 37 |  | 721 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 48 | 0 | 0 | 24 | 52 | 25 | 22 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 154 | 0 | 0 | 94 | 0 | 94 | 0 | 106 | 0 | 5 | 95 | 280 | 220 | 0 | 0 | 5 | 86 | 0 |  | 7081 | 2824 | 9905 | 3438 | 721 | 1505 | 0 | 3164 | 480 | 46 | 0 | 235 | 116 | 200 | 0 | 89.43
12:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 29 | 55 | 19 | 25 | 29 | 25 | 33 | 42 | 0 | 46 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 99 | 27 | 16 | 2 | 0 | 0 | 0 | 335 | 330 | 198 | 78 | 0 | 29 | 5 | 0 | 43 | 0 | 32 | 43 | 18 | 11 | 25 | 21 | 126 | 173 | 0 | 20 | 2 | 30 | 42 | 48 | 0 | 110 | 142 | 30 | 89 | 0 | 0 | 0 | 0 | 8 | 300 | 21 | 5 | 0 | 290 | 108 | 45 | 154 | 25 | 133 | 20 | 76 | 152 | 142 | 240 | 108 | 90 | 91 | 5 | 300 | 54 | 110 | 114 | 0 | 90 | 350 | 86 | 51 | 144 | 113 | 0 | 17 | 31 | 70 | 37 |  | 720 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 34 | 29 | 48 | 0 | 0 | 24 | 52 | 30 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 202 | 0 | 11 | 0 | 208 | 0 | 0 | 94 | 0 | 95 | 0 | 104 | 0 | 7 | 95 | 300 | 215 | 0 | 0 | 5 | 91 | 0 |  | 7316 | 3011 | 10327 | 3336 | 720 | 1490 | 178 | 3372 | 500 | 46 | 0 | 347 | 126 | 212 | 0 | 89.43
13:00 | 0 | 0 | 0 | 0 | 340 | 100 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 40 | 7 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 100 | 103 | 35 | 16 | 4 | 0 | 0 | 0 | 310 | 310 | 186 | 78 | 0 | 29 | 5 | 0 | 51 | 0 | 31 | 52 | 18 | 8 | 25 | 21 | 126 | 158 | 0 | 20 | 2 | 30 | 42 | 45 | 0 | 110 | 141 | 30 | 89 | 0 | 0 | 0 | 0 | 8 | 305 | 21 | 5 | 0 | 286 | 20 | 75 | 154 | 25 | 133 | 20 | 90 | 160 | 147 | 241 | 108 | 90 | 91 | 4 | 300 | 54 | 110 | 114 | 0 | 90 | 350 | 90 | 50 | 144 | 113 | 0 | 17 | 29 | 72 | 55 |  | 721 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 34 | 33 | 48 | 0 | 0 | 24 | 52 | 31 | 19 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 214 | 0 | 11 | 0 | 203 | 0 | 0 | 94 | 0 | 94 | 0 | 102 | 0 | 7 | 95 | 350 | 215 | 0 | 0 | 5 | 88 | 0 |  | 7288 | 3087 | 10375 | 3294 | 721 | 1499 | 120 | 3464 | 549 | 46 | 0 | 351 | 126 | 205 | 0 | 89.42
14:00 | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 37 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 28 | 25 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 100 | 103 | 40 | 0 | 4 | 0 | 0 | 0 | 295 | 285 | 189 | 78 | 0 | 29 | 5 | 0 | 51 | 0 | 31 | 52 | 19 | 8 | 25 | 8 | 130 | 158 | 0 | 20 | 2 | 30 | 42 | 48 | 0 | 110 | 141 | 35 | 86 | 0 | 0 | 0 | 0 | 8 | 300 | 21 | 5 | 0 | 277 | 0 | 0 | 152 | 0 | 134 | 18 | 90 | 160 | 145 | 240 | 108 | 90 | 90 | 4 | 300 | 54 | 110 | 114 | 0 | 90 | 350 | 91 | 43 | 144 | 113 | 0 | 17 | 26 | 72 | 55 |  | 721 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 9 | 0 | 0 | 0 | 0 | 34 | 39 | 47 | 0 | 0 | 32 | 52 | 30 | 18 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 213 | 0 | 11 | 0 | 196 | 0 | 0 | 94 | 0 | 94 | 0 | 104 | 0 | 7 | 113 | 350 | 214 | 0 | 0 | 4 | 78 | 0 |  | 7155 | 3116 | 10271 | 3273 | 721 | 1495 | 0 | 3512 | 549 | 46 | 0 | 363 | 130 | 182 | 0 | 89.42
15:00 | 0 | 0 | 0 | 0 | 340 | 100 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 158 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 25 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 103 | 44 | 0 | 2 | 0 | 0 | 0 | 290 | 290 | 188 | 78 | 0 | 29 | 5 | 0 | 51 | 0 | 26 | 52 | 19 | 8 | 25 | 8 | 136 | 169 | 0 | 20 | 1 | 30 | 41 | 48 | 0 | 110 | 140 | 60 | 86 | 0 | 0 | 0 | 0 | 8 | 300 | 21 | 2 | 0 | 287 | 0 | 0 | 152 | 0 | 149 | 15 | 90 | 160 | 138 | 240 | 108 | 90 | 90 | 3 | 300 | 54 | 110 | 114 | 0 | 90 | 350 | 91 | 33 | 144 | 113 | 0 | 17 | 21 | 72 | 55 |  | 720 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 9 | 0 | 0 | 0 | 0 | 34 | 39 | 47 | 0 | 0 | 32 | 52 | 30 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 198 | 0 | 11 | 0 | 186 | 0 | 0 | 94 | 0 | 94 | 0 | 101 | 0 | 5 | 113 | 370 | 212 | 0 | 0 | 3 | 57 | 0 |  | 7341 | 3083 | 10424 | 3392 | 720 | 1488 | 0 | 3576 | 570 | 46 | 0 | 358 | 136 | 138 | 0 | 89.41
16:00 | 0 | 0 | 0 | 0 | 340 | 96 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 40 | 160 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 25 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 60 | 95 | 44 | 0 | 2 | 0 | 0 | 0 | 280 | 280 | 181 | 78 | 0 | 29 | 5 | 0 | 51 | 0 | 24 | 52 | 20 | 8 | 25 | 8 | 130 | 187 | 0 | 20 | 1 | 30 | 42 | 48 | 0 | 110 | 140 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 2 | 0 | 300 | 0 | 0 | 141 | 0 | 149 | 10 | 90 | 160 | 137 | 240 | 108 | 90 | 91 | 2 | 300 | 54 | 110 | 114 | 0 | 90 | 350 | 88 | 21 | 144 | 113 | 0 | 17 | 14 | 72 | 55 |  | 720 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 34 | 39 | 46 | 0 | 0 | 32 | 52 | 30 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 190 | 0 | 0 | 94 | 0 | 94 | 0 | 99 | 0 | 2 | 113 | 370 | 173 | 0 | 0 | 2 | 36 | 0 |  | 7236 | 3007 | 10243 | 3368 | 720 | 1446 | 0 | 3520 | 570 | 46 | 0 | 355 | 130 | 88 | 0 | 89.41
17:00 | 0 | 0 | 0 | 0 | 340 | 102 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 157 | 0 | 0 | 0 | 93 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 25 | 33 | 24 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 30 | 93 | 44 | 0 | 5 | 0 | 0 | 0 | 285 | 280 | 181 | 78 | 0 | 26 | 5 | 0 | 51 | 0 | 32 | 52 | 20 | 8 | 25 | 8 | 126 | 188 | 0 | 20 | 0 | 30 | 42 | 48 | 0 | 110 | 141 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 295 | 21 | 2 | 0 | 298 | 0 | 0 | 159 | 0 | 149 | 4 | 90 | 160 | 132 | 240 | 108 | 90 | 105 | 1 | 300 | 54 | 110 | 114 | 0 | 50 | 350 | 90 | 7 | 144 | 113 | 0 | 0 | 5 | 84 | 55 |  | 719 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 8 | 0 | 0 | 0 | 0 | 34 | 39 | 46 | 0 | 0 | 32 | 24 | 30 | 19 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 191 | 0 | 11 | 0 | 175 | 0 | 0 | 94 | 0 | 94 | 0 | 99 | 0 | 2 | 50 | 370 | 173 | 0 | 0 | 0 | 13 | 0 |  | 7118 | 2840 | 9958 | 3319 | 719 | 1454 | 0 | 3365 | 569 | 46 | 0 | 328 | 126 | 32 | 0 | 89.4
18:00 | 0 | 0 | 0 | 0 | 340 | 104 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 158 | 0 | 0 | 0 | 93 | 140 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 9 | 33 | 33 | 24 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 30 | 95 | 46 | 0 | 4 | 0 | 0 | 0 | 340 | 335 | 202 | 78 | 0 | 26 | 5 | 0 | 51 | 0 | 33 | 52 | 20 | 10 | 25 | 8 | 142 | 187 | 0 | 20 | 0 | 30 | 42 | 48 | 0 | 110 | 138 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 295 | 21 | 8 | 0 | 300 | 0 | 0 | 150 | 0 | 149 | 0 | 90 | 160 | 132 | 240 | 108 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 50 | 350 | 89 | 0 | 144 | 113 | 0 | 16 | 0 | 103 | 55 |  | 720 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 90 | 9 | 0 | 0 | 0 | 0 | 34 | 40 | 87 | 0 | 16 | 32 | 26 | 30 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 191 | 0 | 11 | 0 | 173 | 0 | 0 | 94 | 0 | 94 | 0 | 105 | 0 | 0 | 90 | 380 | 172 | 0 | 0 | 0 | 0 | 0 |  | 7354 | 2965 | 10319 | 3442 | 720 | 1457 | 0 | 3463 | 580 | 46 | 0 | 469 | 142 | 0 | 0 | 89.4
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 340 | 104 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 158 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 100 | 105 | 45 | 0 | 8 | 0 | 0 | 0 | 315 | 305 | 213 | 78 | 0 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 10 | 25 | 8 | 148 | 187 | 0 | 20 | 0 | 30 | 41 | 50 | 0 | 110 | 140 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 310 | 23 | 11 | 200 | 300 | 304 | 100 | 160 | 99 | 149 | 0 | 90 | 160 | 138 | 240 | 108 | 90 | 105 | 0 | 300 | 54 | 102 | 114 | 0 | 100 | 350 | 76 | 0 | 144 | 113 | 0 | 34 | 0 | 115 | 0 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 39 | 8 | 0 | 90 | 9 | 0 | 0 | 0 | 0 | 34 | 40 | 96 | 0 | 50 | 32 | 52 | 30 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 214 | 0 | 11 | 70 | 203 | 0 | 0 | 105 | 120 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 217 | 0 | 0 | 0 | 0 | 0 |  | 8227 | 3575 | 11802 | 3593 | 717 | 1523 | 893 | 3709 | 660 | 46 | 0 | 513 | 148 | 0 | 0 | 89.38
19:30 | 0 | 0 | 0 | 0 | 340 | 105 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 190 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 100 | 105 | 44 | 0 | 12 | 0 | 0 | 0 | 310 | 305 | 213 | 45 | 0 | 29 | 25 | 0 | 51 | 0 | 33 | 52 | 22 | 10 | 25 | 15 | 144 | 186 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 141 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 120 | 300 | 251 | 100 | 153 | 100 | 149 | 0 | 90 | 180 | 145 | 240 | 98 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 350 | 90 | 0 | 144 | 113 | 0 | 17 | 0 | 115 | 0 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 34 | 12 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 34 | 40 | 96 | 0 | 50 | 38 | 52 | 30 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 219 | 0 | 11 | 100 | 220 | 0 | 0 | 105 | 120 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 217 | 0 | 0 | 0 | 0 | 0 |  | 8113 | 3673 | 11786 | 3651 | 717 | 1495 | 791 | 3724 | 700 | 46 | 0 | 518 | 144 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 340 | 105 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 219 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 100 | 105 | 46 | 0 | 16 | 0 | 0 | 0 | 310 | 305 | 206 | 45 | 0 | 29 | 35 | 0 | 51 | 0 | 33 | 52 | 22 | 10 | 25 | 18 | 142 | 187 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 141 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 23 | 11 | 40 | 300 | 153 | 100 | 161 | 100 | 149 | 0 | 90 | 180 | 145 | 240 | 99 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 350 | 89 | 0 | 144 | 113 | 0 | 26 | 0 | 115 | 0 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 91 | 10 | 0 | 0 | 0 | 0 | 34 | 40 | 96 | 0 | 50 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 214 | 0 | 11 | 40 | 213 | 0 | 0 | 105 | 40 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 217 | 0 | 0 | 0 | 0 | 0 |  | 7982 | 3513 | 11495 | 3665 | 717 | 1501 | 473 | 3743 | 700 | 46 | 0 | 508 | 142 | 0 | 0 | 89.39
21:00 | 0 | 0 | 0 | 0 | 340 | 105 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 219 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 34 | 100 | 98 | 50 | 0 | 27 | 0 | 0 | 0 | 310 | 305 | 204 | 8 | 0 | 29 | 40 | 0 | 51 | 0 | 33 | 52 | 22 | 10 | 25 | 21 | 140 | 188 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 135 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 11 | 40 | 300 | 54 | 70 | 162 | 50 | 149 | 0 | 90 | 180 | 145 | 240 | 99 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 350 | 90 | 0 | 144 | 113 | 0 | 17 | 0 | 115 | 5 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 91 | 10 | 0 | 0 | 0 | 0 | 34 | 40 | 96 | 0 | 50 | 40 | 52 | 30 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 10 | 0 | 0 | 185 | 0 | 11 | 0 | 200 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 221 | 0 | 0 | 0 | 0 | 0 |  | 7774 | 3435 | 11209 | 3619 | 717 | 1504 | 214 | 3738 | 730 | 46 | 10 | 491 | 140 | 0 | 0 | 89.38
22:00 | 0 | 0 | 0 | 0 | 340 | 105 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 93 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 24 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 100 | 98 | 50 | 0 | 35 | 0 | 0 | 0 | 320 | 310 | 214 | 8 | 0 | 29 | 40 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 25 | 21 | 132 | 188 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 133 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 0 | 300 | 0 | 0 | 162 | 0 | 149 | 0 | 90 | 184 | 150 | 240 | 99 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 0 | 100 | 350 | 90 | 0 | 144 | 113 | 0 | 17 | 0 | 115 | 55 |  | 718 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 10 | 0 | 0 | 0 | 0 | 34 | 0 | 96 | 0 | 24 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 0 | 189 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 221 | 0 | 0 | 0 | 0 | 0 |  | 7489 | 3216 | 10705 | 3633 | 718 | 1502 | 0 | 3744 | 700 | 46 | 0 | 230 | 132 | 0 | 0 | 89.38
23:00 | 0 | 0 | 0 | 0 | 340 | 105 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 40 | 216 | 0 | 0 | 0 | 93 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 28 | 28 | 33 | 24 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 30 | 94 | 50 | 0 | 38 | 0 | 0 | 0 | 320 | 320 | 212 | 8 | 0 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 22 | 10 | 25 | 21 | 130 | 186 | 0 | 20 | 0 | 30 | 42 | 51 | 0 | 110 | 134 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 0 | 300 | 0 | 0 | 162 | 0 | 149 | 0 | 90 | 100 | 150 | 240 | 99 | 90 | 68 | 0 | 300 | 54 | 110 | 105 | 0 | 100 | 350 | 88 | 0 | 144 | 113 | 0 | 17 | 0 | 115 | 55 |  | 717 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 190 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 221 | 0 | 0 | 0 | 0 | 0 |  | 7111 | 3050 | 10161 | 3622 | 717 | 1505 | 0 | 3374 | 640 | 46 | 0 | 127 | 130 | 0 | 0 | 89.37
24:00 | 0 | 0 | 0 | 0 | 340 | 105 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 28 | 28 | 33 | 24 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 97 | 50 | 0 | 39 | 0 | 0 | 0 | 310 | 305 | 213 | 8 | 0 | 29 | 40 | 0 | 51 | 0 | 0 | 50 | 22 | 10 | 25 | 21 | 124 | 188 | 0 | 20 | 0 | 30 | 42 | 51 | 0 | 110 | 134 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 0 | 300 | 0 | 0 | 162 | 0 | 149 | 0 | 90 | 0 | 150 | 240 | 99 | 90 | 34 | 0 | 300 | 54 | 110 | 70 | 0 | 100 | 330 | 90 | 0 | 144 | 69 | 0 | 17 | 0 | 115 | 55 |  | 718 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 189 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 360 | 224 | 0 | 0 | 0 | 0 | 0 |  | 6747 | 2949 | 9696 | 3583 | 718 | 1509 | 0 | 3066 | 560 | 46 | 0 | 90 | 124 | 0 | 0 | 89.37
KWH | 0 | 0 | 0 | 0 | 8200255 | 2425454 | 0 | 0 | 0 |  | 0 | 7088750 | 3466560 | 0 | 0 | 851202 | 3894111 | 0 | 754000 | 0 | 1592640 | 1843200 | 0 | 0 | 0 | 0 | 1093680 | 544439 | 1158248 | 406008 | 600000 | 654840 | 670600 | 820400 | 643200 | 0 | 1104480 | 0 | 0 | 0 | 275239 | 0 | 0 | 0 | 0 |  | 527520 | 0 | 175519 | 896880 | 2386560 | 725280 | 186384 | 446880 | 0 | 0 | 0 | 7558000 | 7150000 | 4888000 | 2024000 | 0 | 635832 | 319680 | 0 | 1167582 | 0 | 327664 | 1235246 | 481104 | 230400 | 563000 | 416210 | 2520000 | 4519680 | 0 | 442512 | 14850 | 716000 | 771264 | 1175400 | 0 | 2890472 | 3378000 | 1134144 | 2134080 | 0 | 0 | 0 | 0 | 219060 | 7191000 | 518352 | 184896 | 301056 | 5048289 | 666043 | 422871 | 3561600 | 321167 | 338270 | 149850 | 1729920 | 2348160 | 3464218 | 5774000 | 1875600 | 1689600 | 1506290 | 30480 | 7045527 | 1348920 | 2475626 | 2292540 | 0 | 1351680 | 7565000 | 2000640 | 348230 | 3470400 | 2220545 | 0 | 457920 | 215389 | 1685760 | 1082880 |  | 17405818 | 0 | 8691264 | 0 | 0 | 0 | 0 | 0 | 113760 | 13056 | 0 | 2180540 | 198891 | 0 | 0 | 0 | 0 | 362181 | 400140 | 952704 | 0 | 179439 | 345928 | 806774 | 316423 | 483120 | 0 | 166464 | 0 | 0 | 4835900 | 0 | 5000 | 0 | 0 | 4780909 | 0 | 278291 | 163200 | 4778818 | 0 | 0 | 2043840 | 190147 | 2592960 | 0 | 1883788 | 0 | 47504 | 1833120 | 9793700 | 5104745 | 0 | 0 | 36000 | 617040 | 0 |  | 161027228 | 71601464 | 232628692 | 83710987 | 17405818 | 36613965 | 2064484 | 68264440 | 14629600 | 1104480 | 5000 | 4850575 | 2520000 | 1459343 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 9102283.05 | 3201599.28 | 0 | 0 | 0 |  | 0 | 7726737.5 | 3847881.6 | 0 | 0 | 7201168.92 | 4049875.44 | 0 | 1304420 | 0 | 14524876.8 | 18137088 | 0 | 0 | 0 | 0 | 7983864 | 4208513.47 | 11420325.28 | 304506 | 450000 | 0 | 0 | 0 | 6219744 | 0 | 298209.6 | 0 | 0 | 0 | 2556970.31 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1702534.3 | 8565204 | 20763072 | 5744217.6 | 234843.84 | 1327233.6 | 0 | 0 | 0 | 5592920 | 7150000 | 4496960 | 2610960 | 0 | 718490.16 | 447552 | 0 | 1996565.22 | 0 | 3309406.4 | 11796599.3 | 611002.08 | 172800 | 985250 | 312157.5 | 18900000 | 4790860.8 | 0 | 561990.24 | 236709 | 1174240 | 1234022.4 | 2092212 | 0 | 3295138.08 | 3513120 | 2234263.68 | 4076092.8 | 0 | 0 | 0 | 0 | 446882.4 | 7262910 | 388764 | 140520.96 | 5120962.56 | 38165064.84 | 11309410.14 | 7070403.12 | 18520320 | 5369912.24 | 3328576.8 | 1751746.5 | 14098848 | 25477536 | 24422736.9 | 5369820 | 17105472 | 15966720 | 13119785.9 | 0 | 53264184.12 | 11749093.2 | 21760752.54 | 22879549.2 | 0 | 9002188.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100257511.68 | 0 | 9125827.2 | 0 | 0 | 0 | 0 | 0 | 1193342.4 | 136826.88 | 0 | 2464010.2 | 308281.05 | 0 | 0 | 0 | 0 | 3563861.04 | 4065422.4 | 8431430.4 | 0 | 2426015.28 | 3352042.32 | 7817640.06 | 3069303.1 | 927590.4 | 0 | 126013.248 | 0 | 0 | 26210578 | 0 | 142650 | 0 | 0 | 6310799.88 | 0 | 417436.5 | 2776032 | 5591217.06 | 0 | 0 | 21337689.6 | 3234400.47 | 24607190.4 | 0 | 14618194.88 | 0 | 524919.2 | 13546756.8 | 42994343 | 0 | 0 | 0 | 0 | 0 | 0 |  | 556276640.47 | 309577325.448 | 865853965.918 | 78510977.738 | 100257511.68 | 39985072.43 | 34881120.53 | 474198871 | 69204921 | 298209.6 | 142650 | 46961257.24 | 18900000 | 2513374.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 340 | 103 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 29 | 55 | 19 | 25 | 29 | 25 | 33 | 42 | 0 | 46 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 99 | 27 | 16 | 2 | 0 | 0 | 0 | 335 | 330 | 198 | 78 | 0 | 29 | 5 | 0 | 43 | 0 | 32 | 43 | 18 | 11 | 25 | 21 | 126 | 173 | 0 | 20 | 2 | 30 | 42 | 48 | 0 | 110 | 142 | 30 | 89 | 0 | 0 | 0 | 0 | 8 | 300 | 21 | 5 | 0 | 290 | 108 | 45 | 154 | 25 | 133 | 20 | 76 | 152 | 142 | 240 | 108 | 90 | 91 | 5 | 300 | 54 | 110 | 114 | 0 | 90 | 350 | 86 | 51 | 144 | 113 | 0 | 17 | 31 | 70 | 37 |  | 720 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 8 | 0 | 0 | 0 | 0 | 34 | 29 | 48 | 0 | 0 | 24 | 52 | 30 | 20 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 202 | 0 | 11 | 0 | 208 | 0 | 0 | 94 | 0 | 95 | 0 | 104 | 0 | 7 | 95 | 300 | 215 | 0 | 0 | 5 | 91 | 0 |  | 10327 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 340 | 104 | 0 | 0 | 0 | 0 | 0 | 300 | 150 | 0 | 0 | 55 | 158 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 105 | 45 | 0 | 8 | 0 | 0 | 0 | 315 | 305 | 213 | 78 | 0 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 10 | 25 | 8 | 148 | 187 | 0 | 20 | 0 | 30 | 41 | 50 | 0 | 110 | 140 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 310 | 23 | 11 | 200 | 300 | 304 | 100 | 160 | 99 | 149 | 0 | 90 | 160 | 138 | 240 | 108 | 90 | 105 | 0 | 300 | 54 | 102 | 114 | 0 | 100 | 350 | 76 | 0 | 144 | 113 | 0 | 34 | 0 | 115 | 0 |  | 717 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 39 | 8 | 0 | 90 | 9 | 0 | 0 | 0 | 0 | 34 | 40 | 96 | 0 | 50 | 32 | 52 | 30 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 214 | 0 | 11 | 70 | 203 | 0 | 0 | 105 | 120 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 217 | 0 | 0 | 0 | 0 | 0 |  | 11802 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 340 | 108 | 0 | 0 | 0 | 0 | 0 | 300 | 305 | 0 | 0 | 55 | 225 | 0 | 0 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 108 | 45 | 19 | 10 | 0 | 0 | 0 | 335 | 335 | 225 | 45 | 0 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 11 | 25 | 21 | 163 | 200 | 0 | 20 | 0 | 30 | 42 | 50 | 0 | 110 | 150 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 330 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 90 | 200 | 145 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 8 | 100 | 400 | 93 | 0 | 162 | 113 | 0 | 17 |  | 115 | 55 |  | 730 | 0 | 410 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 92 | 10 | 110 | 0 | 0 | 0 | 34 | 41 | 100 | 0 | 50 | 40 | 52 | 30 | 22 | 0 | 7 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 225 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 340 | 108 | 0 | 0 | 0 | 0 | 0 | 300 | 305 | 0 | 0 | 55 | 225 | 0 | 0 | 0 | 93 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 30 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 100 | 42 | 19 | 10 | 0 | 0 | 0 | 325 | 330 | 210 | 45 | 0 | 29 | 5 | 0 | 51 | 0 | 33 | 52 | 22 | 11 | 25 | 20 | 138 | 200 | 0 | 20 | 1.6 | 30 | 42 | 50 | 0 | 110 | 150 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 330 | 21 | 11 | 100 | 300 | 200 | 100 | 190 | 100 | 149 | 20 | 90 | 200 | 140 | 370 | 115 | 90 | 105 | 5 | 300 | 54 | 110 | 114 | 0 | 100 | 400 | 90 | 50 | 162 | 113 | 0 | 17 | 30 | 115 | 55 |  | 730 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 110 | 0 | 0 | 0 | 34 | 40 | 100 | 0 | 50 | 0 | 52 | 25 | 22 | 0 | 6 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 100 | 200 | 0 | 0 | 105 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 620 | 225 |  | 50 | 6 | 50 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 340 | 105 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 28 | 30 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 97 | 32 | 0 | 10 | 0 | 0 | 0 | 325 | 280 | 202 | 45 | 0 | 29 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 108 | 191 | 0 | 20 | 1 | 30 | 42 | 51 | 0 | 110 | 134 | 40 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 21 | 8 | 0 | 186 | 0 | 0 | 174 | 0 | 149 | 7 | 90 | 34 | 135 | 364 | 95 | 82 | 105 | 1 | 300 | 54 | 110 | 34 | 0 | 60 | 0 | 91 | 15 | 144 | 113 | 0 | 17 | 11 | 34 | 55 | 0 | 717 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 203 | 0 | 0 | 100 | 0 | 113 | 0 | 106 | 0 | 1 | 113 | 290 | 183 | 0 | 0 | 1 | 30 | 0 | 0
199
| Minimum Generation |  | 7763 | 5:00
| Highest Generation |  | 11802 | 19:00
| Day Peak Generation |  | 10327 | 12:00
| Evening Peak Generation |  | 11802 | 19:00
| HVDC Max Flow |  | 721 | 1:00
| HVDC EvPeak Flow |  | 717 | 19:00
| Load factor L.F |  | 82.13%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-09
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10327 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 8037 | MW
Evening Peak Generation : |  | 11802 | MW Hour : | 19:00 | Available Max Generation : |  | 13480 | MW
E.P. Demand (at gen end) : |  | 11802 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11802 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1480 | MW
Total Gen. (MKWH) : |  | 232.6287 | System Load Factor : | 82.13% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -192 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-09
Actual : | 89.34 | Ft.(MSL) , | Rule curve : | 91.88 | Ft.( MSL )
Gas Consumed : | Total = | 897.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 118496050.168
: |  | Coal : | 69204921 | Oil : | 556183898.77 | Total : | 743884869.938
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4293.08 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1462.3871 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1310.6962 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1184.4829 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1070.3128 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 863.7108 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 479.7246 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 222.2971 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 666.1521 |  |  | 0 | 0%
Total | 0 |  | 11552.8435 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Raozan unit- 1,2
6) Sirajganj Unit 1,4
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Chowmuhoni 132/33 kV T-1 transformer was under shut down from 09:06 to 14:40 for C/M.
b) Aminbazar-Kaliakoir 230 kV Ckt-1 was under shut down from 08:47 to 17:08 for C/M.
c) Shahjibazar-Ashuganj 132 kV Ckt-3 was under shut down from 08:56 to 17:27 for C/M.
d) Savar 33 kV B-bus was under shut down from 08:45 to 16:41 due to CB replacement of 33 kV PBS feeder
e) Tongi-Tongi 80 MW P/S 132 kV Ckt was under shut down from 09:14 to 17:52 for D/W.
f) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 09:48 to 13:03 for C/M.
g) Mirsarai EPZ-BSRM 230 kV Ckt-2 was under shut down from 10:22 to 14:37 for C/M.
h) Meghnaghat 230 kV CB 805B was under shut down from 10:31 to 12:09 for D/W.
i) Hasnabad 230 kV dia-1,mid CB 805 was under shut down from 10:31 to 17:02 for C/M.
j) Nawabganj 132/33 kV T-1 transformer was under shut down from 11:02 to 12:06 for C/M.
k) Hathazari-Rampur 230 kV bay-1 was under shut down from 10:52 to 11:40 for D/W.
l) Hathazari-Rampur 230 kV bay-2 was under shut down from 11:42 to 12:15 for D/W.
m) Hasnabad-APR 230 kV Ckt was under shut down from 13:05 to 18:08 for C/M.
n) Feni-Chowmuhoni 132 kV Ckt-2 was under shut down from 13:47 to 17:33 for C/M.
o) Mirsarai EPZ-BSRM 230 kV Ckt-2 was under shut down from 15:06 to 16:54 for D/W.
p) TK chemical 132/33 kV T-1 transformer was under shut down from 16:08 to 18:04 for oil leakage maint.
q) Bhulta 230 kV CB 155 was under shut down from 15:52 to 16:51 to attend trip Ckt supervision relay
r) Cumilla(N)-Daudkandi 132 kV Ckt-2 tripped at 16:45 showing dist C phase,Z1 & directional O/C relay at
Cumilla(N) end and was switched on at 16:59.
s) Chowmuhoni 132/33 kV T-2 transformer was under shut down from 15:02 to 18:58 for tan delta test.
t) Summit Meghan 400 MW CCPP GT-2 was synchronized at 00:55(09-03-2022).
u) Bibiyana(S) CCPP was shut down at 04:12(09-03-2022) due to DP high.
v) Faridpur 132/33 kV T-1 transformer & 33 kV bus section 1 & 2 were under shut down since | [5 empty] | About 40 MW power interruption occurred under
at 07:07(09-03-2022) for C/M by WZPDCL. | [5 empty] | Faridpur S/S area since 07:07.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 8200255
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 2425454
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7088750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3466560 | GT-2 under maint.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 851202
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Engine problem & Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 406008
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 754000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 158 | 3894111 | Machine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1592640 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1093680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1843200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 544439
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1158248
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1254840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 670600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 820400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 643200 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5048289
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 304 | 666043
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 422871
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 99 | 321167
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 338270
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1689600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 76 | 2000640 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3470400 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 215389
| Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 0 | 1082880 | Engine problem
| Dhaka area Total |  |  |  | 5696 | 2967 | 51963136
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 275239
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 149850
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 725280 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1104480 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1506290
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 175519 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 896880
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1729920 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 186384
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 446880
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 105 | 2386560
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30480
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 7045527
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1348920
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 102 | 2475626
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1351680
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2220545
| Chattogram area Total |  |  |  | 2382 | 1244 | 24056060
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4888000 | #REF!
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7558000 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7150000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 635832 | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 319680 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 78 | 2024000 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1167582
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 3464218 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 327664 | Engine problem
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 160 | 2348160 | Engine problem
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 481104
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 230400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2520000 | Maintenance at Tripura end.
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 563000 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1235246
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 8 | 416210 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 301056 | low demand.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2292540
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 34 | 457920 | 33 kV feeder O/L
| Chandpur 115(Doreen) |  | IPP | 115 | 0 | 115 | 1685760 | Engine problem
| Cumilla Area Total |  |  |  | 2899 | 2055 | 40066372
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 187 | 4519680 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 442512
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14850
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 160 | 3561600 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 108 | 1875600 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 348230
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 527520
| Mymensingh Area Total |  |  |  | 622 | 497 | 11289992
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 771264 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2890472 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3378000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1175400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 184896
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1134144 | GT-8 under maint.
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2134080
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 23 | 518352
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7191000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 240 | 5774000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 219060
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 7565000 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1464 | 33651668
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 717 | 17405818
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 113760
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 8 | 13056 | low demand.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8691264
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 70 | 163200 | Low demand.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2043840
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 617040
| Khulna Area Total |  |  |  | 2229 | 1349 | 29047978
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 9 | 198891 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 2180540 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 278291 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 460 | 9793700 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 217 | 5104745
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 787 | 17556167
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 362181 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 400140 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 179439
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 345928 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 214 | 4780909 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 203 | 4778818 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 316423 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 483120 | Engine problem
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 166464 | Engine problem
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 806774
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 952704 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 120 | 190147 | low demand.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2592960
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1833120
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36000
| Rajshahi Area Total |  |  |  | 2129 | 1126 | 18225127
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4835900 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 5000
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1883788
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47504
| Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 0 | 0 | 0 | On test
| Rangpur Area Total |  |  |  | 605 | 313 | 6772192
| Total |  |  |  | 20985 | 11802 | 232628692
| Eastern Grid Total |  |  |  | 13976 | 8227 | 161027228
| Western Grid Total |  |  |  | 7009 | 3575 | 71601464
| National Grid Total |  |  |  | 20985 | 11802 | 232628692
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-08
(a) ENTIRE EASTERN GRID : |  | 7803 | MW | (b) ENTIRE WESTERN GRID : |  | 3551 | MW
i) Dhaka area |  | 4173 | MW | i) Khulna area |  | 1313 | MW
ii) Chittagong area |  | 1290 | MW | ii) Rajshahi area |  | 1181 | MW
iii) Comilla area |  | 928 | MW | iii) Barisal area |  | 286 | MW
iv) Mymensingh area |  | 995 | MW | iv) Rangpur area |  | 771 | MW
v) Sylhet area |  | 417 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11354 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 18:00 | Valuka | 118 | 18:00 | Central S/S | 76 | 19:00
Munsiganj | 74 | 20:00 | Tangail | 188 | 20:00 | Noapara | 47 | 15:00
Sonargaon | 82 | 18:30 | Mymensing | 202 | 19:00 | Jessore | 104 | 19:00
Bhulta | 213 | 12:00 | Kishoreganj | 126 | 20:00 | Benapol | 48 | 18:30
Madanganj | 25 | 23:00 | Netrokona | 144 | 12:00 | Jhenida(Old) | 98 | 19:00
Rahim steel | 25 | 12:00 | Jamalpur | 133 | 19:00 | Bottail | 108 | 18:30
Ghorasal | 72 | 15:00 | Sherpur | 132 | 18:30 | G.K Project | 45 | 19:00
Narsingdi | 210 | 0:00 | Srimongal | 49 | 18:30 | Faridpur | 103 | 19:00
Haripur(SBU) | 102 | 0:00 | Shahjibazar | 88 | 18:30 | Rajbari | 52 | 19:00
Sreenagar | 32 | 20:00 | Fenchuganj | 35 | 18:00 | Madaripur | 74 | 19:00
Shyampur | 176 | 11:00 | Kulawara | 32 | 18:30 | Sariatpur | 46 | 19:00
Shitalakhya | 107 | 11:00 | Sylhet | 124 | 19:00 | Gopalganj | 80 | 19:00
Matuail | 60 | 12:00 | Chatak | 17 | 19:30 | Bagerhat | 83 | 19:30
Char Saidpur | 44 | 20:00 | Sunamganj | 38 | 19:00 | Mongla | 44 | 20:00
Ullon | 31 | 22:00 | Biani Bazar | 49 | 19:00 | Satkhira | 93 | 19:00
Hasnabad | 71 | 19:30 | Comilla (S) | 156 | 18:30 | Gallamari | 40 | 18:30
Magbazar | 96 | 15:00 | Comilla(N) | 109 | 19:00 | Magura | 46 | 19:00
Maniknagar | 64 | 11:00 | Chandpur | 56 | 23:00 | Norail | 35 | 19:00
Bangabhaban | 8 | 10:00 | Feni | 102 | 18:30 | Chuadanga | 78 | 19:00
Motijheel | 29 | 12:00 | Chowmuhani | 158 | 19:30 | Barisal(N) | 44 | 19:00
Narinda | 48 | 13:00 | Ashuganj | 32 | 14:00 | Barisal (S) | 79 | 18:30
Kazla | 80 | 10:00 | Daudkandi | 103 | 19:00 | Patuakhali | 68 | 21:00
Dhanmondi | 152 | 13:00 | B.Baria | 136 | 19:30 | Bhandaria | 40 | 21:00
Lalbag | 84 | 13:00 | Ramganj | 62 | 18:30 | Borguna | 12 | 18:30
Madartek | 64 | 19:30 | Chaddagram | 32 | 18:30 | Borhan Uddin | 46 | 20:00
Dhaka University | 30 | 12:00 | PHP | 10 | 17:00 | Ishurdi | 52 | 18:30
Aftabnagar | 27 | 18:30 | Kochua | 48 | 18:30 | Ruppur Paromanobik | 3 | 10:00
Fatullah | 58 | 18:30 | Madunaghat | 39 | 18:00 | Natore | 113 | 19:00
Nawabganj | 37 | 21:00 | Hathazari | 81 | 19:30 | Bogra | 137 | 19:00
Keraniganj | 68 | 19:00 | Khulshi | 171 | 19:00 | Naogaon | 102 | 18:30
Banani | 54 | 15:00 | Halishahar | 81.5 | 14:00 | Rajshahi | 101 | 20:00
Mirpur | 109 | 19:00 | Baraulia | 134 | 12:00 | Rajshahi New | 33 | 19:00
Kalyanpur | 84 | 19:00 | Sikalbaha | 21 | 0:00 | C.Nawabganj | 54 | 18:30
Gulshan | 98 | 13:00 | Dohazari | 78 | 18:30 | Amnura | 49 | 19:30
Uttara | 60 | 18:30 | Cox'sbazar | 102 | 18:30 | Pabna | 84 | 19:00
Uttara New | 28 | 15:00 | Chandraghona | 22 | 18:30 | Shahjadpur | 89 | 18:30
Kamrangirchar | 59 | 18:30 | Kaptai | 4 | 19:00 | Serajganj | 98 | 19:30
Savar | 162 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 92 | 8:00
Bhasantec | 114 | 18:30 | Bakulia | 109 | 18:30 | Joypurhat | 54 | 8:00
Agargaon | 68 | 12:00 | Julda | 29 | 19:00 | Sherpur(Bogura) | 56 | 19:00
Satmosjid | 89 | 13:00 | TK chemical | 23 | 19:00 | Mohastangor | 58 | 19:00
Old Tongi | 121 | 15:00 | Modern Steel | 0 | 1:00 | Bhangura | 29 | 7:00
Kabirpur | 236 | 15:00 | Shahmirpur | 41 | 19:00 | Rangpur | 126 | 19:00
Manikgonj | 62 | 19:30 | Khagrachhari | 22 | 18:30 | Lalmonirhat | 42 | 8:00
Joydevpur | 173 | 18:00 | Matarbari | 34 | 18:30 | Saidpur | 95 | 9:00
New Tongi | 76 | 11:00 | Baroiar Hat | 39 | 18:30 | Purbasadipur | 103 | 19:30
Kodda | 251 | 18:30 | Rangamati | 10 | 18:00 | Thakurgaon | 72 | 19:00
Dhamrai | 106 | 17:00 | Agrabad | 68 | 18:30 | Palashbari | 106 | 19:00
Rajendrapur | 98 | 19:00 | Rampur | 5 | 14:00 | Barapukuria | 53 | 10:00
Bashundara | 121 | 18:00 | Abul Khair 230 | 154 | 23:00 | Panchagar | 48 | 19:30
Purbachal | 16 | 21:00 | BSRM | 160 | 1:00 | Joldhaka | 58 | 19:00
Tongi Millgate | 44 | 16:00 | GPH Ispat | 98 | 16:00 | Kurigram | 58 | 18:30
Bashundhara Cement |  |  | Goalpara | 21 | 13:00 | Mithapukur | 34 | 8:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 416 | 5:00 | 404 | 16:00 | Kaliakoir | 402 | 0.125 | 379 | 0.5
| Bheramara | 402 | 6:00 | 393 | 11:00 | Bhulta | 419 | 0.20833 | 394 | 0.5
| Ashuganj(N) | 426 | 6:00 | 404 | 12:00 | Gopalganj | 412 | 0.625 | 401 | 0.79167
| Payra | 419 | 6:00 | 411 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 235 | 13:00 | Hathazari | 241 | 1:00 | 231 | 12:00
| Ishurdi | 246 | 3:00 | 227 | 13:00 | Megnaghat | 242 | 9:00 | 236 | 1:00
| Ashuganj | 252 | 6:00 | 240 | 12:00 | Fenchuganj | 245 | 6:00 | 238 | 13:00
| Serajganj | 242 | 7:00 | 230 | 12:00 | Siddhirganj | 241 | 6:00 | 224 | 11:00
| Baghabari | 240 | 1:00 | 227 | 12:00 | Maniknagar | 240 | 6:00 | 224 | 12:00
| Barapukuria | 234 | 1:00 | 222 | 19:00 | Agargaon | 239 | 4:00 | 223 | 12:00
| Bogra | 237 | 24:00 | 223 | 13:00 | Barisal | 243 | 19:00 | 238 | 18:30
| Rajshahi | 238 | 3:00 | 224 | 13:00 | Bhola 225 MW | 246 | 6:00 | 241 | 19:30
| Khulna South | 245 | 5:00 | 221 | 13:00 | AKSML | 241 | 19:00 | 229 | 12:00
| Rampura | 238 | 4:00 | 223 | 12:00 | BSRM | 241 | 3:00 | 233 | 15:00
| Haripur | 237 | 3:00 | 223 | 12:00 | Bibiyana | 246 | 8:00 | 238 | 12:00
| Hasnabad | 236 | 7:00 | 224 | 12:00 | Bhulta | 241 | 6:00 | 226 | 14:00
| Shyampur | 239 | 6:00 | 224 | 12:00 | Ashuganj (S) | 248 | 6:00 | 235 | 12:00
| Aminbazar | 236 | 1:00 | 224 | 2:00 | Kaliakoir | 236 | 6:00 | 222 | 12:00
| Tongi | 235 | 4:00 | 222 | 15:00 | GPH | 241 | 20:00 | 228 | 12:00
| Comilla (N) | 241 | 6:00 | 229 | 12:00 | Jhenaidah | 242 | 5:00 | 220 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 13:00 | 127 | 12:00 | PHP | 138 | 2:00 | 131 | 12:00
| Munsiganj | 138 | 8:00 | 128 | 12:00 | Kachua | 139 | 14:00 | 131 | 12:00
| Sonargaon | 134 | 4:00 | 127 | 12:00 | Madanhat | 140 | 9:00 | 134 | 11:00
| Bhulta | 130 | 4:00 | 122 | 12:00 | Hathazari | 141 | 1:00 | 135 | 12:00
| Madanganj | 136 | 5:00 | 128 | 12:00 | Khulshi | 139 | 1:00 | 132 | 8:00
| Rahim steel | 136 | 3:00 | 126 | 12:00 | Halishahar | 139 | 1:00 | 132 | 12:00
| Ghorasal | 142 | 8:00 | 138 | 12:00 | Baraulia | 141 | 20:00 | 135 | 12:00
| Narsingdi | 133 | 1:00 | 126 | 16:00 | Sikalbaha | 142 | 10:00 | 137 | 5:00
| Haripur(SBU) | 136 | 3:00 | 126 | 12:00 | Dohazari | 137 | 9:00 | 130 | 11:00
| Sreenagar | 134 | 10:00 | 129 | 12:00 | Cox'sbazar | 130 | 9:00 | 122 | 18:30
| Shyampur | 136 | 6:00 | 127 | 12:00 | Chandraghona | 141 | 18:30 | 135 | 12:00
| Shitalakhya | 139 | 8:00 | 128 | 12:00 | Kaptai | 138 | 17:00 | 135 | 11:00
| Matuail | 139 | 13:00 | 127 | 12:00 | A. Khaer Stl. | 140 | 5:00 | 136 | 18:00
| Char Saidpur | 138 | 7:00 | 128 | 13:00 | Bakulia | 141 | 6:00 | 134 | 12:00
| Ullon | 134 | 6:00 | 124 | 12:00 | Julda | 139 | 6:00 | 136 | 9:00
| Hasnabad | 136 | 6:00 | 130 | 12:00 | TK Chemical | 140 | 1:00 | 134 | 12:00
| Magbazar | 135 | 5:00 | 125 | 12:00 | Modern Steel | 139 | 1:00 | 133 | 12:00
| Maniknagar | 140 | 6:00 | 131 | 12:00 | Shahmirpur | 140 | 7:00 | 135 | 18:00
| Bangabhaban | 140 | 6:00 | 131 | 12:00 | Khagrachhari | 141 | 21:00 | 133 | 12:00
| Motijheel | 140 | 6:00 | 131 | 12:00 | Matarbari | 131 | 3:00 | 124 | 18:30
| Narinda | 140 | 6:00 | 131 | 12:00 | Baroiar Hat | 139 | 4:00 | 135 | 13:00
| Kazla | 140 | 6:00 | 131 | 12:00 | Rangamati | 140 | 6:00 | 133 | 12:00
| Dhanmondi | 137 | 8:00 | 126 | 12:00 | Agrabad | 140 | 6:00 | 134 | 12:00
| Lalbag | 138 | 7:00 | 129 | 12:00 | Rampur | 139 | 18:30 | 134 | 12:00
| Madartek | 135 | 6:00 | 125 | 12:00 | Goalpara S/S | 140 | 3:00 | 127 | 13:00
| Dhaka University | 134 | 4:00 | 124 | 12:00 | Khulna Central S/S | 139 | 3:00 | 125 | 12:00
| Aftabnagar | 134 | 4:00 | 124 | 12:00 | Noapara | 138 | 1:00 | 125 | 12:00
| Fatullah | 135 | 8:00 | 127 | 12:00 | Jessore | 136 | 1:00 | 125 | 12:00
| Nawabganj | 140 | 6:00 | 129 | 15:00 | Benapol | 137 | 4:00 | 122 | 12:00
| Keraniganj | 139 | 6:00 | 129 | 12:00 | Jhenida(Old) | 139 | 4:00 | 124 | 13:00
| Banani | 136 | 6:00 | 124 | 12:00 | Bottail | 138 | 2:00 | 126 | 13:00
| Mirpur | 130 | 5:00 | 125 | 12:00 | G.K Project | 141 | 1:00 | 132 | 12:00
| Kalyanpur | 134 | 1:00 | 127 | 15:00 | Faridpur | 139 | 3:00 | 131 | 12:00
| Gulshan | 134 | 4:00 | 123 | 12:00 | Rajbari | 139 | 5:00 | 129 | 13:00
| Uttara | 139 | 7:00 | 131 | 12:00 | Madaripur | 141 | 4:00 | 136 | 18:30
| Uttara New | 138 | 1:00 | 131 | 12:00 | Shariyatpur S/S | 141 | 4:00 | 136 | 18:30
| Kamrangirchar | 138 | 6:00 | 129 | 12:00 | Gopalganj | 142 | 4:00 | 135 | 19:00
| Savar | 136 | 8:00 | 128 | 12:00 | Bagerhat | 137 | 3:00 | 125 | 12:00
| Bhasantec | 141 | 6:00 | 130 | 12:00 | Mongla | 136 | 3:00 | 127 | 20:00
| Agargaon | 142 | 6:00 | 131 | 12:00 | Satkhira | 138 | 1:00 | 125 | 12:00
| Satmosjid | 141 | 6:00 | 131 | 12:00 | Gallamari | 141 | 5:00 | 134 | 13:00
| Old Tongi | 140 | 1:00 | 132 | 10:00 | Magura | 138 | 1:00 | 126 | 12:00
| Kabirpur | 140 | 21:00 | 127 | 12:00 | Narail | 138 | 6:00 | 125 | 12:00
| Manikgonj | 134 | 4:00 | 126 | 11:00 | Chuadanga | 135 | 3:00 | 117 | 13:00
| Joydevpur | 143 | 6:00 | 138 | 12:00 | Barisal(N) | 142 | 5:00 | 137 | 18:30
| New Tongi | 140 | 22:00 | 132 | 12:00 | Barisal (S) | 141 | 4:00 | 136 | 18:30
| Kodda | 140 | 20:00 | 131 | 12:00 | Patuakhali(S) | 138 | 1:00 | 134 | 20:00
| Dhamrai | 142 | 06:.00 | 128 | 16:00 | Bhandaria | 140 | 4:00 | 134 | 19:00
| Rajendrapur | 138 | 8:00 | 131 | 13:00 | Borguna | 141 | 5:00 | 136 | 18:30
| Bashundara | 139 | 4:00 | 131 | 12:00 | Jhenaidah(New) | 139 | 5:00 | 125 | 13:00
| Purbachal | 134 | 7:00 | 124 | 12:00 | Ishurdi | 140 | 24:00 | 127 | 13:00
| Tongi Millgate | 139 | 1:00 | 131 | 12:00 | Ruppur Paromanobik | 137 | 18:00 | 126 | 13:00
| Bashundhara Cement |  |  |  |  | Natore | 138 | 22:00 | 127 | 13:00
| Valuka | 130 | 1:00 | 108 | 19:00 | Bogra | 139 | 2:00 | 129 | 13:00
| Tangail | 135 | 1:00 | 122 | 18:30 | Noagaon | 134 | 0:00 | 124 | 13:00
| Mymensing | 132 | 1:00 | 114 | 18:30 | Rajshahi | 136 | 6:00 | 127 | 13:00
| Kishorganj | 133 | 1:00 | 120 | 18:30 | Rajshahi New | 136 | 20:00 | 128 | 13:00
| Netrokona | 131 | 1:00 | 108 | 18:30 | C.Nawabganj | 135 | 21:00 | 123 | 12:00
| Jamalpur | 136 | 1:00 | 121 | 18:30 | Amnura | 136 | 24:00 | 124 | 12:00
| Sherpur | 136 | 1:00 | 118 | 18:30 | Pabna | 139 | 24:00 | 125 | 14:00
| Srimongal | 141 | 7:00 | 135 | 17:00 | Shahjadpur | 144 | 1:00 | 138 | 8:00
| Shahjibazar | 139 | 5:00 | 133 | 15:00 | Serajganj | 139 | 24:00 | 128 | 13:00
| Fenchuganj | 141 | 6:00 | 133 | 18:30 | Niyamatpur | 133 | 24:00 | 121 | 8:00
| Khulawara | 141 | 2:00 | 133 | 18:30 | Joypurhat | 136 | 24:00 | 124 | 7:00
| Sylhet | 138 | 4:00 | 129 | 18:30 | Sherpur(Bogura) | 140 | 24:00 | 129 | 13:00
| Chatak | 137 | 5:00 | 129 | 14:00 | Mohastangor | 138 | 24:00 | 127 | 18:30
| Sunamganj | 136 | 3:00 | 125 | 18:30 | Bhangura | 140 | 1:00 | 130 | 12:00
| Biani Bazar | 137 | 5:00 | 127 | 18:30 | Rangpur | 132 | 24:00 | 118 | 19:00
| Comilla(s) | 133 | 0:00 | 127 | 10:00 | Lalmonirhat | 133 | 4:00 | 118 | 19:00
| Comilla(n) | 142 | 6:00 | 133 | 12:00 | Saidpur | 131 | 1:00 | 117 | 19:00
| Chandpur | 140 | 17:00 | 126 | 5:00 | Purbasadipur | 132 | 1:00 | 112 | 19:00
| Feni | 141 | 7:00 | 134 | 3:00 | Thakurgaon | 131 | 4:00 | 111 | 18:30
| Chowmuhani | 136 | 16:00 | 130 | 5:00 | Palashbari | 135 | 24:00 | 121 | 19:00
| Ashuganj | 142 | 5:00 | 136 | 18:00 | Barapukuria | 134 | 1:00 | 122 | 19:00
| Daudkandi | 138 | 6:00 | 129 | 12:00 | Panchagar | 133 | 4:00 | 109 | 19:00
| B.Baria | 137 | 4:00 | 130 | 18:00 | Joldhaka | 133 | 3:00 | 113 | 18:30
| Ramganj | 138 | 2:00 | 126 | 12:00 | Kurigram | 131 | 1:00 | 116 | 19:00
| Chaddagram | 141 | 7:00 | 134 | 12:00 | Mithapukur | 134 | 6:00 | 123 | 19:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 206 | 6747 | 2949 | 9696 |  |  |  | QF-LDC-11
0:30 | 132 | 6448 | 2768.5 | 9216.5 | Date: | 2022-03-08
1:00 | 58 | 6149 | 2588 | 8737
1:30 | 96 | 6036 | 2534 | 8570
2:00 | 134 | 5923 | 2480 | 8403
2:30 | 171 | 5746.5 | 2466 | 8212.5 | [5 empty] | Gen. at Eve. Peak | 11802 | 11802 MW (19:00 )
3:00 | 208 | 5570 | 2452 | 8022 | [6 empty] | 19:00
3:30 | 246 | 5477.5 | 2458.5 | 7936 | [5 empty] | Gen. at Day Peak | 10327 | 10327 MW (12:00 )
4:00 | 284 | 5385 | 2465 | 7850 | [6 empty] | 12:00
4:30 | 257 | 5366.5 | 2440 | 7806.5 | [5 empty] | Highest Generation | 11802
5:00 | 230 | 5348 | 2415 | 7763 | [6 empty] | 19:00
5:30 | 180 | 5419.5 | 2476 | 7895.5
6:00 | 130 | 5491 | 2537 | 8028
6:30 | 132 | 5676.5 | 2603.5 | 8280
7:00 | 134 | 5862 | 2670 | 8532
7:30 | 163 | 6064.5 | 2733 | 8797.5
8:00 | 192 | 6267 | 2796 | 9063
8:30 | 145 | 6465 | 2774 | 9239
9:00 | 98 | 6663 | 2752 | 9415
9:30 | 53 | 6755 | 2756 | 9511
10:00 | 8 | 6847 | 2760 | 9607
10:30 | 39 | 6964 | 2792 | 9756
11:00 | 70 | 7081 | 2824 | 9905
11:30 | 102 | 7198.5 | 2917.5 | 10116
12:00 | 134 | 7316 | 3011 | 10327
12:30 | 103 | 7302 | 3049 | 10351
13:00 | 72 | 7288 | 3087 | 10375
13:30 | 149 | 7221.5 | 3101.5 | 10323
14:00 | 226 | 7155 | 3116 | 10271
14:30 | 153 | 7248 | 3099.5 | 10347.5
15:00 | 80 | 7341 | 3083 | 10424
15:30 | 182 | 7288.5 | 3045 | 10333.5
16:00 | 284 | 7236 | 3007 | 10243
16:30 | 180 | 7177 | 2923.5 | 10100.5
17:00 | 76 | 7118 | 2840 | 9958
17:30 | 146 | 7236 | 2902.5 | 10138.5
18:00 | 216 | 7354 | 2965 | 10319
18:30 | 151 | 7790.5 | 3270 | 11060.5
19:00 | 86 | 8227 | 3575 | 11802
19:30 | 18 | 8113 | 3673 | 11786
20:00 | 100 | 7982 | 3513 | 11495 |  |  |  | Executive Engineer
20:30 | 72 | 7878 | 3474 | 11352 |  |  |  | Network Operation Division
21:00 | 44 | 7774 | 3435 | 11209
21:30 | 34 | 7631.5 | 3325.5 | 10957
22:00 | 24 | 7489 | 3216 | 10705 |  |  |  |  | Page 6 of 7
22:30 | 68 | 7300 | 3133 | 10433
23:00 | 112 | 7111 | 3050 | 10161
23:30 | 159 | 6929 | 2999.5 | 9928.5
24:00 | 206 | 6747 | 2949 | 9696
11802 MW (19:00 )
10327 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-08 |  | Energy |  | 232628692
[13 empty] | 2022-03-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3583 | 718 | 1509 | 0 | 3066 | 560 | 46 | 0 | 90 | 124 | 0 | 0
0:30 | 3528.5 | 719.5 | 1535.5 | 0 | 2665.5 | 564.5 | 46 | 0 | 45 | 112 | 0 | 0 | Date: | 2022-03-08
1:00 | 3474 | 721 | 1562 | 0 | 2265 | 569 | 46 | 0 | 0 | 100 | 0 | 0
1:30 | 3462 | 721 | 1563 | 0 | 2121 | 559 | 46 | 0 | 0 | 98 | 0 | 0 | [8 empty] | Total Energy | 232.6287 | Total Energy Gen 232.629 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.629 MKWHr
2:00 | 3450 | 721 | 1564 | 0 | 1977 | 549 | 46 | 0 | 0 | 96 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3443.5 | 721 | 1565.5 | 0 | 1807 | 534.5 | 46 | 0 | 0 | 95 | 0 | 0 | [8 empty] | Energy Requirement | 232.6287
3:00 | 3437 | 721 | 1567 | 0 | 1637 | 520 | 46 | 0 | 0 | 94 | 0 | 0
3:30 | 3400.5 | 720.5 | 1574 | 0 | 1582 | 520 | 46 | 0 | 0 | 93 | 0 | 0 | [6 empty] | Shortage
4:00 | 3364 | 720 | 1581 | 0 | 1527 | 520 | 46 | 0 | 0 | 92 | 0 | 0
4:30 | 3347.5 | 720.5 | 1554 | 0 | 1527 | 519.5 | 46 | 0 | 0 | 92 | 0 | 0
5:00 | 3331 | 721 | 1527 | 0 | 1527 | 519 | 46 | 0 | 0 | 92 | 0 | 0
5:30 | 3350.5 | 721 | 1556 | 0 | 1612 | 519 | 46 | 0 | 0 | 91 | 0 | 0
6:00 | 3370 | 721 | 1585 | 0 | 1697 | 519 | 46 | 0 | 0 | 90 | 0 | 0
6:30 | 3399 | 720.5 | 1584 | 0 | 1914.5 | 519 | 46 | 0 | 0 | 89 | 8 | 0 |  |  |  |  | Coal
7:00 | 3428 | 720 | 1583 | 0 | 2132 | 519 | 46 | 0 | 0 | 88 | 16 | 0
7:30 | 3413.5 | 720 | 1564.5 | 0 | 2400 | 519 | 46 | 0 | 0 | 93 | 41.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3399 | 720 | 1546 | 0 | 2668 | 519 | 46 | 0 | 0 | 98 | 67 | 0
8:30 | 3402 | 720 | 1518.5 | 0 | 2801 | 504.5 | 46 | 0 | 49.5 | 101 | 96.5 | 0
9:00 | 3405 | 720 | 1491 | 0 | 2934 | 490 | 46 | 0 | 99 | 104 | 126 | 0
9:30 | 3390.5 | 720.5 | 1488 | 0 | 3002.5 | 485 | 46 | 0 | 123 | 107 | 148.5 | 0
10:00 | 3376 | 721 | 1485 | 0 | 3071 | 480 | 46 | 0 | 147 | 110 | 171 | 0
10:30 | 3407 | 721 | 1495 | 0 | 3117.5 | 480 | 46 | 0 | 191 | 113 | 185.5 | 0
11:00 | 3438 | 721 | 1505 | 0 | 3164 | 480 | 46 | 0 | 235 | 116 | 200 | 0
11:30 | 3387 | 720.5 | 1497.5 | 89 | 3268 | 490 | 46 | 0 | 291 | 121 | 206 | 0
12:00 | 3336 | 720 | 1490 | 178 | 3372 | 500 | 46 | 0 | 347 | 126 | 212 | 0
12:30 | 3315 | 720.5 | 1494.5 | 149 | 3418 | 524.5 | 46 | 0 | 349 | 126 | 208.5 | 0
13:00 | 3294 | 721 | 1499 | 120 | 3464 | 549 | 46 | 0 | 351 | 126 | 205 | 0
13:30 | 3294 | 721 | 1499 | 120 | 3464 | 549 | 46 | 0 | 351 | 126 | 205 | 0
14:00 | 3294 | 721 | 1499 | 120 | 3464 | 549 | 46 | 0 | 351 | 126 | 205 | 0
14:30 | 3343 | 720.5 | 1493.5 | 60 | 3520 | 559.5 | 46 | 0 | 354.5 | 131 | 171.5 | 0
15:00 | 3392 | 720 | 1488 | 0 | 3576 | 570 | 46 | 0 | 358 | 136 | 138 | 0
15:30 | 3380 | 720 | 1467 | 0 | 3548 | 570 | 46 | 0 | 356.5 | 133 | 113 | 0
16:00 | 3368 | 720 | 1446 | 0 | 3520 | 570 | 46 | 0 | 355 | 130 | 88 | 0
16:30 | 3319 | 719.5 | 1450 | 0 | 3442.5 | 569.5 | 46 | 0 | 341.5 | 128 | 60 | 0
17:00 | 3319 | 719 | 1454 | 0 | 3365 | 569 | 46 | 0 | 328 | 126 | 32 | 0
17:30 | 3380.5 | 719.5 | 1455.5 | 0 | 3414 | 574.5 | 46 | 0 | 398.5 | 134 | 16 | 0
18:00 | 3442 | 720 | 1457 | 0 | 3463 | 580 | 46 | 0 | 469 | 142 | 0 | 0
18:30 | 3517.5 | 718.5 | 1490 | 446.5 | 3586 | 620 | 46 | 0 | 491 | 145 | 0 | 0
19:00 | 3593 | 717 | 1523 | 893 | 3709 | 660 | 46 | 0 | 513 | 148 | 0 | 0
19:30 | 3651 | 717 | 1495 | 791 | 3724 | 700 | 46 | 0 | 518 | 144 | 0 | 0
20:00 | 3665 | 717 | 1501 | 473 | 3743 | 700 | 46 | 0 | 508 | 142 | 0 | 0
20:30 | 3642 | 717 | 1502.5 | 343.5 | 3740.5 | 715 | 46 | 5 | 499.5 | 141 | 0 | 0
21:00 | 3619 | 717 | 1504 | 214 | 3738 | 730 | 46 | 10 | 491 | 140 | 0 | 0
21:30 | 3626 | 717.5 | 1503 | 107 | 3741 | 715 | 46 | 5 | 360.5 | 136 | 0 | 0
22:00 | 3633 | 718 | 1502 | 0 | 3744 | 700 | 46 | 0 | 230 | 132 | 0 | 0
22:30 | 3627.5 | 717.5 | 1503.5 | 0 | 3559 | 670 | 46 | 0 | 178.5 | 131 | 0 | 0
23:00 | 3622 | 717 | 1505 | 0 | 3374 | 640 | 46 | 0 | 127 | 130 | 0 | 0
23:30 | 3602.5 | 717.5 | 1507 | 0 | 3220 | 600 | 46 | 0 | 108.5 | 127 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.1° C
24:00 | 3583 | 718 | 1509 | 0 | 3066 | 560 | 46 | 0 | 90 | 124 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 232.629 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.629 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1104480
2 | Karnaphuli Hydro PP Unit-4 & 5 |  |  |  |  | 0
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 7 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  |  | 275239
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 8 | 14 | 18 | 20 | 20 | 20 | 18 | 15 | 10 | 4 | [9 empty] | 149850
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 34 |  |  |  | 175519
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 58 | 91 | 91 | 90 | 90 | 91 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 68 | 34 | 1506290
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 200 | 120 | 40 | 40 |  |  |  | 301056
14 | Titas 50 MW Peaking PP | [10 empty] | 18 | 32 | 31 | 31 | 26 | 24 | 32 | 33 |  | 33 | 33 | 33 | 33 |  |  |  | 327664
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 37 | 37 | 37 | 37 | 92 | 94 | 92 | 57 | 59 | 95 | [15 empty] | 754000
17 | Siddhirganj 335 MW CCPP | 160 | 160 | 156 | 160 | 160 | 165 | 173 | 171 | 162 | 164 | 166 |  | 7 | 37 | 158 | 160 | 157 | 158 |  | 158 | 190 | 219 | 219 | 220 | 216 | 223 | 3894111
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 15 | 15 | 15 | 15 | 17 | 74 | 163 | 250 | 270 | 280 | 290 | 286 | 277 | 287 | 300 | 298 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5048289
19 | Ashuganj 195MW PP (APSCL-United) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 88 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 45 | 45 | 8 | 8 | 8 | 8 | 2024000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8200255
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 29 | 23 | 23 | 23 | 29 | 29 | 29 | 29 | 29 | 26 | 26 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 635832
33 | Ashuganj 225 MW CCPP | 210 | 211 | 208 | 203 | 210 | 209 | 190 | 191 | 200 | 218 | 186 | 198 | 186 | 189 | 188 | 181 | 181 | 202 |  | 213 | 213 | 206 | 204 | 214 | 212 | 213 | 4888000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 305 | 270 | 270 | 285 | 345 | 330 | 310 | 285 | 290 | 280 | 280 | 335 |  | 305 | 305 | 305 | 305 | 310 | 320 | 305 | 7150000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 285 | 285 | 285 | 285 | 320 | 285 | 285 | 300 | 285 | 335 | 310 | 295 | 290 | 280 | 285 | 340 |  | 315 | 310 | 310 | 310 | 320 | 320 | 310 | 7558000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 25 | 35 | 40 | 40 | 40 | 40 | 319680
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7088750
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 210 | 210 | 212 | 213 | 214 | 216 | 215 | 214 | 203 | 188 | 175 | 173 | 158 | 158 | 169 | 187 | 188 | 187 |  | 187 | 186 | 187 | 188 | 188 | 186 | 188 | 4519680
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 5 | 17 | 30 | 41 | 49 | 51 | 50 | 43 | 33 | 21 | 7 | 0 | [8 empty] | 348230
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 42 | 42 | 42 |  | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 771264
46 | Shajibazar 330 MW CCPP | 148 | 147 | 146 | 140 | 142 | 142 | 142 | 141 | 141 | 143 | 140 | 142 | 141 | 141 | 140 | 140 | 141 | 138 |  | 140 | 141 | 141 | 135 | 133 | 134 | 134 | 3378000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1134144
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 89 | 89 | 86 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 86 | 86 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2134080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 219060
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 184896
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 51 | 48 | 48 | 47 | 45 | 45 | 48 | 45 | 48 | 48 | 48 | 48 | 48 |  | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 1175400
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 518352
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 280 | 290 | 280 | 295 | 295 | 290 | 280 | 290 | 310 | 300 | 305 | 300 | 300 | 300 | 295 | 295 |  | 310 | 290 | 280 | 300 | 290 | 290 | 290 | 7191000
| Bibiyana South 400 MW | 350 | 330 | 307 | 238 | 203 | 180 | 175 | 230 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 330 | 7565000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | 17 | 17 | 17 | 32 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1158248
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 527520
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | [13 empty] | 186384
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 406008
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 442512
63 | Impoprt (Tripura) | 100 | 96 | 94 | 92 | 92 | 90 | 88 | 98 | 104 | 110 | 116 | 126 | 126 | 130 | 136 | 130 | 126 | 142 |  | 148 | 144 | 142 | 140 | 132 | 130 | 124 | 2520000
64 | Malancha, Ctg. EPZ (United) | 31 | 32 | 40 | 40 | 41 | 42 | 40 | 10 | 3 | 2 | 2 | 2 | 4 | 4 | 2 | 2 | 5 | 4 |  | 8 | 12 | 16 | 27 | 35 | 38 | 39 | 446880
65 | Feni 22MW PP (Doreen) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 20 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 481104
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 230400
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 16 | 25 | 25 | 25 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 563000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 8 | 8 | 8 | 8 | 8 |  | 8 | 15 | 18 | 21 | 21 | 21 | 21 | 416210
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 28 | 28 | 20 | 28 | 28 | 9 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 654840
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 670600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820400
73 | Ghorashal 108MW PP (Regent) | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 100 | 103 | 100 | 96 | 102 | 104 |  | 104 | 105 | 105 | 105 | 105 | 105 | 105 | 2425454
| Feni Lanka Power | 75 | 70 | 70 | 52 | 52 | 52 | 70 | 70 | 70 | 73 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 105 | 70 | 2292540
Chowmuhani 113 MW
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 108 | 108 | 108 | 128 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3470400
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 36 | 51 | 51 | 42 | 50 | 50 | 50 | 50 | 24 | 24 |  | 50 | 51 | 51 | 51 | 24 | 24 | 24 | 643200
79 | Kodda 150MW PP | [8 empty] | 82 | 82 | 115 | 150 | 150 | 150 | 150 | 150 | 115 | 140 |  | 150 | 150 | 150 | 150 | 100 | 32 | 0 | 1843200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 52 | 52 | 52 | 45 | 43 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 43 | 50 | 1235246
| Gazipur 100 MW PP | 90 | 17 |  |  |  | 6 | 24 | 50 | 74 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1689600
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 30480
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1348920
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 68 | 68 | 68 | 68 | 68 | 95 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 102 | 110 | 110 | 110 | 110 | 110 | 110 | 2475626
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3466560
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 91 | 80 | 53 | 53 | 53 | 62 | 90 | 90 | 90 | 89 | 80 | 86 | 90 | 91 | 91 | 88 | 90 | 89 |  | 76 | 90 | 89 | 90 | 90 | 88 | 90 | 2000640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 50 | 100 | 100 | 90 | 60 | 30 | 30 |  | 100 | 100 | 100 | 100 | 100 | 30 |  | 896880
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1167582
94 | Gagnagar 102 MW PP (Digital Power) | [5 empty] | 16 | 48 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 72 | 1592640
95 | Patenga 50MW PP (Baraka) | [5 empty] | 1 | 18 | 31 | 31 | 31 | 31 | 27 | 35 | 40 | 44 | 44 | 44 | 46 |  | 45 | 44 | 46 | 50 | 50 | 50 | 50 | 725280
96 | Chattogram 108 MW PP (ECPV) | 96 | 93 | 105 | 104 | 104 | 104 | 104 | 96 | 93 | 98 | 91 | 99 | 103 | 103 | 103 | 95 | 93 | 95 |  | 105 | 105 | 105 | 98 | 98 | 94 | 97 | 2386560
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 12 | 31 | 55 | 55 | 40 | 40 | 40 | 55 | 55 | 40 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 40 | 0 | 851202
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 35 |  | 0 | 29 | 29 |  |  | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 |  |  | 544439
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2890472
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14850
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1093680
104 | Keranigonj 300 MW PP (APR) | [11 empty] | 108 | 20 | [6 empty] | 304 | 251 | 153 | 54 |  |  |  | 666043
105 | Bramhangoan 100 MW PP (Aggreko) | [11 empty] | 45 | 75 | [6 empty] | 100 | 100 | 100 | 70 |  |  |  | 422871
106 | Mymensingh 200 MW PP (United) | 183 | 140 | 100 | 100 | 100 | 122 | 136 | 148 | 158 | 157 | 155 | 154 | 154 | 152 | 152 | 141 | 159 | 150 |  | 160 | 153 | 161 | 162 | 162 | 162 | 162 | 3561600
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 25 | 25 | [6 empty] | 99 | 100 | 100 | 50 |  |  |  | 321167
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 124 | 115 | 115 | 120 | 136 | 132 | 136 | 132 | 135 | 133 | 133 | 134 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 338270
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 50 | 10 | 10 | 10 | 30 | 50 | 70 | 76 | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1729920
116 | Chandpur 200MW (Desh energy) | [7 empty] | 36 | 58 | 85 | 93 | 152 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 180 | 180 | 180 | 184 | 100 |  | 2348160
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 150 | 150 | 150 | 150 | 143 | 142 | 140 | 140 | 140 | 142 | 147 | 145 | 138 | 137 | 132 | 132 |  | 138 | 145 | 145 | 145 | 150 | 150 | 150 | 3464218
118 | Bibiyana-III 400 MW CCPP | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 241 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5774000
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 105 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 98 | 99 | 99 | 99 | 99 | 99 | 1875600
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7045527
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 43 | 55 | 90 | 90 | 90 | 90 | 90 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1351680
| Anlima Energy Ltd. | 113 | 113 | 17 | 17 | 17 | 17 | 40 | 69 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 69 | 2220545
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 16 |  | 34 | 17 | 26 | 17 | 17 | 17 | 17 | 457920
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 10 | 19 | 26 | 29 | 31 | 29 | 26 | 21 | 14 | 5 | 0 | [8 empty] | 215389
| Chandpur 115(Doreen) | 72 | 53 |  |  |  |  | 6 | 71 | 72 | 72 | 72 | 70 | 72 | 72 | 72 | 72 | 84 | 103 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1685760
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 41 | 38 | 38 | 37 | 37 | 37 | 55 | 55 | 55 | 55 | 55 | 55 |  |  |  |  | 5 | 55 | 55 | 55 | 1082880
120 | Eastern Zone Total | 6149 | 5923 | 5570 | 5385 | 5348 | 5491 | 5862 | 6267 | 6663 | 6847 | 7081 | 7316 | 7288 | 7155 | 7341 | 7236 | 7118 | 7354 |  | 8227 | 8113 | 7982 | 7774 | 7489 | 7111 | 6747 | 161027228
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 19 |  | 39 | 34 | 34 | 34 |  |  |  | 113760
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 35 | 35 | 35 | 35 | 35 | 70 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2043840
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 28 | 53 | 73 | 86 | 91 | 88 | 78 | 57 | 36 | 13 | [9 empty] | 617040
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 220 | 220 | 224 | 182 | 220 | 223 | 221 | 216 | 221 | 220 | 215 | 215 | 214 | 212 | 173 | 173 | 172 |  | 217 | 217 | 217 | 221 | 221 | 221 | 224 | 5104745
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 278291
| Bhola 225 MW CCPP | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 89 | 90 | 88 | 90 | 90 |  | 90 | 91 | 91 | 91 | 91 | 92 | 91 | 2180540
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 | 9 | 9 | 8 | 8 | 9 |  | 9 | 9 | 10 | 10 | 10 | 9 | 9 | 198891
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [9 empty] | 70 | 100 | 40 |  |  |  |  | 163200
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 3 |  | 8 | 12 | [5 empty] | 13056
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 721 | 721 | 721 | 720 | 721 | 721 | 720 | 720 | 720 | 721 | 721 | 720 | 721 | 721 | 720 | 720 | 719 | 720 |  | 717 | 717 | 717 | 717 | 718 | 717 | 718 | 17405818
147 | Bheramara 410 MW CCPP | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 300 | 280 | 300 | 320 | 340 | 360 | 360 | 360 | 320 | 320 |  | 410 | 410 | 410 | 410 | 410 | 405 | 405 | 8691264
148 | Payra 1320 MW | 370 | 350 | 320 | 320 | 320 | 320 | 320 | 320 | 290 | 280 | 280 | 300 | 350 | 350 | 370 | 370 | 370 | 380 |  | 460 | 500 | 500 | 530 | 500 | 440 | 360 | 9793700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 200 | 200 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 199 | 199 | 200 | 200 | 199 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4835900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [11 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 |  |  | 362181
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 36000
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 184 | 182 | 182 | 187 | 183 | 188 | 195 | 191 | 181 | 169 | 173 | 202 | 214 | 213 | 198 | 188 | 191 | 191 |  | 214 | 219 | 214 | 185 | 186 | 180 | 178 | 4780909
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 185 | 185 | 190 | 186 | 191 | 198 | 195 | 183 | 156 | 154 | 208 | 203 | 196 | 186 | 190 | 175 | 173 |  | 203 | 220 | 213 | 200 | 189 | 190 | 189 | 4778818
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [8 empty] | 5 | 5 | 5 | 29 | 33 | 39 | 39 | 39 | 39 | 40 |  | 40 | 40 | 40 | 40 |  |  |  | 400140
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 18 | 18 | 18 | 19 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 483120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 166464
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 16 |  | 50 | 50 | 50 | 50 | 24 |  |  | 179439
167 | Katakhali 50 MW Peaking PP | [8 empty] | 12 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 |  | 32 | 38 | 40 | 40 |  |  |  | 345928
168 | Santahar 50 MW Peaking PP | [10 empty] | 25 | 30 | 31 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 |  |  |  | 316423
169 | Natore 52 MW PP (Rajlanka) | [5 empty] | 5 | 16 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 24 | 26 |  | 52 | 52 | 52 | 52 | 52 | 16 | 0 | 806774
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 36 | 48 | 48 | 48 | 47 | 47 | 46 | 46 | 87 |  | 96 | 96 | 96 | 96 | 96 | 95 | 90 | 952704
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 120 | 120 | 40 |  |  |  |  | 190147
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 105 | 94 | 95 | 94 | 94 | 94 | 94 | 94 | 94 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2592960
172 | Confidence Power Bogura Unit-1 113 MW | [5 empty] | 35 | 80 | 95 | 95 | 95 | 95 | 95 | 95 | 113 | 113 | 113 | 50 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1833120
173 | Rangpur 20 MW GTPP | [21 empty] | 0 | 0
175 | Saidpur 20 MW GTPP | [22 empty] | 10 |  |  |  | 5000
176 | Rangpur 113 MW PP (Confidence) | 44 |  |  |  |  | 34 | 54 | 90 | 97 | 106 | 106 | 104 | 102 | 104 | 101 | 99 | 99 | 105 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1883788
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 5 | 7 | 7 | 7 | 5 | 2 | 2 | 0 | [8 empty] | 47504
178 | Energypac Power Venture Thakurgaon Ltd.
178