## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-15 | Tuesday
|  |  | Date (day): | 2022-03-15 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11915.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12391 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-14 | 2022-03-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 250 | 280 | 300 | 65 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 102 | 102 | 102
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 270 | 270 | 180 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 275 | 300 | 285 | 300 | 35 |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 90 | 90 | 90 | 245 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 54 | 54 | 54 |  | 26 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 298 | 298 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 304 | 307 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 100 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 100 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 96 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 92 | 92 | 92 | 92 |  | 12 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 150 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 0 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2862 | 3018 | 2975 | 3080 | 1198 | 1377
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 17 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 81 | 81 | 81 |  | 149 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 89 | 90 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 16 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 5 | 90 | 90
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 300 | 300 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 107 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1074 | 1203 | 1304 | 1289 | 180 | 885
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 214 | 217 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 315 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | maintenance work.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 182 | 80 | 180 | 15 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 150 | 143 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 41 | 41 | 41 |  | 11
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 85 | 90 | 90 |  | 73 | Engine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 7 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 132 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 38 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 120 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 107 | 115 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 36 | 36 | 36 |  | 18 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 115 | 115 | 96 | 99 | 100 | 100
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1904 | 2139 | 2008 | 2233 | 294 | 111
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 67 | 84 | 100 | 100
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 178 | 187 | 200 | 200 |  |  | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 98 | 108 | 108 | 108 |  | 7 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 6 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 434 | 405 | 501.6 | 450 | 0 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Under Maint. |  | 22-03-022
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 156 | 158 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 51 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 89 | 89 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 22 | 22
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 290 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 240 | 241 | 240 | 250 | 150 |  | Gas shortage
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 260 | 265 | 260 | 265 | 118 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1232 | 1259 | 1259 | 1274 | 852 | 200
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 710 | 711 | 734 | 734
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 0 | 35 |  | 19 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 158 | 158 | 158
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 275 | 280 | 290 | 120 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 10 | 99 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1328 | 1381 | 1427 | 1462 | 120 | 88
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 29 | 10 | 10 |  |  | Engine problem
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 91 | 90 | 92 | 102 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 21 | 11 | 20 | 75 |  | Gas shortage
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 310 | 500 | 500 | 500 |  |  | Line O/L
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 214 | 220 | 225 | 225
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 644 | 861 | 836 | 847 | 177 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 6 | 44 | 44 | 44 |  | 27 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 50 | 50 | 50
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 213 | 179 | 220 | 220
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 214 | 159 | 200 | 220
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 25 | 30 |  | 20 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 47 | 93 | 93 | 93 |  | 11 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 100 | 168 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 976 | 1105 | 1089 | 1248 | 380 | 494
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 78 | 80 | 80 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 14 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 112 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 419 | 528 | 516 | 508 | 74 | 210
|  | Total |  |  |  |  | 22296 | 21215 | 10873 | 11899 | 11915.6 | 12391 | 3275 | 3373
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10312.8564 | 11286 | 11301.7448 | 11752.6537
| A. |  | 2022-03-14 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 11899 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8350 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11899 | MW
| 3 | Day peak Generation : |  |  | 10873 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11286 | MW
| 4 | Evening peak Generation : |  |  | 11899 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 249.592 | MKWHr | By Solar | 1.4564 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 109.8223 | MKWHr |  | By Oil: | 101.6077 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.1966 | MKWHr |  | By Hydro: | 1.5054 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3275 | MW | Dhaka | 4258 | 4258 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3373 | MW | Chittagong | 1172 | 1172 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6648 | MW | Khulna | 1248 | 1248 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 855.95 | MMCFD |  |  | Rajshahi | 1176 | 1176 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 110055167.468 | ii) Oil : | Taka | 837404842.49 | Comilla | 1031 | 1031 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 72710281.43 | Total | Taka | 1020170291.388 | Mymensingh | 952 | 952 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.068 | MKWHr. | Sylhet | 450 | 450 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 244 | MW (E to W) at | 21:00 | hrs | Barisal | 296 | 296 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -44 | MW at | 7:00 | hrs | Rangpur | 703 | 703 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 11286 | 11286 |  | 0
| B. |  | 2022-03-15 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12391 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 291 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 253.8082 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8783 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2015 | MKWHr. | ii) HVDC Flow at Peak Time |  | 711 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8022 | MKWHr. | iii) Maximum HVDC Flow : |  | 719 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.86 |  | (b) Today: | 88.79 |  | (c) Rule Curve: |  | 90.76
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 245 | 270 | 0 | 0 | 30 | 90 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 96 | 50 | 0 | 37 | 0 | 0 | 0 | 320 | 0 | 218 | 73 | 92 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 112 | 104 | 0 | 20 | 0 | 0 | 30 | 48 | 0 | 0 | 227 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 11 | 0 | 298 | 0 | 0 | 178 | 0 | 140 | 0 | 90 | 18 | 141 | 364 | 108 | 105 | 97 | 0 | 300 | 54 | 110 | 52 | 116 | 100 | 0 | 92 | 0 | 144 | 113 | 0 | 36 | 0 | 34 | 55 |  | 711 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 219 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 300 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6397 | 2904 | 9301 | 3061 | 711 | 1551 | 0 | 3320 | 500 | 46 | 0 | 0 | 112 | 0 | 0 | 88.87
2:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 260 | 270 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 98 | 50 | 0 | 39 | 0 | 0 | 0 | 330 | 0 | 218 | 73 | 91 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 112 | 106 | 0 | 20 | 0 | 0 | 30 | 48 | 0 | 0 | 176 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 21 | 11 | 0 | 195 | 0 | 0 | 177 | 0 | 149 | 0 | 90 | 0 | 147 | 364 | 80 | 105 | 90 | 0 | 300 | 54 | 102 | 0 | 117 | 100 | 175 | 92 | 0 | 144 | 113 | 0 | 36 | 0 | 0 | 55 |  | 710 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 300 | 220 | 0 | 0 | 0 | 0 | 0 |  | 6184 | 2765 | 8949 | 3122 | 710 | 1558 | 0 | 2902 | 499 | 46 | 0 | 0 | 112 | 0 | 0 | 88.87
3:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 260 | 270 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 94 | 24 | 0 | 40 | 0 | 0 | 0 | 350 | 0 | 218 | 73 | 91 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 106 | 106 | 0 | 20 | 0 | 0 | 30 | 48 | 0 | 0 | 147 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 295 | 21 | 11 | 0 | 60 | 0 | 0 | 177 | 0 | 149 | 0 | 90 | 0 | 147 | 363 | 78 | 70 | 68 | 0 | 300 | 54 | 110 | 0 | 117 | 80 | 200 | 92 | 0 | 144 | 113 | 0 | 0 | 0 | 0 | 55 |  | 711 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 34 | 0 | 0 | 70 | 300 | 222 | 0 | 0 | 0 | 0 | 0 |  | 5903 | 2689 | 8592 | 3137 | 711 | 1565 | 0 | 2527 | 500 | 46 | 0 | 0 | 106 | 0 | 0 | 88.86
4:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 260 | 270 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 25 | 0 | 42 | 0 | 0 | 0 | 345 | 0 | 218 | 73 | 92 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 102 | 106 | 0 | 20 | 0 | 0 | 30 | 48 | 0 | 0 | 148 | 50 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 30 | 0 | 0 | 178 | 0 | 149 | 0 | 90 | 0 | 148 | 364 | 78 | 35 | 68 | 0 | 300 | 54 | 110 | 0 | 116 | 70 | 180 | 92 | 0 | 144 | 113 | 0 | 14 | 0 | 0 | 55 |  | 711 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 0 | 0 | 0 | 70 | 300 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5815 | 2594 | 8409 | 3049 | 711 | 1570 | 0 | 2431 | 500 | 46 | 0 | 0 | 102 | 0 | 0 | 88.86
5:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 260 | 270 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 91 | 25 | 0 | 42 | 0 | 0 | 0 | 325 | 0 | 218 | 73 | 90 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 31 | 20 | 98 | 106 | 0 | 20 | 0 | 0 | 30 | 48 | 0 | 0 | 160 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 30 | 0 | 0 | 187 | 0 | 149 | 0 | 90 | 0 | 145 | 363 | 78 | 35 | 68 | 0 | 300 | 54 | 110 | 0 | 117 | 70 | 150 | 92 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 710 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 94 | 0 | 0 | 0 | 0 | 80 | 300 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5768 | 2582 | 8350 | 2995 | 710 | 1569 | 0 | 2432 | 500 | 46 | 0 | 0 | 98 | 0 | 0 | 88.86
6:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 260 | 280 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 6 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 92 | 25 | 0 | 40 | 0 | 0 | 0 | 320 | 0 | 219 | 73 | 87 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 27 | 20 | 96 | 107 | 0 | 20 | 0 | 0 | 30 | 48 | 0 | 0 | 160 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 0 | 33 | 0 | 0 | 179 | 0 | 149 | 0 | 90 | 0 | 148 | 364 | 85 | 38 | 68 | 0 | 300 | 54 | 102 | 34 | 117 | 87 | 200 | 92 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 710 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 54 | 0 | 0 | 113 | 300 | 221 | 0 | 0 | 0 | 0 | 0 |  | 5828 | 2737 | 8565 | 2995 | 710 | 1575 | 0 | 2643 | 500 | 46 | 0 | 0 | 96 | 0 | 0 | 88.86
7:00 | 0 | 0 | 0 | 0 | 300 | 98 | 0 | 0 | 0 |  | 0 | 260 | 280 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 16 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 6 | 28 | 31 | 0 | 39 | 0 | 0 | 0 | 355 | 0 | 219 | 73 | 90 | 29 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 24 | 22 | 92 | 107 | 0 | 20 | 0 | 0 | 30 | 48 | 0 | 0 | 159 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 11 | 0 | 144 | 0 | 0 | 179 | 0 | 149 | 2 | 90 | 8 | 150 | 364 | 107 | 70 | 72 | 1 | 300 | 35 | 110 | 80 | 117 | 100 | 180 | 85 | 4 | 144 | 113 | 0 | 17 | 3 | 5 | 55 |  | 711 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 300 | 220 | 0 | 0 | 0 | 2 | 0 |  | 6051 | 2794 | 8845 | 3031 | 711 | 1547 | 0 | 2906 | 500 | 46 | 0 | 0 | 92 | 12 | 0 | 88.85
8:00 | 0 | 0 | 0 | 0 | 300 | 98 | 0 | 0 | 0 |  | 0 | 260 | 285 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 22 | 25 | 30 | 33 | 33 | 26 | 0 | 46 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 40 | 12 | 42 | 0 | 8 | 0 | 0 | 0 | 320 | 0 | 218 | 73 | 89 | 29 | 52 | 0 | 51 | 0 | 0 | 45 | 22 | 5 | 24 | 22 | 104 | 96 | 0 | 20 | 1 | 0 | 30 | 48 | 0 | 0 | 160 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 0 | 255 | 24 | 30 | 179 | 50 | 149 | 7 | 90 | 45 | 150 | 364 | 108 | 85 | 88 | 2 | 282 | 35 | 110 | 114 | 116 | 100 | 150 | 82 | 16 | 144 | 113 | 0 | 17 | 10 | 41 | 39 |  | 711 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 34 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 82 | 0 | 2 | 113 | 300 | 222 | 0 | 0 | 1 | 33 | 118 |  | 6434 | 3051 | 9485 | 2984 | 711 | 1542 | 104 | 3359 | 500 | 46 | 0 | 63 | 104 | 72 | 0 | 88.85
9:00 | 0 | 0 | 0 | 0 | 300 | 98 | 0 | 0 | 0 |  | 0 | 260 | 275 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 84 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 10 | 33 | 33 | 51 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 12 | 44 | 0 | 3 | 0 | 0 | 0 | 345 | 0 | 217 | 73 | 90 | 29 | 52 | 0 | 51 | 0 | 0 | 41 | 19 | 8 | 24 | 21 | 112 | 69 | 0 | 17 | 1 | 0 | 30 | 48 | 0 | 0 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 5 | 0 | 278 | 53 | 70 | 179 | 70 | 149 | 13 | 90 | 67 | 150 | 314 | 108 | 90 | 83 | 3 | 300 | 35 | 110 | 114 | 116 | 100 | 245 | 93 | 30 | 144 | 113 | 0 | 17 | 19 | 40 | 25 |  | 711 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 48 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 218 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 113 | 0 | 105 | 0 | 3 | 113 | 300 | 222 | 0 | 0 | 2 | 58 | 118 |  | 6801 | 3104 | 9905 | 2952 | 711 | 1528 | 193 | 3567 | 499 | 46 | 0 | 168 | 112 | 129 | 0 | 88.85
10:00 | 0 | 0 | 0 | 0 | 290 | 95 | 0 | 0 | 0 |  | 0 | 260 | 285 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 12 | 50 | 0 | 2 | 0 | 0 | 0 | 325 | 0 | 220 | 73 | 91 | 29 | 52 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 20 | 21 | 108 | 69 | 0 | 17 | 2 | 0 | 30 | 48 | 0 | 0 | 157 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 305 | 22 | 2 | 0 | 291 | 108 | 100 | 179 | 99 | 149 | 17 | 90 | 92 | 150 | 316 | 99 | 90 | 89 | 3 | 300 | 35 | 110 | 114 | 116 | 97 | 220 | 93 | 42 | 144 | 113 | 0 | 17 | 26 | 39 | 31 |  | 710 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 12 | 5 | 48 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 217 | 0 | 11 | 0 | 220 | 0 | 0 | 105 | 0 | 112 | 0 | 106 | 0 | 4 | 113 | 300 | 218 | 0 | 0 | 4 | 78 | 115 |  | 7005 | 3141 | 10146 | 2922 | 710 | 1535 | 307 | 3627 | 500 | 46 | 0 | 215 | 108 | 176 | 0 | 88.85
11:00 | 0 | 0 | 0 | 0 | 290 | 98 | 0 | 0 | 0 |  | 0 | 270 | 265 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 12 | 50 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 218 | 73 | 90 | 29 | 52 | 0 | 51 | 0 | 40 | 43 | 17 | 8 | 17 | 15 | 106 | 67 | 0 | 17 | 2 | 0 | 30 | 48 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 2 | 20 | 296 | 155 | 100 | 178 | 99 | 149 | 19 | 90 | 189 | 150 | 316 | 89 | 90 | 89 | 4 | 300 | 35 | 110 | 114 | 110 | 90 | 220 | 94 | 47 | 144 | 113 | 0 | 17 | 29 | 51 | 32 |  | 710 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 43 | 6 | 47 | 0 | 43 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 217 | 0 | 11 | 0 | 217 | 0 | 0 | 105 | 20 | 112 | 0 | 102 | 0 | 5 | 113 | 300 | 214 | 0 | 0 | 4 | 90 | 115 |  | 7167 | 3244 | 10411 | 2942 | 710 | 1512 | 394 | 3715 | 500 | 46 | 0 | 286 | 106 | 200 | 0 | 88.84
12:00 | 0 | 0 | 0 | 0 | 280 | 101 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 29 | 33 | 33 | 49 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 12 | 50 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 214 | 78 | 90 | 29 | 51 | 0 | 51 | 0 | 40 | 38 | 17 | 8 | 16 | 20 | 128 | 67 | 0 | 17 | 2 | 20 | 30 | 48 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 295 | 22 | 2 | 120 | 298 | 304 | 100 | 178 | 100 | 149 | 19 | 90 | 200 | 150 | 240 | 98 | 96 | 89 | 4 | 300 | 35 | 107 | 114 | 107 | 90 | 260 | 92 | 50 | 150 | 113 | 0 | 17 | 32 | 96 | 0 |  | 710 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 43 | 6 | 47 | 0 | 43 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 213 | 0 | 11 | 10 | 214 | 0 | 0 | 105 | 100 | 112 | 0 | 100 | 0 | 5 | 113 | 310 | 214 | 0 | 0 | 5 | 93 | 115 |  | 7506 | 3367 | 10873 | 2942 | 710 | 1534 | 734 | 3774 | 509 | 46 | 0 | 286 | 128 | 210 | 0 | 88.84
13:00 | 0 | 0 | 0 | 0 | 270 | 101 | 0 | 0 | 0 |  | 0 | 270 | 250 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 49 | 0 | 46 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 12 | 50 | 0 | 3 | 0 | 0 | 0 | 315 | 0 | 214 | 86 | 84 | 29 | 50 | 0 | 51 | 0 | 39 | 35 | 17 | 8 | 16 | 20 | 134 | 67 | 0 | 20 | 2 | 20 | 30 | 48 | 0 | 0 | 156 | 60 | 85 | 0 | 0 | 0 | 0 | 10 | 295 | 19 | 5 | 200 | 296 | 298 | 100 | 177 | 99 | 149 | 19 | 90 | 200 | 150 | 241 | 98 | 105 | 79 | 4 | 300 | 35 | 92 | 114 | 115 | 90 | 250 | 84 | 45 | 162 | 113 | 0 | 17 | 31 | 100 | 0 |  | 710 | 0 | 390 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 89 | 22 | 0 | 0 | 0 | 0 | 43 | 8 | 47 | 0 | 43 | 10 | 52 | 0 | 19 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 211 | 0 | 11 | 63 | 213 | 0 | 0 | 105 | 165 | 112 | 0 | 98 | 0 | 6 | 113 | 340 | 214 | 0 | 0 | 5 | 88 | 115 |  | 7579 | 3560 | 11139 | 2891 | 710 | 1515 | 925 | 3786 | 540 | 81 | 60 | 297 | 134 | 200 | 0 | 88.84
14:00 | 0 | 0 | 0 | 0 | 260 | 101 | 0 | 0 | 0 |  | 0 | 270 | 240 | 0 | 0 | 40 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 49 | 0 | 46 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 92 | 12 | 49 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 212 | 86 | 85 | 28 | 48 | 0 | 51 | 0 | 37 | 41 | 18 | 7 | 16 | 20 | 130 | 67 | 0 | 20 | 2 | 20 | 30 | 48 | 0 | 0 | 156 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 270 | 19 | 8 | 150 | 298 | 210 | 100 | 176 | 100 | 149 | 16 | 90 | 200 | 142 | 241 | 107 | 105 | 90 | 4 | 300 | 54 | 110 | 114 | 115 | 90 | 260 | 92 | 39 | 162 | 113 | 0 | 26 | 27 | 100 | 0 |  | 710 | 0 | 380 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 89 | 22 | 0 | 0 | 0 | 0 | 43 | 30 | 47 | 0 | 43 | 24 | 52 | 0 | 19 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 211 | 0 | 11 | 50 | 213 | 0 | 0 | 105 | 120 | 112 | 0 | 102 | 0 | 6 | 113 | 350 | 210 | 0 | 0 | 4 | 81 | 115 |  | 7547 | 3510 | 11057 | 2976 | 710 | 1472 | 730 | 3858 | 550 | 81 | 40 | 331 | 130 | 179 | 0 | 88.84
15:00 | 0 | 0 | 0 | 0 | 260 | 98 | 0 | 0 | 0 |  | 0 | 270 | 285 | 0 | 0 | 40 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 49 | 0 | 46 | 35 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | 92 | 12 | 49 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 209 | 76 | 92 | 27 | 45 | 0 | 51 | 0 | 38 | 42 | 19 | 3 | 33 | 20 | 124 | 67 | 0 | 17 | 1 | 20 | 30 | 50 | 0 | 0 | 154 | 60 | 84 | 0 | 0 | 0 | 0 | 9 | 290 | 19 | 8 | 150 | 296 | 202 | 100 | 174 | 100 | 149 | 12 | 90 | 200 | 133 | 240 | 108 | 105 | 90 | 3 | 300 | 54 | 110 | 114 | 110 | 90 | 253 | 93 | 30 | 162 | 113 | 0 | 36 | 21 | 99 | 34 |  | 711 | 0 | 360 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 88 | 23 | 0 | 0 | 0 | 0 | 43 | 36 | 47 | 0 | 43 | 24 | 52 | 21 | 19 | 0 | 8 | 10 | 0 | 199 | 0 | 0 | 0 | 0 | 209 | 0 | 11 | 50 | 212 | 0 | 0 | 105 | 120 | 112 | 0 | 102 | 0 | 5 | 113 | 360 | 209 | 0 | 0 | 3 | 63 | 115 |  | 7603 | 3513 | 11116 | 2976 | 711 | 1522 | 722 | 3874 | 569 | 81 | 40 | 359 | 124 | 138 | 0 | 88.83
16:00 | 0 | 0 | 0 | 0 | 260 | 98 | 0 | 0 | 0 |  | 0 | 270 | 265 | 0 | 0 | 42 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 40 | 0 | 46 | 35 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 12 | 48 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 210 | 86 | 92 | 24 | 45 | 0 | 51 | 0 | 38 | 35 | 19 | 3 | 33 | 20 | 116 | 67 | 0 | 17 | 1 | 20 | 30 | 50 | 0 | 0 | 157 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 300 | 19 | 8 | 120 | 296 | 304 | 100 | 174 | 100 | 149 | 8 | 90 | 200 | 118 | 241 | 108 | 90 | 90 | 2 | 300 | 54 | 110 | 114 | 110 | 90 | 261 | 81 | 20 | 162 | 113 | 0 | 36 | 13 | 99 | 55 |  | 710 | 0 | 345 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 89 | 26 | 0 | 0 | 0 | 0 | 43 | 43 | 47 | 0 | 43 | 24 | 52 | 21 | 18 | 0 | 8 | 40 | 0 | 199 | 0 | 0 | 0 | 0 | 192 | 0 | 11 | 80 | 213 | 0 | 0 | 105 | 50 | 112 | 0 | 102 | 0 | 4 | 113 | 380 | 210 | 0 | 0 | 1 | 42 | 115 |  | 7581 | 3478 | 11059 | 2933 | 710 | 1526 | 754 | 3823 | 619 | 81 | 40 | 366 | 116 | 91 | 0 | 88.83
17:00 | 0 | 0 | 0 | 0 | 250 | 101 | 0 | 0 | 0 |  | 0 | 270 | 265 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 40 | 0 | 46 | 35 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 7 | 49 | 0 | 3 | 0 | 0 | 0 | 315 | 0 | 210 | 76 | 90 | 25 | 46 | 0 | 51 | 0 | 38 | 40 | 19 | 11 | 33 | 20 | 120 | 66 | 0 | 19 | 0 | 20 | 30 | 50 | 0 | 0 | 157 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 19 | 8 | 80 | 296 | 132 | 100 | 175 | 100 | 149 | 3 | 90 | 200 | 115 | 241 | 108 | 90 | 90 | 0 | 300 | 54 | 110 | 114 | 115 | 90 | 264 | 92 | 7 | 162 | 113 | 0 | 36 | 5 | 99 | 55 |  | 710 | 0 | 325 | 0 | 0 | 40 | 0 | 0 | 4 | 0 | 0 | 89 | 24 | 0 | 0 | 0 | 0 | 43 | 43 | 47 | 0 | 43 | 27 | 52 | 21 | 18 | 0 | 8 | 76 | 0 | 199 | 0 | 0 | 0 | 0 | 151 | 0 | 11 | 60 | 210 | 0 | 0 | 105 | 50 | 94 | 0 | 103 | 0 | 2 | 113 | 380 | 210 | 0 | 0 | 0 | 17 | 115 |  | 7358 | 3390 | 10748 | 2868 | 710 | 1511 | 522 | 3834 | 655 | 81 | 40 | 373 | 120 | 34 | 0 | 88.83
18:00 | 0 | 0 | 0 | 0 | 250 | 101 | 0 | 0 | 0 |  | 0 | 270 | 285 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 0 | 33 | 49 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 5 | 33 | 92 | 6 | 50 | 0 | 2 | 0 | 0 | 0 | 330 | 0 | 210 | 123 | 90 | 29 | 50 | 0 | 51 | 0 | 40 | 43 | 22 | 11 | 31 | 21 | 116 | 84 | 0 | 19 | 0 | 30 | 30 | 50 | 0 | 0 | 158 | 60 | 87 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 8 | 80 | 298 | 103 | 100 | 175 | 100 | 149 | 0 | 90 | 200 | 113 | 240 | 108 | 90 | 90 | 0 | 300 | 54 | 110 | 114 | 115 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 710 | 0 | 310 | 0 | 0 | 80 | 0 | 0 | 4 | 0 | 0 | 89 | 24 | 0 | 0 | 0 | 0 | 43 | 43 | 81 | 0 | 43 | 32 | 52 | 21 | 21 | 0 | 8 | 79 | 0 | 199 | 0 | 10 | 0 | 0 | 158 | 0 | 13 | 20 | 202 | 0 | 0 | 105 | 50 | 94 | 0 | 112 | 0 | 0 | 113 | 400 | 213 | 0 | 0 | 0 | 1 | 115 |  | 7464 | 3445 | 10909 | 2872 | 710 | 1590 | 453 | 3866 | 678 | 81 | 90 | 452 | 116 | 1 | 0 | 88.83
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 49 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 16 | 51 | 93 | 6 | 50 | 0 | 10 | 0 | 0 | 0 | 320 | 0 | 213 | 152 | 90 | 29 | 53 | 0 | 51 | 0 | 40 | 43 | 22 | 7 | 30 | 21 | 134 | 82 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 0 | 157 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 200 | 298 | 306 | 100 | 184 | 100 | 149 | 0 | 90 | 200 | 125 | 240 | 108 | 90 | 90 | 0 | 300 | 54 | 110 | 114 | 115 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 711 | 0 | 290 | 0 | 0 | 157 | 0 | 0 | 21 | 10 | 0 | 91 | 28 | 0 | 0 | 0 | 0 | 43 | 46 | 93 | 0 | 50 | 38 | 52 | 21 | 21 | 0 | 8 | 79 | 0 | 199 | 15 | 10 | 0 | 0 | 186 | 0 | 21 | 90 | 186 | 0 | 0 | 105 | 168 | 105 | 0 | 111 | 0 | 0 | 113 | 500 | 216 | 0 | 0 | 0 | 0 | 115 |  | 7946 | 3899 | 11845 | 2888 | 711 | 1673 | 964 | 3905 | 778 | 81 | 182 | 529 | 134 | 0 | 0 | 88.82
19:30 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 49 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 16 | 51 | 100 | 6 | 48 | 0 | 16 | 0 | 0 | 0 | 315 | 0 | 215 | 152 | 87 | 29 | 53 | 0 | 51 | 0 | 33 | 43 | 22 | 7 | 32 | 21 | 128 | 84 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 275 | 24 | 11 | 200 | 300 | 305 | 100 | 185 | 100 | 149 | 0 | 90 | 200 | 136 | 241 | 108 | 90 | 90 | 0 | 300 | 54 | 110 | 114 | 117 | 100 | 263 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 710 | 0 | 284 | 0 | 0 | 158 | 0 | 0 | 36 | 10 | 0 | 91 | 28 | 0 | 0 | 0 | 0 | 43 | 45 | 93 | 0 | 50 | 40 | 52 | 21 | 21 | 0 | 8 | 79 | 0 | 199 | 15 | 10 | 0 | 0 | 191 | 0 | 21 | 99 | 176 | 0 | 0 | 105 | 168 | 97 | 0 | 111 | 0 | 0 | 113 | 520 | 216 | 0 | 0 | 0 | 0 | 115 |  | 7934 | 3925 | 11859 | 2877 | 710 | 1654 | 972 | 3918 | 798 | 81 | 183 | 538 | 128 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 16 | 51 | 97 | 5 | 49 | 0 | 15 | 0 | 0 | 0 | 325 | 0 | 214 | 153 | 90 | 29 | 54 | 0 | 51 | 0 | 36 | 43 | 22 | 7 | 33 | 21 | 134 | 84 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 200 | 300 | 305 | 100 | 186 | 99 | 149 | 0 | 90 | 200 | 137 | 240 | 108 | 90 | 90 | 0 | 300 | 54 | 110 | 114 | 116 | 100 | 264 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 710 | 0 | 285 | 0 | 0 | 157 | 0 | 0 | 40 | 0 | 0 | 91 | 28 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 40 | 52 | 21 | 21 | 0 | 8 | 78 | 0 | 199 | 14 | 10 | 0 | 0 | 188 | 0 | 21 | 99 | 173 | 0 | 0 | 105 | 170 | 97 | 0 | 112 | 0 | 0 | 113 | 510 | 216 | 0 | 0 | 0 | 0 | 115 |  | 7963 | 3903 | 11866 | 2888 | 710 | 1660 | 973 | 3918 | 787 | 81 | 181 | 534 | 134 | 0 | 0 | 88.82
21:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 16 | 51 | 100 | 5 | 50 | 0 | 26 | 0 | 0 | 0 | 315 | 0 | 217 | 182 | 85 | 29 | 54 | 0 | 51 | 0 | 41 | 43 | 22 | 7 | 33 | 21 | 132 | 84 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 200 | 298 | 307 | 100 | 187 | 100 | 149 | 0 | 90 | 200 | 143 | 241 | 108 | 90 | 90 | 0 | 300 | 54 | 110 | 114 | 115 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 711 | 0 | 275 | 0 | 0 | 158 | 0 | 0 | 33 | 0 | 0 | 91 | 29 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 40 | 52 | 21 | 22 | 0 | 8 | 78 | 0 | 199 | 14 | 10 | 0 | 0 | 179 | 0 | 21 | 99 | 159 | 0 | 0 | 105 | 168 | 113 | 0 | 112 | 0 | 0 | 113 | 500 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8024 | 3875 | 11899 | 2845 | 711 | 1717 | 974 | 3948 | 777 | 81 | 182 | 532 | 132 | 0 | 0 | 88.82
22:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 16 | 51 | 100 | 5 | 50 | 0 | 34 | 0 | 0 | 0 | 320 | 0 | 220 | 182 | 85 | 29 | 55 | 0 | 51 | 0 | 42 | 43 | 22 | 7 | 33 | 21 | 128 | 88 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 80 | 300 | 251 | 100 | 188 | 100 | 149 | 0 | 90 | 200 | 148 | 240 | 108 | 90 | 90 | 0 | 280 | 54 | 110 | 114 | 116 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 711 | 0 | 270 | 0 | 0 | 158 | 0 | 0 | 33 | 0 | 0 | 91 | 28 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 40 | 52 | 21 | 21 | 0 | 8 | 79 | 0 | 199 | 0 | 0 | 0 | 0 | 170 | 0 | 21 | 0 | 157 | 0 | 0 | 105 | 47 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 209 | 0 | 0 | 0 | 0 | 115 |  | 7850 | 3604 | 11454 | 2840 | 711 | 1693 | 578 | 3954 | 778 | 81 | 158 | 533 | 128 | 0 | 0 | 88.81
23:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 16 | 0 | 100 | 5 | 50 | 0 | 39 | 0 | 0 | 0 | 355 | 0 | 201 | 182 | 91 | 29 | 56 | 0 | 51 | 0 | 41 | 43 | 22 | 7 | 33 | 21 | 118 | 101 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 300 | 52 | 100 | 197 | 100 | 149 | 0 | 90 | 200 | 147 | 240 | 108 | 90 | 90 | 0 | 280 | 54 | 110 | 114 | 117 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 714 | 0 | 265 | 0 | 0 | 70 | 0 | 0 | 31 | 0 | 0 | 91 | 27 | 0 | 0 | 0 | 0 | 43 | 42 | 41 | 0 | 0 | 40 | 52 | 21 | 21 | 0 | 8 | 78 | 0 | 199 | 0 | 0 | 0 | 0 | 163 | 0 | 21 | 0 | 151 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 220 | 0 | 0 | 0 | 0 | 115 |  | 7561 | 3357 | 10918 | 2857 | 714 | 1719 | 252 | 3905 | 777 | 81 | 70 | 425 | 118 | 0 | 0 | 88.81
24:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 100 | 5 | 50 | 0 | 39 | 0 | 0 | 0 | 320 | 0 | 176 | 182 | 90 | 29 | 56 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 21 | 120 | 104 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 298 | 23 | 70 | 188 | 55 | 149 | 0 | 90 | 200 | 150 | 401 | 108 | 90 | 90 | 0 | 281 | 54 | 110 | 114 | 110 | 100 | 15 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 719 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 43 | 35 | 0 | 0 | 0 | 40 | 52 | 21 | 21 | 0 | 8 | 83 | 0 | 199 | 0 | 0 | 0 | 0 | 165 | 0 | 11 | 0 | 144 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 220 | 0 | 0 | 0 | 0 | 115 |  | 7308 | 3198 | 10506 | 2697 | 719 | 1718 | 148 | 3900 | 762 | 81 | 0 | 361 | 120 | 0 | 0 | 88.81
KWH | 0 | 0 | 0 | 0 | 6709264 | 2382590 | 0 | 0 | 0 |  | 0 | 6306050 | 6651433 | 0 | 0 | 887151 | 1615437 | 0 | 0 | 0 | 1708992 | 2351040 | 0 | 0 | 0 | 0 | 1302840 | 841523 | 1238108 | 463104 | 600000 | 651600 | 776160 | 811200 | 824640 | 0 | 1105380 | 400000 | 0 | 0 | 345468 | 0 | 0 | 0 | 0 |  | 397200 | 77449 | 222324 | 1599240 | 753600 | 1079520 | 0 | 465600 | 0 | 0 | 0 | 8274500 | 0 | 5186000 | 2442181 | 2122410 | 656856 | 1237440 | 0 | 1192829 | 0 | 544432 | 1080451 | 467712 | 217260 | 692200 | 516930 | 2802240 | 1994880 | 0 | 420084 | 13450 | 310000 | 720000 | 1171200 | 0 | 0 | 3643000 | 1398048 | 2075520 | 0 | 0 | 0 | 0 | 245880 | 7257500 | 527376 | 204720 | 1615104 | 5956580 | 3198328 | 1559385 | 4233600 | 1568086 | 3605330 | 134865 | 2099520 | 3082080 | 3419054 | 7181000 | 2403600 | 2116800 | 2085054 | 29881 | 6937636 | 1215867 | 2647079 | 2059980 | 2769480 | 2234880 | 5014800 | 2190720 | 329950 | 3718080 | 2703545 | 0 | 685080 | 215561 | 1535040 | 1077840 |  | 17201454 | 0 | 8106624 | 0 | 0 | 1113137 | 0 | 0 | 176640 | 12160 | 0 | 2203104 | 536900 | 0 | 0 | 0 | 0 | 592144 | 459020 | 1015824 | 0 | 637688 | 322479 | 963840 | 190991 | 488880 | 0 | 196344 | 602181 | 0 | 4863800 | 46000 | 34000 | 0 | 0 | 5008436 | 0 | 327252 | 705600 | 5133109 | 0 | 0 | 2708160 | 1284299 | 2652672 | 0 | 2142547 | 0 | 42591 | 2643840 | 9730600 | 5218909 | 0 | 0 | 33480 | 656640 | 1934887 |  | 169605817 | 79986232 | 249592049 | 71822158 | 17201454 | 38000164 | 9930802 | 84519212 | 15196581 | 1505380 | 1193137 | 5964503 | 2802240 | 1456418 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7447283.04 | 3145018.8 | 0 | 0 | 0 |  | 0 | 6873594.5 | 7383090.63 | 0 | 0 | 7505297.46 | 1680054.48 | 0 | 0 | 0 | 15586007.04 | 23134233.6 | 0 | 0 | 0 | 0 | 9510732 | 6504972.79 | 12207744.88 | 347328 | 450000 | 0 | 0 | 0 | 7974268.8 | 0 | 298452.6 | 108000 | 0 | 0 | 3209397.72 | 0 | 0 | 0 | 0 |  | 0 | 748931.83 | 2156542.8 | 15272742 | 6556320 | 8549798.4 | 0 | 1382832 | 0 | 0 | 0 | 6123130 | 0 | 4771120 | 3150413.49 | 2440771.5 | 742247.28 | 1732416 | 0 | 2039737.59 | 0 | 5498763.2 | 10318307.05 | 593994.24 | 162945 | 1211350 | 387697.5 | 21016800 | 2114572.8 | 0 | 533506.68 | 214393 | 508400 | 1152000 | 2084736 | 0 | 0 | 3788720 | 2754154.56 | 3964243.2 | 0 | 0 | 0 | 0 | 501595.2 | 7330075 | 395532 | 155587.2 | 27472919.04 | 45031744.8 | 54307609.44 | 26072917.2 | 22014720 | 26218397.92 | 35476447.2 | 1576571.85 | 17111088 | 33440568 | 24104330.7 | 6678330 | 21920832 | 20003760 | 18160820.34 | 0 | 52448528.16 | 10590201.57 | 23267824.41 | 20558600.4 | 23734443.6 | 14884300.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99080375.04 | 0 | 8511955.2 | 0 | 0 | 15428078.82 | 0 | 0 | 1852953.6 | 127436.8 | 0 | 2489507.52 | 832195 | 0 | 0 | 0 | 0 | 5826696.96 | 4663643.2 | 8990042.4 | 0 | 8621541.76 | 3124821.51 | 9339609.6 | 1852612.7 | 938649.6 | 0 | 148632.408 | 3631151.43 | 0 | 26361796 | 1593900 | 970020 | 0 | 0 | 6611135.52 | 0 | 490878 | 12002256 | 6005737.53 | 0 | 0 | 28273190.4 | 21845925.99 | 25173857.28 | 0 | 16626164.72 | 0 | 470630.55 | 19537977.6 | 42717334 | 0 | 0 | 0 | 0 | 0 | 0 |  | 758794807.29 | 384140707.138 | 1142935514.428 | 68205692.458 | 99080375.04 | 41849475.01 | 167920025.59 | 593516139.48 | 72710281.43 | 406452.6 | 17991998.82 | 57976678.6 | 21016800 | 2261595.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 280 | 101 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 29 | 33 | 33 | 49 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 12 | 50 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 214 | 78 | 90 | 29 | 51 | 0 | 51 | 0 | 40 | 38 | 17 | 8 | 16 | 20 | 128 | 67 | 0 | 17 | 2 | 20 | 30 | 48 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 295 | 22 | 2 | 120 | 298 | 304 | 100 | 178 | 100 | 149 | 19 | 90 | 200 | 150 | 240 | 98 | 96 | 89 | 4 | 300 | 35 | 107 | 114 | 107 | 90 | 260 | 92 | 50 | 150 | 113 | 0 | 17 | 32 | 96 | 0 |  | 710 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 43 | 6 | 47 | 0 | 43 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 213 | 0 | 11 | 10 | 214 | 0 | 0 | 105 | 100 | 112 | 0 | 100 | 0 | 5 | 113 | 310 | 214 | 0 | 0 | 5 | 93 | 115 |  | 10873 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 | 0 | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 16 | 51 | 100 | 5 | 50 | 0 | 26 | 0 | 0 | 0 | 315 | 0 | 217 | 182 | 85 | 29 | 54 | 0 | 51 | 0 | 41 | 43 | 22 | 7 | 33 | 21 | 132 | 84 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 200 | 298 | 307 | 100 | 187 | 100 | 149 | 0 | 90 | 200 | 143 | 241 | 108 | 90 | 90 | 0 | 300 | 54 | 110 | 114 | 115 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 711 | 0 | 275 | 0 | 0 | 158 | 0 | 0 | 33 | 0 | 0 | 91 | 29 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 40 | 52 | 21 | 22 | 0 | 8 | 78 | 0 | 199 | 14 | 10 | 0 | 0 | 179 | 0 | 21 | 99 | 159 | 0 | 0 | 105 | 168 | 113 | 0 | 112 | 0 | 0 | 113 | 500 | 220 | 0 | 0 | 0 | 0 | 115 |  | 11899 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 | 0 | 0 | 270 | 300 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 0 | 20 | 0 | 0 | 0 | 360 | 0 | 220 | 180 | 90 | 29 | 55 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 22 | 163 | 100 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 0 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 250 | 108 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 |  | 100 | 55 |  | 734 | 0 | 290 | 0 | 0 | 158 | 0 | 0 | 35 | 40 | 0 | 92 | 10 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 40 | 52 | 30 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 20 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 225 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 0 | 280 | 102 | 0 | 0 | 0 | 0 | 0 | 270 | 285 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 90 | 50 | 0 | 10 | 0 | 0 | 0 | 360 | 0 | 220 | 80 | 90 | 29 | 55 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 22 | 138 | 100 | 0 | 20 | 1.6 | 30 | 30 | 50 | 0 | 0 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 240 | 108 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 260 | 92 | 50 | 162 | 113 | 0 | 36 | 30 | 100 | 55 |  | 734 | 0 | 280 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 0 | 52 | 25 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 100 | 200 | 0 | 0 | 105 | 100 | 113 | 0 | 113 | 0 | 8 | 113 | 500 | 225 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 230 | 99 | 0 | 0 | 0 | 0 | 0 | 270 | 275 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 75 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 18 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 92 | 32 | 50 | 0 | 8 | 0 | 0 | 0 | 315 | 0 | 184 | 178 | 83 | 29 | 54 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 27 | 17 | 112 | 108 | 0 | 20 | 1 | 30 | 30 | 51 | 0 | 0 | 157 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 22 | 8 | 0 | 300 | 0 | 25 | 182 | 26 | 149 | 7 | 90 | 51 | 140 | 388 | 108 | 90 | 88 | 1 | 281 | 54 | 110 | 114 | 105 | 100 | 50 | 92 | 14 | 144 | 113 | 0 | 17 | 11 | 79 | 55 | 0 | 720 | 0 | 280 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 34 | 0 | 20 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 0 | 178 | 0 | 0 | 105 | 0 | 94 | 0 | 55 | 0 | 1 | 113 | 370 | 210 | 0 | 0 | 1 | 31 | 115 | 0
199
| Minimum Generation |  | 8350 | 5:00
| Highest Generation |  | 11899 | 21:00
| Day Peak Generation |  | 10873 | 12:00
| Evening Peak Generation |  | 11899 | 21:00
| HVDC Max Flow |  | 719 | 24:00
| HVDC EvPeak Flow |  | 711 | 21:00
| Load factor L.F |  | 87.4%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-15
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10873 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 8783 | MW
Evening Peak Generation : |  | 11899 | MW Hour : | 21:00 | Available Max Generation : |  | 12391 | MW
E.P. Demand (at gen end) : |  | 11899 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12100 | MW
Maximum Generation : |  | 11899 | MW Hour : | 21:00 | Reserve(Generation end) |  | 291 | MW
Total Gen. (MKWH) : |  | 249.592 | System Load Factor : | 87.4% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -44 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-15
Actual : | 88.79 | Ft.(MSL) , | Rule curve : | 90.76 | Ft.( MSL )
Gas Consumed : | Total = | 855.95 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 110055167.468
: |  | Coal : | 72710281.43 | Oil : | 837404842.49 | Total : | 1020170291.388
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4269.4012 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1454.1633 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1303.2974 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1177.7866 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1064.2674 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 858.832 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 477.2175 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 221.0468 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 662.3882 |  |  | 0 | 0%
Total | 0 |  | 11488.4004 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Raozan unit- 1,2
6) Sirajganj Unit 1,4
7) Siddhirganj 210 MW .
8) Kushiara 163 MW.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bhulta-Haripur 230 kV Ckt-2 was under shut down from 08:21 to 16:22 for C/M.
b) Baraulia 132/33 kV T-2 transformer was under shut down from 08:19 to 14:42 for C/M. | [5 empty] | About 10 MW power interruption occurred under
Baraulia S/S area from 08:19 to 14:42.
c) Netrokona 33 kV Bus under T-3 & T-4 transformers was under shut down from 08:21 to 14:09 for D/W.
d) Ashuganj-Shahjibazar 132 kV Ckt-3 was under shut down from 09:06 to 17:57 for A/M.
e) Madunaghat-Hathazari 132 kV Ckt-1 was under shut down from 09:20 to 10:46 for D/W.
f) Barapukuria-Bogura 230 kV Ckt-2 was under shut down from 09:29 to 10:47(15/03/2022) for D/W.
g) Aminbazar-Keraniganj 230 kV Ckt-2 was under shut down from 10:15 to 11:11 for D/W.
h) Tongi 132/33 kV T-3 transformer was under shut down from 10:14 to 11:10 for C/M.
i) Hasnabad-Postogula 132 kV Ckt-1 was shut down at 10:46 for D/W.
j) Sherpur(Bogura) 132/33 kV T-3 transformer was under shut down from 08:55 to 10:48 for C/M.
k) Madunaghat-Hathazari 132 kV Ckt-2 was under shut down from 11:07 to 16:43 for C/M.
l) Hasnabad 230/132 kV T-01 transformer was under shut down from 10:43 to 14:45 for C/M.
m) Chattak 33 kV Bus under T-2 transformer was under shut down from 08:35 to 11:58 for C/M.
n) Bheramara 230/132 kV T-02 transformer was under shut down from 08:01 to 15:57 for C/M.
o) Mymensingh-Kishoreganj 132 kV Ckt-2 tripped at 13:01 showing dist. C-phase and was switched on at
13:08.
p) Cox's Bazar 132/33 kV T-2 transformer was under shut down from 12:49 to 13:14 for C/M.
q) Siddhirganj 335 MW CCPP GT was synchronized at 13:13.
r) Hasnabad 230/132 kV T-03 transformer was under shut down from 15:10 to 16:24 for C/M.
s) Barapukuria Unit-1 was synchronized at 14:57.
t) Bogura 230/132 kV T-01 transformer tripped at 02:45(15/03/2022) showing Lockout at HT side and
No Relay at LT side.
u) Ishwardi 230/132 kV T-02 transformer tripped at 04:22(15/03/2022) due to winging temperature high.
v) Hathazari-Baroirhat 132 kV Ckt-2 is under shut down since 07:01(15/03/2022) for D/W.
w) Agargaon 230/132 kV T-02 transformer is under shut down since 07:16(15/03/2022) for C/M.
x) Kallyanpur-Lalbag 132 kV Ckt-1 is under shut down since 07:18(15/03/2022) for C/M.
y) Kulaura 132/33 kV T-2 transformer is under shut down since 07:19(15/03/2022) for C/M. | [5 empty] | About 05 MW power interruption occurred under
Kulaura S/S area since 07:19.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6709264 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2382590
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6306050 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6651433 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 887151
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 463104
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 90 | 1615437 | Gas shortage & ST U/M.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1708992 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1302840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2351040
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 841523
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1238108
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1251600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 776160
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 824640 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 5956580
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 307 | 3198328
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 1559385
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1568086
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3605330
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 2116800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 2190720 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3718080
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 215561
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1077840
| Dhaka area Total |  |  |  | 5696 | 3018 | 61327842
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 345468 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 134865
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1079520
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 81 | 1505380 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 90 | 2085054 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 77449 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 222324 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1599240
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2099520 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 465600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 5 | 753600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29881
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 6937636
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1215867
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2647079
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2234880
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2703545
| Chattogram area Total |  |  |  | 2382 | 1203 | 26136908
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 5186000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 8274500
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 656856 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1237440
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 182 | 2442181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1192829
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 3419054
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 544432 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2122410 | Engine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3082080
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 467712
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 217260 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 2802240
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 692200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1080451 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 516930 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1615104
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2059980
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2769480
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 685080 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 115 | 115 | 99 | 1535040 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2139 | 42599259
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 84 | 1994880 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 420084
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13450
87 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 187 | 4233600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 108 | 2403600
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 329950
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 397200
| Mymensingh Area Total |  |  |  | 622 | 405 | 9792764
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 310000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3643000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 1171200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 204720
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1398048
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2075520
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 527376
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7257500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 241 | 7181000 | Gas shortage
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245880
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 265 | 5014800 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1259 | 29749044
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 711 | 17201454
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 176640 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 158 | 1113137 | ST under maint.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 12160 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 275 | 8106624 | ST under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 99 | 705600
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2708160
115 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 656640
| Khulna Area Total |  |  |  | 2229 | 1381 | 30680415
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 536900 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2203104 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 21 | 327252 | Gas shortage
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 9730600 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5218909
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 861 | 18016765
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 592144 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 44 | 459020 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 637688
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 322479 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 179 | 5008436 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 159 | 5133109 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 190991 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 488880
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 196344 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 963840
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 1015824 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 168 | 1284299 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2652672
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2643840
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33480
| Rajshahi Area Total |  |  |  | 2129 | 1105 | 21623046
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 602181 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4863800 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 14 | 46000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 34000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 2142547
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42591
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1934887 | On test
| Rangpur Area Total |  |  |  | 720 | 528 | 9666006
| Total |  |  |  | 21215 | 11899 | 249592049
| Eastern Grid Total |  |  |  | 14091 | 8024 | 169605817
| Western Grid Total |  |  |  | 7124 | 3875 | 79986232
| National Grid Total |  |  |  | 21215 | 11899 | 249592049
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-14
(a) ENTIRE EASTERN GRID : |  | 7863 | MW | (b) ENTIRE WESTERN GRID : |  | 3423 | MW
i) Dhaka area |  | 4258 | MW | i) Khulna area |  | 1248 | MW
ii) Chittagong area |  | 1172 | MW | ii) Rajshahi area |  | 1176 | MW
iii) Comilla area |  | 1031 | MW | iii) Barisal area |  | 296 | MW
iv) Mymensingh area |  | 952 | MW | iv) Rangpur area |  | 703 | MW
v) Sylhet area |  | 450 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11286 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 122 | 19:30 | Valuka | 118 | 11:00 | Central S/S | 69 | 13:00
Munsiganj | 84 | 21:00 | Tangail | 189 | 20:00 | Noapara | 41 | 18:30
Sonargaon | 80 | 23:00 | Mymensing | 220 | 20:00 | Jessore | 106 | 19:30
Bhulta | 197 | 20:00 | Kishoreganj | 112 | 22:00 | Benapol | 46 | 7:00
Madanganj | 26 | 1:00 | Netrokona | 129 | 18:00 | Jhenida(Old) | 98 | 19:30
Rahim steel | 30 | 12:00 | Jamalpur | 138 | 8:00 | Bottail | 102 | 20:00
Ghorasal | 75 | 21:00 | Sherpur | 120 | 8:00 | G.K Project | 43 | 21:00
Narsingdi | 164 | 21:00 | Srimongal | 40 | 18:30 | Faridpur | 111 | 19:00
Haripur(SBU) | 113 | 19:30 | Shahjibazar | 107 | 21:00 | Rajbari | 52 | 19:00
Sreenagar | 35 | 21:00 | Fenchuganj | 35 | 18:00 | Madaripur | 80 | 18:30
Shyampur | 198 | 11:00 | Kulawara | 38 | 18:30 | Sariatpur | 50 | 19:30
Shitalakhya | 109 | 12:00 | Sylhet | 128 | 19:00 | Gopalganj | 85 | 19:00
Matuail | 63 | 11:00 | Chatak | 22 | 19:00 | Bagerhat | 71 | 18:30
Char Saidpur | 44 | 1:00 | Sunamganj | 42 | 19:00 | Mongla | 38 | 12:00
Ullon | 29 | 21:00 | Biani Bazar | 61 | 18:30 | Satkhira | 93 | 20:00
Hasnabad | 77 | 19:00 | Comilla (S) | 134 | 13:00 | Gallamari | 54 | 22:00
Magbazar | 110 | 15:00 | Comilla(N) | 149 | 20:00 | Magura | 44 | 21:00
Maniknagar | 74 | 12:00 | Chandpur | 57 | 20:00 | Norail | 36 | 19:00
Bangabhaban | 9 | 10:00 | Feni | 103 | 18:30 | Chuadanga | 74 | 21:00
Motijheel | 32 | 12:00 | Chowmuhani | 158 | 20:00 | Barisal(N) | 44 | 19:00
Narinda | 52 | 13:00 | Ashuganj | 37 | 13:00 | Barisal (S) | 82 | 18:30
Kazla | 87 | 21:00 | Daudkandi | 115 | 20:00 | Patuakhali | 89 | 21:00
Dhanmondi | 186 | 13:00 | B.Baria | 140 | 19:00 | Bhandaria | 40 | 19:00
Lalbag | 87 | 12:00 | Ramganj | 68 | 18:30 | Borguna | 12 | 18:30
Madartek | 72 | 22:00 | Chaddagram | 40 | 18:30 | Borhan Uddin | 32 | 21:00
Dhaka University | 33 | 12:00 | PHP | 8 | 13:00 | Ishurdi | 64 | 19:00
Aftabnagar | 28 | 19:00 | Kochua | 52 | 18:30 | Ruppur Paromanobik | 4 | 9:00
Fatullah | 60 | 12:00 | Madunaghat | 54 | 18:30 | Natore | 119 | 19:00
Nawabganj | 40 | 21:00 | Hathazari | 76 | 19:00 | Bogra | 138 | 21:00
Keraniganj | 70 | 19:00 | Khulshi | 176 | 19:00 | Naogaon | 110 | 20:00
Banani | 47 | 13:00 | Halishahar | 86 | 14:00 | Rajshahi | 112 | 20:00
Mirpur | 115 | 19:00 | Baraulia | 115 | 1:00 | Rajshahi New | 38 | 21:00
Kalyanpur | 87 | 18:30 | Sikalbaha | 30 | 21:00 | C.Nawabganj | 56 | 9:00
Gulshan | 108 | 12:00 | Dohazari | 82 | 20:00 | Amnura | 52 | 22:00
Uttara | 75 | 14:00 | Cox'sbazar | 105 | 13:00 | Pabna | 86 | 19:30
Uttara New | 29 | 12:00 | Chandraghona | 24 | 18:30 | Shahjadpur | 89 | 20:00
Kamrangirchar | 65 | 13:00 | Kaptai | 4 | 19:00 | Serajganj | 97 | 20:00
Savar | 160 | 19:00 | A. Khaer Stl. |  | 1:00 | Niyamatpur | 91 | 21:00
Bhasantec | 117 | 19:00 | Bakulia | 113 | 18:30 | Joypurhat | 54 | 21:00
Agargaon | 76 | 14:00 | Julda | 28 | 12:00 | Sherpur(Bogura) | 56 | 18:30
Satmosjid | 87 | 14:00 | TK chemical | 25 | 19:00 | Mohastangor | 56 | 18:30
Old Tongi | 108 | 15:00 | Modern Steel | 0 | 1:00 | Bhangura | 31 | 19:00
Kabirpur | 256 | 16:00 | Shahmirpur | 41.3 | 19:30 | Rangpur | 109 | 22:00
Manikgonj | 76 | 19:00 | Khagrachhari | 26 | 18:30 | Lalmonirhat | 40 | 18:30
Joydevpur | 179 | 15:00 | Matarbari | 37 | 18:00 | Saidpur | 100 | 9:00
New Tongi | 82 | 15:00 | Baroiar Hat | 42 | 19:00 | Purbasadipur | 102 | 8:00
Kodda | 273 | 18:00 | Rangamati | 12 | 18:30 | Thakurgaon | 73 | 19:30
Dhamrai | 122 | 10:00 | Agrabad | 74 | 18:00 | Palashbari | 108 | 8:00
Rajendrapur | 106 | 20:00 | Rampur | 10 | 18:30 | Barapukuria | 51 | 8:00
Bashundara | 153 | 18:00 | Abul Khair 230 | 138 | 10:00 | Panchagar | 51 | 18:30
Purbachal | 2 |  | BSRM | 164 | 16:00 | Joldhaka | 60 | 8:00
Tongi Millgate | 54 | 15:00 | GPH Ispat | 95 | 14:00 | Kurigram | 62 | 18:30
Bashundhara Cement |  |  | Goalpara | 26 | 13:00 | Mithapukur | 27 | 18:30
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 21:00 | 403 | 12:00 | Kaliakoir | 397 | 0.25 | 375 | 0.45833
| Bheramara | 402 | 24:00 | 393 | 13:00 | Bhulta | 418 | 0.875 | 396 | 0.45833
| Ashuganj(N) | 424 | 24:00 | 404 | 12:00 | Gopalganj | 411 | 0.625 | 395 | 0.79167
| Payra | 418 | 22:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 238 | 8:00 | Hathazari | 241 | 5:00 | 231 | 12:00
| Ishurdi | 241 | 2:00 | 232 | 12:00 | Megnaghat | 239 | 6:00 | 230 | 12:00
| Ashuganj | 248 | 22:00 | 236 | 12:00 | Fenchuganj | 241 | 6:00 | 234 | 15:00
| Serajganj | 240 | 1:00 | 233 | 11:00 | Siddhirganj | 238 | 6:00 | 228 | 11:00
| Baghabari | 240 | 21:00 | 233 | 10:00 | Maniknagar | 236 | 6:00 | 223 | 12:00
| Barapukuria | 234 | 24:00 | 226 | 7:00 | Agargaon | 237 | 6:00 | 223 | 12:00
| Bogra | 236 | 24:00 | 225 | 8:00 | Barisal | 242 | 6:00 | 236 | 18:30
| Rajshahi | 239 | 1:00 | 229 | 8:00 | Bhola 225 MW | 246 | 1:00 | 241 | 19:00
| Khulna South | 243 | 5:00 | 230 | 12:00 | AKSML | 240 | 6:00 | 229 | 12:00
| Rampura | 238 | 6:00 | 224 | 10:00 | BSRM | 241 | 6:00 | 229 | 12:00
| Haripur | 236 | 22:00 | 223 | 12:00 | Bibiyana | 241 | 2:00 | 235 | 18:00
| Hasnabad | 236 | 23:00 | 225 | 11:00 | Bhulta | 239 | 21:00 | 226 | 11:00
| Shyampur | 237 | 22:00 | 224 | 12:00 | Ashuganj (S) | 245 | 24:00 | 234 | 11:00
| Aminbazar | 239 | 1:00 | 225 | 2:00 | Kaliakoir | 234 | 22:00 | 221 | 11:00
| Tongi | 234 | 23:00 | 223 | 9:00 | GPH | 242 | 6:00 | 230 | 12:00
| Comilla (N) | 239 | 6:00 | 231 | 11:00 | Jhenaidah | 239 | 3:00 | 228 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 139 | 9:00 | 125 | 11:00 | PHP | 140 | 7:00 | 134 | 15:00
| Munsiganj | 137 | 0:00 | 127 | 12:00 | Kachua | 141 | 6:00 | 136 | 11:00
| Sonargaon | 135 | 1:00 | 126 | 10:00 | Madanhat | 139 | 3:00 | 133 | 13:00
| Bhulta | 127 | 21:00 | 117 | 12:00 | Hathazari | 142 | 5:00 | 135 | 12:00
| Madanganj | 136 | 22:00 | 126 | 12:00 | Khulshi | 138 | 7:00 | 131 | 15:00
| Rahim steel | 134 | 21:00 | 125 | 12:00 | Halishahar | 140 | 6:00 | 133 | 15:00
| Ghorasal | 142 | 24:00 | 140 | 1:00 | Baraulia | 142 | 5:00 | 134 | 12:00
| Narsingdi | 125 | 6:00 | 128 | 15:00 | Sikalbaha | 139 | 1:00 | 133 | 15:00
| Haripur(SBU) | 134 | 21:00 | 125 | 12:00 | Dohazari | 138 | 6:00 | 127 | 15:00
| Sreenagar | 139 | 0:00 | 131 | 11:00 | Cox'sbazar | 130 | 7:00 | 119 | 14:00
| Shyampur | 135 | 21:00 | 127 | 12:00 | Chandraghona | 142 | 7:00 | 134 | 15:00
| Shitalakhya | 137 | 22:00 | 127 | 12:00 | Kaptai | 140 | 21:00 | 138 | 1:00
| Matuail | 139 | 9:00 | 125 | 11:00 | A. Khaer Stl. | 139 | 5:00 | 133 | 11:00
| Char Saidpur | 136 | 23:00 | 127 | 11:00 | Bakulia | 141 | 7:00 | 133 | 15:00
| Ullon | 136 | 0:00 | 124 | 11:00 | Julda | 142 | 7:00 | 135 | 15:00
| Hasnabad | 137 | 0:00 | 130 | 13:00 | TK Chemical | 140 | 9:00 | 133 | 15:00
| Magbazar | 135 | 22:00 | 125 | 11:00 | Modern Steel | 138 | 1:00 | 133 | 14:00
| Maniknagar | 138 | 6:00 | 129 | 11:00 | Shahmirpur | 141 | 7:00 | 134 | 19:30
| Bangabhaban | 138 | 6:00 | 129 | 11:00 | Khagrachhari | 141 | 21:00 | 134 | 12:00
| Motijheel | 138 | 6:00 | 129 | 11:00 | Matarbari | 132 | 7:00 | 121 | 15:00
| Narinda | 138 | 6:00 | 129 | 11:00 | Baroiar Hat | 139 | 1:00 | 134 | 15:00
| Kazla | 138 | 6:00 | 129 | 11:00 | Rangamati | 140 | 6:00 | 133 | 15:00
| Dhanmondi | 135 | 5:00 | 124 | 12:00 | Agrabad | 140 | 6:00 | 132 | 15:00
| Lalbag | 139 | 0:00 | 131 | 11:00 | Rampur | 139 | 8:00 | 133 | 16:00
| Madartek | 135 | 0:00 | 124 | 11:00 | Goalpara S/S | 137 | 3:00 | 130 | 12:00
| Dhaka University | 135 | 0:00 | 124 | 11:00 | Khulna Central S/S | 138 | 2:00 | 132 | 12:00
| Aftabnagar | 135 | 23:00 | 125 | 10:00 | Noapara | 138 | 17:00 | 130 | 12:00
| Fatullah | 136 | 21:00 | 128 | 11:00 | Jessore | 135 | 4:00 | 127 | 8:00
| Nawabganj | 138 | 6:00 | 131 | 11:00 | Benapol | 135 | 21:00 | 126 | 8:00
| Keraniganj | 139 | 22:00 | 131 | 12:00 | Jhenida(Old) | 137 | 3:00 | 130 | 8:00
| Banani | 135 | 0:00 | 125 | 11:00 | Bottail | 138 | 3:00 | 133 | 8:00
| Mirpur | 134 | 0:00 | 126 | 12:00 | G.K Project | 141 | 2:00 | 138 | 7:00
| Kalyanpur | 135 | 0:00 | 128 | 11:00 | Faridpur | 139 | 6:00 | 132 | 18:30
| Gulshan | 134 | 22:00 | 123 | 11:00 | Rajbari | 138 | 1:00 | 131 | 19:00
| Uttara | 138 | 4:00 | 130 | 11:00 | Madaripur | 142 | 4:00 | 134 | 18:30
| Uttara New | 139 | 3:00 | 131 | 11:00 | Shariyatpur S/S | 141 | 3:00 | 133 | 19:00
| Kamrangirchar | 139 | 0:00 | 127 | 20:00 | Gopalganj | 141 | 2:00 | 132 | 19:00
| Savar | 136 | 0:00 | 128 | 11:00 | Bagerhat | 137 | 5:00 | 129 | 12:00
| Bhasantec | 139 | 5:00 | 135 | 20:00 | Mongla | 136 | 16:00 | 130 | 12:00
| Agargaon | 141 | 1:00 | 131 | 12:00 | Satkhira | 137 | 4:00 | 129 | 11:00
| Satmosjid | 140 | 6:00 | 131 | 12:00 | Gallamari | 140 | 4:00 | 131 | 19:00
| Old Tongi | 139 | 21:00 | 133 | 11:00 | Magura | 137 | 2:00 | 130 | 7:00
| Kabirpur | 136 | 23:00 | 124 | 11:00 | Narail | 136 | 4:00 | 129 | 8:00
| Manikgonj | 132 | 5:00 | 122 | 16:00 | Chuadanga | 133 | 4:00 | 124 | 12:00
| Joydevpur | 143 | 00:00 | 137 | 15:00 | Barisal(N) | 141 | 7:00 | 135 | 18:30
| New Tongi | 139 | 3:00 | 132 | 11:00 | Barisal (S) | 141 | 4:00 | 135 | 18:30
| Kodda | 141 | 13:00 | 133 | 11:00 | Patuakhali(S) | 138 | 8:00 | 133 | 18:30
| Dhamrai | 141 | 00:00 | 129 | 11:00 | Bhandaria | 140 | 4:00 | 132 | 19:00
| Rajendrapur | 138 | 8:00 | 130 | 12:00 | Barguna | 142 | 6:00 | 134 | 19:00
| Bashundara | 139 | 00:00 | 131 | 11:00
| Purbachal | 134 | 21:00 | 126 | 11:00 | Ishurdi | 140 | 21:00 | 135 | 12:00
| Tongi Millgate | 139 | 0:00 | 131 | 11:00 | Ruppur Paromanobik | 139 | 2:00 | 135 | 9:00
| Bashundhara Cement |  |  |  |  | Natore | 139 | 1:00 | 133 | 8:00
| Valuka | 125 | 2:00 | 105 | 15:00 | Bogra | 138 | 2:00 | 131 | 8:00
| Tangail | 134 | 3:00 | 119 | 15:00 | Noagaon | 133 | 3:00 | 131 | 8:00
| Mymensing | 127 | 1:00 | 112 | 18:00 | Rajshahi | 138 | 19:30 | 131 | 12:00
| Kishorganj | 131 | 6:00 | 119 | 15:00 | Rajshahi New | 138 | 19:30 | 131 | 7:00
| Netrokona | 127 | 5:00 | 105 | 18:00 | C.Nawabganj | 135 | 2:00 | 129 | 8:00
| Jamalpur | 135 | 1:00 | 120 | 8:00 | Amnura | 137 | 19:30 | 127 | 7:00
| Sherpur | 134 | 2:00 | 117 | 19:00 | Pabna | 138 | 2:00 | 133 | 12:00
| Srimongal | 139 | 5:00 | 133 | 19:00 | Shahjadpur | 144 | 2:00 | 136 | 10:00
| Shahjibazar | 138 | 4:00 | 132 | 11:00 | Serajganj | 139 | 3:00 | 130 | 8:00
| Fenchuganj | 138 | 6:00 | 130 | 15:00 | Niyamatpur | 132 | 24:00 | 120 | 8:00
| Khulawara | 137 | 2:00 | 129 | 18:30 | Joypurhat | 135 | 20:00 | 122 | 8:00
| Sylhet | 133 | 5:00 | 124 | 18:30 | Sherpur(Bogura) | 139 | 24:00 | 131 | 8:00
| Chatak | 133 | 6:00 | 122 | 18:30 | Mohastangor | 138 | 2:00 | 129 | 8:00
| Sunamganj | 131 | 4:00 | 119 | 18:00 | Bhangura | 140 | 2:00 | 133 | 8:00
| Biani Bazar | 133 | 5:00 | 121 | 18:30 | Rangpur | 134 | 2:00 | 121 | 9:00
| Comilla(s) | 132 | 22:00 | 127 | 12:00 | Lalmonirhat | 131 | 4:00 | 123 | 13:00
| Comilla(n) | 141 | 6:00 | 133 | 11:00 | Saidpur | 132 | 19:30 | 120 | 7:00
| Chandpur | 143 | 19:30 | 138 | 2:00 | Purbasadipur | 134 | 19:30 | 120 | 7:00
| Feni | 140 | 5:00 | 134 | 15:00 | Thakurgaon | 136 | 23:00 | 120 | 7:00
| Chowmuhani | 139 | 7:00 | 134 | 16:00 | Palashbari | 134 | 24:00 | 114 | 7:00
| Ashuganj | 140 | 3:00 | 135 | 12:00 | Barapukuria | 134 | 24:00 | 126 | 7:00
| Daudkandi | 137 | 5:00 | 129 | 11:00 | Panchagar | 136 | 19:30 | 114 | 7:00
| B.Baria | 136 | 06:0 | 130 | 15:00 | Joldhaka | 132 | 21:00 | 118 | 7:00
| Ramganj | 140 | 7:00 | 137 | 1:00 | Kurigram | 131 | 1:00 | 120 | 13:00
| Chaddagram | 140 | 6:00 | 134 | 15:00 | Mithapukur | 136 | 2:00 | 125 | 7:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 226 | 7308 | 3198 | 10506 |  |  |  | QF-LDC-11
0:30 | 245 | 6852.5 | 3051 | 9903.5 | Date: | 2022-03-14
1:00 | 264 | 6397 | 2904 | 9301
1:30 | 273 | 6290.5 | 2834.5 | 9125
2:00 | 282 | 6184 | 2765 | 8949
2:30 | 292 | 6043.5 | 2727 | 8770.5 | [5 empty] | Gen. at Eve. Peak | 11899 | 11899 MW (21:00 )
3:00 | 302 | 5903 | 2689 | 8592 | [6 empty] | 21:00
3:30 | 297 | 5859 | 2641.5 | 8500.5 | [5 empty] | Gen. at Day Peak | 10873 | 10873 MW (12:00 )
4:00 | 292 | 5815 | 2594 | 8409 | [6 empty] | 12:00
4:30 | 301 | 5791.5 | 2588 | 8379.5 | [5 empty] | Highest Generation | 11899
5:00 | 310 | 5768 | 2582 | 8350 | [6 empty] | 21:00
5:30 | 266 | 5798 | 2659.5 | 8457.5
6:00 | 222 | 5828 | 2737 | 8565
6:30 | 133 | 5939.5 | 2765.5 | 8705
7:00 | 44 | 6051 | 2794 | 8845
7:30 | 44 | 6242.5 | 2922.5 | 9165
8:00 | 44 | 6434 | 3051 | 9485
8:30 | 108 | 6617.5 | 3077.5 | 9695
9:00 | 172 | 6801 | 3104 | 9905
9:30 | 206 | 6903 | 3122.5 | 10025.5
10:00 | 240 | 7005 | 3141 | 10146
10:30 | 246 | 7086 | 3192.5 | 10278.5
11:00 | 252 | 7167 | 3244 | 10411
11:30 | 271 | 7336.5 | 3305.5 | 10642
12:00 | 290 | 7506 | 3367 | 10873
12:30 | 308 | 7542.5 | 3463.5 | 11006
13:00 | 326 | 7579 | 3560 | 11139
13:30 | 329 | 7563 | 3535 | 11098
14:00 | 332 | 7547 | 3510 | 11057
14:30 | 383 | 7575 | 3511.5 | 11086.5
15:00 | 434 | 7603 | 3513 | 11116
15:30 | 443 | 7592 | 3495.5 | 11087.5
16:00 | 452 | 7581 | 3478 | 11059
16:30 | 464 | 7469.5 | 3434 | 10903.5
17:00 | 476 | 7358 | 3390 | 10748
17:30 | 471 | 7411 | 3417.5 | 10828.5
18:00 | 466 | 7464 | 3445 | 10909
18:30 | 432 | 7705 | 3672 | 11377
19:00 | 398 | 7946 | 3899 | 11845
19:30 | 396 | 7934 | 3925 | 11859
20:00 | 302 | 7963 | 3903 | 11866 |  |  |  | Executive Engineer
20:30 | 273 | 7993.5 | 3889 | 11882.5 |  |  |  | Network Operation Division
21:00 | 244 | 8024 | 3875 | 11899
21:30 | 230 | 7937 | 3739.5 | 11676.5
22:00 | 216 | 7850 | 3604 | 11454 |  |  |  |  | Page 6 of 7
22:30 | 219 | 7705.5 | 3480.5 | 11186
23:00 | 222 | 7561 | 3357 | 10918
23:30 | 224 | 7434.5 | 3277.5 | 10712
24:00 | 226 | 7308 | 3198 | 10506
11899 MW (21:00 )
10873 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-14 |  | Energy |  | 249592049
[13 empty] | 2022-03-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2697 | 719 | 1718 | 148 | 3900 | 762 | 81 | 0 | 361 | 120 | 0 | 0
0:30 | 2879 | 715 | 1634.5 | 74 | 3610 | 631 | 63.5 | 0 | 180.5 | 116 | 0 | 0 | Date: | 2022-03-14
1:00 | 3061 | 711 | 1551 | 0 | 3320 | 500 | 46 | 0 | 0 | 112 | 0 | 0
1:30 | 3091.5 | 710.5 | 1554.5 | 0 | 3111 | 499.5 | 46 | 0 | 0 | 112 | 0 | 0 | [8 empty] | Total Energy | 249.592 | Total Energy Gen 249.592 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.592 MKWHr
2:00 | 3122 | 710 | 1558 | 0 | 2902 | 499 | 46 | 0 | 0 | 112 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3129.5 | 710.5 | 1561.5 | 0 | 2714.5 | 499.5 | 46 | 0 | 0 | 109 | 0 | 0 | [8 empty] | Energy Requirement | 249.592
3:00 | 3137 | 711 | 1565 | 0 | 2527 | 500 | 46 | 0 | 0 | 106 | 0 | 0
3:30 | 3093 | 711 | 1567.5 | 0 | 2479 | 500 | 46 | 0 | 0 | 104 | 0 | 0 | [6 empty] | Shortage
4:00 | 3049 | 711 | 1570 | 0 | 2431 | 500 | 46 | 0 | 0 | 102 | 0 | 0
4:30 | 3022 | 710.5 | 1569.5 | 0 | 2431.5 | 500 | 46 | 0 | 0 | 100 | 0 | 0
5:00 | 2995 | 710 | 1569 | 0 | 2432 | 500 | 46 | 0 | 0 | 98 | 0 | 0
5:30 | 2995 | 710 | 1572 | 0 | 2537.5 | 500 | 46 | 0 | 0 | 97 | 0 | 0
6:00 | 2995 | 710 | 1575 | 0 | 2643 | 500 | 46 | 0 | 0 | 96 | 0 | 0
6:30 | 3013 | 710.5 | 1561 | 0 | 2774.5 | 500 | 46 | 0 | 0 | 94 | 6 | 0 |  |  |  |  | Coal
7:00 | 3031 | 711 | 1547 | 0 | 2906 | 500 | 46 | 0 | 0 | 92 | 12 | 0
7:30 | 3007.5 | 711 | 1544.5 | 52 | 3132.5 | 500 | 46 | 0 | 31.5 | 98 | 42 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2984 | 711 | 1542 | 104 | 3359 | 500 | 46 | 0 | 63 | 104 | 72 | 0
8:30 | 2968 | 711 | 1535 | 148.5 | 3463 | 499.5 | 46 | 0 | 115.5 | 108 | 100.5 | 0
9:00 | 2952 | 711 | 1528 | 193 | 3567 | 499 | 46 | 0 | 168 | 112 | 129 | 0
9:30 | 2937 | 710.5 | 1531.5 | 250 | 3597 | 499.5 | 46 | 0 | 191.5 | 110 | 152.5 | 0
10:00 | 2922 | 710 | 1535 | 307 | 3627 | 500 | 46 | 0 | 215 | 108 | 176 | 0
10:30 | 2932 | 710 | 1523.5 | 350.5 | 3671 | 500 | 46 | 0 | 250.5 | 107 | 188 | 0
11:00 | 2942 | 710 | 1512 | 394 | 3715 | 500 | 46 | 0 | 286 | 106 | 200 | 0
11:30 | 2942 | 710 | 1523 | 564 | 3744.5 | 504.5 | 46 | 0 | 286 | 117 | 205 | 0
12:00 | 2942 | 710 | 1534 | 734 | 3774 | 509 | 46 | 0 | 286 | 128 | 210 | 0
12:30 | 2916.5 | 710 | 1524.5 | 829.5 | 3780 | 524.5 | 63.5 | 30 | 291.5 | 131 | 205 | 0
13:00 | 2891 | 710 | 1515 | 925 | 3786 | 540 | 81 | 60 | 297 | 134 | 200 | 0
13:30 | 2891 | 710 | 1515 | 925 | 3786 | 540 | 81 | 60 | 297 | 134 | 200 | 0
14:00 | 2891 | 710 | 1515 | 925 | 3786 | 540 | 81 | 60 | 297 | 134 | 200 | 0
14:30 | 2933.5 | 710.5 | 1518.5 | 823.5 | 3830 | 554.5 | 81 | 50 | 328 | 129 | 169 | 0
15:00 | 2976 | 711 | 1522 | 722 | 3874 | 569 | 81 | 40 | 359 | 124 | 138 | 0
15:30 | 2954.5 | 710.5 | 1524 | 738 | 3848.5 | 594 | 81 | 40 | 362.5 | 120 | 114.5 | 0
16:00 | 2933 | 710 | 1526 | 754 | 3823 | 619 | 81 | 40 | 366 | 116 | 91 | 0
16:30 | 2868 | 710 | 1518.5 | 638 | 3828.5 | 637 | 81 | 40 | 369.5 | 118 | 62.5 | 0
17:00 | 2868 | 710 | 1511 | 522 | 3834 | 655 | 81 | 40 | 373 | 120 | 34 | 0
17:30 | 2870 | 710 | 1550.5 | 487.5 | 3850 | 666.5 | 81 | 65 | 412.5 | 118 | 17.5 | 0
18:00 | 2872 | 710 | 1590 | 453 | 3866 | 678 | 81 | 90 | 452 | 116 | 1 | 0
18:30 | 2880 | 710.5 | 1631.5 | 708.5 | 3885.5 | 728 | 81 | 136 | 490.5 | 125 | 0.5 | 0
19:00 | 2888 | 711 | 1673 | 964 | 3905 | 778 | 81 | 182 | 529 | 134 | 0 | 0
19:30 | 2877 | 710 | 1654 | 972 | 3918 | 798 | 81 | 183 | 538 | 128 | 0 | 0
20:00 | 2888 | 710 | 1660 | 973 | 3918 | 787 | 81 | 181 | 534 | 134 | 0 | 0
20:30 | 2866.5 | 710.5 | 1688.5 | 973.5 | 3933 | 782 | 81 | 181.5 | 533 | 133 | 0 | 0
21:00 | 2845 | 711 | 1717 | 974 | 3948 | 777 | 81 | 182 | 532 | 132 | 0 | 0
21:30 | 2842.5 | 711 | 1705 | 776 | 3951 | 777.5 | 81 | 170 | 532.5 | 130 | 0 | 0
22:00 | 2840 | 711 | 1693 | 578 | 3954 | 778 | 81 | 158 | 533 | 128 | 0 | 0
22:30 | 2848.5 | 712.5 | 1706 | 415 | 3929.5 | 777.5 | 81 | 114 | 479 | 123 | 0 | 0
23:00 | 2857 | 714 | 1719 | 252 | 3905 | 777 | 81 | 70 | 425 | 118 | 0 | 0
23:30 | 2777 | 716.5 | 1718.5 | 200 | 3902.5 | 769.5 | 81 | 35 | 393 | 119 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.5° C
24:00 | 2697 | 719 | 1718 | 148 | 3900 | 762 | 81 | 0 | 361 | 120 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 249.592 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.592 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1105380
2 | Karnaphuli Hydro PP Unit-4 & 5 | [12 empty] | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 400000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 14 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 345468
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 7 | 13 | 17 | 19 | 19 | 19 | 16 | 12 | 8 | 3 | [9 empty] | 134865
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 33 |  | 51 | 51 | 51 | 51 | 51 |  |  | 222324
12 | Hathazari 100 MW peaking PP | [17 empty] | 5 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 77449
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 97 | 90 | 68 | 68 | 68 | 68 | 72 | 88 | 83 | 89 | 89 | 89 | 79 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2085054
| Daudkandi 200 MW PP (B.Trac) | [10 empty] | 20 | 120 | 200 | 150 | 150 | 120 | 80 | 80 |  | 200 | 200 | 200 | 200 | 80 |  |  | 1615104
14 | Titas 50 MW Peaking PP | [10 empty] | 40 | 40 | 39 | 37 | 38 | 38 | 38 | 40 |  | 40 | 33 | 36 | 41 | 42 | 41 | 41 | 544432
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 90 | 90 | 90 | 90 | 90 | [8 empty] | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1615437
18 | Kodda 300 MW PP Unit-2 (Summit) | 298 | 195 | 60 | 30 | 30 | 33 | 144 | 255 | 278 | 291 | 296 | 298 | 296 | 298 | 296 | 296 | 296 | 298 |  | 298 | 300 | 300 | 298 | 300 | 300 | 298 | 5956580
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 78 | 86 | 86 | 76 | 86 | 76 | 123 |  | 152 | 152 | 153 | 182 | 182 | 182 | 182 | 2442181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 290 | 290 | 280 | 270 | 260 | 260 | 260 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6709264
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 27 | 24 | 25 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 656856
33 | Ashuganj 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 219 | 219 | 218 | 217 | 220 | 218 | 214 | 214 | 212 | 209 | 210 | 210 | 210 |  | 213 | 215 | 214 | 217 | 220 | 201 | 176 | 5186000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 320 | 330 | 350 | 345 | 325 | 320 | 355 | 320 | 345 | 325 | 315 | 320 | 315 | 320 | 340 | 320 | 315 | 330 |  | 320 | 315 | 325 | 315 | 320 | 355 | 320 | 8274500
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 50 | 48 | 45 | 45 | 46 | 50 |  | 53 | 53 | 54 | 54 | 55 | 56 | 56 | 1237440
36 | Chandpur 150 MW CCPP | 92 | 91 | 91 | 92 | 90 | 87 | 90 | 89 | 90 | 91 | 90 | 90 | 84 | 85 | 92 | 92 | 90 | 90 |  | 90 | 87 | 90 | 85 | 85 | 91 | 90 | 2122410
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 245 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6306050
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 104 | 106 | 106 | 106 | 106 | 107 | 107 | 96 | 69 | 69 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 84 |  | 82 | 84 | 84 | 84 | 88 | 101 | 104 | 1994880
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 16 | 30 | 42 | 47 | 50 | 45 | 39 | 30 | 20 | 7 | 0 | [8 empty] | 329950
44 | Fenchugonj CCPP Phase-1 | [11 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 310000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720000
46 | Shajibazar 330 MW CCPP | 227 | 176 | 147 | 148 | 160 | 160 | 159 | 160 | 160 | 157 | 156 | 156 | 156 | 156 | 154 | 157 | 157 | 158 |  | 157 | 158 | 158 | 158 | 158 | 158 | 156 | 3643000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 50 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1398048
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 86 | 86 | 89 | 89 | 85 | 84 | 84 | 84 | 86 | 87 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2075520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245880
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 2 | 2 | 2 | 5 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 204720
55 | Fenchugonj 51 MW PP (Barakatullah) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 51 | 51 | 51 | 51 | 1171200
56 | Shahjahanulla 25 MW PP | 21 | 21 | 21 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 22 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 527376
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 290 | 295 | 300 | 300 | 300 | 280 | 300 | 300 | 305 | 290 | 295 | 295 | 270 | 290 | 300 | 290 | 290 |  | 300 | 275 | 280 | 290 | 270 | 280 | 295 | 7257500
| Bibiyana South 400 MW |  | 175 | 200 | 180 | 150 | 200 | 180 | 150 | 245 | 220 | 220 | 260 | 250 | 260 | 253 | 261 | 264 | 265 |  | 265 | 263 | 264 | 265 | 265 | 265 | 15 | 5014800
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 17 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1238108
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 15 | [7 empty] | 6 | 22 | 22 | 22 | 397200
60 | Barabkunda 22 MW PP (Regent) | [26 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 463104
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 20 | 20 | 17 | 17 | 19 | 19 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 420084
63 | Impoprt (Tripura) | 112 | 112 | 106 | 102 | 98 | 96 | 92 | 104 | 112 | 108 | 106 | 128 | 134 | 130 | 124 | 116 | 120 | 116 |  | 134 | 128 | 134 | 132 | 128 | 118 | 120 | 2802240
64 | Malancha, Ctg. EPZ (United) | 37 | 39 | 40 | 42 | 42 | 40 | 39 | 8 | 3 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 3 | 2 |  | 10 | 16 | 15 | 26 | 34 | 39 | 39 | 465600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 17 | 17 | 17 | 18 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 467712
66 | Feni 11 MW PP (Doreen) | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 7 | 3 | 3 | 11 | 11 |  | 7 | 7 | 7 | 7 | 7 | 7 | 11 | 217260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 31 | 27 | 24 | 24 | 24 | 20 | 17 | 16 | 16 | 16 | 33 | 33 | 33 | 31 |  | 30 | 32 | 33 | 33 | 33 | 33 | 33 | 692200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 21 | 21 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 516930
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 30 | 30 | 29 | 29 | 28 | 28 | 25 | 28 | 28 |  | 26 | 28 | 29 | 29 | 29 | 29 | 29 | 651600
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 776160
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811200
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 102 | 98 | 98 | 98 | 95 | 98 | 101 | 101 | 101 | 98 | 98 | 101 | 101 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2382590
| Feni Lanka Power | 52 |  |  |  |  | 34 | 80 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2059980
| Chowmuhani 113 MW | 116 | 117 | 117 | 116 | 117 | 117 | 117 | 116 | 116 | 116 | 110 | 107 | 115 | 115 | 110 | 110 | 115 | 115 |  | 115 | 117 | 116 | 115 | 116 | 117 | 110 | 2769480
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 150 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3718080
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 8 |  |  |  |  | 6 | 16 | 26 | 51 | 42 | 42 | 49 | 49 | 49 | 49 | 40 | 40 | 49 |  | 49 | 49 | 50 | 50 | 50 | 42 | 51 | 824640
79 | Kodda 150MW PP | [7 empty] | 48 | 115 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2351040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 45 | 41 | 43 | 43 | 38 | 35 | 41 | 42 | 35 | 40 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1080451
| Gazipur 100 MW PP | 105 | 105 | 70 | 35 | 35 | 38 | 70 | 85 | 90 | 90 | 90 | 96 | 105 | 105 | 105 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2116800
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 29881
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1215867
| Karnaphuli Power Ltd. | 110 | 102 | 110 | 110 | 110 | 102 | 110 | 110 | 110 | 110 | 110 | 107 | 92 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2647079
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 270 | 270 | 270 | 270 | 270 | 280 | 280 | 285 | 275 | 285 | 265 | 275 | 250 | 240 | 285 | 265 | 265 | 285 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6651433
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 92 | 92 | 92 | 92 | 92 | 92 | 85 | 82 | 93 | 93 | 94 | 92 | 84 | 92 | 93 | 81 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2190720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | [5 empty] | 6 | 40 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 |  | 93 | 100 | 97 | 100 | 100 | 100 | 100 | 1599240
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1192829
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 24 |  |  |  | 24 | 40 | 70 | 84 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1708992
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 24 | 25 | 25 | 25 | 31 | 42 | 44 | 50 | 50 | 50 | 50 | 49 | 49 | 48 | 49 | 50 |  | 50 | 48 | 49 | 50 | 50 | 50 | 50 | 1079520
96 | Chattogram 108 MW PP (ECPV) | 96 | 98 | 94 | 91 | 91 | 92 | 28 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 7 | 6 |  | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 753600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 |  |  |  |  | 5 | 15 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 887151
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 841523
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13450
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1302840
104 | Keranigonj 300 MW PP (APR) | [7 empty] | 24 | 53 | 108 | 155 | 304 | 298 | 210 | 202 | 304 | 132 | 103 |  | 306 | 305 | 305 | 307 | 251 | 52 | 23 | 3198328
105 | Bramhangoan 100 MW PP (Aggreko) | [7 empty] | 30 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 1559385
106 | Mymensingh 200 MW PP (United) | 178 | 177 | 177 | 178 | 187 | 179 | 179 | 179 | 179 | 179 | 178 | 178 | 177 | 176 | 174 | 174 | 175 | 175 |  | 184 | 185 | 186 | 187 | 188 | 197 | 188 | 4233600
112 | Aurahati 100MW PP (Aggreko) | [7 empty] | 50 | 70 | 99 | 99 | 100 | 99 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 99 | 100 | 100 | 100 | 55 | 1568086
114 | Kodda 149 MW PP Unit-1 (Summit) | 140 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3605330
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2099520
116 | Chandpur 200MW (Desh energy) | 18 | [5 empty] | 8 | 45 | 67 | 92 | 189 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3082080
117 | Ashuganj 150MW PP (Midland) | 141 | 147 | 147 | 148 | 145 | 148 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 142 | 133 | 118 | 115 | 113 |  | 125 | 136 | 137 | 143 | 148 | 147 | 150 | 3419054
118 | Bibiyana-III 400 MW CCPP | 364 | 364 | 363 | 364 | 363 | 364 | 364 | 364 | 314 | 316 | 316 | 240 | 241 | 241 | 240 | 241 | 241 | 240 |  | 240 | 241 | 240 | 241 | 240 | 240 | 401 | 7181000
| Jamalpur 115 MW PP (United) | 108 | 80 | 78 | 78 | 78 | 85 | 107 | 108 | 108 | 99 | 89 | 98 | 98 | 107 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2403600
| Anwara 300 MW PP (United) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 282 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 280 | 280 | 281 | 6937636
| Juldah unit-2 (Acorn) | 100 | 100 | 80 | 70 | 70 | 87 | 100 | 100 | 100 | 97 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2234880
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2703545
| Bhairob 54.5 MW | 36 | 36 |  | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 685080
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 10 | 19 | 26 | 29 | 32 | 31 | 27 | 21 | 13 | 5 | 0 | [8 empty] | 215561
| Chandpur 115(Doreen) | 34 | [5 empty] | 5 | 41 | 40 | 39 | 51 | 96 | 100 | 100 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1535040
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 39 | 25 | 31 | 32 |  |  |  | 34 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1077840
120 | Eastern Zone Total | 6397 | 6184 | 5903 | 5815 | 5768 | 5828 | 6051 | 6434 | 6801 | 7005 | 7167 | 7506 | 7579 | 7547 | 7603 | 7581 | 7358 | 7464 |  | 7946 | 7934 | 7963 | 8024 | 7850 | 7561 | 7308 | 169605817
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 4 |  | 21 | 36 | 40 | 33 | 33 | 31 | 31 | 176640
| Khulna 225 MW CCPP | [12 empty] | 60 | 40 | 40 | 40 | 40 | 80 |  | 157 | 158 | 157 | 158 | 158 | 70 | 0 | 1113137
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2708160
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 33 | 58 | 78 | 90 | 93 | 88 | 81 | 63 | 42 | 17 | 1 | [8 empty] | 656640
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 222 | 221 | 221 | 221 | 220 | 222 | 222 | 218 | 214 | 214 | 214 | 210 | 209 | 210 | 210 | 213 |  | 216 | 216 | 216 | 220 | 209 | 220 | 220 | 5218909
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 13 |  | 21 | 21 | 21 | 21 | 21 | 21 | 11 | 327252
| Bhola 225 MW CCPP | 90 | 90 | 90 | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 89 | 89 | 88 | 89 | 89 | 89 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2203104
140 | Bhola 33 MW PP (Venture) | 24 | 24 | 23 | 22 | 21 | 21 | 19 | 18 | 17 | 17 | 18 | 19 | 22 | 22 | 23 | 26 | 24 | 24 |  | 28 | 28 | 28 | 29 | 28 | 27 | 21 | 536900
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 |  | 10 | 63 | 50 | 50 | 80 | 60 | 20 |  | 90 | 99 | 99 | 99 |  |  |  | 705600
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 10 | 10 | [5 empty] | 12160
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 711 | 710 | 711 | 711 | 710 | 710 | 711 | 711 | 711 | 710 | 710 | 710 | 710 | 710 | 711 | 710 | 710 | 710 |  | 711 | 710 | 710 | 711 | 711 | 714 | 719 | 17201454
147 | Bheramara 410 MW CCPP | 410 | 340 | 340 | 280 | 280 | 310 | 330 | 360 | 320 | 330 | 380 | 410 | 390 | 380 | 360 | 345 | 325 | 310 |  | 290 | 284 | 285 | 275 | 270 | 265 | 255 | 8106624
148 | Payra 1320 MW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 310 | 340 | 350 | 360 | 380 | 380 | 400 |  | 500 | 520 | 510 | 500 | 500 | 500 | 480 | 9730600
149
150 | Barapukuria TPP Unit-1 | [14 empty] | 10 | 40 | 76 | 79 |  | 79 | 79 | 78 | 78 | 79 | 78 | 83 | 602181
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 199 | 200 | 200 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4863800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [9 empty] | 12 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 592144
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 5 | 4 | 3 | 1 | 0 | 0 | [8 empty] | 33480
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 219 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 218 | 217 | 217 | 213 | 211 | 211 | 209 | 192 | 151 | 158 |  | 186 | 191 | 188 | 179 | 170 | 163 | 165 | 5008436
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 217 | 214 | 213 | 213 | 212 | 213 | 210 | 202 |  | 186 | 176 | 173 | 159 | 157 | 151 | 144 | 5133109
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [8 empty] | 5 | 5 | 6 | 6 | 8 | 30 | 36 | 43 | 43 | 43 |  | 46 | 45 | 44 | 44 | 44 | 42 | 35 | 459020
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 19 | 19 | 18 | 18 | 21 |  | 21 | 21 | 21 | 22 | 21 | 21 | 21 | 488880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196344
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 50 | 50 | 50 | 50 | 50 |  |  | 637688
167 | Katakhali 50 MW Peaking PP | [12 empty] | 10 | 24 | 24 | 24 | 27 | 32 |  | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 322479
168 | Santahar 50 MW Peaking PP | [14 empty] | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 190991
169 | Natore 52 MW PP (Rajlanka) | 25 |  |  |  |  | 18 | 39 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 963840
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 15 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 81 |  | 93 | 93 | 93 | 93 | 93 | 41 | 0 | 1015824
171 | Baghabari 200 MW PP (Paramount) | [10 empty] | 20 | 100 | 165 | 120 | 120 | 50 | 50 | 50 |  | 168 | 168 | 170 | 168 | 47 |  |  | 1284299
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 94 | 113 | 113 | 113 | 113 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 94 | 94 |  | 105 | 97 | 97 | 113 | 113 | 113 | 113 | 2652672
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 70 | 70 | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2643840
173 | Rangpur 20 MW GTPP | [19 empty] | 15 | 15 | 14 | 14 |  |  |  | 46000
175 | Saidpur 20 MW GTPP | [17 empty] | 10 |  | 10 | 10 | 10 | 10 |  |  |  | 34000
176 | Rangpur 113 MW PP (Confidence) | 113 | 70 | 34 |  |  | 54 | 70 | 82 | 105 | 106 | 102 | 100 | 98 | 102 | 102 | 102 | 103 | 112 |  | 111 | 111 | 112 | 112 | 113 | 113 | 113 | 2142547
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 6 | 6 | 5 | 4 | 2 | 0 | [8 empty] | 42591
178 | Energypac Power Venture Thakurgaon Ltd. | [7 empty] | 118 | 118 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1934887
178