## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-16 | Wednesday
|  |  | Date (day): | 2022-03-16 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12312.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12903 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-15 | 2022-03-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 230 | 300 | 280 | 300 | 65 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 98 | 102 | 102 | 102
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 280 | 280 | 280 | 170 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 275 | 220 | 285 | 300 | 35 |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 90 | 140 | 140 | 140 | 195 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 51 | 54 | 54 |  | 26 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 286 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 301 | 304 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 100 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 98 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 85 | 92 | 92 | 92 |  | 12 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 48 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 2926 | 3059 | 3035 | 3140 | 1138 | 1377
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 81 | 81 | 81 | 81 |  | 149 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 89 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 4 | 26 | 25 | 25 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 72 | 72 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 26 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 94 | 92 | 90 | 90 |  |  | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 281 | 281 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 113 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1170 | 1278 | 1324 | 1314 | 180 | 885
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 220 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 320 | 300 | 330 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 100 | 300
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 26 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 178 | 175 | 177 | 177 | 18 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 137 | 150 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 35 | 41 | 41 |  | 11
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 83 | 90 | 90 |  | 73 | Engine problem.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 180 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 7 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 138 | 152 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 11 | 21 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 200 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 96 | 100 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 107 | 115 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 36 | 36 | 36 |  | 18 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 115 | 115 | 98 | 99 | 100 | 100
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1804 | 2131 | 2145 | 2500 | 297 | 111
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 84 | 104 | 100 | 100
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 180 | 190 | 200 | 200 |  |  | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 108 | 108 | 108 |  | 7 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 462 | 444 | 501.6 | 450 | 0 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 32 | 30 | 30 |  | 60 | GT-4 under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Under Maint. |  | 22-03-022
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 156 | 160 | 160 | 170 |  | Gas shortage
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 89 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 19 | 24 | 22 | 22
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 391 | 390 | 400 | 400 | 0 |  | Gas shortage
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 50 | 137 | 260 | 265 | 118 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1181 | 1269 | 1419 | 1424 | 702 | 200
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 720 | 718 | 734 | 734
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 0 | 35 |  | 19 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 100 | 158 | 158 | 158
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 290 | 300 | 300 | 110 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 38 | 99 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1323 | 1397 | 1447 | 1472 | 110 | 88
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 26 | 10 | 10 |  |  | Engine problem
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 91 | 90 | 92 | 102 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 20 | 75 |  | Gas shortage
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 360 | 622 | 500 | 500 |  |  | Line O/L
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 212 | 220 | 225 | 225
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 691 | 970 | 836 | 847 | 177 | 0
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 6 | 43 | 44 | 44 |  | 27 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 50 | 50 | 50
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 23 | 31 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 146 | 199 | 220 | 220
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 180 | 200 | 220
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 25 | 30 |  | 20 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 43 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 54 | 92 | 93 | 93 |  | 11 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 165 | 172 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 898 | 1117 | 1089 | 1248 | 380 | 494
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 68 | 80 | 80 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 9 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 101 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 500 | 505 | 516 | 508 | 74 | 210
|  | Total |  |  |  |  | 22296 | 21215 | 10955 | 12170 | 12312.6 | 12903 | 3058 | 3373
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10345.5887 | 11493 | 11627.6674 | 12185.2242
| A. |  | 2022-03-15 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12170 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8783 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12170 | MW
| 3 | Day peak Generation : |  |  | 10955 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11493 | MW
| 4 | Evening peak Generation : |  |  | 12170 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 255.5292 | MKWHr | By Solar | 1.4152 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 107.8258 | MKWHr |  | By Oil: | 105.9867 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.8757 | MKWHr |  | By Hydro: | 1.9428 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3058 | MW | Dhaka | 4175 | 4175 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3373 | MW | Chittagong | 1244 | 1244 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 6431 | MW | Khulna | 1310 | 1310 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 860.5 | MMCFD |  |  | Rajshahi | 1241 | 1241 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 111581547.456 | ii) Oil : | Taka | 863833894.5 | Comilla | 1044 | 1044 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 86505766.7 | Total | Taka | 1061921208.656 | Mymensingh | 997 | 997 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.128 | MKWHr. | Sylhet | 458 | 458 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 228 | MW (E to W) at | 21:00 | hrs | Barisal | 306 | 306 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -194 | MW at | 7:00 | hrs | Rangpur | 718 | 718 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.0° C |  |  | Total | 11493 | 11493 |  | 0
| B. |  | 2022-03-16 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12903 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11200 | MW
| 4 | Reserve(Generation end) |  |  |  | 603 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 258.2588 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8859 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3804 | MKWHr. | ii) HVDC Flow at Peak Time |  | 718 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1027 | MKWHr. | iii) Maximum HVDC Flow : |  | 720 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.79 |  | (b) Today: | 88.63 |  | (c) Rule Curve: |  | 90.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-15
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 250 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 6 | 46 | 0 | 39 | 0 | 0 | 0 | 320 | 0 | 221 | 177 | 85 | 29 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 21 | 116 | 105 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 300 | 0 | 0 | 180 | 0 | 140 | 0 | 90 | 200 | 147 | 388 | 98 | 90 | 102 | 0 | 281 | 54 | 110 | 114 | 111 | 100 | 25 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 719 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 52 | 0 | 22 | 0 | 8 | 83 | 0 | 199 | 0 | 0 | 0 | 0 | 160 | 0 | 11 | 0 | 138 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 190 | 0 | 0 | 0 | 0 | 115 |  | 7040 | 2952 | 9992 | 2713 | 719 | 1608 | 0 | 3874 | 722 | 81 | 0 | 159 | 116 | 0 | 0 | 88.8
2:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 250 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 29 | 33 | 33 | 25 | 0 | 46 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 60 | 6 | 48 | 0 | 40 | 0 | 0 | 0 | 320 | 0 | 182 | 178 | 84 | 29 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 20 | 114 | 106 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 159 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 265 | 24 | 11 | 0 | 298 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 120 | 147 | 388 | 108 | 90 | 93 | 0 | 281 | 54 | 110 | 114 | 110 | 100 | 50 | 74 | 0 | 162 | 113 | 0 | 13 | 0 | 99 | 55 |  | 719 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 82 | 0 | 199 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 145 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 400 | 214 | 0 | 0 | 0 | 0 | 17 |  | 6710 | 2841 | 9551 | 2713 | 719 | 1628 | 0 | 3551 | 681 | 81 | 0 | 64 | 114 | 0 | 0 | 88.8
3:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 270 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 6 | 50 | 0 | 40 | 0 | 0 | 0 | 320 | 0 | 183 | 177 | 86 | 29 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 21 | 108 | 106 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 0 | 0 | 300 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 0 | 142 | 388 | 108 | 90 | 96 | 0 | 281 | 54 | 102 | 90 | 111 | 100 | 50 | 74 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 720 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 82 | 0 | 199 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 152 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 370 | 219 | 0 | 0 | 0 | 0 | 0 |  | 6320 | 2789 | 9109 | 2712 | 720 | 1668 | 0 | 3169 | 651 | 81 | 0 | 0 | 108 | 0 | 0 | 88.8
4:00 | 0 | 0 | 0 | 0 | 250 | 102 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 15 | 90 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 17 | 50 | 0 | 40 | 0 | 0 | 0 | 320 | 0 | 182 | 177 | 84 | 29 | 56 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 21 | 104 | 106 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 0 | 0 | 300 | 0 | 0 | 189 | 0 | 149 | 0 | 90 | 0 | 143 | 388 | 108 | 90 | 105 | 0 | 280 | 54 | 110 | 17 | 110 | 100 | 50 | 74 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 720 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 159 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 360 | 217 | 0 | 0 | 0 | 0 | 0 |  | 6197 | 2758 | 8955 | 2724 | 720 | 1672 | 0 | 3013 | 641 | 81 | 0 | 0 | 104 | 0 | 0 | 88.79
5:00 | 0 | 0 | 0 | 0 | 240 | 99 | 0 | 0 | 0 |  | 0 | 270 | 260 | 0 | 0 | 15 | 90 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 19 | 48 | 0 | 40 | 0 | 0 | 0 | 320 | 0 | 182 | 177 | 86 | 29 | 56 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 21 | 98 | 107 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 157 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 8 | 0 | 300 | 0 | 0 | 181 | 0 | 149 | 0 | 90 | 0 | 147 | 387 | 107 | 90 | 105 | 0 | 280 | 54 | 103 | 17 | 109 | 100 | 50 | 80 | 0 | 162 | 113 | 0 | 17 | 0 | 0 | 55 |  | 719 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 163 | 0 | 0 | 105 | 0 | 94 | 0 | 70 | 0 | 0 | 50 | 340 | 219 | 0 | 0 | 0 | 0 | 0 |  | 6131 | 2652 | 8783 | 2742 | 719 | 1657 | 0 | 2866 | 620 | 81 | 0 | 0 | 98 | 0 | 0 | 88.79
6:00 | 0 | 0 | 0 | 0 | 230 | 99 | 0 | 0 | 0 |  | 0 | 270 | 280 | 0 | 0 | 15 | 90 | 0 | 0 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 54 | 15 | 55 | 19 | 25 | 29 | 33 | 33 | 8 | 0 | 46 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 7 | 19 | 50 | 0 | 40 | 0 | 0 | 0 | 340 | 0 | 193 | 179 | 85 | 29 | 56 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 21 | 94 | 107 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 310 | 22 | 8 | 0 | 300 | 0 | 0 | 182 | 0 | 149 | 0 | 90 | 0 | 147 | 388 | 108 | 90 | 105 | 0 | 280 | 54 | 110 | 51 | 107 | 100 | 50 | 92 | 0 | 162 | 113 | 0 | 17 | 0 | 10 | 55 |  | 719 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 0 | 172 | 0 | 0 | 105 | 0 | 94 | 0 | 50 | 0 | 0 | 50 | 340 | 221 | 0 | 0 | 0 | 0 | 17 |  | 6310 | 2671 | 8981 | 2782 | 719 | 1711 | 0 | 2966 | 620 | 81 | 0 | 8 | 94 | 0 | 0 | 88.79
7:00 | 0 | 0 | 0 | 0 | 230 | 99 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 35 | 90 | 0 | 0 | 0 | 50 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 33 | 33 | 22 | 0 | 46 | 35 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 18 | 50 | 0 | 37 | 0 | 0 | 0 | 320 | 0 | 186 | 178 | 85 | 29 | 54 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 21 | 108 | 108 | 0 | 20 | 0 | 30 | 30 | 51 | 0 | 0 | 155 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 305 | 22 | 8 | 0 | 300 | 40 | 25 | 182 | 26 | 149 | 2 | 90 | 28 | 143 | 388 | 108 | 90 | 98 | 0 | 281 | 54 | 110 | 98 | 107 | 100 | 50 | 92 | 4 | 162 | 113 | 0 | 17 | 3 | 33 | 55 |  | 720 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 80 | 0 | 199 | 0 | 0 | 0 | 0 | 189 | 0 | 11 | 0 | 175 | 0 | 0 | 105 | 0 | 94 | 0 | 55 | 0 | 0 | 100 | 350 | 221 | 0 | 0 | 0 | 8 | 115 |  | 6770 | 2866 | 9636 | 2753 | 720 | 1692 | 91 | 3412 | 629 | 81 | 0 | 133 | 108 | 17 | 0 | 88.78
8:00 | 0 | 0 | 0 | 0 | 230 | 99 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 75 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 18 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 32 | 50 | 0 | 8 | 0 | 0 | 0 | 315 | 0 | 184 | 178 | 83 | 29 | 54 | 0 | 51 | 0 | 0 | 43 | 19 | 5 | 27 | 17 | 112 | 108 | 0 | 20 | 1 | 30 | 30 | 51 | 0 | 0 | 157 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 270 | 22 | 8 | 0 | 300 | 0 | 25 | 182 | 26 | 149 | 7 | 90 | 51 | 140 | 388 | 108 | 90 | 88 | 1 | 281 | 54 | 110 | 114 | 105 | 100 | 50 | 92 | 14 | 144 | 113 | 0 | 17 | 11 | 79 | 55 |  | 720 | 0 | 280 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 34 | 0 | 20 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 0 | 178 | 0 | 0 | 105 | 0 | 94 | 0 | 55 | 0 | 1 | 113 | 370 | 210 | 0 | 0 | 1 | 31 | 115 |  | 6801 | 3014 | 9815 | 2738 | 720 | 1611 | 51 | 3613 | 649 | 81 | 40 | 133 | 112 | 67 | 0 | 88.78
9:00 | 0 | 0 | 0 | 0 | 230 | 99 | 0 | 0 | 0 |  | 0 | 270 | 285 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 84 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 71 | 50 | 0 | 4 | 0 | 0 | 0 | 320 | 0 | 187 | 180 | 85 | 26 | 56 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 23 | 0 | 112 | 105 | 0 | 20 | 1 | 30 | 30 | 50 | 0 | 0 | 157 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 8 | 0 | 298 | 0 | 25 | 180 | 25 | 149 | 12 | 90 | 51 | 140 | 388 | 107 | 90 | 88 | 3 | 281 | 54 | 110 | 114 | 105 | 100 | 50 | 92 | 26 | 144 | 113 | 0 | 17 | 20 | 100 | 55 |  | 720 | 0 | 275 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 91 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 43 | 0 | 43 | 0 | 20 | 0 | 8 | 79 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 0 | 179 | 0 | 0 | 105 | 0 | 94 | 0 | 55 | 0 | 3 | 113 | 350 | 221 | 0 | 0 | 3 | 55 | 115 |  | 6869 | 3084 | 9953 | 2703 | 720 | 1628 | 50 | 3686 | 629 | 81 | 40 | 181 | 112 | 123 | 0 | 88.78
10:00 | 0 | 0 | 0 | 0 | 230 | 98 | 0 | 0 | 0 |  | 0 | 270 | 265 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 33 | 33 | 21 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 73 | 50 | 0 | 2 | 0 | 0 | 0 | 355 | 0 | 209 | 180 | 85 | 23 | 56 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 25 | 11 | 118 | 83 | 0 | 20 | 2 | 30 | 30 | 48 | 0 | 0 | 157 | 60 | 75 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 8 | 10 | 300 | 210 | 100 | 180 | 96 | 149 | 16 | 90 | 51 | 138 | 390 | 98 | 90 | 89 | 4 | 0 | 54 | 110 | 114 | 108 | 100 | 50 | 92 | 36 | 154 | 113 | 0 | 17 | 27 | 100 | 55 |  | 719 | 0 | 265 | 0 | 0 | 40 | 0 | 0 | 4 | 0 | 0 | 91 | 14 | 0 | 0 | 0 | 0 | 0 | 5 | 48 | 0 | 43 | 20 | 43 | 0 | 21 | 0 | 8 | 77 | 0 | 200 | 0 | 0 | 0 | 0 | 194 | 0 | 11 | 0 | 179 | 0 | 0 | 105 | 80 | 94 | 0 | 104 | 0 | 5 | 113 | 350 | 221 | 0 | 0 | 4 | 73 | 115 |  | 7026 | 3246 | 10272 | 2761 | 719 | 1604 | 496 | 3449 | 627 | 81 | 40 | 210 | 118 | 167 | 0 | 88.77
11:00 | 0 | 0 | 0 | 0 | 230 | 98 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 90 | 50 | 0 | 2 | 0 | 0 | 0 | 355 | 0 | 219 | 180 | 84 | 26 | 53 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 25 | 11 | 122 | 81 | 0 | 20 | 2 | 30 | 30 | 48 | 0 | 0 | 154 | 60 | 84 | 0 | 0 | 0 | 0 | 10 | 310 | 16 | 8 | 100 | 290 | 202 | 100 | 180 | 99 | 149 | 18 | 90 | 51 | 140 | 390 | 108 | 88 | 89 | 4 | 240 | 54 | 110 | 114 | 106 | 90 | 50 | 93 | 42 | 162 | 113 | 0 | 17 | 30 | 100 | 38 |  | 720 | 0 | 270 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 6 | 48 | 0 | 43 | 23 | 43 | 0 | 21 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 177 | 0 | 0 | 105 | 100 | 94 | 0 | 100 | 0 | 6 | 113 | 350 | 212 | 0 | 0 | 5 | 85 | 115 |  | 7414 | 3260 | 10674 | 2741 | 720 | 1633 | 601 | 3703 | 631 | 81 | 40 | 210 | 122 | 192 | 0 | 88.77
12:00 | 0 | 0 | 0 | 0 | 230 | 98 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 4 | 0 | 92 | 94 | 50 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 184 | 178 | 80 | 29 | 53 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 0 | 11 | 138 | 84 | 0 | 20 | 2 | 30 | 20 | 48 | 0 | 0 | 154 | 60 | 81 | 0 | 0 | 0 | 0 | 10 | 310 | 19 | 8 | 200 | 286 | 301 | 100 | 180 | 98 | 149 | 19 | 72 | 51 | 137 | 391 | 109 | 88 | 89 | 4 | 281 | 54 | 110 | 96 | 107 | 90 | 50 | 85 | 45 | 162 | 113 | 0 | 17 | 31 | 98 | 48 |  | 720 | 0 | 270 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 43 | 23 | 43 | 0 | 21 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 146 | 0 | 11 | 38 | 177 | 0 | 0 | 105 | 165 | 94 | 0 | 101 | 0 | 6 | 113 | 360 | 212 | 0 | 0 | 5 | 90 | 115 |  | 7543 | 3412 | 10955 | 2601 | 720 | 1628 | 902 | 3708 | 638 | 81 | 100 | 237 | 138 | 202 | 0 | 88.76
13:00 | 0 | 0 | 0 | 0 | 245 | 98 | 0 | 0 | 0 |  | 0 | 270 | 260 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 17 | 0 | 92 | 95 | 50 | 0 | 3 | 0 | 0 | 0 | 315 | 0 | 184 | 178 | 82 | 29 | 53 | 0 | 43 | 0 | 27 | 43 | 19 | 5 | 25 | 15 | 138 | 84 | 0 | 20 | 2 | 30 | 20 | 48 | 0 | 0 | 154 | 50 | 84 | 0 | 0 | 0 | 0 | 10 | 295 | 19 | 11 | 200 | 283 | 300 | 100 | 178 | 98 | 149 | 18 | 72 | 51 | 135 | 392 | 109 | 88 | 100 | 4 | 281 | 54 | 95 | 96 | 105 | 90 | 50 | 88 | 41 | 162 | 113 | 0 | 33 | 32 | 97 | 55 |  | 719 | 0 | 270 | 0 | 0 | 100 | 0 | 0 | 3 | 0 | 0 | 89 | 18 | 0 | 0 | 0 | 0 | 34 | 17 | 55 | 0 | 43 | 23 | 43 | 0 | 19 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 140 | 0 | 11 | 98 | 177 | 0 | 0 | 105 | 168 | 94 | 0 | 101 | 0 | 6 | 113 | 420 | 210 | 0 | 0 | 5 | 89 | 115 |  | 7630 | 3574 | 11204 | 2657 | 719 | 1600 | 964 | 3721 | 701 | 81 | 100 | 326 | 138 | 197 | 0 | 88.76
14:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 270 | 270 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 16 | 0 | 92 | 95 | 50 | 0 | 3 | 0 | 0 | 0 | 320 | 0 | 184 | 178 | 81 | 29 | 54 | 0 | 43 | 0 | 40 | 43 | 19 | 5 | 33 | 15 | 144 | 84 | 0 | 20 | 2 | 30 | 22 | 50 | 0 | 0 | 155 | 60 | 81 | 0 | 0 | 0 | 0 | 10 | 275 | 19 | 11 | 100 | 295 | 207 | 70 | 186 | 70 | 149 | 15 | 61 | 95 | 127 | 392 | 108 | 88 | 105 | 4 | 281 | 54 | 110 | 96 | 108 | 90 | 50 | 91 | 42 | 162 | 113 | 0 | 36 | 27 | 99 | 55 |  | 718 | 0 | 275 | 0 | 0 | 100 | 0 | 0 | 2 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 43 | 42 | 55 | 0 | 43 | 24 | 43 | 0 | 19 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 155 | 0 | 11 | 20 | 177 | 0 | 0 | 105 | 50 | 94 | 0 | 102 | 0 | 6 | 113 | 410 | 210 | 0 | 0 | 4 | 79 | 115 |  | 7527 | 3409 | 10936 | 2755 | 718 | 1597 | 517 | 3785 | 688 | 81 | 100 | 372 | 144 | 179 | 0 | 88.75
15:00 | 0 | 0 | 0 | 0 | 300 | 98 | 0 | 0 | 0 |  | 0 | 270 | 250 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 48 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 16 | 0 | 82 | 96 | 50 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 186 | 177 | 74 | 25 | 54 | 0 | 51 | 0 | 38 | 40 | 19 | 5 | 33 | 14 | 144 | 96 | 0 | 20 | 2 | 30 | 32 | 45 | 0 | 0 | 154 | 60 | 82 | 0 | 0 | 0 | 0 | 10 | 285 | 19 | 11 | 200 | 296 | 210 | 100 | 186 | 100 | 149 | 11 | 61 | 124 | 125 | 392 | 108 | 88 | 94 | 2 | 281 | 54 | 110 | 80 | 105 | 90 | 45 | 92 | 33 | 162 | 113 | 0 | 36 | 21 | 99 | 42 |  | 716 | 0 | 270 | 0 | 0 | 100 | 0 | 0 | 4 | 0 | 0 | 88 | 19 | 0 | 0 | 0 | 0 | 43 | 44 | 55 | 0 | 43 | 24 | 43 | 0 | 19 | 0 | 8 | 81 | 0 | 200 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 65 | 177 | 0 | 0 | 105 | 170 | 94 | 0 | 100 | 0 | 5 | 113 | 420 | 210 | 0 | 0 | 4 | 63 | 115 |  | 7653 | 3593 | 11246 | 2786 | 716 | 1583 | 845 | 3775 | 701 | 81 | 100 | 374 | 144 | 141 | 0 | 88.75
16:00 | 0 | 0 | 0 | 0 | 300 | 98 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 40 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 48 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 20 | 16 | 0 | 92 | 95 | 44 | 0 | 2 | 0 | 0 | 0 | 330 | 0 | 197 | 177 | 74 | 25 | 48 | 0 | 51 | 0 | 38 | 43 | 22 | 5 | 0 | 14 | 138 | 97 | 0 | 20 | 1 | 30 | 32 | 45 | 0 | 0 | 153 | 60 | 82 | 0 | 0 | 0 | 0 | 9 | 290 | 19 | 11 | 150 | 286 | 210 | 100 | 186 | 100 | 145 | 6 | 71 | 172 | 123 | 393 | 108 | 88 | 102 | 1 | 281 | 54 | 110 | 96 | 109 | 90 | 43 | 84 | 20 | 162 | 113 | 0 | 36 | 12 | 99 | 42 |  | 716 | 0 | 275 | 0 | 0 | 50 | 0 | 0 | 4 | 0 | 0 | 88 | 20 | 0 | 0 | 0 | 0 | 43 | 43 | 46 | 0 | 43 | 24 | 43 | 0 | 19 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 190 | 0 | 11 | 50 | 177 | 0 | 0 | 105 | 70 | 94 | 0 | 95 | 0 | 4 | 113 | 420 | 210 | 0 | 0 | 2 | 41 | 115 |  | 7632 | 3397 | 11029 | 2787 | 716 | 1607 | 680 | 3821 | 698 | 81 | 50 | 364 | 138 | 87 | 0 | 88.74
17:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 270 | 250 | 0 | 0 | 45 | 90 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 24 | 33 | 33 | 48 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 19 | 16 | 0 | 92 | 92 | 49 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 186 | 177 | 68 | 21 | 50 | 0 | 51 | 0 | 38 | 43 | 22 | 5 | 0 | 14 | 132 | 99 | 0 | 20 | 0 | 30 | 32 | 48 | 0 | 0 | 157 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 19 | 11 | 150 | 283 | 236 | 100 | 176 | 100 | 145 | 2 | 71 | 180 | 122 | 391 | 108 | 92 | 105 | 0 | 265 | 54 | 107 | 114 | 114 | 100 | 80 | 84 | 8 | 162 | 113 | 0 | 36 | 4 | 99 | 55 |  | 715 | 0 | 280 | 0 | 0 | 50 | 0 | 0 | 4 | 0 | 0 | 89 | 18 | 0 | 0 | 0 | 0 | 43 | 43 | 54 | 0 | 43 | 24 | 43 | 0 | 21 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 196 | 0 | 11 | 50 | 177 | 0 | 0 | 105 | 70 | 94 | 0 | 100 | 0 | 2 | 113 | 420 | 208 | 0 | 0 | 0 | 16 | 115 |  | 7660 | 3390 | 11050 | 2811 | 715 | 1602 | 706 | 3851 | 698 | 81 | 50 | 372 | 132 | 32 | 0 | 88.74
18:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 280 | 270 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 21 | 25 | 24 | 33 | 33 | 48 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 18 | 51 | 92 | 94 | 50 | 0 | 6 | 0 | 0 | 0 | 320 | 0 | 206 | 178 | 0 | 26 | 51 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 30 | 14 | 144 | 100 | 0 | 20 | 0 | 30 | 32 | 50 | 0 | 0 | 155 | 60 | 88 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 11 | 100 | 284 | 107 | 50 | 177 | 50 | 149 | 0 | 71 | 183 | 135 | 390 | 108 | 105 | 105 | 0 | 281 | 54 | 105 | 114 | 115 | 100 | 102 | 90 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 716 | 0 | 285 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 89 | 22 | 0 | 0 | 0 | 0 | 43 | 43 | 72 | 0 | 43 | 32 | 43 | 21 | 21 | 0 | 8 | 76 | 0 | 200 | 0 | 8 | 0 | 0 | 199 | 0 | 11 | 20 | 176 | 0 | 0 | 105 | 70 | 94 | 0 | 95 | 0 | 0 | 113 | 420 | 213 | 0 | 0 | 0 | 0 | 115 |  | 7507 | 3413 | 10920 | 2834 | 716 | 1633 | 397 | 3880 | 696 | 81 | 58 | 481 | 144 | 0 | 0 | 88.73
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 280 | 250 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 21 | 25 | 26 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 26 | 51 | 92 | 97 | 50 | 0 | 12 | 0 | 0 | 0 | 315 | 0 | 214 | 178 | 0 | 23 | 53 | 0 | 51 | 0 | 42 | 43 | 22 | 11 | 24 | 18 | 160 | 100 | 0 | 20 | 0 | 30 | 32 | 50 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 200 | 290 | 305 | 100 | 179 | 100 | 149 | 0 | 71 | 180 | 142 | 390 | 108 | 105 | 105 | 0 | 281 | 54 | 106 | 114 | 116 | 100 | 116 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 46 |  | 716 | 0 | 285 | 0 | 0 | 158 | 0 | 0 | 24 | 4 | 0 | 90 | 26 | 0 | 0 | 0 | 0 | 43 | 43 | 93 | 0 | 50 | 32 | 43 | 21 | 21 | 0 | 8 | 69 | 0 | 200 | 0 | 8 | 0 | 0 | 201 | 0 | 11 | 72 | 176 | 0 | 0 | 105 | 171 | 94 | 0 | 105 | 0 | 0 | 113 | 520 | 216 | 0 | 0 | 0 | 0 | 115 |  | 8018 | 3833 | 11851 | 2904 | 716 | 1649 | 948 | 3909 | 789 | 81 | 166 | 529 | 160 | 0 | 0 | 88.72
19:30 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 280 | 250 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 26 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 26 | 51 | 93 | 97 | 50 | 0 | 20 | 0 | 0 | 0 | 320 | 0 | 216 | 178 | 0 | 26 | 53 | 0 | 51 | 0 | 42 | 43 | 22 | 7 | 24 | 18 | 158 | 103 | 0 | 20 | 0 | 30 | 32 | 50 | 0 | 0 | 155 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 200 | 298 | 307 | 100 | 188 | 100 | 149 | 0 | 71 | 180 | 146 | 390 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 114 | 117 | 100 | 115 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 717 | 0 | 285 | 0 | 0 | 158 | 0 | 0 | 32 | 8 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 43 | 93 | 0 | 50 | 36 | 43 | 21 | 22 | 0 | 8 | 68 | 0 | 200 | 0 | 8 | 0 | 0 | 204 | 0 | 11 | 98 | 176 | 0 | 0 | 105 | 171 | 94 | 0 | 105 | 0 | 0 | 113 | 622 | 218 | 0 | 0 | 0 | 0 | 115 |  | 8075 | 3984 | 12059 | 2913 | 717 | 1650 | 976 | 3963 | 890 | 81 | 166 | 545 | 158 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 280 | 250 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 26 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 26 | 51 | 100 | 97 | 50 | 0 | 17 | 0 | 0 | 0 | 320 | 0 | 217 | 178 | 0 | 26 | 52 | 0 | 51 | 0 | 42 | 52 | 22 | 7 | 33 | 21 | 152 | 103 | 0 | 20 | 0 | 30 | 32 | 50 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 200 | 300 | 305 | 100 | 189 | 100 | 149 | 0 | 72 | 180 | 148 | 390 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 114 | 115 | 100 | 118 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 718 | 0 | 285 | 0 | 0 | 158 | 0 | 0 | 27 | 8 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 43 | 93 | 0 | 50 | 40 | 43 | 22 | 22 | 0 | 8 | 68 | 0 | 200 | 0 | 8 | 0 | 0 | 205 | 0 | 11 | 98 | 176 | 0 | 0 | 105 | 173 | 94 | 0 | 105 | 0 | 0 | 113 | 622 | 218 | 0 | 0 | 0 | 0 | 115 |  | 8094 | 3988 | 12082 | 2935 | 718 | 1636 | 976 | 3983 | 890 | 81 | 166 | 545 | 152 | 0 | 0 | 88.72
21:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 |  | 0 | 280 | 220 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 26 | 51 | 100 | 92 | 50 | 0 | 26 | 0 | 0 | 0 | 320 | 0 | 220 | 175 | 83 | 26 | 54 | 0 | 51 | 0 | 35 | 52 | 22 | 7 | 33 | 21 | 152 | 104 | 0 | 20 | 0 | 30 | 32 | 50 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 200 | 300 | 304 | 100 | 190 | 100 | 149 | 0 | 72 | 180 | 150 | 390 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 100 | 115 | 100 | 137 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 718 | 0 | 290 | 0 | 0 | 158 | 0 | 0 | 27 | 0 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 43 | 92 | 0 | 50 | 31 | 43 | 27 | 22 | 0 | 8 | 68 | 0 | 200 | 0 | 9 | 0 | 0 | 199 | 0 | 11 | 99 | 180 | 0 | 0 | 105 | 172 | 94 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8181 | 3989 | 12170 | 3042 | 718 | 1616 | 975 | 4004 | 890 | 81 | 167 | 525 | 152 | 0 | 0 | 88.72
22:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 0 | 0 |  | 0 | 280 | 255 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 26 | 40 | 100 | 96 | 50 | 0 | 26 | 0 | 0 | 0 | 330 | 0 | 190 | 178 | 85 | 26 | 56 | 0 | 51 | 0 | 41 | 52 | 22 | 7 | 33 | 21 | 150 | 103 | 0 | 20 | 0 | 30 | 32 | 50 | 0 | 0 | 157 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 80 | 298 | 103 | 100 | 190 | 100 | 149 | 0 | 82 | 182 | 150 | 366 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 114 | 117 | 100 | 205 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 717 | 0 | 310 | 0 | 0 | 40 | 0 | 0 | 27 | 0 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 43 | 92 | 0 | 50 | 31 | 43 | 29 | 22 | 0 | 8 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 193 | 0 | 11 | 0 | 182 | 0 | 0 | 105 | 70 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 220 | 0 | 0 | 0 | 0 | 115 |  | 7956 | 3598 | 11554 | 3084 | 717 | 1663 | 453 | 4034 | 810 | 81 | 40 | 522 | 150 | 0 | 0 | 88.72
23:00 | 0 | 0 | 0 | 0 | 300 | 92 | 0 | 0 | 0 |  | 0 | 280 | 255 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 26 | 19 | 100 | 92 | 50 | 0 | 27 | 0 | 0 | 0 | 335 | 0 | 185 | 178 | 85 | 26 | 56 | 0 | 51 | 0 | 42 | 43 | 22 | 7 | 33 | 21 | 140 | 106 | 0 | 20 | 0 | 30 | 32 | 51 | 0 | 0 | 158 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 82 | 200 | 150 | 327 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 114 | 116 | 100 | 240 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 716 | 0 | 325 | 0 | 0 | 40 | 0 | 0 | 24 | 0 | 0 | 91 | 24 | 0 | 0 | 0 | 0 | 43 | 43 | 92 | 0 | 50 | 24 | 43 | 29 | 22 | 0 | 8 | 71 | 0 | 200 | 0 | 0 | 0 | 0 | 198 | 0 | 11 | 0 | 198 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 480 | 220 | 0 | 0 | 0 | 0 | 115 |  | 7565 | 3492 | 11057 | 3120 | 716 | 1666 | 0 | 4051 | 751 | 81 | 40 | 492 | 140 | 0 | 0 | 88.7
24:00 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 0 | 0 |  | 0 | 280 | 285 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 25 | 0 | 46 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 26 | 0 | 88 | 92 | 50 | 0 | 22 | 0 | 0 | 0 | 330 | 0 | 194 | 178 | 85 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 22 | 7 | 33 | 21 | 130 | 107 | 0 | 20 | 0 | 30 | 32 | 51 | 0 | 0 | 157 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 65 | 200 | 150 | 316 | 108 | 105 | 105 | 0 | 280 | 54 | 110 | 114 | 110 | 100 | 240 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 716 | 0 | 335 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 91 | 23 | 0 | 0 | 0 | 0 | 42 | 0 | 92 | 0 | 50 | 0 | 43 | 0 | 22 | 0 | 8 | 72 | 0 | 200 | 0 | 0 | 0 | 0 | 214 | 0 | 11 | 0 | 212 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 430 | 222 | 0 | 0 | 0 | 0 | 17 |  | 7309 | 3265 | 10574 | 3157 | 716 | 1686 | 0 | 3854 | 702 | 81 | 40 | 208 | 130 | 0 | 0 | 88.69
KWH | 0 | 0 | 0 | 0 | 6369936 | 2335545 | 0 | 0 | 0 |  | 0 | 6516000 | 6524975 | 0 | 0 | 1177280 | 2629528 | 0 | 0 | 0 | 1922256 | 2730720 | 0 | 0 | 0 | 0 | 1294560 | 1064741 | 1190006 | 374040 | 600000 | 550620 | 793080 | 804800 | 876480 | 0 | 1102800 | 840000 | 0 | 0 | 311972 | 0 | 0 | 0 | 0 |  | 525600 | 248072 | 254476 | 1819800 | 1579200 | 1192800 | 0 | 443040 | 0 | 0 | 0 | 8199500 | 0 | 4726000 | 4282181 | 1674120 | 596736 | 1294560 | 0 | 1137233 | 0 | 458888 | 1051454 | 488412 | 199080 | 641900 | 411840 | 3102720 | 2327040 | 0 | 445104 | 15300 | 716000 | 716000 | 1191600 | 0 | 0 | 3500000 | 1396896 | 2063040 | 0 | 0 | 0 | 0 | 241200 | 7145500 | 510648 | 214032 | 1962816 | 7113270 | 3090929 | 1312119 | 4344000 | 1308676 | 3596832 | 126360 | 1866240 | 2658240 | 3382254 | 9265000 | 2506800 | 2247600 | 2398690 | 28439 | 6430800 | 1345378 | 2634543 | 2306220 | 2657760 | 2356800 | 1853700 | 2123520 | 310660 | 3892320 | 2704800 | 0 | 675360 | 218509 | 1976640 | 1294920 |  | 17380363 | 0 | 6802272 | 0 | 0 | 1319040 | 0 | 0 | 155520 | 11008 | 0 | 2185340 | 480200 | 0 | 0 | 0 | 0 | 502080 | 471213 | 1018880 | 0 | 722178 | 377682 | 986400 | 181088 | 486000 | 0 | 193968 | 1846690 | 0 | 4857200 | 0 | 26000 | 0 | 0 | 4637355 | 0 | 273792 | 667200 | 4409827 | 0 | 0 | 2694240 | 1536776 | 2319552 | 0 | 2320905 | 0 | 44214 | 2619744 | 11171800 | 5178136 | 0 | 0 | 37440 | 634320 | 2171313 |  | 174809506 | 80719736 | 255529242 | 68232774 | 17380363 | 39593002 | 9878516 | 88353468 | 17875690 | 1942800 | 1345040 | 6409627 | 3102720 | 1415242 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7070628.96 | 3082919.4 | 0 | 0 | 0 |  | 0 | 7102440 | 7242722.25 | 0 | 0 | 9959788.8 | 2734709.12 | 0 | 0 | 0 | 17530974.72 | 26870284.8 | 0 | 0 | 0 | 0 | 9450288 | 8230447.93 | 11733459.16 | 280530 | 450000 | 0 | 0 | 0 | 8475561.6 | 0 | 297756 | 226800 | 0 | 0 | 2898219.88 | 0 | 0 | 0 | 0 |  | 0 | 2398856.24 | 2468417.2 | 17379090 | 13739040 | 9446976 | 0 | 1315828.8 | 0 | 0 | 0 | 6067630 | 0 | 4347920 | 5524013.49 | 1925238 | 674311.68 | 1812384 | 0 | 1944668.43 | 0 | 4634768.8 | 10041385.7 | 620283.24 | 149310 | 1123325 | 308880 | 23270400 | 2466662.4 | 0 | 565282.08 | 243882 | 1174240 | 1145600 | 2121048 | 0 | 0 | 3640000 | 2751885.12 | 3940406.4 | 0 | 0 | 0 | 0 | 492048 | 7216955 | 382986 | 162664.32 | 33387500.16 | 53776321.2 | 52483974.42 | 21938629.68 | 22588800 | 21881062.72 | 35392826.88 | 1477148.4 | 15209856 | 28841904 | 23844890.7 | 8616450 | 22862016 | 21239820 | 20892589.9 | 0 | 48616848 | 11718242.38 | 23157632.97 | 23016075.6 | 22777003.2 | 15696288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100110890.88 | 0 | 7142385.6 | 0 | 0 | 18281894.4 | 0 | 0 | 1631404.8 | 115363.84 | 0 | 2469434.2 | 744310 | 0 | 0 | 0 | 0 | 4940467.2 | 4787524.08 | 9017088 | 0 | 9763846.56 | 3659738.58 | 9558216 | 1756553.6 | 933120 | 0 | 146833.776 | 11135540.7 | 0 | 26326024 | 0 | 741780 | 0 | 0 | 6121308.6 | 0 | 410688 | 11349072 | 5159497.59 | 0 | 0 | 28127865.6 | 26140559.76 | 22012548.48 | 0 | 18010222.8 | 0 | 488564.7 | 19359908.16 | 49044202 | 0 | 0 | 0 | 0 | 0 | 0 |  | 788549796.73 | 399486853.906 | 1188036650.636 | 67697995.686 | 100110890.88 | 43883551.77 | 167180798.74 | 615348954.22 | 86505766.7 | 524556 | 19023674.4 | 62280467.14 | 23270400 | 2209595.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 230 | 98 | 0 | 0 | 0 |  | 0 | 270 | 275 | 0 | 0 | 55 | 90 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 42 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 22 | 4 | 0 | 92 | 94 | 50 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 184 | 178 | 80 | 29 | 53 | 0 | 43 | 0 | 0 | 43 | 19 | 5 | 0 | 11 | 138 | 84 | 0 | 20 | 2 | 30 | 20 | 48 | 0 | 0 | 154 | 60 | 81 | 0 | 0 | 0 | 0 | 10 | 310 | 19 | 8 | 200 | 286 | 301 | 100 | 180 | 98 | 149 | 19 | 72 | 51 | 137 | 391 | 109 | 88 | 89 | 4 | 281 | 54 | 110 | 96 | 107 | 90 | 50 | 85 | 45 | 162 | 113 | 0 | 17 | 31 | 98 | 48 |  | 720 | 0 | 270 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 43 | 23 | 43 | 0 | 21 | 0 | 8 | 78 | 0 | 200 | 0 | 0 | 0 | 0 | 146 | 0 | 11 | 38 | 177 | 0 | 0 | 105 | 165 | 94 | 0 | 101 | 0 | 6 | 113 | 360 | 212 | 0 | 0 | 5 | 90 | 115 |  | 10955 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 | 0 | 0 | 280 | 220 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 26 | 33 | 33 | 50 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 26 | 51 | 100 | 92 | 50 | 0 | 26 | 0 | 0 | 0 | 320 | 0 | 220 | 175 | 83 | 26 | 54 | 0 | 51 | 0 | 35 | 52 | 22 | 7 | 33 | 21 | 152 | 104 | 0 | 20 | 0 | 30 | 32 | 50 | 0 | 0 | 156 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 200 | 300 | 304 | 100 | 190 | 100 | 149 | 0 | 72 | 180 | 150 | 390 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 100 | 115 | 100 | 137 | 92 | 0 | 162 | 113 | 0 | 36 | 0 | 99 | 55 |  | 718 | 0 | 290 | 0 | 0 | 158 | 0 | 0 | 27 | 0 | 0 | 91 | 26 | 0 | 0 | 0 | 0 | 43 | 43 | 92 | 0 | 50 | 31 | 43 | 27 | 22 | 0 | 8 | 68 | 0 | 200 | 0 | 9 | 0 | 0 | 199 | 0 | 11 | 99 | 180 | 0 | 0 | 105 | 172 | 94 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 0 | 0 | 0 | 115 |  | 12170 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 0 | 0 | 0 | 280 | 300 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 51 | 100 | 90 | 50 | 0 | 20 | 0 | 0 | 0 | 330 | 300 | 220 | 177 | 90 | 29 | 55 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 22 | 163 | 100 | 0 | 20 | 0 | 30 | 30 | 50 | 0 | 0 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 108 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 265 | 92 | 0 | 162 | 113 | 0 | 36 |  | 100 | 55 |  | 734 | 0 | 300 | 0 | 0 | 158 | 0 | 0 | 35 | 40 | 0 | 92 | 10 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 40 | 52 | 30 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 20 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 225 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 0 | 280 | 102 | 0 | 0 | 0 | 0 | 0 | 280 | 285 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 51 | 100 | 90 | 50 | 0 | 5 | 0 | 0 | 0 | 300 | 100 | 220 | 177 | 90 | 29 | 55 | 0 | 51 | 0 | 41 | 43 | 22 | 11 | 33 | 22 | 138 | 100 | 0 | 20 | 1.6 | 30 | 30 | 50 | 0 | 0 | 160 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 108 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 260 | 92 | 50 | 162 | 113 | 0 | 36 | 30 | 100 | 55 |  | 734 | 0 | 300 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 90 | 10 | 0 | 0 | 0 | 0 | 43 | 44 | 93 | 0 | 50 | 0 | 52 | 25 | 22 | 0 | 8 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 100 | 200 | 0 | 0 | 105 | 100 | 113 | 0 | 113 | 0 | 8 | 113 | 500 | 225 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 93 | 0 | 0 | 0 | 0 | 0 | 280 | 260 | 0 | 0 | 55 | 140 | 0 | 0 | 0 | 93 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 23 | 22 | 25 | 20 | 33 | 25 | 25 | 0 | 46 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 0 | 80 | 84 | 50 | 0 | 7 | 0 | 0 | 0 | 280 | 5 | 183 | 177 | 84 | 20 | 55 | 0 | 51 | 0 | 0 | 40 | 22 | 7 | 31 | 20 | 108 | 109 | 0 | 20 | 1 | 30 | 32 | 51 | 0 | 0 | 159 | 40 | 86 | 0 | 0 | 0 | 0 | 0 | 270 | 22 | 8 | 0 | 296 | 0 | 0 | 191 | 0 | 145 | 6 | 90 | 100 | 113 | 364 | 108 | 88 | 105 | 1 | 275 | 54 | 110 | 96 | 106 | 90 | 250 | 80 | 16 | 148 | 113 | 0 | 17 | 11 | 99 | 54 | 0 | 717 | 0 | 300 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 52 | 0 | 22 | 0 | 8 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 160 | 0 | 11 | 0 | 160 | 0 | 0 | 105 | 0 | 94 | 0 | 105 | 0 | 1 | 113 | 290 | 164 | 0 | 0 | 1 | 32 | 115 | 0
199
| Minimum Generation |  | 8783 | 5:00
| Highest Generation |  | 12170 | 21:00
| Day Peak Generation |  | 10955 | 12:00
| Evening Peak Generation |  | 12170 | 21:00
| HVDC Max Flow |  | 720 | 3:00
| HVDC EvPeak Flow |  | 718 | 21:00
| Load factor L.F |  | 87.49%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-16
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10955 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 8859 | MW
Evening Peak Generation : |  | 12170 | MW Hour : | 21:00 | Available Max Generation : |  | 12903 | MW
E.P. Demand (at gen end) : |  | 12170 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12300 | MW
Maximum Generation : |  | 12170 | MW Hour : | 21:00 | Reserve(Generation end) |  | 603 | MW
Total Gen. (MKWH) : |  | 255.5292 | System Load Factor : | 87.49% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -194 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-16
Actual : | 88.63 | Ft.(MSL) , | Rule curve : | 90.6 | Ft.( MSL )
Gas Consumed : | Total = | 860.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 111581547.456
: |  | Coal : | 86505766.7 | Oil : | 863833894.5 | Total : | 1061921208.656
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4320.8928 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1472.0466 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1319.3867 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1192.3483 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1077.4136 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 869.4414 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 482.6694 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 223.7657 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 670.573 |  |  | 0 | 0%
Total | 0 |  | 11628.5375 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,5
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Raozan unit- 1,2
6) Sirajganj Unit 1,4
7) Siddhirganj 210 MW .
8) Kushiara 163 MW.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barapukuria-Bogura 230 kV Ckt-2 was under shut down from 09:29 to 10:47(15/03/2022) for D/W.
b) Saver 33 kV Bus-b was under shut down from 08:17 to 16:54 for C/M.
c) Madunaghat-Sholoshar 132 kV Ckt-1 was under shut down from 09:27 to 13:29 for D/W.
d) Kodda-Rajendrapur 132 kV Ckt-1 was under shut down from 09:37 to 15:17 for D/W.
e) Ashuganj-Shahjibazar 132 kV Ckt was under shut down from 09:49 to 17:58 for A/M.
f) Hasnabad 230/132 kV T-02 transformer was under shut down from 10:50 to 11:55 for C/M.
g) Agargaon 230/132 kV T-01 transformer was under shut down from 11:03 to 13:45 for C/M.
h) Hasnabad-Keraniganj 230 kV Ckt-2 was under shut down from 12:37 to 13:07 for C/M.
i) Hasnabad-APR 230 kV Ckt tripped at 12:34 showing no relay at Hasnabad end and was switched
on at 13:07.
j) Hasnabad-Keraniganj 230 kV Ckt-1 was under shut down from 12:16 to 13:41 for C/M.
k) Joydevpur 132/33 kV T-2 transformer was under shut down from 11:51 to 12:50 for C/M. | [5 empty] | About 40 MW power interruption occurred under
Joydevpur S/S area from 11:51 to 12:50.
l) Anwara 300 MW tripped at 09:50 and was synchronized at 10:03.
m) Chandpur 150 MW CCPP GT tripped at 17:10 due to DP high and was synchronized at 20:34.
n) Fenchuganj 132/33 kV T2 transformer was switched on at 18:40.
o) Bibiyana south STG was synchronized at 16:36.
p) Kallyanpur-Lalbag 132 kV Ckt-1 was switched on at 00:16(15/03/2022).
q) Bakulia 132/33 kV T-3 transformer was under shut down from 06:04(16/03/2022) to 08:55 for C/M.
r) Chatak 132/33 kV T-1 transformer was shut down at 06:16(16/03/2022) for C/M.
s) Hathazari-Baroirhat 132 kV Ckt-2 is under shut down since 07:12(16/03/2022) for D/W.
t) Sherpur-Sirajganj 132 kV Ckt-2 is under shut down since 04:15(16/03/2022) due to red hot maintenance.
u) Ashuganj(S) CCPP GT was synchronized at 07:56(16-03-2022).
v) Kishoreganj 132/33 kV T-2 transformer was under shut down from 07:50(16/03/2022) to 09:20 for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6369936 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2335545
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6516000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 220 | 6524975 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1177280
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 374040
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 140 | 2629528 | Gas shortage & ST U/M.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1922256 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1294560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2730720
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1064741
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1190006
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1150620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 793080
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 804800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 876480 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 7113270
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 304 | 3090929
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 1312119
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1308676
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3596832
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2247600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 2123520 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3892320
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 218509
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 1294920
| Dhaka area Total |  |  |  | 5696 | 3059 | 63953262
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 311972 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 126360
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1192800
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 81 | 1942800 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2398690
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 26 | 248072 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 254476 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1819800
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 72 | 1866240 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 443040
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 92 | 1579200 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28439
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 281 | 6430800 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1345378
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2634543
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2356800
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2704800
| Chattogram area Total |  |  |  | 2382 | 1278 | 27684210
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 220 | 4726000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 8199500
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 596736 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1294560
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 175 | 4282181 | Engine problem
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1137233
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 3382254
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 458888 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 83 | 1674120 | Engine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 2658240 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 488412
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 199080 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 3102720
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 641900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1051454
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 411840 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1962816
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2306220 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2657760
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 675360 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 115 | 115 | 99 | 1976640 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2131 | 43883914
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2327040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 445104
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15300
87 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 4344000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 108 | 2506800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 310660
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 525600
| Mymensingh Area Total |  |  |  | 622 | 444 | 10474504
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 716000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 156 | 3500000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1191600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 214032
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1396896
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2063040
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 510648
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7145500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 390 | 9265000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 241200
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 137 | 1853700 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1269 | 28813616
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 718 | 17380363
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 155520 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 158 | 1319040 | ST under maint.
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 11008 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 290 | 6802272 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 99 | 667200
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2694240
115 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 634320
| Khulna Area Total |  |  |  | 2229 | 1397 | 29663963
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 480200 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 91 | 2185340 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 273792 | Gas shortage
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 11171800
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5178136
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 970 | 19289268
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 502080 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 43 | 471213 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 722178
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 377682 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 199 | 4637355 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4409827 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 181088 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 486000
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 193968 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 986400
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 1018880 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 172 | 1536776
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2319552
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2619744
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37440
| Rajshahi Area Total |  |  |  | 2129 | 1117 | 20500183
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 68 | 1846690 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4857200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 9 | 26000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2320905
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 44214
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2171313 | On test
| Rangpur Area Total |  |  |  | 720 | 505 | 11266322
| Total |  |  |  | 21215 | 12170 | 255529242
| Eastern Grid Total |  |  |  | 14091 | 8181 | 174809506
| Western Grid Total |  |  |  | 7124 | 3989 | 80719736
| National Grid Total |  |  |  | 21215 | 12170 | 255529242
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-15
(a) ENTIRE EASTERN GRID : |  | 7918 | MW | (b) ENTIRE WESTERN GRID : |  | 3575 | MW
i) Dhaka area |  | 4175 | MW | i) Khulna area |  | 1310 | MW
ii) Chittagong area |  | 1244 | MW | ii) Rajshahi area |  | 1241 | MW
iii) Comilla area |  | 1044 | MW | iii) Barisal area |  | 306 | MW
iv) Mymensingh area |  | 997 | MW | iv) Rangpur area |  | 718 | MW
v) Sylhet area |  | 458 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11493 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 122 | 18:00 | Valuka | 122 | 15:00 | Central S/S | 73 | 19:30
Munsiganj | 90 | 13:00 | Tangail | 194 | 7:00 | Noapara | 43 | 19:00
Sonargaon | 87 | 12:00 | Mymensing | 216 | 19:00 | Jessore | 118 | 19:30
Bhulta | 196 | 1:00 | Kishoreganj | 118 | 21:00 | Benapol | 50 | 20:00
Madanganj | 28 | 19:00 | Netrokona | 123 | 8:00 | Jhenida(Old) | 98 | 20:00
Rahim steel | 23 | 17:00 | Jamalpur | 139 | 7:00 | Bottail | 113 | 19:30
Ghorasal | 76 | 12:00 | Sherpur | 128 | 22:00 | G.K Project | 44 | 20:00
Narsingdi | 159 | 20:00 | Srimongal | 44 | 18:30 | Faridpur | 111 | 19:00
Haripur(SBU) | 105 | 21:00 | Shahjibazar | 110 | 21:00 | Rajbari | 50 | 19:00
Sreenagar | 37 | 20:00 | Fenchuganj | 38 | 18:30 | Madaripur | 85 | 19:00
Shyampur | 198 | 10:00 | Kulawara | 38 | 18:30 | Sariatpur | 50 | 18:30
Shitalakhya | 108 | 15:00 | Sylhet | 133 | 19:00 | Gopalganj | 81 | 19:30
Matuail | 69 | 12:00 | Chatak | 25 | 18:30 | Bagerhat | 92 | 19:30
Char Saidpur | 42 | 13:00 | Sunamganj | 43 | 19:30 | Mongla | 48 | 11:00
Ullon | 37 | 21:00 | Biani Bazar | 52 | 19:00 | Satkhira | 95 | 20:00
Hasnabad | 76 | 13:00 | Comilla (S) | 160 | 19:00 | Gallamari | 50 | 19:00
Magbazar | 101 | 12:00 | Comilla(N) | 138 | 19:00 | Magura | 44 | 18:30
Maniknagar | 71 | 13:00 | Chandpur | 57 | 19:30 | Norail | 36 | 19:30
Bangabhaban | 9 | 11:00 | Feni | 109 | 19:30 | Chuadanga | 69 | 18:30
Motijheel | 32 | 12:00 | Chowmuhani | 168 | 21:00 | Barisal(N) | 46 | 18:30
Narinda | 56 | 13:00 | Ashuganj | 40 | 2:00 | Barisal (S) | 84 | 18:30
Kazla | 83 | 19:00 | Daudkandi | 125 | 21:00 | Patuakhali | 90 | 21:00
Dhanmondi | 168 | 13:00 | B.Baria | 140 | 19:30 | Bhandaria | 40 | 20:00
Lalbag | 88 | 13:00 | Ramganj | 66 | 20:00 | Borguna | 14 | 21:00
Madartek | 72 | 21:00 | Chaddagram | 39 | 21:00 | Borhan Uddin | 34 | 19:00
Dhaka University | 34 | 12:00 | PHP | 6 | 18:30 | Ishurdi | 59 | 20:00
Aftabnagar | 28 | 17:00 | Kochua | 50 | 20:00 | Ruppur Paromanobik | 4 | 17:00
Fatullah | 64 | 12:00 | Madunaghat | 51 | 21:00 | Natore | 114 | 20:00
Nawabganj | 41 | 21:00 | Hathazari | 82 | 18:30 | Bogra | 144 | 21:00
Keraniganj | 64 | 18:30 | Khulshi | 158 | 17:00 | Naogaon | 112 | 8:00
Banani | 49 | 14:00 | Halishahar | 84 | 14:00 | Rajshahi | 121 | 19:30
Mirpur | 114 | 19:00 | Baraulia | 119 | 15:00 | Rajshahi New | 39 | 20:00
Kalyanpur | 128 | 13:00 | Sikalbaha | 31 | 19:30 | C.Nawabganj | 60 | 20:00
Gulshan | 104 | 16:00 | Dohazari | 76 | 20:00 | Amnura | 59 | 21:00
Uttara | 76 | 19:30 | Cox'sbazar | 107 | 21:00 | Pabna | 88 | 20:00
Uttara New | 30 | 13:00 | Chandraghona | 24 | 19:00 | Shahjadpur | 95 | 20:00
Kamrangirchar | 68 | 13:00 | Kaptai | 4 | 18:30 | Serajganj | 100 | 20:00
Savar | 165 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 93 | 21:00
Bhasantec | 117 | 19:00 | Bakulia | 119 | 19:00 | Joypurhat | 54 | 21:00
Agargaon | 76 | 13:00 | Julda | 27 | 1:00 | Sherpur(Bogura) | 54 | 8:00
Satmosjid | 86 | 19:30 | TK chemical | 26 | 22:00 | Mohastangor | 58 | 19:00
Old Tongi | 100 | 18:00 | Modern Steel | 0 | 1:00 | Bhangura | 30 | 19:00
Kabirpur | 245 | 12:00 | Shahmirpur | 46.5 | 18:30 | Rangpur | 122 | 20:00
Manikgonj | 80 | 19:30 | Khagrachhari | 24 | 14:00 | Lalmonirhat | 42 | 19:00
Joydevpur | 185 | 19:00 | Matarbari | 35 | 19:30 | Saidpur | 100 | 9:00
New Tongi | 78 | 18:30 | Baroiar Hat | 44 | 18:30 | Purbasadipur | 104 | 12:00
Kodda | 270 | 19:00 | Rangamati | 12 | 18:30 | Thakurgaon | 78 | 19:30
Dhamrai | 104 | 19:00 | Agrabad | 76 | 18:30 | Palashbari | 104 | 20:00
Rajendrapur | 110 | 18:30 | Rampur | 11 | 21:00 | Barapukuria | 48 | 8:00
Bashundara | 156 | 12:00 | Abul Khair 230 | 168 | 7:00 | Panchagar | 49 | 20:00
Purbachal | 17 | 18:30 | BSRM | 157 | 7:00 | Joldhaka | 62 | 8:00
Tongi Millgate | 50 | 16:00 | GPH Ispat | 95 | 21:00 | Kurigram | 58 | 20:00
Bashundhara Cement |  |  | Goalpara | 26 | 12:00 | Mithapukur | 28 | 18:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 412 | 1:00 | 403 | 12:00 | Kaliakoir | 400 | 0.20833 | 380 | 0.625
| Bheramara | 401 | 8:00 | 392 | 19:00 | Bhulta | 418 | 0.041667 | 401 | 0.41667
| Ashuganj(N) | 425 | 1:00 | 406 | 16:00 | Gopalganj | 407 | 0.625 | 394 | 0.83333
| Payra | 417 | 1:00 | 406 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 242 | 6:00 | 235 | 9:00
| Ishurdi | 242 | 1:00 | 234 | 8:00 | Megnaghat | 241 | 8:00 | 236 | 11:00
| Ashuganj | 250 | 2:00 | 240 | 10:00 | Fenchuganj | 242 | 2:00 | 235 | 16:00
| Serajganj | 241 | 1:00 | 233 | 7:00 | Siddhirganj | 240 | 3:00 | 229 | 14:00
| Baghabari | 239 | 23:00 | 231 | 7:00 | Maniknagar | 238 | 3:00 | 226 | 15:00
| Barapukuria | 233 | 1:00 | 227 | 8:00 | Agargaon | 238 | 2:00 | 226 | 16:00
| Bogra | 236 | 1:00 | 226 | 8:00 | Barisal | 241 | 8:00 | 235 | 19:30
| Rajshahi | 237 | 2:00 | 228 | 7:00 | Bhola 225 MW | 245 | 4:00 | 240 | 20:00
| Khulna South | 244 | 4:00 | 233 | 7:00 | AKSML | 242 | 8:00 | 229 | 10:00
| Rampura | 238 | 1:00 | 226 | 15:00 | BSRM | 240 | 4:00 | 229 | 10:00
| Haripur | 236 | 1:00 | 227 | 16:00 | Bibiyana | 241 | 1:00 | 235 | 18:30
| Hasnabad | 236 | 3:00 | 227 | 15:00 | Bhulta | 240 | 2:00 | 229 | 15:00
| Shyampur | 237 | 1:00 | 227 | 16:00 | Ashuganj (S) | 246 | 1:00 | 236 | 15:00
| Aminbazar | 239 | 1:00 | 229 | 2:00 | Kaliakoir | 236 | 1:00 | 224 | 15:00
| Tongi | 235 | 1:00 | 223 | 15:00 | GPH | 242 | 4:00 | 228 | 10:00
| Comilla (N) | 239 | 2:00 | 232 | 10:00 | Jhenaidah | 240 | 4:00 | 230 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 1:00 | 128 | 15:00 | PHP | 140 | 8:00 | 135 | 13:00
| Munsiganj | 137 | 1:00 | 129 | 15:00 | Kachua | 141 | 7:00 | 137 | 3:00
| Sonargaon | 135 | 4:00 | 128 | 16:00 | Madanhat | 140 | 7:00 | 135 | 14:00
| Bhulta | 126 | 1:00 | 121 | 10:00 | Hathazari | 141 | 5:00 | 137 | 9:00
| Madanganj | 136 | 1:00 | 128 | 16:00 | Khulshi | 138 | 9:00 | 129 | 10:00
| Rahim steel | 134 | 1:00 | 129 | 11:00 | Halishahar | 139 | 7:00 | 131 | 10:00
| Ghorasal | 142 | 1:00 | 140 | 13:00 | Baraulia | 141 | 7:00 | 134 | 18:30
| Narsingdi | 129 | 4:00 | 128 | 15:00 | Sikalbaha | 141 | 9:00 | 129 | 22:00
| Haripur(SBU) | 134 | 1:00 | 129 | 11:00 | Dohazari | 137 | 9:00 | 127 | 10:00
| Sreenagar | 138 | 1:00 | 133 | 12:00 | Cox'sbazar | 129 | 8:00 | 120 | 15:00
| Shyampur | 135 | 7:00 | 129 | 16:00 | Chandraghona | 141 | 8:00 | 134 | 10:00
| Shitalakhya | 137 | 1:00 | 129 | 16:00 | Kaptai | 140 | 1:00 | 138 | 13:00
| Matuail | 134 | 1:00 | 128 | 15:00 | A. Khaer Stl. | 138 | 3:00 | 132 | 10:00
| Char Saidpur | 137 | 1:00 | 130 | 12:00 | Bakulia | 139 | 19:00 | 131 | 10:00
| Ullon | 136 | 1:00 | 125 | 12:00 | Julda | 138 | 1:00 | 134 | 17:00
| Hasnabad | 136 | 1:00 | 130 | 16:00 | TK Chemical | 140 | 4:00 | 136 | 2:00
| Magbazar | 137 | 2:00 | 126 | 12:00 | Modern Steel | 139 | 9:00 | 134 | 14:00
| Maniknagar | 139 | 7:00 | 132 | 10:00 | Shahmirpur | 139 | 7:00 | 134 | 12:00
| Bangabhaban | 139 | 7:00 | 132 | 10:00 | Khagrachhari | 141 | 21:00 | 132 | 10:00
| Motijheel | 139 | 7:00 | 132 | 10:00 | Matarbari | 131 | 8:00 | 121 | 20:00
| Narinda | 139 | 7:00 | 132 | 10:00 | Baroiar Hat | 139 | 6:00 | 135 | 12:00
| Kazla | 139 | 7:00 | 132 | 10:00 | Rangamati | 140 | 8:00 | 133 | 10:00
| Dhanmondi | 135 | 1:00 | 128 | 12:00 | Agrabad | 139 | 7:00 | 133 | 14:00
| Lalbag | 139 | 7:00 | 132 | 15:00 | Rampur | 138 | 8:00 | 134 | 10:00
| Madartek | 136 | 2:00 | 124 | 16:00 | Goalpara S/S | 138 | 1:00 | 133 | 7:00
| Dhaka University | 136 | 1:00 | 125 | 14:00 | Khulna Central S/S | 138 | 2:00 | 134 | 8:00
| Aftabnagar | 137 | 1:00 | 125 | 14:00 | Noapara | 137 | 4:00 | 131 | 7:00
| Fatullah | 136 | 22:00 | 130 | 12:00 | Jessore | 133 | 1:00 | 128 | 7:00
| Nawabganj | 138 | 1:00 | 132 | 15:00 | Benapol | 135 | 3:00 | 127 | 7:00
| Keraniganj | 139 | 7:00 | 132 | 16:00 | Jhenida(Old) | 135 | 1:00 | 131 | 11:00
| Banani | 136 | 2:00 | 125 | 10:00 | Bottail | 138 | 3:00 | 133 | 7:00
| Mirpur | 134 | 1:00 | 126 | 16:00 | G.K Project | 141 | 4:00 | 137 | 16:00
| Kalyanpur | 134 | 1:00 | 127 | 12:00 | Faridpur | 135 | 1:00 | 130 | 19:30
| Gulshan | 134 | 1:00 | 124 | 14:00 | Rajbari | 137 | 1:00 | 130 | 20:00
| Uttara | 139 | 5:00 | 130 | 15:00 | Madaripur | 140 | 4:00 | 135 | 22:00
| Uttara New | 140 | 1:00 | 130 | 12:00 | Shariyatpur S/S | 140 | 4:00 | 134 | 19:30
| Kamrangirchar | 139 | 5:00 | 132 | 15:00 | Gopalganj | 140 | 4:00 | 132 | 18:30
| Savar | 136 | 1:00 | 126 | 16:00 | Bagerhat | 137 | 4:00 | 129 | 8:00
| Bhasantec | 140 | 3:00 | 129 | 12:00 | Mongla | 137 | 4:00 | 130 | 7:00
| Agargaon | 141 | 1:00 | 131 | 12:00 | Satkhira | 137 | 3:00 | 130 | 7:00
| Satmosjid | 140 | 1:00 | 130 | 12:00 | Gallamari | 138 | 4:00 | 130 | 18:30
| Old Tongi | 140 | 1:00 | 132 | 15:00 | Magura | 138 | 3:00 | 130 | 7:00
| Kabirpur | 140 | 6:00 | 128 | 15:00 | Narail | 136 | 5:00 | 129 | 18:30
| Manikgonj | 135 | 5:00 | 127 | 12:00 | Chuadanga | 133 | 2:00 | 125 | 13:00
| Joydevpur | 143 | 7:00 | 137 | 10:00 | Barisal(N) | 140 | 1:00 | 134 | 21:00
| New Tongi | 141 | 2:00 | 131 | 15:00 | Barisal (S) | 139 | 3:00 | 134 | 18:30
| Kodda | 140 | 1:00 | 128 | 15:00 | Patuakhali(S) | 138 | 1:00 | 132 | 19:00
| Dhamrai | 142 | 1:00 | 133 | 16:00 | Bhandaria | 140 | 4:00 | 132 | 18:30
| Rajendrapur | 139 | 2:00 | 124 | 12:00 | Barguna | 140 | 3:00 | 138 | 18:30
| Bashundara | 140 | 1:00 | 130 | 15:00
| Purbachal | 134 | 22:00 | 124 | 14:00 | Ishurdi | 140 | 1:00 | 136 | 12:00
| Tongi Millgate | 141 | 1:00 | 130 | 16:00 | Ruppur Paromanobik | 139 | 1:00 | 135 | 12:00
| Bashundhara Cement |  |  |  |  | Natore | 140 | 1:00 | 132 | 7:00
| Valuka | 125 | 5:00 | 108 | 14:00 | Bogra | 139 | 1:00 | 131 | 8:00
| Tangail | 134 | 3:00 | 124 | 12:00 | Noagaon | 132 | 4:00 | 122 | 8:00
| Mymensing | 125 | 6:00 | 113 | 12:00 | Rajshahi | 135 | 17:00 | 129 | 7:00
| Kishorganj | 130 | 6:00 | 121 | 12:00 | Rajshahi New | 135 | 21:00 | 129 | 7:00
| Netrokona | 122 | 2:00 | 108 | 12:00 | C.Nawabganj | 133 | 1:00 | 125 | 7:00
| Jamalpur | 136 | 5:00 | 120 | 8:00 | Amnura | 134 | 19:00 | 125 | 7:00
| Sherpur | 137 | 4:00 | 119 | 7:00 | Pabna | 139 | 4:00 | 134 | 7:00
| Srimongal | 141 | 7:00 | 134 | 14:00 | Shahjadpur | 143 | 1:00 | 136 | 11:00
| Shahjibazar | 139 | 4:00 | 132 | 15:00 | Serajganj | 138 | 1:00 | 130 | 7:00
| Fenchuganj | 139 | 7:00 | 131 | 15:00 | Niyamatpur | 130 | 1:00 | 119 | 8:00
| Khulawara | 138 | 8:00 | 130 | 18:30 | Joypurhat | 133 | 1:00 | 121 | 8:00
| Sylhet | 134 | 6:00 | 126 | 14:00 | Sherpur(Bogura) | 140 | 1:00 | 129 | 8:00
| Chatak | 135 | 7:00 | 125 | 14:00 | Mohastangor | 138 | 1:00 | 127 | 8:00
| Sunamganj | 132 | 8:00 | 121 | 15:00 | Bhangura | 140 | 1:00 | 133 | 9:00
| Biani Bazar | 134 | 7:00 | 124 | 15:00 | Rangpur | 135 | 1:00 | 119 | 8:00
| Comilla(s) | 131 | 4:00 | 126 | 18:30 | Lalmonirhat | 131 | 1:00 | 118 | 8:00
| Comilla(n) | 140 | 5:00 | 136 | 15:00 | Saidpur | 134 | 5:00 | 122 | 8:00
| Chandpur | 142 | 7:00 | 140 | 5:00 | Purbasadipur | 132 | 1:00 | 121 | 8:00
| Feni | 140 | 7:00 | 134 | 15:00 | Thakurgaon | 134 | 21:00 | 122 | 8:00
| Chowmuhani | 138 | 9:00 | 135 | 12:00 | Palashbari | 134 | 1:00 | 121 | 8:00
| Ashuganj | 140 | 4:00 | 136 | 12:00 | Barapukuria | 133 | 20:00 | 127 | 8:00
| Daudkandi | 138 | 20:00 | 132 | 10:00 | Panchagar | 136 | 1:00 | 123 | 8:00
| B.Baria | 136 | 5:00 | 130 | 16:00 | Joldhaka | 134 | 1:00 | 119 | 8:00
| Ramganj | 140 | 7:00 | 136 | 5:00 | Kurigram | 132 | 2:00 | 118 | 8:00
| Chaddagram | 140 | 6:00 | 135 | 14:00 | Mithapukur | 136 | 1:00 | 123 | 8:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 270 | 7309 | 3265 | 10574 |  |  |  | QF-LDC-11
0:30 | 223 | 7174.5 | 3108.5 | 10283 | Date: | 2022-03-15
1:00 | 176 | 7040 | 2952 | 9992
1:30 | 202 | 6875 | 2896.5 | 9771.5
2:00 | 228 | 6710 | 2841 | 9551
2:30 | 251 | 6515 | 2815 | 9330 | [5 empty] | Gen. at Eve. Peak | 12170 | 12170 MW (21:00 )
3:00 | 274 | 6320 | 2789 | 9109 | [6 empty] | 21:00
3:30 | 310 | 6258.5 | 2773.5 | 9032 | [5 empty] | Gen. at Day Peak | 10955 | 10955 MW (12:00 )
4:00 | 346 | 6197 | 2758 | 8955 | [6 empty] | 12:00
4:30 | 294 | 6164 | 2705 | 8869 | [5 empty] | Highest Generation | 12170
5:00 | 242 | 6131 | 2652 | 8783 | [6 empty] | 21:00
5:30 | 182 | 6220.5 | 2661.5 | 8882
6:00 | 122 | 6310 | 2671 | 8981
6:30 | 158 | 6540 | 2768.5 | 9308.5
7:00 | 194 | 6770 | 2866 | 9636
7:30 | 157 | 6785.5 | 2940 | 9725.5
8:00 | 120 | 6801 | 3014 | 9815
8:30 | 129 | 6835 | 3049 | 9884
9:00 | 138 | 6869 | 3084 | 9953
9:30 | 253 | 6947.5 | 3165 | 10112.5
10:00 | 368 | 7026 | 3246 | 10272
10:30 | 299 | 7220 | 3253 | 10473
11:00 | 230 | 7414 | 3260 | 10674
11:30 | 272 | 7478.5 | 3336 | 10814.5
12:00 | 314 | 7543 | 3412 | 10955
12:30 | 282 | 7586.5 | 3493 | 11079.5
13:00 | 250 | 7630 | 3574 | 11204
13:30 | 276 | 7578.5 | 3491.5 | 11070
14:00 | 302 | 7527 | 3409 | 10936
14:30 | 394 | 7590 | 3501 | 11091
15:00 | 486 | 7653 | 3593 | 11246
15:30 | 432 | 7642.5 | 3495 | 11137.5
16:00 | 378 | 7632 | 3397 | 11029
16:30 | 375 | 7646 | 3393.5 | 11039.5
17:00 | 372 | 7660 | 3390 | 11050
17:30 | 370 | 7583.5 | 3401.5 | 10985
18:00 | 368 | 7507 | 3413 | 10920
18:30 | 348 | 7762.5 | 3623 | 11385.5
19:00 | 328 | 8018 | 3833 | 11851
19:30 | 314 | 8075 | 3984 | 12059
20:00 | 228 | 8094 | 3988 | 12082 |  |  |  | Executive Engineer
20:30 | 228 | 8137.5 | 3988.5 | 12126 |  |  |  | Network Operation Division
21:00 | 228 | 8181 | 3989 | 12170
21:30 | 175 | 8068.5 | 3793.5 | 11862
22:00 | 122 | 7956 | 3598 | 11554 |  |  |  |  | Page 6 of 7
22:30 | 193 | 7760.5 | 3545 | 11305.5
23:00 | 264 | 7565 | 3492 | 11057
23:30 | 267 | 7437 | 3378.5 | 10815.5
24:00 | 270 | 7309 | 3265 | 10574
12170 MW (21:00 )
10955 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-15 |  | Energy |  | 255529242
[13 empty] | 2022-03-15 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3157 | 716 | 1686 | 0 | 3854 | 702 | 81 | 40 | 208 | 130 | 0 | 0
0:30 | 2935 | 717.5 | 1647 | 0 | 3864 | 712 | 81 | 20 | 183.5 | 123 | 0 | 0 | Date: | 2022-03-15
1:00 | 2713 | 719 | 1608 | 0 | 3874 | 722 | 81 | 0 | 159 | 116 | 0 | 0
1:30 | 2713 | 719 | 1618 | 0 | 3712.5 | 701.5 | 81 | 0 | 111.5 | 115 | 0 | 0 | [8 empty] | Total Energy | 255.5292 | Total Energy Gen 255.529 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 255.529 MKWHr
2:00 | 2713 | 719 | 1628 | 0 | 3551 | 681 | 81 | 0 | 64 | 114 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 2712.5 | 719.5 | 1648 | 0 | 3360 | 666 | 81 | 0 | 32 | 111 | 0 | 0 | [8 empty] | Energy Requirement | 255.5292
3:00 | 2712 | 720 | 1668 | 0 | 3169 | 651 | 81 | 0 | 0 | 108 | 0 | 0
3:30 | 2718 | 720 | 1670 | 0 | 3091 | 646 | 81 | 0 | 0 | 106 | 0 | 0 | [6 empty] | Shortage
4:00 | 2724 | 720 | 1672 | 0 | 3013 | 641 | 81 | 0 | 0 | 104 | 0 | 0
4:30 | 2733 | 719.5 | 1664.5 | 0 | 2939.5 | 630.5 | 81 | 0 | 0 | 101 | 0 | 0
5:00 | 2742 | 719 | 1657 | 0 | 2866 | 620 | 81 | 0 | 0 | 98 | 0 | 0
5:30 | 2762 | 719 | 1684 | 0 | 2916 | 620 | 81 | 0 | 4 | 96 | 0 | 0
6:00 | 2782 | 719 | 1711 | 0 | 2966 | 620 | 81 | 0 | 8 | 94 | 0 | 0
6:30 | 2767.5 | 719.5 | 1701.5 | 45.5 | 3189 | 624.5 | 81 | 0 | 70.5 | 101 | 8.5 | 0 |  |  |  |  | Coal
7:00 | 2753 | 720 | 1692 | 91 | 3412 | 629 | 81 | 0 | 133 | 108 | 17 | 0
7:30 | 2745.5 | 720 | 1651.5 | 71 | 3512.5 | 639 | 81 | 20 | 133 | 110 | 42 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2738 | 720 | 1611 | 51 | 3613 | 649 | 81 | 40 | 133 | 112 | 67 | 0
8:30 | 2720.5 | 720 | 1619.5 | 50.5 | 3649.5 | 639 | 81 | 40 | 157 | 112 | 95 | 0
9:00 | 2703 | 720 | 1628 | 50 | 3686 | 629 | 81 | 40 | 181 | 112 | 123 | 0
9:30 | 2732 | 719.5 | 1616 | 273 | 3567.5 | 628 | 81 | 40 | 195.5 | 115 | 145 | 0
10:00 | 2761 | 719 | 1604 | 496 | 3449 | 627 | 81 | 40 | 210 | 118 | 167 | 0
10:30 | 2751 | 719.5 | 1618.5 | 548.5 | 3576 | 629 | 81 | 40 | 210 | 120 | 179.5 | 0
11:00 | 2741 | 720 | 1633 | 601 | 3703 | 631 | 81 | 40 | 210 | 122 | 192 | 0
11:30 | 2671 | 720 | 1630.5 | 751.5 | 3705.5 | 634.5 | 81 | 70 | 223.5 | 130 | 197 | 0
12:00 | 2601 | 720 | 1628 | 902 | 3708 | 638 | 81 | 100 | 237 | 138 | 202 | 0
12:30 | 2629 | 719.5 | 1614 | 933 | 3714.5 | 669.5 | 81 | 100 | 281.5 | 138 | 199.5 | 0
13:00 | 2657 | 719 | 1600 | 964 | 3721 | 701 | 81 | 100 | 326 | 138 | 197 | 0
13:30 | 2657 | 719 | 1600 | 964 | 3721 | 701 | 81 | 100 | 326 | 138 | 197 | 0
14:00 | 2657 | 719 | 1600 | 964 | 3721 | 701 | 81 | 100 | 326 | 138 | 197 | 0
14:30 | 2721.5 | 717.5 | 1591.5 | 904.5 | 3748 | 701 | 81 | 100 | 350 | 141 | 169 | 0
15:00 | 2786 | 716 | 1583 | 845 | 3775 | 701 | 81 | 100 | 374 | 144 | 141 | 0
15:30 | 2786.5 | 716 | 1595 | 762.5 | 3798 | 699.5 | 81 | 75 | 369 | 141 | 114 | 0
16:00 | 2787 | 716 | 1607 | 680 | 3821 | 698 | 81 | 50 | 364 | 138 | 87 | 0
16:30 | 2811 | 715.5 | 1604.5 | 693 | 3836 | 698 | 81 | 50 | 368 | 135 | 59.5 | 0
17:00 | 2811 | 715 | 1602 | 706 | 3851 | 698 | 81 | 50 | 372 | 132 | 32 | 0
17:30 | 2822.5 | 715.5 | 1617.5 | 551.5 | 3865.5 | 697 | 81 | 54 | 426.5 | 138 | 16 | 0
18:00 | 2834 | 716 | 1633 | 397 | 3880 | 696 | 81 | 58 | 481 | 144 | 0 | 0
18:30 | 2869 | 716 | 1641 | 672.5 | 3894.5 | 742.5 | 81 | 112 | 505 | 152 | 0 | 0
19:00 | 2904 | 716 | 1649 | 948 | 3909 | 789 | 81 | 166 | 529 | 160 | 0 | 0
19:30 | 2913 | 717 | 1650 | 976 | 3963 | 890 | 81 | 166 | 545 | 158 | 0 | 0
20:00 | 2935 | 718 | 1636 | 976 | 3983 | 890 | 81 | 166 | 545 | 152 | 0 | 0
20:30 | 2988.5 | 718 | 1626 | 975.5 | 3993.5 | 890 | 81 | 166.5 | 535 | 152 | 0 | 0
21:00 | 3042 | 718 | 1616 | 975 | 4004 | 890 | 81 | 167 | 525 | 152 | 0 | 0
21:30 | 3063 | 717.5 | 1639.5 | 714 | 4019 | 850 | 81 | 103.5 | 523.5 | 151 | 0 | 0
22:00 | 3084 | 717 | 1663 | 453 | 4034 | 810 | 81 | 40 | 522 | 150 | 0 | 0
22:30 | 3102 | 716.5 | 1664.5 | 226.5 | 4042.5 | 780.5 | 81 | 40 | 507 | 145 | 0 | 0
23:00 | 3120 | 716 | 1666 | 0 | 4051 | 751 | 81 | 40 | 492 | 140 | 0 | 0
23:30 | 3138.5 | 716 | 1676 | 0 | 3952.5 | 726.5 | 81 | 40 | 350 | 135 | 0 | 0 | Max Temp. in Dhaka |  | 35.0° C
24:00 | 3157 | 716 | 1686 | 0 | 3854 | 702 | 81 | 40 | 208 | 130 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 255.529 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 255.529 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1102800
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | [5 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 311972
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 7 | 12 | 16 | 18 | 19 | 18 | 15 | 11 | 6 | 2 | [9 empty] | 126360
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 51 | 51 | 40 | 19 | 0 | 254476
12 | Hathazari 100 MW peaking PP | [11 empty] | 4 | 17 | 16 | 16 | 16 | 16 | 18 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 248072
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 102 | 93 | 96 | 105 | 105 | 105 | 98 | 88 | 88 | 89 | 89 | 89 | 100 | 105 | 94 | 102 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2398690
| Daudkandi 200 MW PP (B.Trac) | [9 empty] | 10 | 100 | 200 | 200 | 100 | 200 | 150 | 150 | 100 |  | 200 | 200 | 200 | 200 | 80 | 0 |  | 1962816
14 | Titas 50 MW Peaking PP | [12 empty] | 27 | 40 | 38 | 38 | 38 | 41 |  | 42 | 42 | 42 | 35 | 41 | 42 | 0 | 458888
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 2629528
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 298 | 300 | 300 | 300 | 300 | 300 | 300 | 298 | 300 | 290 | 286 | 283 | 295 | 296 | 286 | 283 | 284 |  | 290 | 298 | 300 | 300 | 298 | 300 | 300 | 7113270
19 | Ashuganj 195MW PP (APSCL-United) | 177 | 178 | 177 | 177 | 177 | 179 | 178 | 178 | 180 | 180 | 180 | 178 | 178 | 178 | 177 | 177 | 177 | 178 |  | 178 | 178 | 178 | 175 | 178 | 178 | 178 | 4282181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 245 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6369936
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 23 | 26 | 29 | 29 | 29 | 25 | 25 | 21 | 26 |  | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 596736
33 | Ashuganj 225 MW CCPP | 221 | 182 | 183 | 182 | 182 | 193 | 186 | 184 | 187 | 209 | 219 | 184 | 184 | 184 | 186 | 197 | 186 | 206 |  | 214 | 216 | 217 | 220 | 190 | 185 | 194 | 4726000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 320 | 340 | 320 | 315 | 320 | 355 | 355 | 315 | 315 | 320 | 320 | 330 | 320 | 320 |  | 315 | 320 | 320 | 320 | 330 | 335 | 330 | 8199500
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 56 | 56 | 56 | 54 | 54 | 56 | 56 | 53 | 53 | 53 | 54 | 54 | 48 | 50 | 51 |  | 53 | 53 | 52 | 54 | 56 | 56 | 56 | 1294560
36 | Chandpur 150 MW CCPP | 85 | 84 | 86 | 84 | 86 | 85 | 85 | 83 | 85 | 85 | 84 | 80 | 82 | 81 | 74 | 74 | 68 | [5 empty] | 83 | 85 | 85 | 85 | 1674120
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6516000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 105 | 106 | 106 | 106 | 107 | 107 | 108 | 108 | 105 | 83 | 81 | 84 | 84 | 84 | 96 | 97 | 99 | 100 |  | 100 | 103 | 103 | 104 | 103 | 106 | 107 | 2327040
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 14 | 26 | 36 | 42 | 45 | 41 | 42 | 33 | 20 | 8 | 0 | [8 empty] | 310660
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 22 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 716000
46 | Shajibazar 330 MW CCPP | 158 | 159 | 158 | 156 | 157 | 156 | 155 | 157 | 157 | 157 | 154 | 154 | 154 | 155 | 154 | 153 | 157 | 155 |  | 158 | 155 | 158 | 156 | 157 | 158 | 157 | 3500000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 60 | 60 | 60 | 50 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1396896
48 | Shahjibazar 86MW PP (Shahjibazar) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 86 | 75 | 84 | 81 | 84 | 81 | 82 | 82 | 86 | 88 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2063040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241200
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 214032
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 48 | 48 | 48 | 48 | 50 | 45 | 45 | 48 | 50 |  | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 1191600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 510648
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 265 | 280 | 280 | 280 | 310 | 305 | 270 | 280 | 290 | 310 | 310 | 295 | 275 | 285 | 290 | 300 | 280 |  | 300 | 290 | 280 | 280 | 290 | 300 | 290 | 7145500
| Bibiyana South 400 MW | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 43 | 80 | 102 |  | 116 | 115 | 118 | 137 | 205 | 240 | 240 | 1853700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 17 |  | 17 | 35 | 35 | 55 | 55 | 55 | 35 | 1190006
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 525600
60 | Barabkunda 22 MW PP (Regent) | [25 empty] | 0 | 0
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 |  |  | 19 | 19 | 19 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 374040
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 445104
63 | Impoprt (Tripura) | 116 | 114 | 108 | 104 | 98 | 94 | 108 | 112 | 112 | 118 | 122 | 138 | 138 | 144 | 144 | 138 | 132 | 144 |  | 160 | 158 | 152 | 152 | 150 | 140 | 130 | 3102720
64 | Malancha, Ctg. EPZ (United) | 39 | 40 | 40 | 40 | 40 | 40 | 37 | 8 | 4 | 2 | 2 | 0 | 3 | 3 | 2 | 2 | 2 | 6 |  | 12 | 20 | 17 | 26 | 26 | 27 | 22 | 443040
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488412
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 7 | 7 | 7 | 7 | 7 | 7 | 199080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 27 | 23 | 25 | 25 |  | 25 | 33 | 33 |  |  | 30 |  | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 641900
68 | Cumilla 25 MW PP (Summit) | 21 | 20 | 21 | 21 | 21 | 21 | 21 | 17 | 0 | 11 | 11 | 11 | 15 | 15 | 14 | 14 | 14 | 14 |  | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 411840
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 18 | 18 | 24 | 18 | 24 | 20 | 24 | 24 | 24 | 24 | 24 | 24 |  | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 550620
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793080
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804800
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 99 | 99 | 99 | 99 | 99 | 98 | 98 | 98 | 98 | 102 | 98 | 98 | 100 | 102 |  | 102 | 102 | 102 | 102 | 99 | 92 | 96 | 2335545
| Feni Lanka Power | 114 | 114 | 90 | 17 | 17 | 51 | 98 | 114 | 114 | 114 | 114 | 96 | 96 | 96 | 80 | 96 | 114 | 114 |  | 114 | 114 | 114 | 100 | 114 | 114 | 114 | 2306220
| Chowmuhani 113 MW | 111 | 110 | 111 | 110 | 109 | 107 | 107 | 105 | 105 | 108 | 106 | 107 | 105 | 108 | 105 | 109 | 114 | 115 |  | 116 | 117 | 115 | 115 | 117 | 116 | 110 | 2657760
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 144 | 144 | 154 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3892320
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 51 | 25 |  |  |  | 8 | 22 | 42 | 42 | 21 | 42 | 42 | 42 | 50 | 48 | 48 | 48 | 48 |  | 50 | 50 | 50 | 50 | 50 | 51 | 25 | 876480
79 | Kodda 150MW PP | 150 | 64 |  |  |  | 8 | 133 | 133 | 133 | 133 | 133 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 48 | 2730720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 43 | 43 | 43 |  | 43 | 43 | 52 | 52 | 52 | 43 | 43 | 1051454
| Gazipur 100 MW PP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 88 | 88 | 88 | 88 | 88 | 88 | 92 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2247600
| Kaptai 7 MW Solar PP | [7 empty] | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 28439
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1345378
| Karnaphuli Power Ltd. | 110 | 110 | 102 | 110 | 103 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 95 | 110 | 110 | 110 | 107 | 105 |  | 106 | 110 | 110 | 110 | 110 | 110 | 110 | 2634543
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 250 | 250 | 270 | 275 | 260 | 280 | 275 | 275 | 285 | 265 | 275 | 275 | 260 | 270 | 250 | 275 | 250 | 270 |  | 250 | 250 | 250 | 220 | 255 | 255 | 285 | 6524975
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 92 | 74 | 74 | 74 | 80 | 92 | 92 | 92 | 92 | 92 | 93 | 85 | 88 | 91 | 92 | 84 | 84 | 90 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2123520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 60 |  |  |  | 7 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 82 | 92 | 92 | 92 |  | 92 | 93 | 100 | 100 | 100 | 100 | 88 | 1819800
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1137233
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 50 | 16 | 24 | 50 | 75 | 84 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 84 | 84 |  | 84 | 84 | 84 | 93 | 93 | 93 | 93 | 1922256
95 | Patenga 50MW PP (Baraka) | 46 | 48 | 50 | 50 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 44 | 49 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1192800
96 | Chattogram 108 MW PP (ECPV) | 6 | 6 | 6 | 17 | 19 | 19 | 18 | 32 | 71 | 73 | 90 | 94 | 95 | 95 | 96 | 95 | 92 | 94 |  | 97 | 97 | 97 | 92 | 96 | 92 | 92 | 1579200
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 15 | 15 | 15 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 45 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1177280
100 | Manikganj 55 MW PP (Northern) | 55 | 17 |  |  |  | 15 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1064741
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15300
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1294560
104 | Keranigonj 300 MW PP (APR) | [6 empty] | 40 |  |  | 210 | 202 | 301 | 300 | 207 | 210 | 210 | 236 | 107 |  | 305 | 307 | 305 | 304 | 103 | 0 | 0 | 3090929
105 | Bramhangoan 100 MW PP (Aggreko) | [6 empty] | 25 | 25 | 25 | 100 | 100 | 100 | 100 | 70 | 100 | 100 | 100 | 50 |  | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 1312119
106 | Mymensingh 200 MW PP (United) | 180 | 180 | 180 | 189 | 181 | 182 | 182 | 182 | 180 | 180 | 180 | 180 | 178 | 186 | 186 | 186 | 176 | 177 |  | 179 | 188 | 189 | 190 | 190 | 200 | 200 | 4344000
112 | Aurahati 100MW PP (Aggreko) | [6 empty] | 26 | 26 | 25 | 96 | 99 | 98 | 98 | 70 | 100 | 100 | 100 | 50 |  | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 1308676
114 | Kodda 149 MW PP Unit-1 (Summit) | 140 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 145 | 145 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3596832
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 72 | 72 | 61 | 61 | 71 | 71 | 71 |  | 71 | 71 | 72 | 72 | 82 | 82 | 65 | 1866240
116 | Chandpur 200MW (Desh energy) | 200 | 120 |  |  |  |  | 28 | 51 | 51 | 51 | 51 | 51 | 51 | 95 | 124 | 172 | 180 | 183 |  | 180 | 180 | 180 | 180 | 182 | 200 | 200 | 2658240
117 | Ashuganj 150MW PP (Midland) | 147 | 147 | 142 | 143 | 147 | 147 | 143 | 140 | 140 | 138 | 140 | 137 | 135 | 127 | 125 | 123 | 122 | 135 |  | 142 | 146 | 148 | 150 | 150 | 150 | 150 | 3382254
118 | Bibiyana-III 400 MW CCPP | 388 | 388 | 388 | 388 | 387 | 388 | 388 | 388 | 388 | 390 | 390 | 391 | 392 | 392 | 392 | 393 | 391 | 390 |  | 390 | 390 | 390 | 390 | 366 | 327 | 316 | 9265000
| Jamalpur 115 MW PP (United) | 98 | 108 | 108 | 108 | 107 | 108 | 108 | 108 | 107 | 98 | 108 | 109 | 109 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2506800
| Anwara 300 MW PP (United) | 281 | 281 | 281 | 280 | 280 | 280 | 281 | 281 | 281 |  | 240 | 281 | 281 | 281 | 281 | 281 | 265 | 281 |  | 281 | 281 | 281 | 281 | 281 | 281 | 280 | 6430800
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2356800
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2704800
| Bhairob 54.5 MW | 36 | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 675360
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 11 | 20 | 27 | 30 | 31 | 32 | 27 | 21 | 12 | 4 | 0 | [8 empty] | 218509
| Chandpur 115(Doreen) | 99 | 99 |  |  |  | 10 | 33 | 79 | 100 | 100 | 100 | 98 | 97 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1976640
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 38 | 48 | 55 | 55 | 42 | 42 | 55 | 55 |  | 46 | 55 | 55 | 55 | 55 | 55 | 55 | 1294920
120 | Eastern Zone Total | 7040 | 6710 | 6320 | 6197 | 6131 | 6310 | 6770 | 6801 | 6869 | 7026 | 7414 | 7543 | 7630 | 7527 | 7653 | 7632 | 7660 | 7507 |  | 8018 | 8075 | 8094 | 8181 | 7956 | 7565 | 7309 | 174809506
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [9 empty] | 4 |  |  | 3 | 2 | 4 | 4 | 4 | 10 |  | 24 | 32 | 27 | 27 | 27 | 24 |  | 155520
| Khulna 225 MW CCPP | [7 empty] | 40 | 40 | 40 | 40 | 100 | 100 | 100 | 100 | 50 | 50 | 50 |  | 158 | 158 | 158 | 158 | 40 | 40 | 40 | 1319040
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2694240
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 8 | 31 | 55 | 73 | 85 | 90 | 89 | 79 | 63 | 41 | 16 | [8 empty] | 0 | 634320
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 190 | 214 | 219 | 217 | 219 | 221 | 221 | 210 | 221 | 221 | 212 | 212 | 210 | 210 | 210 | 210 | 208 | 213 |  | 216 | 218 | 218 | 220 | 220 | 220 | 222 | 5178136
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 273792
| Bhola 225 MW CCPP | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 89 | 87 | 88 | 88 | 89 | 89 |  | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 2185340
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 21 | 21 | 22 | 22 | 19 | 15 | 13 | 14 | 16 | 18 | 18 | 21 | 19 | 20 | 18 | 22 |  | 26 | 26 | 26 | 26 | 26 | 24 | 23 | 480200
141 | Noapara 100 MW PP (Bangla Trac) | [11 empty] | 38 | 98 | 20 | 65 | 50 | 50 | 20 |  | 72 | 98 | 98 | 99 | 0 |  | 0 | 667200
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 4 | 8 | 8 | 0 |  |  |  | 11008
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 719 | 719 | 720 | 720 | 719 | 719 | 720 | 720 | 720 | 719 | 720 | 720 | 719 | 718 | 716 | 716 | 715 | 716 |  | 716 | 717 | 718 | 718 | 717 | 716 | 716 | 17380363
147 | Bheramara 410 MW CCPP | 250 | 250 | 250 | 260 | 265 | 270 | 270 | 280 | 275 | 265 | 270 | 270 | 270 | 275 | 270 | 275 | 280 | 285 |  | 285 | 285 | 285 | 290 | 310 | 325 | 335 | 6802272
148 | Payra 1320 MW | 440 | 400 | 370 | 360 | 340 | 340 | 350 | 370 | 350 | 350 | 350 | 360 | 420 | 410 | 420 | 420 | 420 | 420 |  | 520 | 622 | 622 | 622 | 540 | 480 | 430 | 11171800
149
150 | Barapukuria TPP Unit-1 | 83 | 82 | 82 | 81 | 80 | 80 | 80 | 79 | 79 | 77 | 81 | 78 | 81 | 78 | 81 | 78 | 78 | 76 |  | 69 | 68 | 68 | 68 | 70 | 71 | 72 | 1846690
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4857200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 34 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 502080
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 4 | 2 | 0 | 0 | [8 empty] | 37440
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 160 | 167 | 167 | 167 | 177 | 183 | 189 | 200 | 200 | 194 | 177 | 146 | 140 | 155 | 184 | 190 | 196 | 199 |  | 201 | 204 | 205 | 199 | 193 | 198 | 214 | 4637355
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 138 | 145 | 152 | 159 | 163 | 172 | 175 | 178 | 179 | 179 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 176 |  | 176 | 176 | 176 | 180 | 182 | 198 | 212 | 4409827
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [9 empty] | 5 | 6 | 6 | 17 | 42 | 44 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 471213
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 486000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193968
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 722178
167 | Katakhali 50 MW Peaking PP | 9 | [8 empty] | 20 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 32 |  | 32 | 36 | 40 | 31 | 31 | 24 | 0 | 377682
168 | Santahar 50 MW Peaking PP | [17 empty] | 21 |  | 21 | 21 | 22 | 27 | 29 | 29 | 0 | 181088
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 16 | 16 | 16 | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 986400
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 48 | 48 | 48 | 54 | 55 | 55 | 55 | 46 | 54 | 72 |  | 93 | 93 | 93 | 92 | 92 | 92 | 92 | 1018880
171 | Baghabari 200 MW PP (Paramount) | [9 empty] | 80 | 100 | 165 | 168 | 50 | 170 | 70 | 70 | 70 |  | 171 | 171 | 173 | 172 | 70 | 0 | 0 | 1536776
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2319552
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 50 | 50 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2619744
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [17 empty] | 8 |  | 8 | 8 | 8 | 9 | 0 |  |  | 26000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 70 | 50 | 55 | 55 | 55 | 104 | 100 | 101 | 101 | 102 | 100 | 95 | 100 | 95 |  | 105 | 105 | 105 | 113 | 113 | 113 | 113 | 2320905
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 6 | 6 | 6 | 6 | 5 | 4 | 2 | 0 | [8 empty] | 44214
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 17 |  |  |  | 17 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 17 | 2171313
178