## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-20 | Sunday
|  |  | Date (day): | 2022-03-20 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13557.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13987 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-19 | 2022-03-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 180 | 180
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 270 | 280 | 280 | 85 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 98 | 100 | 100 |  | 8 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint |  | 2022-04-04
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 220 | 335 | 335 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 214 | 220 | 220 | 115 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 16 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 280 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 89 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 32 | 90 | 72 | 72 |  | 32 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 58 | 126 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 55 | 55 | 55 | 33 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5696 | 1694 | 2702 | 3338 | 3408 | 611 | 1639
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 81 | 81 |  | 149 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 26 | 56 | 150 | 150 |  | 75 | ST Under S/D
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 34 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 22 | 33 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 5 | 5 | 6 | 6 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 281 | 281 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 74 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 30 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 62 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 884 | 1308 | 1520 | 1510 | 132 | 637
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 188 | 210 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 310 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 310 | 330 | 330 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 40 | 20 | 40 | 15 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 112 | 73 | 110 | 110 | 85 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 113 | 143 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 |  | 20
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 90 | 90 | 90 |  | 73 | ST under S/D
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 170 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 152 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 23 | 43 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 98 | 98 | 98 |  | 16 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 97 | 107 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 115 | 115 | 115 | 0 | 99 | 100 | 100
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1524 | 2023 | 2265 | 2410 | 379 | 149
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 178 | 178 | 160 | 178 | 24 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 180 | 188 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 107 | 108 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 533 | 513 | 565.6 | 532 | 24 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint. |  | 22-03-022
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 217 | 221 | 220 | 220 |  | 110 | ST under maint
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 50 | 30 | 50 |  | 16 | Machine problem
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 85 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 20 | 23 | 22 | 23
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 256 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 402 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 380 | 400 | 383 | 383
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1558 | 1568 | 1572 | 1593 | 251 | 489
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 718 | 718 | 731 | 731
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 0 | 40 |  | 14 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 110 | 170 | 158 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 8 | 0 | 40 |  | 69 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 350 | 360 | 360
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 20 | 94 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1297 | 1375 | 1504 | 1596 | 0 | 83
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 28 | 25 | 27 |  | 6 | Engine problem
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 | 194 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 580 | 650 | 650
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 105 | 100 | 110 | 110
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 644 | 708 | 785 | 787 | 194 | 6
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 40 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 10 | 10 | 10 | 10 |  | 200 | ST Commissioning process
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 204 | 206 | 220 | 220
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 205 | 210 | 220
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 417 | 399 | 414 | 414
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 25 | 30 |  | 20 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 15 | 17 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 53 | 90 | 90 | 92 |  | 12 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 87 | 94 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1049 | 1381 | 1512 | 1663 | 171 | 282
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 52 | 72 | 60 | 60
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 200 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 110 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 70 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 439 | 497 | 496 | 488 | 74 | 125
|  | Total |  |  |  |  | 22296 | 21215 | 9622 | 12075 | 13557.6 | 13987 | 1836 | 3418
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9221.1829 | 11572 | 12992.8403 | 13404.3531
| A. |  | 2022-03-19 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12075 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 8104 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12075 | MW
| 3 | Day peak Generation : |  |  | 9622 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11572 | MW
| 4 | Evening peak Generation : |  |  | 12075 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 241.6315 | MKWHr | By Solar | 1.3988 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 137.0468 | MKWHr |  | By Oil: | 60.6107 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 20.9793 | MKWHr |  | By Hydro: | 1.2505 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1836 | MW | Dhaka | 3820 | 3820 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3418 | MW | Chittagong | 1254 | 1254 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5254 | MW | Khulna | 1373 | 1373 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1068.6 | MMCFD |  |  | Rajshahi | 1371 | 1371 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 142895990.95 | ii) Oil : | Taka | 443870870.59 | Comilla | 1130 | 1130 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 99563053.54 | Total | Taka | 686329915.08 | Mymensingh | 997 | 997 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.195 | MKWHr. | Sylhet | 451 | 451 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -144 | MW (E to W) at | 19:30 | hrs | Barisal | 311 | 311 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -162 | MW at | 20:00 | hrs | Rangpur | 865 | 865 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.5° C |  |  | Total | 11572 | 11572 |  | 0
| B. |  | 2022-03-20 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 36.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13987 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10900 | MW
| 4 | Reserve(Generation end) |  |  |  | 1087 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 258.1405 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9095 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3549 | MKWHr. | ii) HVDC Flow at Peak Time |  | 718 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9904 | MKWHr. | iii) Maximum HVDC Flow : |  | 725 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 87.75 |  | (b) Today: | 87.5 |  | (c) Rule Curve: |  | 89.96
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 290 | 102 | 0 | 0 | 0 |  | 0 | 280 | 275 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 20 | 33 | 16 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 151 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 310 | 160 | 112 | 0 | 29 | 52 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 33 | 22 | 130 | 148 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 219 | 30 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 23 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 108 | 0 | 90 | 17 | 100 | 400 | 112 | 17 | 68 | 0 | 281 | 54 | 110 | 81 | 101 | 10 | 280 | 0 | 0 | 54 | 113 | 0 | 17 | 0 | 51 | 55 |  | 725 | 0 | 410 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 83 | 0 | 200 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 186 | 0 | 227 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 550 | 110 | 0 | 0 | 0 | 0 | 17 |  | 6544 | 3033 | 9577 | 4054 | 725 | 1720 | 0 | 1876 | 833 | 81 | 110 | 48 | 130 | 0 | 0 | 87.8
2:00 | 0 | 0 | 195 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 280 | 265 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 20 | 33 | 16 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 151 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 305 | 171 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 33 | 22 | 126 | 157 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 30 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 70 | 0 | 90 | 17 | 100 | 400 | 115 | 17 | 68 | 0 | 281 | 54 | 110 | 98 | 100 | 10 | 280 | 0 | 0 | 54 | 113 | 0 | 17 | 0 | 17 | 55 |  | 713 | 0 | 410 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 68 | 0 | 200 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 189 | 0 | 73 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 |  | 6428 | 2788 | 9216 | 4072 | 713 | 1540 | 0 | 1806 | 768 | 81 | 110 | 0 | 126 | 0 | 0 | 87.79
3:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 280 | 265 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 10 | 33 | 16 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 140 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 260 | 295 | 173 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 33 | 22 | 124 | 157 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 219 | 30 | 81 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 63 | 0 | 90 | 17 | 100 | 400 | 45 | 17 | 68 | 0 | 281 | 54 | 110 | 70 | 101 | 0 | 280 | 0 | 0 | 17 | 113 | 0 | 17 | 0 | 0 | 55 |  | 717 | 0 | 340 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 68 | 0 | 200 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 174 | 0 | 225 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 500 | 108 | 0 | 0 | 0 | 0 | 0 |  | 6181 | 2795 | 8976 | 3896 | 717 | 1685 | 0 | 1595 | 768 | 81 | 110 | 0 | 124 | 0 | 0 | 87.78
4:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 280 | 270 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 19 | 33 | 17 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 81 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 260 | 270 | 200 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 33 | 22 | 120 | 157 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 222 | 30 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 50 | 0 | 90 | 0 | 50 | 400 | 24 | 17 | 34 | 0 | 281 | 54 | 110 | 34 | 106 | 0 | 280 | 0 | 0 | 17 | 113 | 0 | 17 | 0 | 0 | 17 |  | 713 | 0 | 300 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 55 | 0 | 200 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 165 | 0 | 325 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 109 | 0 | 0 | 0 | 0 | 0 |  | 5883 | 2791 | 8674 | 3757 | 713 | 1783 | 0 | 1355 | 755 | 81 | 110 | 0 | 120 | 0 | 0 | 87.77
5:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 280 | 240 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 19 | 33 | 17 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 80 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 260 | 270 | 219 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 33 | 22 | 114 | 158 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 30 | 84 | 0 | 0 | 0 | 0 | 10 | 270 | 23 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 50 | 0 | 90 | 0 | 50 | 355 | 24 | 17 | 34 | 0 | 281 | 54 | 68 | 34 | 46 | 0 | 280 | 0 | 0 | 17 | 68 | 0 | 17 | 0 | 0 | 17 |  | 712 | 0 | 270 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 53 | 0 | 200 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 163 | 0 | 381 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 109 | 0 | 0 | 0 | 0 | 0 |  | 5619 | 2812 | 8431 | 3667 | 712 | 1789 | 0 | 1205 | 753 | 81 | 110 | 0 | 114 | 0 | 0 | 87.76
6:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 280 | 285 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 19 | 33 | 17 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 80 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 260 | 270 | 219 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 33 | 22 | 106 | 158 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 218 | 30 | 84 | 0 | 0 | 0 | 0 | 10 | 280 | 23 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 46 | 0 | 90 | 0 | 10 | 365 | 24 | 17 | 34 | 0 | 235 | 54 | 51 | 0 | 26 | 0 | 220 | 0 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 17 |  | 718 | 0 | 270 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 53 | 0 | 200 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 163 | 0 | 435 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 109 | 0 | 0 | 0 | 0 | 0 |  | 5234 | 2870 | 8104 | 3560 | 718 | 1896 | 0 | 880 | 753 | 81 | 110 | 0 | 106 | 0 | 0 | 87.75
7:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 280 | 285 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 19 | 33 | 33 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 36 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 310 | 219 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 33 | 22 | 100 | 161 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 30 | 81 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 17 | 0 | 90 | 0 | 10 | 364 | 24 | 17 | 34 | 0 | 210 | 54 | 51 | 0 | 26 | 0 | 235 | 0 | 5 | 17 | 34 | 0 | 17 | 4 | 0 | 17 |  | 719 | 0 | 270 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 53 | 0 | 200 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 173 | 0 | 431 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 109 | 0 | 0 | 0 | 0 | 0 |  | 5261 | 2882 | 8143 | 3640 | 719 | 1905 | 0 | 826 | 753 | 81 | 110 | 0 | 100 | 9 | 0 | 87.74
8:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 300 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 19 | 33 | 33 | 0 | 0 | 46 | 35 | 0 | 150 | 0 | 25 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 42 | 0 | 0 | 0 | 260 | 270 | 183 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 33 | 16 | 92 | 209 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 30 | 81 | 0 | 0 | 0 | 0 | 10 | 290 | 23 | 8 | 0 | 0 | 0 | 0 | 163 | 0 | 36 | 0 | 90 | 0 | 35 | 400 | 43 | 17 | 34 | 1 | 210 | 54 | 51 | 0 | 78 | 0 | 235 | 0 | 17 | 26 | 34 | 0 | 17 | 13 | 0 | 32 |  | 719 | 0 | 280 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 53 | 0 | 199 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 171 | 0 | 436 | 0 | 0 | 67 | 0 | 50 | 0 | 1 | 20 | 500 | 109 | 0 | 0 | 1 | 33 | 35 |  | 5307 | 3046 | 8353 | 3510 | 719 | 1871 | 0 | 1152 | 752 | 81 | 110 | 0 | 92 | 66 | 0 | 87.73
9:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 300 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 10 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 38 | 0 | 0 | 0 | 260 | 270 | 183 | 112 | 0 | 26 | 20 | 0 | 51 | 0 | 0 | 2 | 22 | 5 | 33 | 16 | 92 | 196 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 218 | 30 | 84 | 0 | 0 | 0 | 0 | 10 | 275 | 23 | 8 | 0 | 2 | 0 | 0 | 172 | 0 | 83 | 0 | 90 | 0 | 98 | 351 | 66 | 17 | 34 | 2 | 211 | 54 | 51 | 0 | 107 | 6 | 335 | 5 | 29 | 54 | 34 | 0 | 17 | 21 | 0 | 38 |  | 718 | 0 | 280 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 53 | 0 | 199 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 164 | 0 | 236 | 11 | 0 | 90 | 0 | 90 | 0 | 3 | 35 | 500 | 107 | 0 | 0 | 3 | 57 | 70 |  | 5545 | 3020 | 8565 | 3529 | 718 | 1662 | 0 | 1507 | 752 | 35 | 110 | 45 | 92 | 115 | 0 | 87.72
10:00 | 0 | 0 | 200 | 0 | 290 | 101 | 0 | 0 | 0 |  | 0 | 300 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 11 | 0 | 38 | 0 | 0 | 0 | 280 | 295 | 198 | 112 | 0 | 26 | 20 | 0 | 51 | 0 | 0 | 8 | 22 | 5 | 33 | 16 | 106 | 179 | 0 | 14 | 2 | 30 | 30 | 48 | 0 | 0 | 220 | 30 | 84 | 0 | 0 | 0 | 0 | 10 | 285 | 23 | 8 | 0 | 15 | 0 | 0 | 182 | 0 | 64 | 0 | 60 | 0 | 100 | 352 | 106 | 17 | 34 | 3 | 211 | 54 | 51 | 0 | 65 | 10 | 350 | 17 | 40 | 17 | 34 | 0 | 17 | 27 | 0 | 17 |  | 719 | 0 | 280 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 48 | 0 | 199 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 167 | 0 | 417 | 17 | 0 | 50 | 0 | 110 | 0 | 4 | 35 | 500 | 107 | 0 | 0 | 4 | 75 | 70 |  | 5624 | 3220 | 8844 | 3596 | 719 | 1874 | 0 | 1449 | 747 | 35 | 110 | 53 | 106 | 155 | 0 | 87.71
11:00 | 0 | 0 | 200 | 0 | 290 | 95 | 0 | 0 | 0 |  | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 12 | 0 | 22 | 0 | 0 | 0 | 295 | 330 | 205 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 8 | 22 | 5 | 33 | 19 | 108 | 179 | 0 | 14 | 2 | 30 | 30 | 48 | 0 | 0 | 218 | 30 | 83 | 0 | 0 | 0 | 0 | 10 | 310 | 23 | 8 | 0 | 15 | 0 | 0 | 180 | 0 | 52 | 19 | 60 | 0 | 107 | 353 | 107 | 52 | 34 | 4 | 246 | 54 | 54 | 17 | 76 | 10 | 382 | 18 | 44 | 17 | 37 | 0 | 17 | 27 | 0 | 17 |  | 718 | 0 | 320 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 8 | 53 | 0 | 199 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 200 | 0 | 416 | 17 | 0 | 50 | 0 | 112 | 0 | 5 | 35 | 500 | 106 | 0 | 0 | 5 | 88 | 70 |  | 5861 | 3345 | 9206 | 3784 | 718 | 1901 | 0 | 1551 | 752 | 35 | 110 | 53 | 108 | 194 | 0 | 87.7
12:00 | 0 | 0 | 200 | 0 | 280 | 95 | 0 | 0 | 0 |  | 0 | 300 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 27 | 33 | 25 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 5 | 12 | 0 | 22 | 0 | 0 | 0 | 340 | 305 | 188 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 23 | 22 | 5 | 16 | 18 | 134 | 178 | 0 | 17 | 2 | 30 | 30 | 48 | 0 | 0 | 217 | 30 | 81 | 0 | 0 | 0 | 0 | 10 | 300 | 20 | 8 | 0 | 15 | 0 | 0 | 180 | 0 | 89 | 19 | 76 | 0 | 113 | 404 | 107 | 52 | 34 | 4 | 281 | 54 | 74 | 34 | 97 | 30 | 380 | 32 | 49 | 58 | 62 | 0 | 17 | 27 | 0 | 33 |  | 718 | 0 | 360 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 52 | 0 | 199 | 0 | 0 | 10 | 0 | 204 | 0 | 0 | 0 | 200 | 0 | 417 | 20 | 0 | 87 | 0 | 112 | 0 | 6 | 50 | 520 | 105 | 0 | 0 | 5 | 89 | 70 |  | 6193 | 3429 | 9622 | 3804 | 718 | 1890 | 0 | 1906 | 771 | 35 | 110 | 53 | 134 | 201 | 0 | 87.68
13:00 | 0 | 0 | 200 | 0 | 270 | 95 | 0 | 0 | 0 |  | 0 | 300 | 260 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 27 | 33 | 25 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 5 | 12 | 0 | 22 | 0 | 0 | 0 | 310 | 305 | 183 | 110 | 90 | 29 | 20 | 0 | 51 | 0 | 0 | 29 | 22 | 5 | 28 | 18 | 124 | 162 | 0 | 17 | 2 | 30 | 30 | 50 | 0 | 0 | 215 | 30 | 81 | 0 | 0 | 0 | 0 | 10 | 305 | 20 | 11 | 0 | 26 | 0 | 0 | 178 | 0 | 112 | 19 | 90 | 1 | 115 | 404 | 107 | 58 | 49 | 4 | 281 | 54 | 110 | 70 | 106 | 48 | 381 | 55 | 46 | 90 | 74 | 0 | 17 | 30 | 5 | 37 |  | 717 | 0 | 400 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 16 | 0 | 13 | 0 | 8 | 50 | 0 | 199 | 0 | 0 | 10 | 0 | 201 | 0 | 0 | 0 | 194 | 0 | 417 | 35 | 0 | 94 | 0 | 111 | 0 | 0 | 100 | 560 | 103 | 0 | 0 | 5 | 86 | 70 |  | 6480 | 3572 | 10052 | 3878 | 717 | 1858 | 0 | 2277 | 809 | 35 | 110 | 52 | 124 | 192 | 0 | 87.67
14:00 | 0 | 0 | 200 | 0 | 270 | 95 | 0 | 0 | 0 |  | 0 | 300 | 240 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 58 | 55 | 0 | 0 | 0 | 0 | 54 | 5 | 55 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 31 | 0 | 0 | 0 |  | 0 | 8 | 0 | 10 | 5 | 13 | 0 | 35 | 0 | 0 | 0 | 280 | 305 | 182 | 113 | 88 | 29 | 20 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 18 | 136 | 161 | 0 | 17 | 2 | 30 | 30 | 50 | 0 | 0 | 222 | 30 | 82 | 0 | 0 | 0 | 0 | 10 | 280 | 20 | 11 | 0 | 138 | 0 | 0 | 178 | 0 | 149 | 18 | 90 | 17 | 120 | 404 | 108 | 105 | 92 | 4 | 281 | 54 | 110 | 70 | 105 | 60 | 387 | 72 | 40 | 90 | 76 | 0 | 17 | 27 | 21 | 37 |  | 718 | 0 | 390 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 24 | 0 | 13 | 0 | 8 | 63 | 0 | 200 | 0 | 0 | 10 | 0 | 183 | 0 | 0 | 0 | 171 | 0 | 360 | 53 | 0 | 94 | 0 | 107 | 0 | 6 | 113 | 570 | 99 | 0 | 0 | 4 | 75 | 70 |  | 6908 | 3515 | 10423 | 3821 | 718 | 1770 | 0 | 2709 | 833 | 35 | 110 | 115 | 136 | 176 | 0 | 0
15:00 | 0 | 0 | 200 | 0 | 270 | 93 | 0 | 0 | 0 |  | 0 | 300 | 240 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 64 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 29 | 0 | 0 | 0 | 280 | 280 | 183 | 117 | 90 | 29 | 20 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 33 | 13 | 128 | 176 | 0 | 0 | 2 | 30 | 30 | 50 | 0 | 0 | 218 | 30 | 80 | 0 | 0 | 0 | 0 | 10 | 285 | 13 | 11 | 0 | 195 | 0 | 0 | 187 | 0 | 149 | 14 | 90 | 17 | 120 | 404 | 108 | 105 | 105 | 3 | 281 | 54 | 110 | 70 | 105 | 60 | 386 | 73 | 30 | 96 | 94 | 0 | 17 | 21 | 20 | 39 |  | 718 | 0 | 375 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 24 | 0 | 13 | 0 | 8 | 70 | 0 | 200 | 0 | 0 | 10 | 0 | 160 | 0 | 0 | 0 | 163 | 0 | 351 | 53 | 0 | 94 | 0 | 100 | 0 | 4 | 113 | 570 | 101 | 0 | 0 | 3 | 57 | 70 |  | 6963 | 3452 | 10415 | 3729 | 718 | 1763 | 0 | 2832 | 840 | 35 | 120 | 116 | 128 | 134 | 0 | 0
16:00 | 0 | 0 | 200 | 0 | 270 | 96 | 0 | 0 | 0 |  | 0 | 300 | 270 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 33 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 9 | 0 | 0 | 29 | 0 | 0 | 0 | 290 | 290 | 186 | 117 | 90 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 33 | 13 | 130 | 176 | 0 | 14 | 1 | 30 | 30 | 50 | 0 | 0 | 216 | 30 | 82 | 0 | 0 | 0 | 0 | 10 | 280 | 20 | 11 | 0 | 195 | 0 | 0 | 187 | 0 | 127 | 9 | 90 | 17 | 118 | 405 | 108 | 50 | 105 | 1 | 281 | 54 | 110 | 34 | 105 | 40 | 377 | 76 | 18 | 117 | 94 | 0 | 17 | 13 | 18 | 54 |  | 718 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 24 | 0 | 13 | 0 | 8 | 68 | 0 | 200 | 0 | 0 | 10 | 0 | 160 | 0 | 0 | 0 | 164 | 0 | 352 | 53 | 0 | 94 | 0 | 70 | 0 | 2 | 50 | 570 | 103 | 0 | 0 | 2 | 37 | 70 |  | 6834 | 3332 | 10166 | 3743 | 718 | 1815 | 0 | 2584 | 838 | 35 | 120 | 100 | 130 | 83 | 0 | 0
17:00 | 0 | 0 | 200 | 0 | 270 | 93 | 0 | 0 | 0 |  | 0 | 300 | 255 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 32 | 0 | 0 | 0 |  | 16 | 0 | 0 | 10 | 6 | 21 | 0 | 29 | 0 | 0 | 0 | 280 | 290 | 184 | 117 | 90 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 33 | 20 | 140 | 178 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 30 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 0 | 195 | 0 | 0 | 187 | 0 | 122 | 3 | 90 | 17 | 120 | 366 | 108 | 50 | 105 | 1 | 281 | 54 | 104 | 34 | 105 | 40 | 350 | 82 | 6 | 126 | 100 | 0 | 17 | 5 | 17 | 39 |  | 717 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 52 | 0 | 0 | 0 | 24 | 0 | 14 | 0 | 8 | 73 | 0 | 200 | 0 | 0 | 10 | 0 | 160 | 0 | 0 | 0 | 164 | 0 | 350 | 53 | 0 | 94 | 0 | 70 | 0 | 1 | 50 | 540 | 106 | 0 | 0 | 0 | 15 | 70 |  | 6772 | 3302 | 10074 | 3680 | 717 | 1808 | 0 | 2608 | 813 | 35 | 120 | 122 | 140 | 31 | 0 | 0
18:00 | 0 | 0 | 200 | 0 | 270 | 97 | 0 | 0 | 0 |  | 0 | 300 | 270 | 0 | 0 | 30 | 26 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 19 | 33 | 33 | 6 | 0 | 0 | 35 | 0 | 150 | 3 | 66 | 0 | 0 | 0 |  | 20 | 2 | 49 | 10 | 5 | 50 | 0 | 34 | 0 | 0 | 0 | 285 | 300 | 189 | 117 | 90 | 29 | 40 | 0 | 51 | 0 | 11 | 43 | 18 | 5 | 33 | 20 | 144 | 178 | 0 | 14 | 0 | 30 | 30 | 50 | 0 | 0 | 221 | 30 | 85 | 0 | 0 | 0 | 0 | 10 | 270 | 22 | 11 | 0 | 195 | 0 | 0 | 187 | 0 | 122 | 0 | 90 | 17 | 127 | 366 | 108 | 50 | 105 | 0 | 281 | 54 | 110 | 34 | 105 | 40 | 340 | 89 | 0 | 126 | 113 | 0 | 17 | 0 | 17 | 55 |  | 717 | 0 | 365 | 0 | 0 | 120 | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 5 | 5 | 90 | 0 | 8 | 10 | 24 | 18 | 16 | 0 | 11 | 68 | 0 | 200 | 0 | 0 | 10 | 0 | 159 | 0 | 0 | 0 | 163 | 0 | 305 | 53 | 0 | 94 | 0 | 70 | 0 | 0 | 50 | 520 | 106 | 0 | 0 | 0 | 0 | 70 |  | 7002 | 3312 | 10314 | 3760 | 717 | 1772 | 0 | 2706 | 788 | 35 | 120 | 272 | 144 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 270 | 97 | 0 | 0 | 0 |  | 0 | 300 | 250 | 0 | 0 | 42 | 211 | 0 | 0 | 0 | 64 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 27 | 33 | 33 | 20 | 0 | 0 | 35 | 0 | 150 | 19 | 56 | 0 | 0 | 0 |  | 22 | 0 | 51 | 50 | 6 | 50 | 0 | 33 | 0 | 0 | 0 | 310 | 310 | 214 | 118 | 89 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 21 | 152 | 179 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 50 | 85 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 11 | 0 | 270 | 0 | 0 | 188 | 0 | 142 | 0 | 90 | 75 | 137 | 403 | 108 | 80 | 105 | 0 | 281 | 54 | 110 | 100 | 106 | 100 | 383 | 90 | 0 | 126 | 113 | 0 | 17 | 0 | 45 | 55 |  | 718 | 0 | 360 | 0 | 0 | 180 | 0 | 0 | 40 | 2 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 43 | 7 | 90 | 0 | 43 | 40 | 43 | 31 | 17 | 0 | 11 | 70 | 0 | 200 | 0 | 0 | 10 | 0 | 184 | 0 | 0 | 0 | 182 | 0 | 420 | 94 | 0 | 94 | 0 | 110 | 0 | 0 | 100 | 560 | 107 | 0 | 0 | 0 | 0 | 115 |  | 7977 | 3898 | 11875 | 4150 | 718 | 1905 | 0 | 3451 | 830 | 35 | 180 | 454 | 152 | 0 | 0 | 0
19:30 | 0 | 0 | 200 | 0 | 270 | 98 | 0 | 0 | 0 |  | 0 | 300 | 220 | 0 | 0 | 55 | 214 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 27 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 25 | 56 | 0 | 0 | 0 |  | 22 | 0 | 51 | 50 | 5 | 50 | 0 | 33 | 0 | 0 | 0 | 310 | 310 | 210 | 73 | 90 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 21 | 152 | 178 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 221 | 50 | 85 | 0 | 0 | 0 | 0 | 10 | 256 | 23 | 11 | 0 | 280 | 0 | 0 | 188 | 0 | 149 | 0 | 90 | 170 | 143 | 402 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 98 | 107 | 100 | 400 | 90 | 0 | 126 | 113 | 0 | 17 | 0 | 99 | 55 |  | 718 | 0 | 350 | 0 | 0 | 170 | 0 | 0 | 35 | 8 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 43 | 26 | 90 | 0 | 43 | 40 | 52 | 32 | 17 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 10 | 0 | 206 | 0 | 0 | 0 | 205 | 0 | 399 | 94 | 0 | 94 | 0 | 110 | 0 | 0 | 113 | 580 | 100 | 0 | 0 | 0 | 0 | 115 |  | 8114 | 3961 | 12075 | 4201 | 718 | 1760 | 0 | 3712 | 852 | 35 | 170 | 475 | 152 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 270 | 98 | 0 | 0 | 0 |  | 0 | 300 | 255 | 0 | 0 | 55 | 213 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 25 | 52 | 0 | 0 | 0 |  | 22 | 0 | 17 | 50 | 5 | 50 | 0 | 33 | 0 | 0 | 0 | 310 | 310 | 202 | 26 | 89 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 21 | 156 | 183 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 219 | 50 | 86 | 0 | 0 | 0 | 0 | 10 | 260 | 23 | 11 | 0 | 287 | 0 | 0 | 179 | 0 | 149 | 0 | 90 | 190 | 140 | 402 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 98 | 106 | 100 | 395 | 90 | 0 | 126 | 113 | 0 | 17 | 0 | 91 | 55 |  | 718 | 0 | 345 | 0 | 0 | 140 | 0 | 0 | 0 | 9 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 0 | 25 | 40 | 52 | 31 | 17 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 10 | 0 | 210 | 0 | 0 | 0 | 205 | 0 | 382 | 94 | 0 | 94 | 0 | 111 | 0 | 0 | 113 | 580 | 107 | 0 | 0 | 0 | 0 | 115 |  | 8087 | 3842 | 11929 | 4184 | 718 | 1743 | 0 | 3721 | 852 | 35 | 140 | 380 | 156 | 0 | 0 | 0
21:00 | 0 | 0 | 200 | 0 | 270 | 101 | 0 | 0 | 0 |  | 0 | 300 | 260 | 0 | 0 | 55 | 214 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 25 | 61 | 0 | 0 | 0 |  | 22 | 0 | 17 | 50 | 5 | 50 | 0 | 42 | 0 | 0 | 0 | 320 | 310 | 216 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 21 | 148 | 183 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 222 | 50 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 23 | 11 | 0 | 278 | 0 | 0 | 179 | 0 | 149 | 0 | 90 | 170 | 145 | 402 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 98 | 105 | 100 | 394 | 91 | 0 | 126 | 107 | 0 | 17 | 0 | 90 | 55 |  | 718 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 0 | 25 | 40 | 52 | 31 | 17 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 10 | 0 | 212 | 0 | 0 | 0 | 199 | 0 | 383 | 94 | 0 | 94 | 0 | 111 | 0 | 0 | 113 | 640 | 100 | 0 | 0 | 0 | 0 | 115 |  | 8134 | 3848 | 11982 | 4199 | 718 | 1789 | 0 | 3690 | 912 | 35 | 120 | 371 | 148 | 0 | 0 | 0
22:00 | 0 | 0 | 200 | 0 | 270 | 101 | 0 | 0 | 0 |  | 0 | 320 | 255 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 59 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 6 | 50 | 0 | 42 | 0 | 0 | 0 | 320 | 310 | 216 | 26 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 144 | 184 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 222 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 278 | 0 | 0 | 179 | 0 | 149 | 0 | 90 | 85 | 142 | 401 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 98 | 106 | 100 | 398 | 91 | 0 | 126 | 113 | 0 | 17 | 0 | 79 | 55 |  | 717 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 52 | 30 | 17 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 10 | 0 | 212 | 0 | 0 | 0 | 189 | 0 | 383 | 94 | 0 | 94 | 0 | 111 | 0 | 0 | 113 | 630 | 103 | 0 | 0 | 0 | 0 | 115 |  | 7944 | 3710 | 11654 | 4198 | 717 | 1804 | 0 | 3464 | 902 | 35 | 120 | 270 | 144 | 0 | 0 | 87.55
23:00 | 0 | 0 | 200 | 0 | 280 | 101 | 0 | 0 | 0 |  | 0 | 320 | 240 | 0 | 0 | 55 | 219 | 0 | 0 | 0 | 93 | 100 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 59 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 6 | 50 | 0 | 42 | 0 | 0 | 0 | 320 | 310 | 186 | 55 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 21 | 136 | 186 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 218 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 24 | 11 | 0 | 295 | 0 | 0 | 178 | 0 | 149 | 0 | 90 | 17 | 143 | 401 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 70 | 107 | 100 | 400 | 91 | 0 | 126 | 113 | 0 | 17 | 0 | 50 | 55 |  | 717 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 11 | 73 | 0 | 200 | 0 | 0 | 13 | 0 | 204 | 0 | 0 | 0 | 183 | 0 | 380 | 94 | 0 | 94 | 0 | 111 | 0 | 0 | 113 | 630 | 104 | 0 | 0 | 0 | 0 | 54 |  | 7747 | 3606 | 11353 | 4166 | 717 | 1807 | 0 | 3279 | 903 | 35 | 120 | 190 | 136 | 0 | 0 | 87.54
24:00 | 0 | 0 | 200 | 0 | 280 | 101 | 0 | 0 | 0 |  | 0 | 320 | 250 | 0 | 0 | 15 | 219 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 56 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 6 | 50 | 0 | 42 | 0 | 0 | 0 | 320 | 310 | 218 | 55 | 90 | 29 | 55 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 22 | 140 | 179 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 219 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 275 | 24 | 11 | 0 | 195 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 0 | 145 | 400 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 17 | 100 | 100 | 330 | 92 | 0 | 126 | 113 | 0 | 17 | 0 | 17 | 55 |  | 718 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 13 | 0 | 195 | 0 | 0 | 0 | 183 | 0 | 417 | 94 | 0 | 94 | 0 | 80 | 0 | 0 | 113 | 620 | 105 | 0 | 0 | 0 | 0 | 34 |  | 7347 | 3538 | 10885 | 4114 | 718 | 1860 | 0 | 2860 | 900 | 35 | 120 | 138 | 140 | 0 | 0 | 0
KWH | 0 | 0 | 4814000 | 0 | 6709055 | 2310454 | 0 | 0 | 0 |  | 0 | 7007000 | 6340975 | 0 | 0 | 448907 | 2614474 | 0 | 0 | 0 | 762192 | 1068000 | 0 | 0 | 0 | 0 | 1243440 | 253391 | 626756 | 416376 | 600000 | 541620 | 816500 | 695600 | 74880 | 0 | 406500 | 844000 | 0 | 3700000 | 89278 | 1407499 | 0 | 0 | 0 |  | 299040 | 9744 | 125243 | 248040 | 149760 | 449760 | 0 | 897120 | 0 | 0 | 0 | 7310000 | 7215000 | 4690000 | 2375272 | 1064380 | 650448 | 796320 | 0 | 1172019 | 0 | 10104 | 724430 | 496548 | 174420 | 778300 | 495200 | 2990400 | 4039680 | 0 | 330912 | 15250 | 715000 | 693664 | 1196400 | 0 | 0 | 5076000 | 867072 | 2007360 | 0 | 0 | 0 | 0 | 247140 | 7002500 | 515640 | 241056 | 0 | 2734908 | 0 | 0 | 4360800 | 0 | 2448144 | 104760 | 2054400 | 816000 | 2569309 | 9384000 | 2097600 | 1359600 | 1684429 | 27359 | 6342982 | 1335225 | 2308353 | 1200420 | 2300760 | 1005120 | 8017200 | 1094400 | 326530 | 1880640 | 2056200 | 0 | 443520 | 224692 | 655680 | 986400 |  | 17354909 | 0 | 8373312 | 0 | 0 | 2964480 | 0 | 0 | 84480 | 11964 | 0 | 0 | 510300 | 0 | 0 | 0 | 720000 | 132684 | 27460 | 1010488 | 0 | 107263 | 126095 | 399571 | 136068 | 324720 | 0 | 246420 | 1495418 | 0 | 4865400 | 0 | 0 | 176200 | 0 | 4574691 | 0 | 0 | 0 | 4521364 | 0 | 8614545 | 954240 | 0 | 2006112 | 0 | 1631712 | 0 | 35818 | 1361376 | 14618500 | 2563036 | 0 | 0 | 37320 | 627120 | 1338894 |  | 159679550 | 81951960 | 241631510 | 93681631 | 17354909 | 43365161 | 0 | 54903932 | 20979318 | 1250500 | 2964480 | 2742330 | 2990400 | 1398849 | 0
Fuel Cost | 0 | 0 | 7028440 | 0 | 7447051.05 | 3049799.28 | 0 | 0 | 0 |  | 0 | 7637630 | 7038482.25 | 0 | 0 | 3797753.22 | 2719052.96 | 0 | 0 | 0 | 6951191.04 | 10509120 | 0 | 0 | 0 | 0 | 9077112 | 1958712.43 | 6179814.16 | 312282 | 450000 | 0 | 0 | 0 | 724089.6 | 0 | 109755 | 227880 | 0 | 6697000 | 829392.62 | 1534173.91 | 0 | 0 | 0 |  | 0 | 94224.48 | 1214857.1 | 2368782 | 1302912 | 3562099.2 | 0 | 2664446.4 | 0 | 0 | 0 | 5409400 | 7215000 | 4314800 | 3064100.88 | 1224037 | 735006.24 | 1114848 | 0 | 2004152.49 | 0 | 102050.4 | 6918306.5 | 630615.96 | 130815 | 1362025 | 371400 | 22428000 | 4282060.8 | 0 | 420258.24 | 243085 | 1172600 | 1109862.4 | 2129592 | 0 | 0 | 5279040 | 1708131.84 | 3834057.6 | 0 | 0 | 0 | 0 | 504165.6 | 7072525 | 386730 | 183202.56 | 0 | 20675904.48 | 0 | 0 | 22676160 | 0 | 24089736.96 | 1224644.4 | 16743360 | 8853600 | 18113628.45 | 8727120 | 19130112 | 12848220 | 14671376.59 | 0 | 47952943.92 | 11629809.75 | 20290422.87 | 11980191.6 | 19717513.2 | 6694099.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99964275.84 | 0 | 8791977.6 | 0 | 0 | 41087692.8 | 0 | 0 | 886195.2 | 125382.72 | 0 | 0 | 790965 | 0 | 0 | 0 | 1476000 | 1305610.56 | 278993.6 | 8942818.8 | 0 | 1450195.76 | 1221860.55 | 3871842.99 | 1319859.6 | 623462.4 | 0 | 186539.94 | 9017370.54 | 0 | 26370468 | 0 | 0 | 206154 | 0 | 6038592.12 | 0 | 0 | 0 | 5289995.88 | 0 | 8528399.55 | 9962265.6 | 0 | 19038002.88 | 0 | 12662085.12 | 0 | 395788.9 | 10060568.64 | 64175215 | 0 | 0 | 0 | 0 | 0 | 0 |  | 466854764.63 | 344068579.59 | 810923344.22 | 92839364.5 | 99964275.84 | 50056626.45 | 0 | 376782204.78 | 99563053.54 | 337635 | 41087692.8 | 26000973.01 | 22428000 | 1863518.3 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 280 | 95 | 0 | 0 | 0 |  | 0 | 300 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 27 | 33 | 25 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 26 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 5 | 12 | 0 | 22 | 0 | 0 | 0 | 340 | 305 | 188 | 112 | 0 | 29 | 20 | 0 | 51 | 0 | 0 | 23 | 22 | 5 | 16 | 18 | 134 | 178 | 0 | 17 | 2 | 30 | 30 | 48 | 0 | 0 | 217 | 30 | 81 | 0 | 0 | 0 | 0 | 10 | 300 | 20 | 8 | 0 | 15 | 0 | 0 | 180 | 0 | 89 | 19 | 76 | 0 | 113 | 404 | 107 | 52 | 34 | 4 | 281 | 54 | 74 | 34 | 97 | 30 | 380 | 32 | 49 | 58 | 62 | 0 | 17 | 27 | 0 | 33 |  | 718 | 0 | 360 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 52 | 0 | 199 | 0 | 0 | 10 | 0 | 204 | 0 | 0 | 0 | 200 | 0 | 417 | 20 | 0 | 87 | 0 | 112 | 0 | 6 | 50 | 520 | 105 | 0 | 0 | 5 | 89 | 70 |  | 9622 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 270 | 98 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 55 | 214 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 27 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 25 | 56 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 50 | 5 | 50 | 0 | 33 | 0 | 0 | 0 | 310 | 310 | 210 | 73 | 90 | 29 | 40 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 21 | 152 | 178 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 221 | 50 | 85 | 0 | 0 | 0 | 0 | 10 | 256 | 23 | 11 | 0 | 280 | 0 | 0 | 188 | 0 | 149 | 0 | 90 | 170 | 143 | 402 | 108 | 105 | 105 | 0 | 281 | 54 | 110 | 98 | 107 | 100 | 400 | 90 | 0 | 126 | 113 | 0 | 17 | 0 | 99 | 55 |  | 718 | 0 | 350 | 0 | 0 | 170 | 0 | 0 | 35 | 8 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 43 | 26 | 90 | 0 | 43 | 40 | 52 | 32 | 17 | 0 | 11 | 72 | 0 | 200 | 0 | 0 | 10 | 0 | 206 | 0 | 0 | 0 | 205 | 0 | 399 | 94 | 0 | 94 | 0 | 110 | 0 | 0 | 113 | 580 | 100 | 0 | 0 | 0 | 0 | 115 |  | 12075 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 280 | 100 | 0 | 0 | 0 | 0 | 0 | 300 | 335 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 150 | 25 | 150 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 6 | 50 | 0 | 25 | 0 | 0 | 0 | 330 | 330 | 220 | 110 | 90 | 29 | 40 | 0 | 51 | 0 | 32 | 52 | 22 | 8 | 33 | 22 | 163 | 178 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 220 | 50 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 383 | 72 | 0 | 162 | 113 | 0 | 17 |  | 100 | 55 |  | 731 | 0 | 360 | 0 | 0 | 220 | 0 | 0 | 40 | 40 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 43 | 40 | 92 | 0 | 43 | 40 | 52 | 30 | 22 | 0 | 11 | 60 | 0 | 200 | 0 | 0 | 10 | 0 | 220 | 0 | 0 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 650 | 110 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 180 | 0 | 280 | 100 | 0 | 0 | 0 | 0 | 0 | 300 | 335 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 51 | 0 | 46 | 35 | 0 | 150 | 25 | 150 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 6 | 50 | 0 | 10 | 0 | 0 | 0 | 330 | 330 | 220 | 110 | 90 | 29 | 20 | 0 | 51 | 0 | 32 | 52 | 22 | 8 | 33 | 22 | 138 | 160 | 0 | 17 | 1.6 | 30 | 30 | 50 | 0 | 0 | 220 | 30 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 98 | 113 | 100 | 383 | 72 | 50 | 162 | 113 | 0 | 17 | 30 | 100 | 55 |  | 731 | 0 | 360 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 43 | 40 | 90 | 0 | 43 | 0 | 52 | 25 | 22 | 0 | 11 | 60 | 0 | 200 | 0 | 0 | 10 | 0 | 220 | 0 | 0 | 100 | 210 | 0 | 414 | 105 | 100 | 113 | 0 | 113 | 0 | 8 | 113 | 650 | 110 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 280 | 101 | 0 | 0 | 0 | 0 | 0 | 320 | 280 | 0 | 0 | 55 | 180 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 10 | 5 | 19 | 0 | 14 | 0 | 0 | 0 | 340 | 335 | 185 | 55 | 90 | 23 | 56 | 0 | 51 | 0 | 0 | 16 | 19 | 8 | 33 | 19 | 108 | 178 | 0 | 17 | 1 | 30 | 30 | 50 | 0 | 0 | 222 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 5 | 0 | 45 | 0 | 0 | 180 | 0 | 106 | 9 | 50 | 17 | 145 | 352 | 78 | 70 | 68 | 3 | 281 | 54 | 110 | 17 | 107 | 30 | 340 | 71 | 17 | 54 | 51 | 0 | 17 | 11 | 34 | 37 | 0 | 710 | 0 | 295 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 18 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 5 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 303 | 35 | 0 | 94 | 0 | 100 | 0 | 1 | 70 | 510 | 108 | 0 | 0 | 1 | 35 | 115 | 0
199
| Minimum Generation |  | 8104 | 6:00
| Highest Generation |  | 12075 | 19:30
| Day Peak Generation |  | 9622 | 12:00
| Evening Peak Generation |  | 12075 | 19:30
| HVDC Max Flow |  | 725 | 1:00
| HVDC EvPeak Flow |  | 718 | 19:30
| Load factor L.F |  | 83.38%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-20
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9622 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 9095 | MW
Evening Peak Generation : |  | 12075 | MW Hour : | 19:30 | Available Max Generation : |  | 13987 | MW
E.P. Demand (at gen end) : |  | 12075 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 12075 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1087 | MW
Total Gen. (MKWH) : |  | 241.6315 | System Load Factor : | 83.38% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -162 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-20
Actual : | 87.5 | Ft.(MSL) , | Rule curve : | 89.96 | Ft.( MSL )
Gas Consumed : | Total = | 1068.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142895990.95
: |  | Coal : | 99563053.54 | Oil : | 443870870.59 | Total : | 686329915.08
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4594.0077 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1566.9009 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1404.7259 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1269.5846 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1147.1419 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 925.7147 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 511.5866 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 238.1871 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 713.986 |  |  | 0 | 0%
Total | 0 |  | 12371.8353 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-100 MW & 71 MW
5) Raozan unit- 1
6) Kushiara 163 MW.
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Khulshi 132/33 kV T-1 transformer was under shut down from 08:21 to 09:11 for C/M.
b) Khulshi 132/33 kV T-2 transformer was under shut down from 09:15 to 09:42 for C/M.
c) Chandpur 150 MW CCPP GT was synchronized at 11:57.
d) Sirajganj-Sherpur 132 kV Ckt-2 tripped at 09:16 from Sirajganj end showing Dist. Z2 and was
switched on at 09:39.
e) Sikalbaha 225 MW CCPP STG was synchronized at 17:20 and again tripped at 18:21.
f) Siddhirganj 335 MW CCPP GT was synchronized at 17:24.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4814000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6709055 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 2310454
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7007000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 220 | 6340975 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 448907
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 416376
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 214 | 2614474 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 762192 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1243440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1068000
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 253391 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 626756
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1141620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 816500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 695600
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 74880 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 2734908 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2448144
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1359600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1094400 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1880640 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 224692
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 55 | 55 | 55 | 986400
| Dhaka area Total |  |  |  | 5696 | 2702 | 48072404
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3700000 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 89278
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 104760
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 449760 | 33 kV feeder problem.
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 1250500 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 56 | 1407499
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1684429
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 9744 | Under maint.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 125243 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 248040 | Low demand
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2054400 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 897120
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 5 | 149760 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27359
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 281 | 6342982 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1335225
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2308353
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1005120 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2056200
| Chattogram area Total |  |  |  | 2382 | 1308 | 25245772
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4690000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7310000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7215000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 650448 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 40 | 796320 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 2375272 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1172019
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 2569309
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 10104 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1064380 | Engine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 816000 | High voltage.
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 496548
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 174420 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 2990400
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 778300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 724430 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 495200 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1200420 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 107 | 2300760
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 115 | 115 | 99 | 655680 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2023 | 38928530
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 178 | 4039680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 330912 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15250
87 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 188 | 4360800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 108 | 2097600
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 326530
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 299040
| Mymensingh Area Total |  |  |  | 622 | 513 | 11469812
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 693664 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 221 | 5076000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1196400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 241056
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 867072
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2007360
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 23 | 515640
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 256 | 7002500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9384000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 247140
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8017200
| Sylhet Area Total |  |  |  | 2377 | 1568 | 35963032
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 718 | 17354909
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 84480 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 170 | 2964480 | Low demand
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 8 | 11964 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8373312 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 954240 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 627120
| Khulna Area Total |  |  |  | 2229 | 1375 | 30370505
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 510300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Payra 1320 MW inauguration.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 14618500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 100 | 2563036 | Payra 1320 MW inauguration.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Payra 1320 MW inauguration.
| Barisal Area Total |  |  |  | 2046 | 708 | 17691836
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 720000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 132684 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 26 | 27460 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 107263 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 126095 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 10 | 176200 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 206 | 4574691 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 205 | 4521364 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 399 | 8614545
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 136068 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 324720 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246420
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 399571
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 1010488 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2006112 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1361376
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37320
| Rajshahi Area Total |  |  |  | 2129 | 1381 | 24522377
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1495418
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4865400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 110 | 1631712
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35818
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1338894 | On test
| Rangpur Area Total |  |  |  | 720 | 497 | 9367242
| Total |  |  |  | 21215 | 12075 | 241631510
| Eastern Grid Total |  |  |  | 14091 | 8114 | 159679550
| Western Grid Total |  |  |  | 7124 | 3961 | 81951960
| National Grid Total |  |  |  | 21215 | 12075 | 241631510
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-19
(a) ENTIRE EASTERN GRID : |  | 7652 | MW | (b) ENTIRE WESTERN GRID : |  | 3920 | MW
i) Dhaka area |  | 3820 | MW | i) Khulna area |  | 1373 | MW
ii) Chittagong area |  | 1254 | MW | ii) Rajshahi area |  | 1371 | MW
iii) Comilla area |  | 1130 | MW | iii) Barisal area |  | 311 | MW
iv) Mymensingh area |  | 997 | MW | iv) Rangpur area |  | 865 | MW
v) Sylhet area |  | 451 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11572 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 18:30 | Valuka | 104 | 9:00 | Central S/S | 72 | 19:30
Munsiganj | 82 | 19:30 | Tangail | 204 | 20:00 | Noapara | 44 | 19:30
Sonargaon | 74 | 23:00 | Mymensing | 231 | 20:00 | Jessore | 116 | 19:00
Bhulta | 193 | 18:00 | Kishoreganj | 136 | 23:00 | Benapol | 54 | 19:00
Madanganj | 32 | 23:00 | Netrokona | 128 | 21:00 | Jhenida(Old) | 111 | 19:00
Rahim steel | 5 | 13:00 | Jamalpur | 141 | 10:00 | Bottail | 98 | 18:30
Ghorasal | 70 | 19:30 | Sherpur | 140 | 19:30 | G.K Project | 51 | 19:00
Narsingdi | 167 | 19:30 | Srimongal | 49 | 19:30 | Faridpur | 112 | 19:30
Haripur(SBU) | 94 | 0:00 | Shahjibazar | 106 | 19:30 | Rajbari | 54 | 19:00
Sreenagar | 36 | 18:30 | Fenchuganj | 37 | 19:30 | Madaripur | 87 | 21:00
Shyampur | 180 | 23:00 | Kulawara | 34 | 18:00 | Sariatpur | 54 | 19:00
Shitalakhya | 73 | 23:00 | Sylhet | 130 | 19:00 | Gopalganj | 84 | 19:00
Matuail | 48 | 23:00 | Chatak | 27 | 18:30 | Bagerhat | 91 | 19:00
Char Saidpur | 40 | 17:00 | Sunamganj | 41 | 22:00 | Mongla | 24 | 22:00
Ullon | 40 | 19:30 | Biani Bazar | 51 | 18:30 | Satkhira | 104 | 19:00
Hasnabad | 73 | 23:00 | Comilla (S) | 156 | 20:00 | Gallamari | 46 | 19:30
Magbazar | 85 | 18:30 | Comilla(N) | 149 | 19:30 | Magura | 50 | 19:30
Maniknagar | 53 | 0:00 | Chandpur | 62 | 21:00 | Norail | 39 | 19:00
Bangabhaban | 4 | 12:00 | Feni | 119 | 19:00 | Chuadanga | 89 | 19:00
Motijheel | 21 | 18:30 | Chowmuhani | 185 | 19:00 | Barisal(N) | 44 | 19:30
Narinda | 42 | 18:30 | Ashuganj | 40 | 23:00 | Barisal (S) | 81 | 19:00
Kazla | 70 | 23:00 | Daudkandi | 116 | 19:00 | Patuakhali | 92 | 19:30
Dhanmondi | 116 | 19:00 | B.Baria | 160 | 19:00 | Bhandaria | 43 | 19:00
Lalbag | 56 | 23:00 | Ramganj | 76 | 18:30 | Borguna | 14 | 19:00
Madartek | 75 | 23:00 | Chaddagram | 43 | 19:00 | Borhan Uddin | 40 | 20:00
Dhaka University | 17 | 14:00 | PHP | 8 | 5:00 | Ishurdi | 46 | 19:30
Aftabnagar | 28 | 19:00 | Kochua | 58 | 18:30 | Ruppur Paromanobik | 2 | 1:00
Fatullah | 51 | 0:00 | Madunaghat | 53 | 19:00 | Natore | 138 | 19:30
Nawabganj | 45 | 19:00 | Hathazari | 79 | 19:30 | Bogra | 153 | 19:00
Keraniganj | 54 | 23:00 | Khulshi | 159 | 1:00 | Naogaon | 126 | 19:30
Banani | 42 | 18:30 | Halishahar | 78 | 21:00 | Rajshahi | 141 | 21:00
Mirpur | 99 | 15:00 | Baraulia | 87 | 21:00 | Rajshahi New | 32 | 20:00
Kalyanpur | 84 | 14:00 | Sikalbaha | 29 | 19:30 | C.Nawabganj | 65 | 21:00
Gulshan | 80 | 18:30 | Dohazari | 84 | 19:00 | Amnura | 68 | 19:30
Uttara | 60 | 18:30 | Cox'sbazar | 108 | 14:00 | Pabna | 101 | 19:00
Uttara New | 29 | 22:00 | Chandraghona | 34 | 18:30 | Shahjadpur | 90 | 19:00
Kamrangirchar | 47 | 21:00 | Kaptai | 0 | 1:00 | Serajganj | 102 | 19:30
Savar | 122 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 105 | 19:00
Bhasantec | 112 | 19:00 | Bakulia | 100 | 19:00 | Joypurhat | 61 | 19:00
Agargaon | 66 | 19:30 | Julda | 20 | 19:00 | Sherpur(Bogura) | 56 | 18:30
Satmosjid | 81 | 14:00 | TK chemical | 25 | 21:00 | Mohastangor | 70 | 19:30
Old Tongi | 94 | 15:00 | Modern Steel | 0 | 1:00 | Bhangura | 34 | 19:30
Kabirpur | 173 | 21:00 | Shahmirpur | 29.3 | 18:00 | Rangpur | 147 | 19:00
Manikgonj | 67 | 19:30 | Khagrachhari | 26 | 19:00 | Lalmonirhat | 49 | 19:00
Joydevpur | 147 | 18:30 | Matarbari | 35 | 18:00 | Saidpur | 105 | 18:30
New Tongi | 57 | 20:00 | Baroiar Hat | 58 | 19:30 | Purbasadipur | 112 | 19:00
Kodda | 195 | 21:00 | Rangamati | 12 | 18:30 | Thakurgaon | 91 | 19:00
Dhamrai | 94 | 18:30 | Agrabad | 62 | 18:30 | Palashbari | 123 | 19:30
Rajendrapur | 90 | 19:00 | Rampur | 12 | 19:00 | Barapukuria | 56 | 18:30
Bashundara | 146 | 18:30 | Abul Khair 230 | 12 | 13:00 | Panchagar | 56 | 20:00
Purbachal | 16 | 19:00 | BSRM | 163 | 10:00 | Joldhaka | 68 | 19:30
Tongi Millgate | 36 | 23:00 | GPH Ispat | 89 | 19:30 | Kurigram | 62 | 18:30
Bashundhara Cement |  |  | Goalpara | 21 | 19:00 | Mithapukur | 31 | 19:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 2:00 | 402 | 11:00 | Kaliakoir | 389 | 0.083333 | 374 | 0.45833
| Bheramara | 404 | 9:00 | 397 | 24:00 | Bhulta | 414 | 0.083333 | 396 | 0.45833
| Ashuganj(N) | 420 | 2:00 | 405 | 11:00 | Gopalganj | 412 | 0.625 | 402 | 0.83333
| Payra | 419 | 2:00 | 414 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 236 | 1:00 | 230 | 10:00
| Ishurdi | 238 | 5:00 | 230 | 13:00 | Megnaghat | 241 | 8:00 | 229 | 13:00
| Ashuganj | 248 | 1:00 | 246 | 4:00 | Fenchuganj | 240 | 3:00 | 232 | 16:00
| Serajganj | 236 | 3:00 | 232 | 7:00 | Siddhirganj | 236 | 2:00 | 228 | 9:00
| Baghabari | 235 | 3:00 | 232 | 7:00 | Maniknagar | 234 | 2:00 | 225 | 10:00
| Barapukuria | 230 | 22:00 | 223 | 7:00 | Agargaon | 234 | 5:00 | 223 | 11:00
| Bogra | 229 | 23:00 | 222 | 7:00 | Barisal | 247 | 2:00 | 237 | 18:30
| Rajshahi | 232 | 18:00 | 224 | 13:00 | Bhola 225 MW | 249 | 5:00 | 240 | 18:30
| Khulna South | 241 | 5:00 | 231 | 13:00 | AKSML | 238 | 2:00 | 228 | 11:00
| Rampura | 234 | 1:00 | 224 | 11:00 | BSRM | 237 | 2:00 | 228 | 10:00
| Haripur | 234 | 1:00 | 225 | 11:00 | Bibiyana | 242 | 5:00 | 232 | 22:00
| Hasnabad | 232 | 1:00 | 223 | 12:00 | Bhulta | 236 | 2:00 | 226 | 11:00
| Shyampur | 234 | 2:00 | 224 | 11:00 | Ashuganj (S) | 244 | 3:00 | 236 | 11:00
| Aminbazar | 233 | 1:00 | 224 | 2:00 | Kaliakoir | 230 | 5:00 | 220 | 11:00
| Tongi | 232 | 4:00 | 220 | 11:00 | GPH | 237 | 2:00 | 229 | 10:00
| Comilla (N) | 236 | 2:00 | 226 | 11:00 | Jhenaidah | 236 | 5:00 | 225 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 1:00 | 127 | 11:00 | PHP | 136 | 2:00 | 127 | 11:00
| Munsiganj | 134 | 3:00 | 126 | 11:00 | Kachua | 137 | 19:30 | 126 | 11:00
| Sonargaon | 132 | 1:00 | 126 | 10:00 | Madanhat | 138 | 19:00 | 133 | 9:00
| Bhulta | 128 | 1:00 | 120 | 10:00 | Hathazari | 139 | 17:00 | 135 | 11:00
| Madanganj | 132 | 1:00 | 126 | 11:00 | Khulshi | 136 | 8:00 | 131 | 11:00
| Rahim steel | 133 | 1:00 | 127 | 11:00 | Halishahar | 136 | 2:00 | 131 | 11:00
| Ghorasal | 140 | 1:00 | 138 | 15:00 | Baraulia | 139 | 3:00 | 134 | 11:00
| Narsingdi | 127 | 4:00 | 116 | 11:00 | Sikalbaha | 138 | 3:00 | 133 | 11:00
| Haripur(SBU) | 133 | 1:00 | 127 | 11:00 | Dohazari | 131 | 3:00 | 127 | 10:00
| Sreenagar | 136 | 1:00 | 129 | 11:00 | Cox'sbazar | 132 | 8:00 | 115 | 22:00
| Shyampur | 133 | 3:00 | 127 | 11:00 | Chandraghona | 137 | 1:00 | 134 | 11:00
| Shitalakhya | 133 | 2:00 | 126 | 11:00 | Kaptai | 138 | 1:00 | 125 | 11:00
| Matuail | 133 | 1:00 | 127 | 11:00 | A. Khaer Stl. | 136 | 7:00 | 133 | 10:00
| Char Saidpur | 134 | 2:00 | 126 | 11:00 | Bakulia | 137 | 4:00 | 132 | 11:00
| Ullon | 135 | 1:00 | 129 | 10:00 | Julda | 137 | 2:00 | 133 | 9:00
| Hasnabad | 134 | 1:00 | 128 | 11:00 | TK Chemical | 137 | 7:00 | 133 | 11:00
| Magbazar | 136 | 3:00 | 130 | 11:00 | Modern Steel | 136 | 1:00 | 133 | 11:00
| Maniknagar | 137 | 1:00 | 128 | 11:00 | Shahmirpur | 136 | 2:00 | 133 | 11:00
| Bangabhaban | 137 | 1:00 | 128 | 11:00 | Khagrachhari | 141 | 21:00 | 132 | 11:00
| Motijheel | 137 | 1:00 | 128 | 11:00 | Matarbari | 132 | 8:00 | 118 | 22:00
| Narinda | 137 | 1:00 | 128 | 11:00 | Baroiar Hat | 137 | 1:00 | 127 | 16:00
| Kazla | 137 | 1:00 | 128 | 11:00 | Rangamati | 137 | 3:00 | 132 | 11:00
| Dhanmondi | 134 | 1:00 | 127 | 10:00 | Agrabad | 136 | 2:00 | 133 | 10:00
| Lalbag | 138 | 5:00 | 131 | 11:00 | Rampur | 137 | 9:00 | 134 | 1:00
| Madartek | 135 | 6:00 | 128 | 11:00 | Goalpara S/S | 137 | 2:00 | 133 | 19:00
| Dhaka University | 135 | 2:00 | 129 | 12:00 | Khulna Central S/S | 137 | 3:00 | 132 | 12:00
| Aftabnagar | 135 | 2:00 | 129 | 11:00 | Noapara | 136 | 5:00 | 130 | 19:00
| Fatullah | 134 | 4:00 | 127 | 11:00 | Jessore | 132 | 2:00 | 126 | 19:00
| Nawabganj | 137 | 4:00 | 129 | 12:00 | Benapol | 133 | 4:00 | 125 | 19:00
| Keraniganj | 137 | 2:00 | 130 | 11:00 | Jhenida(Old) | 135 | 4:00 | 127 | 19:00
| Banani | 136 | 7:00 | 129 | 11:00 | Bottail | 137 | 6:00 | 132 | 13:00
| Mirpur | 131 | 1:00 | 124 | 11:00 | G.K Project | 140 | 1:00 | 137 | 19:00
| Kalyanpur | 132 | 5:00 | 119 | 16:00 | Faridpur | 138 | 3:00 | 135 | 13:00
| Gulshan | 135 | 7:00 | 128 | 11:00 | Rajbari | 138 | 2:00 | 133 | 13:00
| Uttara | 136 | 9:00 | 129 | 10:00 | Madaripur | 143 | 6:00 | 136 | 18:30
| Uttara New | 137 | 4:00 | 129 | 10:00 | Shariyatpur S/S | 143 | 5:00 | 135 | 19:00
| Kamrangirchar | 135 | 1:00 | 131 | 11:00 | Gopalganj | 142 | 4:00 | 135 | 21:00
| Savar | 132 | 1:00 | 123 | 11:00 | Bagerhat | 135 | 4:00 | 131 | 12:00
| Bhasantec | 138 | 3:00 | 130 | 11:00 | Mongla | 135 | 3:00 | 130 | 19:00
| Agargaon | 138 | 2:00 | 131 | 11:00 | Satkhira | 136 | 5:00 | 128 | 19:00
| Satmosjid | 138 | 5:00 | 131 | 11:00 | Gallamari | 141 | 5:00 | 133 | 19:00
| Old Tongi | 140 | 4:00 | 133 | 9:00 | Magura | 136 | 5:00 | 126 | 19:00
| Kabirpur | 137 | 19:30 | 126 | 11:00 | Narail | 134 | 6:00 | 125 | 19:00
| Manikgonj | 138 | 6:00 | 131 | 18:00 | Chuadanga | 132 | 5:00 | 119 | 19:00
| Joydevpur | 141 | 19:00 | 135 | 11:00 | Barisal(N) | 145 | 5:00 | 137 | 19:00
| New Tongi | 139 | 4:00 | 130 | 10:00 | Barisal (S) | 143 | 6:00 | 135 | 12:00
| Kodda | 137 | 1:00 | 126 | 10:00 | Patuakhali(S) | 138 | 5:00 | 134 | 15:00
| Dhamrai | 139 | 5:00 | 131 | 11:00 | Bhandaria | 141 | 4:00 | 135 | 19:00
| Rajendrapur | 136 | 14:00 | 126 | 11:00 | Barguna | 140 | 5:00 | 133 | 20:00
| Bashundara | 137 | 19:00 | 129 | 9:00 | Jhenida(New) | 135 | 5:00 | 127 | 19:30
| Purbachal | 135 | 7:00 | 128 | 11:00 | Ishurdi | 138 | 5:00 | 134 | 12:00
| Tongi Millgate | 138 | 12:00 | 130 | 10:00 | Ruppur Paromanobik | 138 | 5:00 | 134 | 11:00
| Bashundhara Cement |  |  |  |  | Natore | 134 | 23:00 | 129 | 7:00
| Valuka | 124 | 3:00 | 110 | 18:00 | Bogra | 132 | 3:00 | 126 | 7:00
| Tangail | 135 | 4:00 | 125 | 18:00 | Noagaon | 125 | 2:00 | 118 | 7:00
| Mymensing | 126 | 2:00 | 114 | 18:00 | Rajshahi | 132 | 18:00 | 127 | 11:00
| Kishorganj | 130 | 6:00 | 120 | 18:30 | Rajshahi New | 132 | 18:00 | 127 | 11:00
| Netrokona | 123 | 3:00 | 108 | 18:00 | C.Nawabganj | 130 | 18:00 | 125 | 7:00
| Jamalpur | 129 | 0:00 | 120 | 7:00 | Amnura | 129 | 17:00 | 123 | 7:00
| Sherpur | 132 | 1:00 | 115 | 19:00 | Pabna | 137 | 5:00 | 132 | 11:00
| Srimongal | 140 | 6:00 | 132 | 18:30 | Shahjadpur | 140 | 1:00 | 135 | 12:00
| Shahjibazar | 138 | 4:00 | 131 | 18:30 | Serajganj | 134 | 1:00 | 128 | 12:00
| Fenchuganj | 137 | 6:00 | 130 | 15:00 | Niyamatpur | 122 | 5:00 | 110 | 19:00
| Khulawara | 136 | 5:00 | 129 | 18:30 | Joypurhat | 125 | 4:00 | 116 | 7:00
| Sylhet | 133 | 5:00 | 124 | 15:00 | Sherpur(Bogura) | 132 | 5:00 | 126 | 7:00
| Chatak | 133 | 5:00 | 124 | 18:30 | Mohastangor | 131 | 23:00 | 124 | 7:00
| Sunamganj | 132 | 5:00 | 120 | 15:00 | Bhangura | 137 | 2:00 | 132 | 11:00
| Biani Bazar | 133 | 8:00 | 122 | 18:30 | Rangpur | 127 | 23:00 | 117 | 7:00
| Comilla(s) | 129 | 4:00 | 124 | 16:00 | Lalmonirhat | 128 | 10:00 | 119 | 19:00
| Comilla(n) | 139 | 2:00 | 132 | 10:00 | Saidpur | 130 | 21:00 | 114 | 7:00
| Chandpur | 139 | 19:00 | 127 | 6:00 | Purbasadipur | 129 | 21:00 | 113 | 7:00
| Feni | 140 | 18:30 | 128 | 10:00 | Thakurgaon | 132 | 22:00 | 113 | 7:00
| Chowmuhani | 134 | 1:00 | 127 | 1:00 | Palashbari | 127 | 23:00 | 118 | 7:00
| Ashuganj | 140 | 3:00 | 135 | 21:00 | Barapukuria | 130 | 22:00 | 123 | 7:00
| Daudkandi | 133 | 8:00 | 127 | 11:00 | Panchagar | 132 | 22:00 | 114 | 7:00
| B.Baria | 137 | 5:00 | 130 | 18:30 | Joldhaka | 125 | 21:00 | 114 | 7:00
| Ramganj | 136 | 7:00 | 125 | 11:00 | Kurigram | 126 | 23:00 | 119 | 18:30
| Chaddagram | 137 | 2:00 | 128 | 10:00 | Mithapukur | 129 | 23:00 | 122 | 7:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 166 | 7347 | 3538 | 10885 |  |  |  | QF-LDC-11
0:30 | 114 | 6945.5 | 3285.5 | 10231 | Date: | 2022-03-19
1:00 | 62 | 6544 | 3033 | 9577
1:30 | 35 | 6486 | 2910.5 | 9396.5
2:00 | 8 | 6428 | 2788 | 9216
2:30 | 62 | 6304.5 | 2791.5 | 9096 | [5 empty] | Gen. at Eve. Peak | 12075 | 12075 MW (19:30 )
3:00 | 116 | 6181 | 2795 | 8976 | [6 empty] | 19:30
3:30 | 132 | 6032 | 2793 | 8825 | [5 empty] | Gen. at Day Peak | 9622 | 9622 MW (12:00 )
4:00 | 148 | 5883 | 2791 | 8674 | [6 empty] | 12:00
4:30 | 198 | 5751 | 2801.5 | 8552.5 | [5 empty] | Highest Generation | 12075
5:00 | 248 | 5619 | 2812 | 8431 | [6 empty] | 19:30
5:30 | 297 | 5426.5 | 2841 | 8267.5
6:00 | 346 | 5234 | 2870 | 8104
6:30 | 257 | 5247.5 | 2876 | 8123.5
7:00 | 168 | 5261 | 2882 | 8143
7:30 | 174 | 5284 | 2964 | 8248
8:00 | 180 | 5307 | 3046 | 8353
8:30 | 175 | 5426 | 3033 | 8459
9:00 | 170 | 5545 | 3020 | 8565
9:30 | 295 | 5584.5 | 3120 | 8704.5
10:00 | 420 | 5624 | 3220 | 8844
10:30 | 410 | 5742.5 | 3282.5 | 9025
11:00 | 400 | 5861 | 3345 | 9206
11:30 | 326 | 6027 | 3387 | 9414
12:00 | 252 | 6193 | 3429 | 9622
12:30 | 241 | 6336.5 | 3500.5 | 9837
13:00 | 230 | 6480 | 3572 | 10052
13:30 | 190 | 6694 | 3543.5 | 10237.5
14:00 | 150 | 6908 | 3515 | 10423
14:30 | 156 | 6935.5 | 3483.5 | 10419
15:00 | 162 | 6963 | 3452 | 10415
15:30 | 157 | 6898.5 | 3392 | 10290.5
16:00 | 152 | 6834 | 3332 | 10166
16:30 | 168 | 6803 | 3317 | 10120
17:00 | 184 | 6772 | 3302 | 10074
17:30 | 170 | 6887 | 3307 | 10194
18:00 | 156 | 7002 | 3312 | 10314
18:30 | 155 | 7489.5 | 3605 | 11094.5
19:00 | 154 | 7977 | 3898 | 11875
19:30 | 144 | 8114 | 3961 | 12075
20:00 | 162 | 8087 | 3842 | 11929 |  |  |  | Executive Engineer
20:30 | 134 | 8110.5 | 3845 | 11955.5 |  |  |  | Network Operation Division
21:00 | 106 | 8134 | 3848 | 11982
21:30 | 69 | 8039 | 3779 | 11818
22:00 | 32 | 7944 | 3710 | 11654 |  |  |  |  | Page 6 of 7
22:30 | 46 | 7845.5 | 3658 | 11503.5
23:00 | 60 | 7747 | 3606 | 11353
23:30 | 113 | 7547 | 3572 | 11119
24:00 | 166 | 7347 | 3538 | 10885
12075 MW (19:30 )
9622 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-19 |  | Energy |  | 241631510
[13 empty] | 2022-03-19 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4114 | 718 | 1860 | 0 | 2860 | 900 | 35 | 120 | 138 | 140 | 0 | 0
0:30 | 4084 | 721.5 | 1790 | 0 | 2368 | 866.5 | 58 | 115 | 93 | 135 | 0 | 0 | Date: | 2022-03-19
1:00 | 4054 | 725 | 1720 | 0 | 1876 | 833 | 81 | 110 | 48 | 130 | 0 | 0
1:30 | 4063 | 719 | 1630 | 0 | 1841 | 800.5 | 81 | 110 | 24 | 128 | 0 | 0 | [8 empty] | Total Energy | 241.6315 | Total Energy Gen 241.632 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 241.632 MKWHr
2:00 | 4072 | 713 | 1540 | 0 | 1806 | 768 | 81 | 110 | 0 | 126 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3984 | 715 | 1612.5 | 0 | 1700.5 | 768 | 81 | 110 | 0 | 125 | 0 | 0 | [8 empty] | Energy Requirement | 241.6315
3:00 | 3896 | 717 | 1685 | 0 | 1595 | 768 | 81 | 110 | 0 | 124 | 0 | 0
3:30 | 3826.5 | 715 | 1734 | 0 | 1475 | 761.5 | 81 | 110 | 0 | 122 | 0 | 0 | [6 empty] | Shortage
4:00 | 3757 | 713 | 1783 | 0 | 1355 | 755 | 81 | 110 | 0 | 120 | 0 | 0
4:30 | 3712 | 712.5 | 1786 | 0 | 1280 | 754 | 81 | 110 | 0 | 117 | 0 | 0
5:00 | 3667 | 712 | 1789 | 0 | 1205 | 753 | 81 | 110 | 0 | 114 | 0 | 0
5:30 | 3613.5 | 715 | 1842.5 | 0 | 1042.5 | 753 | 81 | 110 | 0 | 110 | 0 | 0
6:00 | 3560 | 718 | 1896 | 0 | 880 | 753 | 81 | 110 | 0 | 106 | 0 | 0
6:30 | 3600 | 718.5 | 1900.5 | 0 | 853 | 753 | 81 | 110 | 0 | 103 | 4.5 | 0 |  |  |  |  | Coal
7:00 | 3640 | 719 | 1905 | 0 | 826 | 753 | 81 | 110 | 0 | 100 | 9 | 0
7:30 | 3575 | 719 | 1888 | 0 | 989 | 752.5 | 81 | 110 | 0 | 96 | 37.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3510 | 719 | 1871 | 0 | 1152 | 752 | 81 | 110 | 0 | 92 | 66 | 0
8:30 | 3519.5 | 718.5 | 1766.5 | 0 | 1329.5 | 752 | 58 | 110 | 22.5 | 92 | 90.5 | 0
9:00 | 3529 | 718 | 1662 | 0 | 1507 | 752 | 35 | 110 | 45 | 92 | 115 | 0
9:30 | 3562.5 | 718.5 | 1768 | 0 | 1478 | 749.5 | 35 | 110 | 49 | 99 | 135 | 0
10:00 | 3596 | 719 | 1874 | 0 | 1449 | 747 | 35 | 110 | 53 | 106 | 155 | 0
10:30 | 3690 | 718.5 | 1887.5 | 0 | 1500 | 749.5 | 35 | 110 | 53 | 107 | 174.5 | 0
11:00 | 3784 | 718 | 1901 | 0 | 1551 | 752 | 35 | 110 | 53 | 108 | 194 | 0
11:30 | 3794 | 718 | 1895.5 | 0 | 1728.5 | 761.5 | 35 | 110 | 53 | 121 | 197.5 | 0
12:00 | 3804 | 718 | 1890 | 0 | 1906 | 771 | 35 | 110 | 53 | 134 | 201 | 0
12:30 | 3841 | 717.5 | 1874 | 0 | 2091.5 | 790 | 35 | 110 | 52.5 | 129 | 196.5 | 0
13:00 | 3878 | 717 | 1858 | 0 | 2277 | 809 | 35 | 110 | 52 | 124 | 192 | 0
13:30 | 3878 | 717 | 1858 | 0 | 2277 | 809 | 35 | 110 | 52 | 124 | 192 | 0
14:00 | 3878 | 717 | 1858 | 0 | 2277 | 809 | 35 | 110 | 52 | 124 | 192 | 0
14:30 | 3803.5 | 717.5 | 1810.5 | 0 | 2554.5 | 824.5 | 35 | 115 | 84 | 126 | 163 | 0
15:00 | 3729 | 718 | 1763 | 0 | 2832 | 840 | 35 | 120 | 116 | 128 | 134 | 0
15:30 | 3736 | 718 | 1789 | 0 | 2708 | 839 | 35 | 120 | 108 | 129 | 108.5 | 0
16:00 | 3743 | 718 | 1815 | 0 | 2584 | 838 | 35 | 120 | 100 | 130 | 83 | 0
16:30 | 3680 | 717.5 | 1811.5 | 0 | 2596 | 825.5 | 35 | 120 | 111 | 135 | 57 | 0
17:00 | 3680 | 717 | 1808 | 0 | 2608 | 813 | 35 | 120 | 122 | 140 | 31 | 0
17:30 | 3720 | 717 | 1790 | 0 | 2657 | 800.5 | 35 | 120 | 197 | 142 | 15.5 | 0
18:00 | 3760 | 717 | 1772 | 0 | 2706 | 788 | 35 | 120 | 272 | 144 | 0 | 0
18:30 | 3955 | 717.5 | 1838.5 | 0 | 3078.5 | 809 | 35 | 150 | 363 | 148 | 0 | 0
19:00 | 4150 | 718 | 1905 | 0 | 3451 | 830 | 35 | 180 | 454 | 152 | 0 | 0
19:30 | 4201 | 718 | 1760 | 0 | 3712 | 852 | 35 | 170 | 475 | 152 | 0 | 0
20:00 | 4184 | 718 | 1743 | 0 | 3721 | 852 | 35 | 140 | 380 | 156 | 0 | 0
20:30 | 4191.5 | 718 | 1766 | 0 | 3705.5 | 882 | 35 | 130 | 375.5 | 152 | 0 | 0
21:00 | 4199 | 718 | 1789 | 0 | 3690 | 912 | 35 | 120 | 371 | 148 | 0 | 0
21:30 | 4198.5 | 717.5 | 1796.5 | 0 | 3577 | 907 | 35 | 120 | 320.5 | 146 | 0 | 0
22:00 | 4198 | 717 | 1804 | 0 | 3464 | 902 | 35 | 120 | 270 | 144 | 0 | 0
22:30 | 4182 | 717 | 1805.5 | 0 | 3371.5 | 902.5 | 35 | 120 | 230 | 140 | 0 | 0
23:00 | 4166 | 717 | 1807 | 0 | 3279 | 903 | 35 | 120 | 190 | 136 | 0 | 0
23:30 | 4140 | 717.5 | 1833.5 | 0 | 3069.5 | 901.5 | 35 | 120 | 164 | 138 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 36.5° C
24:00 | 4114 | 718 | 1860 | 0 | 2860 | 900 | 35 | 120 | 138 | 140 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 241.632 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 241.632 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 0 | [17 empty] | 406500
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW PP | [17 empty] | 3 |  | 19 | 25 | 25 | 25 | 0 |  | 0 | 89278
| Teknaf 20MW PP (Solartech) | [10 empty] | 19 | 19 | 19 | 18 | 14 | 9 | 3 | [9 empty] | 104760
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 140 | 81 | 80 | 80 | 36 | 25 | 26 | 26 | 26 | 26 | 26 | 31 | 26 | 33 | 32 | 66 |  | 56 | 56 | 52 | 61 | 59 | 59 | 56 | 1407499
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 0 | 49 |  | 51 | 51 | 17 | 17 | 0 |  |  | 125243
12 | Hathazari 100 MW peaking PP | [13 empty] | 8 |  |  |  | 2 | [8 empty] | 9744
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 68 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 49 | 92 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1684429
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [17 empty] | 11 | [7 empty] | 0 | 10104
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 219 | 220 | 223 | 180 | 150 | 95 | 93 | 0 | [8 empty] | 0 | 26 |  | 211 | 214 | 213 | 214 | 220 | 219 | 219 | 2614474
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 0 | 2 | 15 | 15 | 15 | 26 | 138 | 195 | 195 | 195 | 195 |  | 270 | 280 | 287 | 278 | 278 | 295 | 195 | 2734908
19 | Ashuganj 195MW PP (APSCL-United) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 110 | 113 | 117 | 117 | 117 | 117 |  | 118 | 73 | 26 | 26 | 26 | 55 | 55 | 2375272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 195 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4814000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 280 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 280 | 280 | 6709055
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 26 | 26 | 26 | 29 | 650448
33 | Ashuganj 225 MW CCPP | 160 | 171 | 173 | 200 | 219 | 219 | 219 | 183 | 183 | 198 | 205 | 188 | 183 | 182 | 183 | 186 | 184 | 189 |  | 214 | 210 | 202 | 216 | 216 | 186 | 218 | 4690000
34 | Ashuganj 450 MW CCPP(South) | 310 | 305 | 295 | 270 | 270 | 270 | 310 | 270 | 270 | 295 | 330 | 305 | 305 | 305 | 280 | 290 | 290 | 300 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7215000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 260 | 260 | 260 | 260 | 295 | 260 | 260 | 280 | 295 | 340 | 310 | 280 | 280 | 290 | 280 | 285 |  | 310 | 310 | 310 | 320 | 320 | 320 | 320 | 7310000
35 | Ashuganj 55 MW PP (Precision) | 52 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 |  | 40 | 40 | 40 | 55 | 53 | 55 | 55 | 796320
36 | Chandpur 150 MW CCPP | [12 empty] | 90 | 88 | 90 | 90 | 90 | 90 |  | 89 | 90 | 89 | 90 | 90 | 90 | 90 | 1064380
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 320 | 320 | 320 | 7007000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 148 | 157 | 157 | 157 | 158 | 158 | 161 | 209 | 196 | 179 | 179 | 178 | 162 | 161 | 176 | 176 | 178 | 178 |  | 179 | 178 | 183 | 183 | 184 | 186 | 179 | 4039680
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 5 | 17 | 29 | 40 | 44 | 49 | 46 | 40 | 30 | 18 | 6 | 0 | [8 empty] | 326530
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 693664
46 | Shajibazar 330 MW CCPP | 219 | 220 | 219 | 222 | 220 | 218 | 220 | 220 | 218 | 220 | 218 | 217 | 215 | 222 | 218 | 216 | 220 | 221 |  | 220 | 221 | 219 | 222 | 222 | 218 | 219 | 5076000
47 | Shahjibazar GTPP Unit- 8 & 9 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 50 | 50 | 50 | 50 | 60 | 60 | 60 | 867072
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 81 | 84 | 84 | 84 | 81 | 81 | 84 | 84 | 83 | 81 | 81 | 82 | 80 | 82 | 84 | 85 |  | 85 | 85 | 86 | 86 | 86 | 86 | 86 | 2007360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247140
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 241056
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 48 | 48 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1196400
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 13 | 20 | 22 | 22 |  | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 515640
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 300 | 300 | 290 | 270 | 280 | 300 | 290 | 275 | 285 | 310 | 300 | 305 | 280 | 285 | 280 | 290 | 270 |  | 300 | 256 | 260 | 280 | 280 | 270 | 275 | 7002500
| Bibiyana South 400 MW | 280 | 280 | 280 | 280 | 280 | 220 | 235 | 235 | 335 | 350 | 382 | 380 | 381 | 387 | 386 | 377 | 350 | 340 |  | 383 | 400 | 395 | 394 | 398 | 400 | 330 | 8017200
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 10 | 17 | 17 | 35 | 55 | 55 | 55 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 626756
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 21 | 18 | [9 empty] | 0 | 6 | 16 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 299040
60 | Barabkunda 22 MW PP (Regent) | [25 empty] | 0 | 0
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 416376
62 | Tangail 22 MW PP (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 0 | 14 | 14 | 14 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 330912
63 | Impoprt (Tripura) | 130 | 126 | 124 | 120 | 114 | 106 | 100 | 92 | 92 | 106 | 108 | 134 | 124 | 136 | 128 | 130 | 140 | 144 |  | 152 | 152 | 156 | 148 | 144 | 136 | 140 | 2990400
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 38 | 22 | 22 | 22 | 35 | 29 | 29 | 29 | 34 |  | 33 | 33 | 33 | 42 | 42 | 42 | 42 | 897120
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 496548
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 174420
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 28 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 778300
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 16 | 16 | 19 | 18 | 18 | 18 | 13 | 13 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 495200
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 20 | 20 | 10 | 19 | 19 | 19 | 19 | 19 | 23 | 23 | 23 | 27 | 27 | 24 | 24 | 24 | 25 | 19 |  | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 541620
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816500
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 17 | 17 | 17 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 695600
73 | Ghorashal 108MW PP (Regent) | 102 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 95 | 95 | 95 | 95 | 93 | 96 | 93 | 97 |  | 97 | 98 | 98 | 101 | 101 | 101 | 101 | 2310454
| Feni Lanka Power | 81 | 98 | 70 | 34 | 34 | [5 empty] | 17 | 34 | 70 | 70 | 70 | 34 | 34 | 34 |  | 100 | 98 | 98 | 98 | 98 | 70 | 17 | 1200420
| Chowmuhani 113 MW | 101 | 100 | 101 | 106 | 46 | 26 | 26 | 78 | 107 | 65 | 76 | 97 | 106 | 105 | 105 | 105 | 105 | 105 |  | 106 | 107 | 106 | 105 | 106 | 107 | 100 | 2300760
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 26 | 54 | 17 | 17 | 58 | 90 | 90 | 96 | 117 | 126 | 126 |  | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 1880640
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [17 empty] | 6 |  | 20 | 16 | 16 | 16 | 0 |  |  | 74880
79 | Kodda 150MW PP | 48 | [12 empty] | 55 | 64 | 48 | 48 | 48 |  | 150 | 150 | 150 | 150 | 150 | 100 | 48 | 1068000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 |  |  |  | 2 | 8 | 8 | 23 | 29 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 52 | 52 | 52 | 724430
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 58 | 105 | 105 | 50 | 50 | 50 |  | 80 | 105 | 105 | 105 | 105 | 105 | 105 | 1359600
| Kaptai 7 MW Solar PP | [7 empty] | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 1 | 1 | [9 empty] | 27359
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1335225
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 68 | 51 | 51 | 51 | 51 | 51 | 54 | 74 | 110 | 110 | 110 | 110 | 104 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2308353
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 275 | 265 | 265 | 270 | 240 | 285 | 285 | 255 | 265 | 285 | 300 | 295 | 260 | 240 | 240 | 270 | 255 | 270 |  | 250 | 220 | 255 | 260 | 255 | 240 | 250 | 6340975
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [8 empty] | 5 | 17 | 18 | 32 | 55 | 72 | 73 | 76 | 82 | 89 |  | 90 | 90 | 90 | 91 | 91 | 91 | 92 | 1094400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 8 | 10 | 10 | 10 | 10 | 10 |  | 50 | 50 | 50 | 50 | 10 | 10 | 0 | 248040
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1172019
94 | Gagnagar 102 MW PP (Digital Power) | [13 empty] | 58 | 64 | 40 | 40 | 40 |  | 64 | 93 | 93 | 93 | 93 | 93 | 24 | 762192
95 | Patenga 50MW PP (Baraka) | [9 empty] | 11 | 12 | 12 | 12 | 13 |  |  | 21 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 449760
96 | Chattogram 108 MW PP (ECPV) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 10 | 9 | 6 | 5 |  | 6 | 5 | 5 | 5 | 6 | 6 | 6 | 149760
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 5 | 15 | 30 | 30 | 30 | 30 |  | 42 | 55 | 55 | 55 | 55 | 55 | 15 | 448907
100 | Manikganj 55 MW PP (Northern) | [13 empty] | 5 | 17 | 17 | 17 | 17 |  | 35 | 35 | 55 | 55 | 17 | 0 | 0 | 253391
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15250
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1243440
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 163 | 172 | 182 | 180 | 180 | 178 | 178 | 187 | 187 | 187 | 187 |  | 188 | 188 | 179 | 179 | 179 | 178 | 180 | 4360800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 108 | 70 | 63 | 50 | 50 | 46 | 17 | 36 | 83 | 64 | 52 | 89 | 112 | 149 | 149 | 127 | 122 | 122 |  | 142 | 149 | 149 | 149 | 149 | 149 | 149 | 2448144
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 60 | 60 | 76 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2054400
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 0 | [8 empty] | 1 | 17 | 17 | 17 | 17 | 17 |  | 75 | 170 | 190 | 170 | 85 | 17 | 0 | 816000
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 100 | 50 | 50 | 10 | 10 | 35 | 98 | 100 | 107 | 113 | 115 | 120 | 120 | 118 | 120 | 127 |  | 137 | 143 | 140 | 145 | 142 | 143 | 145 | 2569309
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 400 | 400 | 355 | 365 | 364 | 400 | 351 | 352 | 353 | 404 | 404 | 404 | 404 | 405 | 366 | 366 |  | 403 | 402 | 402 | 402 | 401 | 401 | 400 | 9384000
| Jamalpur 115 MW PP (United) | 112 | 115 | 45 | 24 | 24 | 24 | 24 | 43 | 66 | 106 | 107 | 107 | 107 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2097600
| Anwara 300 MW PP (United) | 281 | 281 | 281 | 281 | 281 | 235 | 210 | 210 | 211 | 211 | 246 | 281 | 281 | 281 | 281 | 281 | 281 | 281 |  | 281 | 281 | 281 | 281 | 281 | 281 | 281 | 6342982
| Juldah unit-2 (Acorn) | 10 | 10 | 0 | [5 empty] | 6 | 10 | 10 | 30 | 48 | 60 | 60 | 40 | 40 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1005120
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 68 | 34 | 34 | 34 | 34 | 34 | 37 | 62 | 74 | 76 | 94 | 94 | 100 | 113 |  | 113 | 113 | 113 | 107 | 113 | 113 | 113 | 2056200
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 13 | 21 | 27 | 27 | 27 | 30 | 27 | 21 | 13 | 5 | [9 empty] | 224692
| Chandpur 115(Doreen) | 51 | 17 | [10 empty] | 5 | 21 | 20 | 18 | 17 | 17 |  | 45 | 99 | 91 | 90 | 79 | 50 | 17 | 655680
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 32 | 38 | 17 | 17 | 33 | 37 | 37 | 39 | 54 | 39 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 986400
120 | Eastern Zone Total | 6544 | 6428 | 6181 | 5883 | 5619 | 5234 | 5261 | 5307 | 5545 | 5624 | 5861 | 6193 | 6480 | 6908 | 6963 | 6834 | 6772 | 7002 |  | 7977 | 8114 | 8087 | 8134 | 7944 | 7747 | 7347 | 159679550
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 17 | 34 |  | 40 | 35 | [5 empty] | 84480
| Khulna 225 MW CCPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 120 | 120 | 120 | 120 |  | 180 | 170 | 140 | 120 | 120 | 120 | 120 | 2964480
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 11 | 17 | 17 | 20 | 35 | 53 | 53 | 53 | 53 | 53 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 954240
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 33 | 57 | 75 | 88 | 89 | 86 | 75 | 57 | 37 | 15 | [9 empty] | 627120
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 108 | 109 | 109 | 109 | 109 | 109 | 107 | 107 | 106 | 105 | 103 | 99 | 101 | 103 | 106 | 106 |  | 107 | 100 | 107 | 100 | 103 | 104 | 105 | 2563036
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 25 | 22 | 22 | 21 | 21 | 19 | 15 | 14 | 13 | 16 | 18 | 19 | 21 | 22 | 23 | 22 | 19 | 21 |  | 27 | 28 | 28 | 28 | 27 | 26 | 25 | 510300
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 2 | 8 | 9 |  |  |  |  | 11964
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 725 | 713 | 717 | 713 | 712 | 718 | 719 | 719 | 718 | 719 | 718 | 718 | 717 | 718 | 718 | 718 | 717 | 717 |  | 718 | 718 | 718 | 718 | 717 | 717 | 718 | 17354909
147 | Bheramara 410 MW CCPP | 410 | 410 | 340 | 300 | 270 | 270 | 270 | 280 | 280 | 280 | 320 | 360 | 400 | 390 | 375 | 370 | 370 | 365 |  | 360 | 350 | 345 | 330 | 320 | 320 | 320 | 8373312
148 | Payra 1320 MW | 550 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 520 | 560 | 570 | 570 | 570 | 540 | 520 |  | 560 | 580 | 580 | 640 | 630 | 630 | 620 | 14618500
149
150 | Barapukuria TPP Unit-1 | 83 | 68 | 68 | 55 | 53 | 53 | 53 | 53 | 53 | 48 | 53 | 52 | 50 | 63 | 70 | 68 | 73 | 68 |  | 70 | 72 | 72 | 72 | 72 | 73 | 80 | 1495418
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4865400
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 60 | 50 | [15 empty] | 720000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 5 |  | 43 | 43 | 43 | 43 |  |  |  | 132684
| Sirajgonj 6.55 MW Solar | [7 empty] | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 37320
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [11 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 13 | 13 | 176200
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 186 | 167 | 164 | 164 | 164 | 173 | 172 | 165 | 168 | 202 | 204 | 201 | 183 | 160 | 160 | 160 | 159 |  | 184 | 206 | 210 | 212 | 212 | 204 | 195 | 4574691
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 189 | 174 | 165 | 163 | 163 | 173 | 171 | 164 | 167 | 200 | 200 | 194 | 171 | 163 | 164 | 164 | 163 |  | 182 | 205 | 205 | 199 | 189 | 183 | 183 | 4521364
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 227 | 73 | 225 | 325 | 381 | 435 | 431 | 436 | 236 | 417 | 416 | 417 | 417 | 360 | 351 | 352 | 350 | 305 |  | 420 | 399 | 382 | 383 | 383 | 380 | 417 | 8614545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 5 |  | 7 | 26 | [5 empty] | 27460
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 |  | 10 | 15 | 13 | 13 | 13 | 13 | 14 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 324720
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246420
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 43 | 43 | 25 | 25 |  |  |  | 107263
167 | Katakhali 50 MW Peaking PP | [17 empty] | 10 |  | 40 | 40 | 40 | 40 |  |  |  | 126095
168 | Santahar 50 MW Peaking PP | [17 empty] | 18 |  | 31 | 32 | 31 | 31 | 30 |  |  | 136068
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 16 | 24 | 24 | 24 | 24 | 24 |  | 43 | 52 | 52 | 52 | 52 | 52 | 8 | 399571
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 45 | 53 | 53 | 53 | 52 | 52 | 52 | 52 | 52 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1010488
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 70 | 35 | 35 | 35 | 35 | 67 | 90 | 50 | 50 | 87 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2006112
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 20 | 35 | 35 | 35 | 50 | 100 | 113 | 113 | 50 | 50 | 50 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1361376
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 50 | 90 | 110 | 112 | 112 | 111 | 107 | 100 | 70 | 70 | 70 |  | 110 | 110 | 111 | 111 | 111 | 111 | 80 | 1631712
177 | Sympa Solar Power 8MW | [7 empty] | 1 | 3 | 4 | 5 | 6 |  | 6 | 4 | 2 | 1 | 0 | [8 empty] | 35818
178 | Energypac Power Venture Thakurgaon Ltd. | 17 | [6 empty] | 35 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 115 | 115 | 115 | 115 | 115 | 54 | 34 | 1338894
178