## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-03-22 | Tuesday
|  |  | Date (day): | 2022-03-22 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13458.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14017 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-03-21 | 2022-03-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 270 | 270 | 270 | 95 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 88 | 100 | 100 |  | 8
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint |  | 2022-04-04
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 2022-03-30
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 290 | 330 | 330 | 120 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 275 | 150 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 217 | 170 | 229 | 229 | 106 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 93 | 93 | 93 |  | 9 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 42 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 270 | 298 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 306 | 200 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 31 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 30 | 100 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 121 | 132 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 100 | 105 | 90 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 91 | 91 | 92 | 92 |  | 12 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 148 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 39 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6258 | 5696 | 2831 | 3128 | 3361 | 3445 | 582 | 1619
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 70 | 70 | 70 |  | 160 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 140 | 151 | 150 | 150 |  | 75 | ST Under S/D
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 94 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 90 | 90 | 90 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 21 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 5 | 0 | 6 | 6 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 265 | 281 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 65 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 95 | 113 | 113 | 113
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1291 | 1452 | 1509 | 1499 | 132 | 648
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 155 | 200 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 270 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 275 | 330 | 330 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 | 16 |  | Gas shortage
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 48 | 20 | 55 | 55 | 0 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 147 | 140 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 32 | 50 |  | 2
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 31 | 73 | 73 | 73 |  | 90 | ST under S/D
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 52 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 142 | 156 | 138 | 163
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 39 | 43 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 22 | 22
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 98 | 98 | 98 |  | 16 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 97 | 107 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 90 | 98 | 100 | 100
|  | Cumilla Area Total |  |  |  |  | 3059 | 3014 | 1696 | 2110 | 2184 | 2327 | 466 | 145
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 68 | 72 | 70 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 17 | 17 | 17
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 180 | 190 | 200 | 200
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 98 | 108 | 115 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 429 | 409 | 475.6 | 454 | 102 | 8
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint. |  | 22-03-022
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 267 | 268 | 265 | 265 |  | 65 | ST under maint
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 55 | 60 | 60 |  | 6 | Machine problem
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 89 | 86 | 86
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Machine problem
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 22 | 22 | 23
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 300 | 300 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 403 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 383 | 394 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1640 | 1659 | 1664 | 1665 | 251 | 434
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 715 | 714 | 729 | 729
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 40 |  | 14 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 130 | 210 | 158 | 225
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 30 |  | 79 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 225 | 300 | 350
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 113 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 98 | 100 | 100
| 114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 94 | 105 | 105 | 105
| 115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 0 | 0
| 116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 50 | 0
|  | Khulna Area Total |  |  |  |  | 2348 | 2229 | 1255 | 1424 | 1442 | 1579 | 0 | 93
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 0 | 80
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 28 | 25 | 27 |  | 6 | Engine problem
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 | 194 |  | Gas shortage
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 670 | 660 | 660
| 122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 100 | 105 | 110 | 110
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 669 | 883 | 795 | 877 | 194 | 6
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 37 | 40 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  |  | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 40 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 4 | 3 | 10 | 10 |  | 200 | ST Commissioning process
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 148 | 132 | 220 | 220
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 156 | 145 | 210 | 220
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 387 | 377 | 414 | 414
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 25 | 30 |  | 20 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 18 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 54 | 92 | 90 | 92 |  | 12 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 177 | 100 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 94 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1113 | 1424 | 1512 | 1663 | 171 | 282
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 84 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 0 |  | 20
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 0 |  | 20
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 111 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 511 | 535 | 516 | 508 | 74 | 125
|  | Total |  |  |  |  | 22291 | 21215 | 11435 | 13024 | 13458.6 | 14017 | 1972 | 3360
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10933.6652 | 12453 | 12868.5462 | 13402.4648
| A. |  | 2022-03-21 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13024 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 9572 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13024 | MW
| 3 | Day peak Generation : |  |  | 11435 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12453 | MW
| 4 | Evening peak Generation : |  |  | 13024 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 272.8316 | MKWHr | By Solar | 1.3937 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 135.7323 | MKWHr |  | By Oil: | 91.6382 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 22.3328 | MKWHr |  | By Hydro: | 1.1939 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1972 | MW | Dhaka | 4634 | 4634 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3360 | MW | Chittagong | 1279 | 1279 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5332 | MW | Khulna | 1479 | 1479 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1068.76 | MMCFD |  |  | Rajshahi | 1411 | 1411 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 137736795.868 | ii) Oil : | Taka | 725870335.35 | Comilla | 1104 | 1104 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 106181200.35 | Total | Taka | 969788331.568 | Mymensingh | 952 | 952 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.193 | MKWHr. | Sylhet | 435 | 435 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 34 | MW (E to W) at | 20:00 | hrs | Barisal | 327 | 327 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -130 | MW at | 7:00 | hrs | Rangpur | 832 | 832 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.6° C |  |  | Total | 12453 | 12453 |  | 0
| B. |  | 2022-03-22 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14017 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11600 | MW
| 4 | Reserve(Generation end) |  |  |  | 517 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 282.8031 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9683 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3324 | MKWHr. | ii) HVDC Flow at Peak Time |  | 714 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2083 | MKWHr. | iii) Maximum HVDC Flow : |  | 718 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 87.42 |  | (b) Today: | 87.28 |  | (c) Rule Curve: |  | 89.64
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-03-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 330 | 255 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 58 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 27 | 33 | 33 | 16 | 0 | 35 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 50 | 0 | 38 | 0 | 0 | 0 | 310 | 310 | 222 | 45 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 22 | 132 | 108 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 266 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 275 | 22 | 11 | 0 | 260 | 0 | 0 | 182 | 0 | 133 | 0 | 76 | 0 | 142 | 400 | 98 | 105 | 105 | 0 | 281 | 54 | 110 | 52 | 89 | 100 | 400 | 93 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 718 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 4 | 0 | 161 | 0 | 0 | 0 | 140 | 0 | 400 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 600 | 107 | 0 | 0 | 0 | 0 | 91 |  | 7616 | 3366 | 10982 | 4078 | 718 | 1845 | 0 | 3060 | 877 | 70 | 120 | 82 | 132 | 0 | 0 | 87.44
2:00 | 0 | 0 | 200 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 330 | 275 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 26 | 33 | 33 | 16 | 0 | 30 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 40 | 0 | 39 | 0 | 0 | 0 | 310 | 315 | 210 | 45 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 22 | 136 | 109 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 266 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 275 | 22 | 11 | 0 | 145 | 0 | 0 | 191 | 0 | 134 | 0 | 90 | 0 | 140 | 400 | 98 | 34 | 105 | 0 | 281 | 54 | 110 | 34 | 88 | 50 | 400 | 92 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 718 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 4 | 0 | 158 | 0 | 0 | 0 | 138 | 0 | 400 | 53 | 0 | 113 | 0 | 70 | 0 | 0 | 35 | 570 | 106 | 0 | 0 | 0 | 0 | 18 |  | 7325 | 3076 | 10401 | 4071 | 718 | 1863 | 0 | 2515 | 849 | 65 | 120 | 64 | 136 | 0 | 0 | 87.44
3:00 | 0 | 0 | 200 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 330 | 265 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 26 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 25 | 0 | 39 | 0 | 0 | 0 | 310 | 315 | 190 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 42 | 19 | 11 | 33 | 19 | 124 | 109 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 263 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 285 | 22 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 129 | 0 | 90 | 0 | 140 | 400 | 75 | 34 | 105 | 0 | 281 | 54 | 110 | 17 | 88 | 50 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 55 |  | 717 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 4 | 0 | 158 | 0 | 0 | 0 | 138 | 0 | 396 | 53 | 0 | 113 | 0 | 70 | 0 | 0 | 35 | 570 | 107 | 0 | 0 | 0 | 0 | 18 |  | 7057 | 3071 | 10128 | 4046 | 717 | 1839 | 0 | 2366 | 849 | 35 | 120 | 32 | 124 | 0 | 0 | 87.43
4:00 | 0 | 0 | 200 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 330 | 255 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 26 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 25 | 0 | 39 | 0 | 0 | 0 | 310 | 315 | 208 | 26 | 90 | 26 | 30 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 19 | 120 | 109 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 268 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 100 | 0 | 90 | 0 | 140 | 400 | 50 | 34 | 105 | 0 | 281 | 54 | 110 | 0 | 87 | 10 | 400 | 70 | 0 | 144 | 113 | 0 | 17 | 0 | 0 | 17 |  | 718 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 4 | 0 | 158 | 0 | 0 | 0 | 139 | 0 | 420 | 53 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 550 | 107 | 0 | 0 | 0 | 0 | 18 |  | 6773 | 3044 | 9817 | 4075 | 718 | 1823 | 0 | 2083 | 827 | 35 | 120 | 16 | 120 | 0 | 0 | 87.43
5:00 | 0 | 0 | 200 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 330 | 290 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 26 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 12 | 0 | 39 | 0 | 0 | 0 | 260 | 315 | 214 | 26 | 90 | 26 | 30 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 19 | 114 | 109 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 268 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 0 | 45 | 0 | 0 | 193 | 0 | 100 | 0 | 90 | 0 | 142 | 400 | 50 | 34 | 68 | 0 | 281 | 45 | 110 | 0 | 89 | 10 | 400 | 53 | 0 | 108 | 113 | 0 | 17 | 0 | 0 | 17 |  | 717 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 4 | 0 | 158 | 0 | 0 | 0 | 146 | 0 | 352 | 53 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 550 | 107 | 0 | 0 | 0 | 0 | 18 |  | 6669 | 2941 | 9610 | 4046 | 717 | 1800 | 0 | 1933 | 829 | 35 | 120 | 16 | 114 | 0 | 0 | 87.42
6:00 | 0 | 0 | 200 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 330 | 235 | 0 | 0 | 1 | 180 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 26 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 6 | 12 | 0 | 39 | 0 | 0 | 0 | 260 | 305 | 220 | 26 | 91 | 26 | 30 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 19 | 108 | 110 | 0 | 17 | 0 | 30 | 30 | 42 | 0 | 0 | 269 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 285 | 22 | 8 | 0 | 55 | 0 | 0 | 193 | 0 | 114 | 0 | 90 | 0 | 142 | 400 | 70 | 50 | 68 | 0 | 281 | 35 | 110 | 17 | 89 | 10 | 400 | 53 | 0 | 108 | 113 | 0 | 17 | 0 | 4 | 32 |  | 718 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 4 | 0 | 157 | 0 | 0 | 0 | 141 | 0 | 352 | 53 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 550 | 98 | 0 | 0 | 0 | 0 | 18 |  | 6634 | 2938 | 9572 | 3993 | 718 | 1724 | 0 | 2029 | 829 | 35 | 120 | 16 | 108 | 0 | 0 | 87.42
7:00 | 0 | 0 | 200 | 0 | 300 | 100 | 0 | 0 | 0 |  | 0 | 330 | 280 | 0 | 0 | 15 | 180 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 26 | 33 | 33 | 16 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 12 | 0 | 37 | 0 | 0 | 0 | 260 | 270 | 225 | 26 | 30 | 26 | 30 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 19 | 106 | 109 | 0 | 17 | 0 | 30 | 30 | 42 | 0 | 0 | 262 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 95 | 0 | 0 | 193 | 0 | 118 | 3 | 90 | 0 | 140 | 400 | 98 | 52 | 68 | 1 | 265 | 35 | 110 | 22 | 88 | 10 | 400 | 53 | 5 | 108 | 96 | 0 | 7 | 0 | 20 | 40 |  | 718 | 0 | 255 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 79 | 0 | 200 | 0 | 0 | 4 | 0 | 158 | 0 | 0 | 0 | 135 | 0 | 382 | 53 | 0 | 77 | 0 | 103 | 0 | 0 | 35 | 550 | 107 | 0 | 0 | 0 | 8 | 55 |  | 6662 | 3096 | 9758 | 3896 | 718 | 1809 | 0 | 2212 | 829 | 35 | 120 | 16 | 106 | 17 | 0 | 87.42
8:00 | 0 | 0 | 200 | 0 | 300 | 92 | 0 | 0 | 0 |  | 0 | 330 | 250 | 0 | 0 | 15 | 229 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 10 | 17 | 22 | 25 | 8 | 33 | 33 | 22 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 12 | 0 | 11 | 0 | 0 | 0 | 260 | 270 | 223 | 26 | 30 | 26 | 48 | 0 | 51 | 0 | 0 | 20 | 19 | 11 | 20 | 20 | 112 | 71 | 0 | 17 | 1 | 30 | 30 | 42 | 0 | 0 | 266 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 8 | 0 | 95 | 0 | 0 | 193 | 0 | 127 | 9 | 90 | 15 | 122 | 399 | 98 | 70 | 72 | 2 | 265 | 35 | 110 | 51 | 88 | 10 | 400 | 56 | 16 | 111 | 95 | 0 | 7 | 9 | 50 | 52 |  | 717 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 16 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 4 | 0 | 160 | 0 | 0 | 0 | 131 | 0 | 383 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 550 | 105 | 0 | 0 | 1 | 27 | 115 |  | 6796 | 3242 | 10038 | 3871 | 717 | 1758 | 0 | 2499 | 829 | 35 | 120 | 32 | 112 | 65 | 0 | 87.41
9:00 | 0 | 0 | 200 | 0 | 280 | 94 | 0 | 0 | 0 |  | 0 | 330 | 275 | 0 | 0 | 40 | 226 | 0 | 0 | 0 | 58 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 8 | 33 | 33 | 42 | 0 | 0 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 5 | 12 | 0 | 2 | 0 | 0 | 0 | 340 | 285 | 218 | 26 | 30 | 23 | 48 | 0 | 51 | 0 | 0 | 35 | 19 | 11 | 25 | 20 | 110 | 71 | 0 | 17 | 1 | 30 | 30 | 42 | 0 | 0 | 266 | 40 | 86 | 0 | 0 | 0 | 0 | 10 | 270 | 23 | 8 | 0 | 95 | 0 | 0 | 193 | 0 | 134 | 15 | 90 | 17 | 140 | 400 | 98 | 90 | 90 | 4 | 281 | 35 | 110 | 51 | 88 | 10 | 400 | 88 | 22 | 144 | 94 | 0 | 17 | 19 | 51 | 55 |  | 717 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 11 | 80 | 0 | 199 | 0 | 0 | 5 | 0 | 160 | 0 | 0 | 0 | 124 | 0 | 326 | 94 | 0 | 113 | 0 | 104 | 0 | 2 | 35 | 550 | 105 | 0 | 0 | 3 | 42 | 115 |  | 7159 | 3224 | 10383 | 3904 | 717 | 1700 | 0 | 2758 | 829 | 35 | 120 | 102 | 110 | 108 | 0 | 87.41
10:00 | 0 | 0 | 200 | 0 | 280 | 90 | 0 | 0 | 0 |  | 0 | 320 | 285 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 75 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 23 | 33 | 33 | 42 | 0 | 0 | 35 | 0 | 150 | 1 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 5 | 14 | 0 | 4 | 0 | 0 | 0 | 270 | 290 | 216 | 26 | 30 | 23 | 48 | 0 | 43 | 0 | 0 | 37 | 19 | 11 | 25 | 20 | 116 | 70 | 0 | 17 | 2 | 30 | 30 | 42 | 0 | 0 | 265 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 8 | 0 | 95 | 0 | 0 | 193 | 0 | 134 | 19 | 90 | 17 | 142 | 402 | 89 | 90 | 95 | 4 | 265 | 35 | 110 | 84 | 88 | 20 | 400 | 92 | 37 | 144 | 94 | 0 | 17 | 26 | 63 | 50 |  | 714 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 5 | 0 | 159 | 0 | 0 | 0 | 129 | 0 | 417 | 90 | 0 | 113 | 0 | 113 | 0 | 4 | 90 | 550 | 108 | 0 | 0 | 4 | 70 | 115 |  | 7326 | 3463 | 10789 | 3870 | 714 | 1813 | 0 | 2956 | 830 | 35 | 120 | 169 | 116 | 166 | 0 | 87.4
11:00 | 0 | 0 | 200 | 0 | 280 | 90 | 0 | 0 | 0 |  | 0 | 320 | 285 | 0 | 0 | 55 | 207 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 23 | 33 | 33 | 43 | 0 | 0 | 35 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 40 | 5 | 37 | 0 | 3 | 0 | 0 | 0 | 270 | 285 | 181 | 8 | 30 | 26 | 48 | 0 | 43 | 0 | 0 | 43 | 19 | 8 | 25 | 18 | 130 | 70 | 0 | 17 | 2 | 30 | 30 | 47 | 0 | 0 | 265 | 60 | 85 | 0 | 0 | 0 | 0 | 10 | 260 | 21 | 8 | 0 | 190 | 0 | 0 | 182 | 0 | 134 | 20 | 90 | 19 | 143 | 377 | 98 | 90 | 105 | 5 | 265 | 35 | 110 | 114 | 91 | 90 | 397 | 91 | 45 | 144 | 95 | 0 | 17 | 31 | 91 | 43 |  | 715 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 43 | 0 | 52 | 0 | 17 | 0 | 11 | 78 | 0 | 199 | 0 | 0 | 5 | 0 | 148 | 0 | 0 | 0 | 148 | 0 | 372 | 73 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 550 | 107 | 0 | 0 | 4 | 86 | 115 |  | 7593 | 3482 | 11075 | 3788 | 715 | 1713 | 0 | 3338 | 827 | 35 | 120 | 211 | 130 | 198 | 0 | 87.4
12:00 | 0 | 0 | 200 | 0 | 270 | 90 | 0 | 0 | 0 |  | 0 | 320 | 275 | 0 | 0 | 55 | 217 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 15 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 150 | 25 | 140 | 0 | 0 | 0 |  | 22 | 0 | 0 | 94 | 5 | 46 | 0 | 6 | 0 | 0 | 0 | 300 | 320 | 155 | 8 | 31 | 29 | 48 | 0 | 43 | 0 | 0 | 39 | 19 | 8 | 25 | 12 | 142 | 68 | 0 | 14 | 2 | 30 | 30 | 47 | 0 | 0 | 267 | 55 | 85 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 8 | 0 | 270 | 0 | 31 | 180 | 30 | 121 | 20 | 90 | 52 | 147 | 404 | 98 | 90 | 105 | 5 | 265 | 35 | 110 | 114 | 97 | 65 | 383 | 91 | 45 | 144 | 95 | 0 | 17 | 32 | 90 | 39 |  | 715 | 0 | 225 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 54 | 0 | 43 | 24 | 52 | 0 | 17 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 4 | 0 | 148 | 0 | 0 | 0 | 156 | 0 | 387 | 94 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 550 | 100 | 0 | 0 | 5 | 91 | 115 |  | 7887 | 3548 | 11435 | 3828 | 715 | 1755 | 61 | 3503 | 828 | 35 | 130 | 233 | 142 | 205 | 0 | 87.4
13:00 | 0 | 0 | 200 | 0 | 270 | 90 | 0 | 0 | 0 |  | 0 | 310 | 275 | 0 | 0 | 55 | 200 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 43 | 0 | 10 | 0 | 0 | 0 | 270 | 285 | 146 | 8 | 31 | 29 | 50 | 0 | 43 | 0 | 0 | 43 | 19 | 8 | 17 | 20 | 134 | 68 | 0 | 14 | 2 | 30 | 30 | 47 | 0 | 0 | 265 | 55 | 84 | 0 | 0 | 0 | 0 | 10 | 290 | 21 | 11 | 0 | 298 | 32 | 100 | 188 | 100 | 117 | 20 | 80 | 150 | 147 | 403 | 98 | 90 | 105 | 5 | 265 | 35 | 110 | 98 | 97 | 90 | 385 | 90 | 45 | 144 | 95 | 0 | 17 | 30 | 76 | 40 |  | 715 | 0 | 215 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 5 | 54 | 0 | 43 | 24 | 52 | 0 | 16 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 4 | 0 | 147 | 0 | 0 | 0 | 156 | 0 | 380 | 94 | 0 | 74 | 0 | 106 | 0 | 5 | 113 | 550 | 100 | 0 | 0 | 5 | 88 | 115 |  | 8063 | 3574 | 11637 | 3729 | 715 | 1734 | 232 | 3594 | 831 | 35 | 200 | 233 | 134 | 200 | 0 | 87.39
14:00 | 0 | 0 | 200 | 0 | 270 | 88 | 0 | 0 | 0 |  | 0 | 310 | 260 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 150 | 25 | 143 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 37 | 0 | 5 | 0 | 0 | 0 | 305 | 320 | 177 | 8 | 81 | 29 | 20 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 16 | 20 | 146 | 68 | 0 | 14 | 2 | 30 | 30 | 47 | 0 | 0 | 260 | 55 | 83 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 11 | 0 | 296 | 0 | 50 | 189 | 30 | 129 | 19 | 90 | 200 | 145 | 405 | 108 | 90 | 105 | 4 | 281 | 35 | 110 | 98 | 102 | 77 | 380 | 91 | 40 | 144 | 94 | 0 | 17 | 27 | 76 | 55 |  | 715 | 0 | 210 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 5 | 54 | 0 | 43 | 24 | 52 | 12 | 16 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 3 | 0 | 140 | 0 | 0 | 0 | 155 | 0 | 352 | 94 | 0 | 94 | 0 | 112 | 0 | 5 | 113 | 550 | 103 | 0 | 0 | 4 | 78 | 115 |  | 8118 | 3584 | 11702 | 3839 | 715 | 1675 | 80 | 3736 | 832 | 35 | 220 | 245 | 146 | 179 | 0 | 87.39
15:00 | 0 | 0 | 200 | 0 | 270 | 90 | 0 | 0 | 0 |  | 0 | 310 | 260 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 49 | 0 | 0 | 35 | 0 | 150 | 25 | 139 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 37 | 0 | 4 | 0 | 0 | 0 | 305 | 320 | 171 | 8 | 73 | 29 | 20 | 0 | 51 | 0 | 5 | 43 | 19 | 8 | 25 | 20 | 146 | 70 | 0 | 17 | 1 | 30 | 30 | 47 | 0 | 0 | 261 | 55 | 83 | 0 | 0 | 0 | 0 | 10 | 310 | 21 | 11 | 0 | 298 | 54 | 100 | 188 | 100 | 133 | 15 | 90 | 200 | 130 | 405 | 107 | 90 | 105 | 3 | 281 | 35 | 110 | 98 | 105 | 77 | 378 | 91 | 29 | 144 | 97 | 0 | 17 | 20 | 82 | 55 |  | 715 | 0 | 210 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 5 | 54 | 0 | 43 | 24 | 52 | 28 | 15 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 4 | 0 | 137 | 0 | 0 | 0 | 149 | 0 | 356 | 94 | 0 | 109 | 0 | 103 | 0 | 4 | 113 | 570 | 103 | 0 | 0 | 3 | 61 | 115 |  | 8279 | 3601 | 11880 | 3826 | 715 | 1688 | 254 | 3742 | 852 | 35 | 220 | 266 | 146 | 136 | 0 | 87.38
16:00 | 0 | 0 | 200 | 0 | 270 | 89 | 0 | 0 | 0 |  | 0 | 300 | 190 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 25 | 33 | 33 | 49 | 0 | 35 | 35 | 0 | 150 | 25 | 142 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 50 | 0 | 4 | 0 | 0 | 0 | 300 | 315 | 170 | 8 | 72 | 29 | 20 | 0 | 51 | 0 | 42 | 43 | 19 | 8 | 25 | 20 | 144 | 67 | 0 | 17 | 1 | 30 | 30 | 47 | 0 | 0 | 265 | 55 | 84 | 0 | 0 | 0 | 0 | 10 | 315 | 21 | 11 | 0 | 298 | 55 | 100 | 188 | 98 | 135 | 9 | 90 | 200 | 130 | 405 | 107 | 90 | 105 | 2 | 264 | 35 | 105 | 98 | 105 | 77 | 380 | 91 | 16 | 144 | 113 | 0 | 17 | 12 | 84 | 37 |  | 715 | 0 | 210 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 7 | 54 | 0 | 43 | 24 | 52 | 32 | 16 | 0 | 11 | 83 | 0 | 200 | 0 | 0 | 4 | 0 | 136 | 0 | 0 | 0 | 148 | 0 | 356 | 94 | 0 | 113 | 0 | 27 | 0 | 2 | 113 | 580 | 103 | 0 | 0 | 1 | 39 | 115 |  | 8212 | 3519 | 11731 | 3818 | 715 | 1614 | 253 | 3643 | 863 | 70 | 220 | 309 | 144 | 82 | 0 | 87.38
17:00 | 0 | 0 | 200 | 0 | 270 | 89 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 25 | 33 | 33 | 41 | 0 | 35 | 35 | 0 | 150 | 25 | 132 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 50 | 0 | 8 | 0 | 0 | 0 | 270 | 285 | 187 | 8 | 72 | 29 | 20 | 0 | 51 | 0 | 42 | 43 | 19 | 8 | 33 | 21 | 144 | 70 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 265 | 55 | 85 | 0 | 0 | 0 | 0 | 10 | 290 | 14 | 11 | 0 | 298 | 22 | 100 | 188 | 70 | 118 | 3 | 90 | 200 | 125 | 403 | 97 | 90 | 105 | 0 | 264 | 35 | 110 | 98 | 105 | 77 | 398 | 91 | 6 | 144 | 113 | 0 | 17 | 4 | 79 | 55 |  | 715 | 0 | 210 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 5 | 54 | 0 | 43 | 24 | 52 | 28 | 17 | 0 | 11 | 82 | 0 | 200 | 0 | 0 | 3 | 0 | 133 | 0 | 0 | 0 | 148 | 0 | 355 | 94 | 0 | 113 | 0 | 108 | 0 | 1 | 113 | 580 | 102 | 0 | 0 | 0 | 15 | 115 |  | 8010 | 3565 | 11575 | 3782 | 715 | 1553 | 192 | 3702 | 862 | 70 | 223 | 303 | 144 | 29 | 0 | 87.38
18:00 | 0 | 0 | 200 | 0 | 270 | 87 | 0 | 0 | 0 |  | 0 | 300 | 150 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 41 | 0 | 35 | 35 | 0 | 150 | 25 | 131 | 0 | 0 | 0 |  | 22 | 0 | 8 | 92 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 270 | 285 | 205 | 8 | 72 | 29 | 20 | 0 | 51 | 0 | 42 | 43 | 19 | 8 | 33 | 21 | 146 | 71 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 266 | 55 | 84 | 0 | 0 | 0 | 0 | 10 | 265 | 20 | 11 | 20 | 298 | 22 | 25 | 189 | 25 | 122 | 0 | 90 | 200 | 130 | 403 | 107 | 90 | 105 | 0 | 281 | 35 | 94 | 98 | 105 | 77 | 400 | 91 | 0 | 144 | 94 | 0 | 17 | 0 | 77 | 55 |  | 715 | 0 | 210 | 0 | 0 | 220 | 0 | 0 | 4 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 7 | 16 | 54 | 0 | 43 | 36 | 52 | 28 | 17 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 3 | 0 | 132 | 0 | 0 | 0 | 147 | 0 | 355 | 94 | 5 | 113 | 0 | 111 | 0 | 0 | 113 | 580 | 105 | 0 | 0 | 0 | 0 | 115 |  | 7920 | 3586 | 11506 | 3807 | 715 | 1521 | 97 | 3725 | 860 | 70 | 220 | 345 | 146 | 0 | 0 | 87.37
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 270 | 88 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 145 | 0 | 0 | 0 |  | 22 | 0 | 51 | 100 | 0 | 50 | 0 | 12 | 0 | 0 | 0 | 345 | 335 | 186 | 8 | 73 | 29 | 20 | 0 | 51 | 0 | 42 | 43 | 19 | 8 | 33 | 21 | 158 | 71 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 267 | 55 | 85 | 0 | 0 | 0 | 0 | 10 | 295 | 22 | 11 | 200 | 298 | 304 | 100 | 189 | 100 | 116 | 0 | 90 | 200 | 138 | 403 | 108 | 90 | 105 | 0 | 281 | 35 | 107 | 81 | 106 | 86 | 385 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 94 | 35 |  | 714 | 0 | 210 | 0 | 0 | 210 | 0 | 0 | 7 | 8 | 0 | 0 | 28 | 28 | 0 | 0 | 0 | 43 | 24 | 92 | 0 | 43 | 40 | 52 | 28 | 17 | 0 | 11 | 80 | 0 | 200 | 14 | 0 | 3 | 0 | 132 | 0 | 0 | 75 | 146 | 0 | 370 | 94 | 176 | 113 | 2 | 111 | 0 | 0 | 113 | 630 | 105 | 0 | 0 | 0 | 0 | 115 |  | 8762 | 4034 | 12796 | 3915 | 714 | 1576 | 955 | 3789 | 910 | 70 | 224 | 485 | 158 | 0 | 0 | 87.35
19:30 | 0 | 0 | 200 | 0 | 270 | 89 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 20 | 26 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 150 | 0 | 0 | 0 |  | 22 | 0 | 51 | 100 | 0 | 50 | 0 | 15 | 0 | 0 | 0 | 310 | 305 | 184 | 8 | 73 | 29 | 20 | 0 | 51 | 0 | 41 | 43 | 19 | 8 | 33 | 21 | 156 | 72 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 267 | 55 | 86 | 0 | 0 | 0 | 0 | 10 | 305 | 22 | 11 | 200 | 298 | 303 | 100 | 189 | 100 | 116 | 0 | 90 | 200 | 140 | 402 | 108 | 90 | 105 | 0 | 281 | 35 | 110 | 98 | 107 | 100 | 385 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 98 | 55 |  | 715 | 0 | 220 | 0 | 0 | 210 | 0 | 0 | 31 | 8 | 0 | 0 | 27 | 64 | 0 | 0 | 0 | 43 | 31 | 92 | 0 | 43 | 40 | 52 | 25 | 18 | 0 | 11 | 81 | 0 | 200 | 15 | 10 | 3 | 0 | 132 | 0 | 0 | 98 | 146 | 0 | 370 | 105 | 177 | 113 | 32 | 111 | 0 | 0 | 113 | 690 | 105 | 0 | 0 | 0 | 0 | 115 |  | 8768 | 4246 | 13014 | 3859 | 715 | 1591 | 978 | 3927 | 971 | 70 | 235 | 512 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 270 | 88 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 151 | 0 | 0 | 0 |  | 22 | 0 | 51 | 100 | 0 | 50 | 0 | 21 | 0 | 0 | 0 | 270 | 275 | 200 | 8 | 73 | 29 | 20 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 21 | 156 | 72 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 268 | 55 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 200 | 298 | 306 | 100 | 190 | 100 | 132 | 0 | 90 | 200 | 140 | 403 | 108 | 90 | 105 | 0 | 281 | 35 | 110 | 98 | 107 | 100 | 394 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 98 | 55 |  | 714 | 0 | 225 | 0 | 0 | 210 | 0 | 0 | 40 | 0 | 0 | 0 | 28 | 80 | 0 | 0 | 0 | 43 | 37 | 92 | 0 | 43 | 40 | 52 | 28 | 18 | 0 | 11 | 84 | 0 | 200 | 15 | 10 | 3 | 0 | 132 | 0 | 0 | 98 | 145 | 0 | 377 | 105 | 177 | 113 | 32 | 111 | 0 | 0 | 113 | 670 | 105 | 0 | 0 | 0 | 0 | 115 |  | 8758 | 4266 | 13024 | 3830 | 714 | 1602 | 981 | 3960 | 954 | 70 | 235 | 522 | 156 | 0 | 0 | 87.36
21:00 | 0 | 0 | 200 | 0 | 270 | 88 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 180 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 151 | 0 | 0 | 0 |  | 22 | 0 | 34 | 100 | 0 | 50 | 0 | 27 | 0 | 0 | 0 | 295 | 300 | 206 | 8 | 72 | 26 | 20 | 0 | 51 | 0 | 42 | 43 | 19 | 11 | 33 | 21 | 152 | 70 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 267 | 55 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 170 | 298 | 246 | 100 | 191 | 99 | 135 | 0 | 90 | 200 | 140 | 403 | 108 | 90 | 105 | 0 | 281 | 47 | 110 | 98 | 107 | 100 | 393 | 91 | 0 | 144 | 113 | 0 | 33 | 0 | 98 | 55 |  | 714 | 0 | 225 | 0 | 0 | 216 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 80 | 0 | 0 | 0 | 43 | 37 | 92 | 0 | 43 | 40 | 52 | 28 | 18 | 0 | 11 | 84 | 0 | 200 | 12 | 10 | 3 | 0 | 132 | 0 | 0 | 20 | 147 | 0 | 385 | 105 | 140 | 113 | 0 | 110 | 0 | 0 | 113 | 620 | 115 | 0 | 0 | 0 | 0 | 115 |  | 8734 | 4083 | 12817 | 3891 | 714 | 1616 | 775 | 3959 | 904 | 70 | 238 | 498 | 152 | 0 | 0 | 87.35
22:00 | 0 | 0 | 200 | 0 | 270 | 88 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 169 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 100 | 0 | 0 | 0 |  | 22 | 0 | 34 | 88 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 280 | 290 | 219 | 8 | 71 | 26 | 20 | 0 | 51 | 0 | 35 | 43 | 19 | 11 | 33 | 21 | 138 | 72 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 267 | 55 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 130 | 298 | 204 | 100 | 191 | 99 | 133 | 0 | 90 | 200 | 142 | 402 | 108 | 90 | 105 | 0 | 281 | 54 | 110 | 98 | 106 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 99 | 55 |  | 715 | 0 | 230 | 0 | 0 | 216 | 0 | 0 | 32 | 0 | 0 | 0 | 27 | 80 | 0 | 0 | 0 | 43 | 37 | 92 | 0 | 43 | 32 | 52 | 28 | 18 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 4 | 0 | 133 | 0 | 0 | 0 | 147 | 0 | 386 | 105 | 50 | 113 | 0 | 115 | 0 | 0 | 113 | 610 | 119 | 0 | 0 | 0 | 0 | 115 |  | 8568 | 3946 | 12514 | 3831 | 715 | 1627 | 583 | 3961 | 890 | 70 | 216 | 483 | 138 | 0 | 0 | 87.35
23:00 | 0 | 0 | 200 | 0 | 270 | 88 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 178 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 26 | 0 | 0 | 0 |  | 19 | 0 | 34 | 88 | 0 | 50 | 0 | 35 | 0 | 0 | 0 | 270 | 275 | 219 | 8 | 72 | 26 | 20 | 0 | 51 | 0 | 33 | 43 | 19 | 11 | 33 | 21 | 148 | 87 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 267 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 280 | 22 | 11 | 100 | 298 | 0 | 50 | 191 | 28 | 135 | 0 | 90 | 200 | 137 | 401 | 108 | 90 | 105 | 0 | 281 | 54 | 110 | 98 | 106 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 35 | 0 | 100 | 55 |  | 714 | 0 | 230 | 0 | 0 | 219 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 48 | 0 | 0 | 0 | 43 | 36 | 92 | 0 | 43 | 32 | 52 | 28 | 18 | 0 | 11 | 81 | 0 | 200 | 0 | 0 | 4 | 0 | 132 | 0 | 0 | 0 | 144 | 0 | 385 | 105 | 0 | 113 | 0 | 109 | 0 | 0 | 113 | 620 | 195 | 0 | 0 | 0 | 0 | 115 |  | 8140 | 3942 | 12082 | 3757 | 714 | 1697 | 178 | 3918 | 901 | 70 | 219 | 480 | 148 | 0 | 0 | 87.34
24:00 | 0 | 0 | 199 | 0 | 270 | 90 | 0 | 0 | 0 |  | 0 | 290 | 150 | 0 | 0 | 55 | 190 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 25 | 0 | 0 | 0 |  | 18 | 0 | 0 | 88 | 0 | 50 | 0 | 38 | 0 | 0 | 0 | 270 | 275 | 221 | 8 | 72 | 29 | 20 | 0 | 51 | 0 | 33 | 43 | 19 | 11 | 33 | 21 | 138 | 86 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 270 | 61 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 22 | 11 | 100 | 300 | 0 | 0 | 191 | 0 | 135 | 0 | 90 | 200 | 137 | 401 | 109 | 90 | 105 | 0 | 281 | 54 | 110 | 98 | 99 | 100 | 400 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 98 | 55 |  | 713 | 0 | 220 | 0 | 0 | 195 | 0 | 0 | 2 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 43 | 25 | 92 | 0 | 43 | 0 | 52 | 28 | 18 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 143 | 0 | 389 | 105 | 0 | 113 | 0 | 109 | 0 | 0 | 113 | 570 | 220 | 0 | 0 | 0 | 0 | 115 |  | 8023 | 3761 | 11784 | 3759 | 713 | 1741 | 100 | 3845 | 850 | 70 | 195 | 373 | 138 | 0 | 0 | 87.34
KWH | 0 | 0 | 4803000 | 0 | 6787827 | 2175590 | 0 | 0 | 0 |  | 0 | 7384000 | 5521338 | 0 | 0 | 943293 | 4840875 | 0 | 0 | 0 | 1589040 | 2538240 | 0 | 0 | 0 | 0 | 1292760 | 753629 | 1031820 | 492732 | 600000 | 539640 | 824800 | 792500 | 861120 | 0 | 345944 | 848000 | 0 | 3700000 | 357555 | 2983527 | 0 | 0 | 0 |  | 523920 | 0 | 232410 | 1190400 | 72000 | 876480 | 0 | 497280 | 0 | 0 | 0 | 7264000 | 7282000 | 4836000 | 451636 | 1540070 | 612648 | 843840 | 0 | 1161010 | 0 | 347960 | 903034 | 451476 | 206640 | 723500 | 519420 | 3208320 | 1943040 | 0 | 375120 | 14000 | 715000 | 680792 | 1112400 | 0 | 0 | 6109000 | 1329216 | 2063040 | 0 | 0 | 0 | 0 | 245880 | 7157500 | 526104 | 242976 | 939840 | 5193816 | 1320414 | 954038 | 4468800 | 891240 | 3040704 | 153090 | 2108160 | 2492640 | 3330400 | 9615000 | 2306400 | 1886400 | 2396181 | 35160 | 6523636 | 1032800 | 2639552 | 1739640 | 2331840 | 1557120 | 9466100 | 2051520 | 310190 | 3371040 | 2515364 | 0 | 489960 | 203865 | 1480320 | 1170000 |  | 17332363 | 0 | 5705280 | 0 | 0 | 3918952 | 0 | 0 | 135360 | 9728 | 0 | 0 | 548800 | 252320 | 0 | 0 | 0 | 245540 | 231314 | 1035208 | 0 | 545891 | 345574 | 845424 | 266536 | 393360 | 0 | 263934 | 1916945 | 0 | 4850700 | 47000 | 29000 | 246400 | 0 | 3723500 | 0 | 0 | 248640 | 3688018 | 0 | 8990909 | 2091840 | 603374 | 2531712 | 57888 | 2221862 | 0 | 35779 | 2072640 | 15565200 | 2755609 | 0 | 0 | 33180 | 608400 | 2156893 |  | 186280572 | 86551073 | 272831645 | 94430135 | 17332363 | 41302192 | 4957546 | 77297814 | 22332845 | 1193944 | 3994952 | 5387870 | 3208320 | 1393664 | 0
Fuel Cost | 0 | 0 | 7012380 | 0 | 7534487.97 | 2871778.8 | 0 | 0 | 0 |  | 0 | 8048560 | 6128685.18 | 0 | 0 | 7980258.78 | 5034510 | 0 | 0 | 0 | 14492044.8 | 24976281.6 | 0 | 0 | 0 | 0 | 9437148 | 5825552.17 | 10173745.2 | 369549 | 450000 | 0 | 0 | 0 | 8327030.4 | 0 | 93404.88 | 228960 | 0 | 6697000 | 3321685.95 | 3252044.43 | 0 | 0 | 0 |  | 0 | 0 | 2254377 | 11368320 | 626400 | 6941721.6 | 0 | 1476921.6 | 0 | 0 | 0 | 5375360 | 7282000 | 4449120 | 582610.44 | 1771080.5 | 692292.24 | 1181376 | 0 | 1985327.1 | 0 | 3514396 | 8623974.7 | 573374.52 | 154980 | 1266125 | 389565 | 24062400 | 2059622.4 | 0 | 476402.4 | 223160 | 1172600 | 1089267.2 | 1980072 | 0 | 0 | 6353360 | 2618555.52 | 3940406.4 | 0 | 0 | 0 | 0 | 501595.2 | 7229075 | 394578 | 184661.76 | 15986678.4 | 39265248.96 | 22420629.72 | 15951515.36 | 23237760 | 14901532.8 | 29920527.36 | 1789622.1 | 17181504 | 27045144 | 23479320 | 8941950 | 21034368 | 17826480 | 20870736.51 | 0 | 49318688.16 | 8995688 | 23201662.08 | 17361607.2 | 19983868.8 | 10370419.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99834410.88 | 0 | 5990544 | 0 | 0 | 54316674.72 | 0 | 0 | 1419926.4 | 101949.44 | 0 | 0 | 850640 | 2462643.2 | 0 | 0 | 0 | 2416113.6 | 2350150.24 | 9161590.8 | 0 | 7380446.32 | 3348612.06 | 8192158.56 | 2585399.2 | 755251.2 | 0 | 199798.038 | 11559178.35 | 0 | 26290794 | 1628550 | 827370 | 288288 | 0 | 4915020 | 0 | 0 | 4229366.4 | 4314981.06 | 0 | 8900999.91 | 21838809.6 | 10263391.74 | 24025946.88 | 546462.72 | 17241649.12 | 0 | 395357.95 | 15316809.6 | 68331228 | 0 | 0 | 0 | 0 | 0 | 0 |  | 674135135.39 | 422280511.988 | 1096415647.378 | 91303497.038 | 99834410.88 | 46433298.83 | 83753114.42 | 533215829.87 | 106181200.35 | 322364.88 | 56772594.72 | 52128796.34 | 24062400 | 2408140.05 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 270 | 90 | 0 | 0 | 0 |  | 0 | 320 | 275 | 0 | 0 | 55 | 217 | 0 | 0 | 0 | 84 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 15 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 150 | 25 | 140 | 0 | 0 | 0 |  | 22 | 0 | 0 | 94 | 5 | 46 | 0 | 6 | 0 | 0 | 0 | 300 | 320 | 155 | 8 | 31 | 29 | 48 | 0 | 43 | 0 | 0 | 39 | 19 | 8 | 25 | 12 | 142 | 68 | 0 | 14 | 2 | 30 | 30 | 47 | 0 | 0 | 267 | 55 | 85 | 0 | 0 | 0 | 0 | 10 | 300 | 21 | 8 | 0 | 270 | 0 | 31 | 180 | 30 | 121 | 20 | 90 | 52 | 147 | 404 | 98 | 90 | 105 | 5 | 265 | 35 | 110 | 114 | 97 | 65 | 383 | 91 | 45 | 144 | 95 | 0 | 17 | 32 | 90 | 39 |  | 715 | 0 | 225 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 54 | 0 | 43 | 24 | 52 | 0 | 17 | 0 | 11 | 78 | 0 | 200 | 0 | 0 | 4 | 0 | 148 | 0 | 0 | 0 | 156 | 0 | 387 | 94 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 550 | 100 | 0 | 0 | 5 | 91 | 115 |  | 11435 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 270 | 88 | 0 | 0 | 0 | 0 | 0 | 290 | 150 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 42 | 0 | 35 | 35 | 0 | 150 | 25 | 151 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 0 | 50 | 0 | 21 | 0 | 0 | 0 | 270 | 275 | 200 | 8 | 73 | 29 | 20 | 0 | 51 | 0 | 41 | 43 | 19 | 11 | 33 | 21 | 156 | 72 | 0 | 17 | 0 | 30 | 30 | 47 | 0 | 0 | 268 | 55 | 89 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 200 | 298 | 306 | 100 | 190 | 100 | 132 | 0 | 90 | 200 | 140 | 403 | 108 | 90 | 105 | 0 | 281 | 35 | 110 | 98 | 107 | 100 | 394 | 91 | 0 | 144 | 113 | 0 | 17 | 0 | 98 | 55 |  | 714 | 0 | 225 | 0 | 0 | 210 | 0 | 0 | 40 | 0 | 0 | 0 | 28 | 80 | 0 | 0 | 0 | 43 | 37 | 92 | 0 | 43 | 40 | 52 | 28 | 18 | 0 | 11 | 84 | 0 | 200 | 15 | 10 | 3 | 0 | 132 | 0 | 0 | 98 | 145 | 0 | 377 | 105 | 177 | 113 | 32 | 111 | 0 | 0 | 113 | 670 | 105 | 0 | 0 | 0 | 0 | 115 |  | 13024 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 270 | 100 | 0 | 0 | 0 | 0 | 0 | 330 | 300 | 0 | 0 | 55 | 229 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 35 | 35 | 0 | 150 | 25 | 150 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 6 | 50 | 0 | 25 | 0 | 0 | 0 | 330 | 330 | 220 | 8 | 73 | 29 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 163 | 100 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 265 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 98 | 113 | 100 | 400 | 92 | 0 | 162 | 113 | 0 | 17 |  | 100 | 55 |  | 729 | 0 | 350 | 0 | 0 | 225 | 0 | 0 | 40 | 30 | 0 | 0 | 27 | 80 | 0 | 0 | 0 | 43 | 40 | 92 | 0 | 43 | 40 | 52 | 30 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 10 | 0 | 220 | 0 | 0 | 100 | 220 | 0 | 414 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 660 | 110 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 200 | 0 | 270 | 100 | 0 | 0 | 0 | 0 | 0 | 330 | 300 | 0 | 0 | 55 | 229 | 0 | 0 | 0 | 93 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 51 | 0 | 35 | 35 | 0 | 150 | 25 | 150 | 0 | 0 | 0 | 0 | 22 | 0 | 51 | 100 | 6 | 50 | 0 | 10 | 0 | 0 | 0 | 330 | 330 | 220 | 8 | 73 | 29 | 55 | 0 | 51 | 0 | 32 | 52 | 22 | 11 | 33 | 22 | 138 | 70 | 0 | 17 | 1.6 | 30 | 30 | 50 | 0 | 0 | 265 | 60 | 86 | 0 | 0 | 0 | 0 | 10 | 300 | 22 | 11 | 100 | 300 | 200 | 100 | 200 | 100 | 149 | 20 | 90 | 200 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 98 | 113 | 100 | 400 | 92 | 50 | 148 | 113 | 0 | 17 | 30 | 100 | 55 |  | 729 | 0 | 300 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 43 | 40 | 90 | 0 | 43 | 0 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 10 | 0 | 220 | 0 | 0 | 100 | 210 | 0 | 414 | 105 | 100 | 113 | 0 | 113 | 0 | 8 | 113 | 660 | 110 |  | 0 | 6 | 50 | 115
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 270 | 98 | 0 | 0 | 0 | 0 | 0 | 300 | 150 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 22 | 33 | 33 | 0 | 0 | 35 | 35 | 0 | 150 | 0 | 131 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 10 | 0 | 12 | 0 | 11 | 0 | 0 | 0 | 275 | 275 | 183 | 8 | 73 | 26 | 56 | 0 | 43 | 0 | 0 | 43 | 16 | 11 | 30 | 21 | 112 | 89 | 0 | 17 | 0 | 30 | 30 | 50 | 0 | 0 | 266 | 60 | 89 | 0 | 0 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 84 | 0 | 0 | 191 | 0 | 116 | 5 | 90 | 15 | 127 | 362 | 109 | 66 | 105 | 1 | 264 | 35 | 110 | 0 | 107 | 50 | 280 | 91 | 13 | 144 | 113 | 0 | 17 | 7 | 24 | 55 | 0 | 716 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 11 | 80 | 0 | 200 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 129 | 0 | 382 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 95 | 520 | 152 | 0 | 0 | 0 | 31 | 52 | 0
199
| Minimum Generation |  | 9572 | 6:00
| Highest Generation |  | 13024 | 20:00
| Day Peak Generation |  | 11435 | 12:00
| Evening Peak Generation |  | 13024 | 20:00
| HVDC Max Flow |  | 718 | 1:00
| HVDC EvPeak Flow |  | 714 | 20:00
| Load factor L.F |  | 87.28%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-03-22
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2022-03-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11435 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 9683 | MW
Evening Peak Generation : |  | 13024 | MW Hour : | 20:00 | Available Max Generation : |  | 14017 | MW
E.P. Demand (at gen end) : |  | 13024 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 13024 | MW Hour : | 20:00 | Reserve(Generation end) |  | 517 | MW
Total Gen. (MKWH) : |  | 272.8316 | System Load Factor : | 87.28% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -130 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-03-22
Actual : | 87.28 | Ft.(MSL) , | Rule curve : | 89.64 | Ft.( MSL )
Gas Consumed : | Total = | 1068.76 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 137736795.868
: |  | Coal : | 106181200.35 | Oil : | 725870335.35 | Total : | 969788331.568
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4794.6243 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1636.5761 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1467.4117 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1326.3186 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1198.3608 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 967.0502 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 532.8277 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 248.7804 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 745.875 |  |  | 0 | 0%
Total | 0 |  | 12917.8248 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,5
3) Ashuganj-4,5
4) Baghabari-100 MW & 71 MW
5) Raozan unit- 1
6) Kushiara 163 MW.
7) Siddhirganj 210 MW .
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sonargaon 132/33 kV T-1 transformer was under shut down from 06:50 to 08:34 for C/M.
b) Kishoreganj 132/33 kV T-1 transformer was under shut down from 07:30 to 07:42 for C/M.
c) Dhamrai 132/33 kV T-1 transformer was under shut down from 12:28 to 18:23 for C/M.
d) Chowddagram-Feni 132 kV Ckt-2 was under shut down from 09:16 to 18:07 for C/M.
e) Hasnabad-Postogula 132 kV Ckt-2 was under shut down from 10:15 to 12:53 for C/M.
f) Haripur-Madanganj 132 kV Ckt was under shut down from 10:54 to 16:13 for D/W.
g) Faridpur 132 kV Bus-A was under shut down from 16:08 to 16:56 for D/W.
h) Meghnaghat summit 305 MW GT-2 was shut down at 16:24 for Gas shortage.
i) Bhola Natun Bidyut 220 MW GT-2 was synchronized at 20:34.
j) Haripur 230/132 kV T02 transformer was under shut down from 23:31 to 01:33(22-03-2022) due to
red hot maintenance at 33 kV end.
k) Haripur 230/132 kV T01 transformer was under shut down from 01:37(22-03-2022) to 02:39 due to
red hot maintenance at 33 kV end.
l) Dohazari-Cox'sbazar 132 kV Ckt-2 tripped at 06:19(22-03-2022) from both end showing Dist. Z1
3-phase relays and was switched on at
m) Bhaluka 132/33 kV T-2 transformer was under shut down from 06:40(22-03-22) to 07:45 for C/M.
n) Sonargaon 132/33 kV T-2 transformer was under shut down from 06:36(22-03-22) to 08:22 for C/M.
o) Baroirhat-Hathazari 132 kV Ckt-1 was shut down since at 07:10(22-03-22).
p) Bhulta 132/33 kV T-2 transformer was under shut down from 07:01(22-03-22) to 09:12 for red hot
maintenance at 33 kV end.
q) Haripur S/S-Haripur 412 MW 132 kV Ckt was shut down at 07:30 for C/M.
r) Bagherhat-Mongla 132 kV Ckt-1 tripped at 07:36(22-03-2022) showing Dist. Z3 at Bagherhat end &
Dist. Z2 at Mongla end and was switched on at 09:24(22-03-2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-03-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4803000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6787827 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 88 | 2175590 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under Maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 290 | 7384000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 5521338 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 943293
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 492732
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 170 | 4840875 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1589040 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1292760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2538240
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 753629
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1031820
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1139640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 824800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 792500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 42 | 861120 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 5193816
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 306 | 1320414
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 100 | 954038
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 891240
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 3040704 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 1886400 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 2051520 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3371040 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 203865
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1170000
| Dhaka area Total |  |  |  | 5696 | 3128 | 63855241
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3700000
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 357555
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 153090
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 876480
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1193944 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 2983527 | ST under S/D
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2396181
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 232410 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1190400
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 2108160 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 497280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 72000 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35160
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 281 | 6523636 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 1032800 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2639552
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1557120 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 113 | 2515364
| Chattogram area Total |  |  |  | 2382 | 1452 | 30064659
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 200 | 4836000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7264000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7282000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 29 | 612648 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 843840 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 451636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1161010
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 3330400 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 347960 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 73 | 1540070 | ST under maint
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2492640
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 451476 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 206640
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3208320
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 723500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 903034 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 519420 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 939840
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1739640 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 107 | 2331840 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 489960 | 33 kV feeder O/L
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 98 | 1480320 | Engine problem
| Cumilla Area Total |  |  |  | 3014 | 2110 | 43156194
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 72 | 1943040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 375120 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 190 | 4468800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 2306400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 310190
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 523920
| Mymensingh Area Total |  |  |  | 622 | 409 | 9941470
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 680792 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 268 | 6109000 | Gas shortage
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1112400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 242976
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1329216
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 2063040
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 22 | 526104
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7157500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9615000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245880
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 394 | 9466100
| Sylhet Area Total |  |  |  | 2377 | 1659 | 39263008
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 714 | 17332363
108 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 135360 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 210 | 3918952
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 9728 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 5705280 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 98 | 248640
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2091840
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 57888 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 608400
| Khulna Area Total |  |  |  | 2229 | 1424 | 30108451
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 252320 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 548800 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Payra 1320 MW inauguration.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 670 | 15565200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 105 | 2755609 | Payra 1320 MW inauguration.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Payra 1320 MW inauguration.
| Barisal Area Total |  |  |  | 2046 | 883 | 19121929
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 245540 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 37 | 231314 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contact expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 545891 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 345574 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 3 | 246400 | ST Commissioning process
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 132 | 3723500 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 145 | 3688018 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 377 | 8990909 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 266536 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 393360 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 263934
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 845424
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 1035208 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 177 | 603374
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2531712
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2072640
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33180
| Rajshahi Area Total |  |  |  | 2129 | 1424 | 26062514
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 84 | 1916945
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4850700 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 47000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 29000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 111 | 2221862
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35779
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2156893
| Rangpur Area Total |  |  |  | 720 | 535 | 11258179
| Total |  |  |  | 21215 | 13024 | 272831645
| Eastern Grid Total |  |  |  | 14091 | 8758 | 186280572
| Western Grid Total |  |  |  | 7124 | 4266 | 86551073
| National Grid Total |  |  |  | 21215 | 13024 | 272831645
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-03-21
(a) ENTIRE EASTERN GRID : |  | 8404 | MW | (b) ENTIRE WESTERN GRID : |  | 4049 | MW
i) Dhaka area |  | 4634 | MW | i) Khulna area |  | 1479 | MW
ii) Chittagong area |  | 1279 | MW | ii) Rajshahi area |  | 1411 | MW
iii) Comilla area |  | 1104 | MW | iii) Barisal area |  | 327 | MW
iv) Mymensingh area |  | 952 | MW | iv) Rangpur area |  | 832 | MW
v) Sylhet area |  | 435 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12453 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 19:00 | Valuka | 114 | 18:30 | Central S/S | 84 | 21:00
Munsiganj | 88 | 21:00 | Tangail | 198 | 18:30 | Noapara | 45 | 19:00
Sonargaon | 107 | 15:00 | Mymensing | 215 | 20:00 | Jessore | 126 | 20:00
Bhulta | 230 | 19:30 | Kishoreganj | 122 | 23:00 | Benapol | 52 | 21:00
Madanganj | 32 | 18:30 | Netrokona | 117 | 6:00 | Jhenida(Old) | 108 | 20:00
Rahim steel | 28 | 17:00 | Jamalpur | 149 | 7:00 | Bottail | 118 | 20:00
Ghorasal | 76 | 17:00 | Sherpur | 144 | 7:00 | G.K Project | 51 | 20:00
Narsingdi | 166 | 19:30 | Srimongal | 45 | 18:30 | Faridpur | 124 | 19:30
Haripur(SBU) | 119 | 21:00 | Shahjibazar | 108 | 19:30 | Rajbari | 58 | 19:00
Sreenagar | 36 | 19:30 | Fenchuganj | 33 | 22:00 | Madaripur | 89 | 19:30
Shyampur | 198 | 0:00 | Kulawara | 34 | 18:00 | Sariatpur | 54 | 19:00
Shitalakhya | 109 | 19:30 | Sylhet | 140 | 18:30 | Gopalganj | 89 | 19:00
Matuail | 72 | 23:00 | Chatak | 26 | 18:30 | Bagerhat | 93 | 19:00
Char Saidpur | 43 | 12:00 | Sunamganj | 40 | 19:00 | Mongla | 38 | 9:00
Ullon | 43 | 23:00 | Biani Bazar | 47 | 18:30 | Satkhira | 110 | 20:00
Hasnabad | 69 | 22:00 | Comilla (S) | 166 | 18:30 | Gallamari | 53 | 19:30
Magbazar | 115 | 16:00 | Comilla(N) | 136 | 19:00 | Magura | 54 | 20:00
Maniknagar | 67 | 16:00 | Chandpur | 59 | 19:00 | Norail | 42 | 20:00
Bangabhaban | 10 | 10:00 | Feni | 100 | 18:30 | Chuadanga | 93 | 21:00
Motijheel | 36 | 13:00 | Chowmuhani | 178 | 19:30 | Barisal(N) | 48 | 21:00
Narinda | 60 | 13:00 | Ashuganj | 36 | 1:00 | Barisal (S) | 90 | 19:00
Kazla | 88 | 19:30 | Daudkandi | 123 | 18:30 | Patuakhali | 95 | 19:30
Dhanmondi | 202 | 13:00 | B.Baria | 150 | 19:00 | Bhandaria | 46 | 21:00
Lalbag | 93 | 13:00 | Ramganj | 76 | 19:00 | Borguna | 14 | 18:30
Madartek | 79 | 23:00 | Chaddagram | 45 | 18:30 | Borhan Uddin | 35 | 19:30
Dhaka University | 40 | 12:00 | PHP | 10 | 1:00 | Ishurdi | 69 | 19:00
Aftabnagar | 29 | 18:00 | Kochua | 56 | 19:00 | Ruppur Paromanobik | 4 | 9:00
Fatullah | 68 | 18:30 | Madunaghat | 54 | 18:30 | Natore | 135 | 20:00
Nawabganj | 45 | 21:00 | Hathazari | 85 | 19:30 | Bogra | 169 | 24:00
Keraniganj | 78 | 19:30 | Khulshi | 177 | 16:00 | Naogaon | 120 | 20:00
Banani | 52 | 15:00 | Halishahar | 99 | 13:00 | Rajshahi | 140 | 19:30
Mirpur | 121 | 18:30 | Baraulia | 132 | 19:30 | Rajshahi New | 44 | 23:00
Kalyanpur | 90 | 18:30 | Sikalbaha | 28 | 18:30 | C.Nawabganj | 68 | 22:00
Gulshan | 112 | 15:00 | Dohazari | 78 | 19:00 | Amnura | 65 | 21:00
Uttara | 68 | 18:00 | Cox'sbazar | 115 | 18:00 | Pabna | 100 | 19:30
Uttara New | 32 | 12:00 | Chandraghona | 30 | 19:00 | Shahjadpur | 99 | 20:00
Kamrangirchar | 68 | 18:30 | Kaptai | 0 | 1:00 | Serajganj | 114 | 19:30
Savar | 173 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 105 | 21:00
Bhasantec | 122 | 18:30 | Bakulia | 115 | 18:30 | Joypurhat | 64 | 20:00
Agargaon | 88 | 14:00 | Julda | 28 | 23:00 | Sherpur(Bogura) | 60 | 19:30
Satmosjid | 87 | 18:30 | TK chemical | 26 | 18:00 | Mohastangor | 66 | 19:30
Old Tongi | 124 | 15:00 | Modern Steel | 0 | 1:00 | Bhangura | 34 | 19:00
Kabirpur | 292 | 18:30 | Shahmirpur | 38.1 | 2:00 | Rangpur | 145 | 19:30
Manikgonj | 101 | 13:00 | Khagrachhari | 24 | 18:30 | Lalmonirhat | 50 | 19:00
Joydevpur | 192 | 18:00 | Matarbari | 39 | 18:30 | Saidpur | 108 | 8:00
New Tongi | 82 | 11:00 | Baroiar Hat | 58 | 19:00 | Purbasadipur | 111 | 20:00
Kodda | 316 | 15:00 | Rangamati | 12 | 18:30 | Thakurgaon | 95 | 19:00
Dhamrai | 90 | 21:00 | Agrabad | 76 | 18:00 | Palashbari | 114 | 19:00
Rajendrapur | 98 | 21:00 | Rampur | 11 | 1:00 | Barapukuria | 58 | 10:00
Bashundara | 164 | 14:00 | Abul Khair 230 | 141 | 15:00 | Panchagar | 61 | 19:00
Purbachal | 18 | 21:00 | BSRM | 156 | 5:00 | Joldhaka | 66 | 19:30
Tongi Millgate | 52 | 17:00 | GPH Ispat | 82 | 6:00 | Kurigram | 66 | 18:30
Bashundhara Cement |  |  | Goalpara | 25 | 19:30 | Mithapukur | 39 | 19:00
Gulshan | 66 | 13:00 | Niamatpur | 50 | 18:30
Halishahar | 58 | 18:30 | Noapara | 39 | 20:00
Haripur | 117 | 11:00 | Pabna | 68 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-03-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 1:00 | 400 | 16:00 | Kaliakoir | 385 | 0.25 | 365 | 0.66667
| Bheramara | 403 | 1:00 | 394 | 19:00 | Bhulta | 406 | 0.041667 | 390 | 0.5
| Ashuganj(N) | 413 | 4:00 | 398 | 12:00 | Gopalganj | 410 | 0.625 | 398 | 0.79167
| Payra | 419 | 6:00 | 412 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 235 | 7:00 | Hathazari | 238 | 3:00 | 231 | 7:00
| Ishurdi | 237 | 18:00 | 232 | 7:00 | Megnaghat | 233 | 6:00 | 224 | 16:00
| Ashuganj | 246 | 10:00 | 235 | 12:00 | Fenchuganj | 239 | 11:00 | 231 | 18:00
| Serajganj | 236 | 1:00 | 234 | 7:00 | Siddhirganj | 233 | 1:00 | 222 | 17:00
| Baghabari | 236 | 18:00 | 222 | 13:00 | Maniknagar | 229 | 1:00 | 218 | 17:00
| Barapukuria | 232 | 17:00 | 227 | 6:00 | Agargaon | 230 | 18:00 | 217 | 12:00
| Bogra | 231 | 17:00 | 224 | 7:00 | Barisal | 244 | 6:00 | 238 | 18:30
| Rajshahi | 235 | 18:00 | 226 | 8:00 | Bhola 225 MW | 248 | 5:00 | 241 | 18:30
| Khulna South | 241 | 5:00 | 232 | 21:00 | AKSML | 238 | 6:00 | 230 | 19:00
| Rampura | 230 | 3:00 | 219 | 12:00 | BSRM | 237 | 6:00 | 231 | 12:00
| Haripur | 227 | 1:00 | 218 | 12:00 | Bibiyana | 237 | 6:00 | 231 | 23:00
| Hasnabad | 231 | 6:00 | 219 | 11:00 | Bhulta | 232 | 1:00 | 221 | 16:00
| Shyampur | 230 | 6:00 | 219 | 11:00 | Ashuganj (S) | 240 | 1:00 | 233 | 12:00
| Aminbazar | 229 | 1:00 | 219 | 2:00 | Kaliakoir | 225 | 2:00 | 217 | 16:00
| Tongi | 229 | 5:00 | 220 | 15:00 | GPH | 237 | 6:00 | 231 | 17:00
| Comilla (N) | 234 | 8:00 | 227 | 12:00 | Jhenaidah | 235 | 4:00 | 228 | 21:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 8:00 | 128 | 12:00 | PHP | 138 | 8:00 | 131 | 2:00
| Munsiganj | 135 | 8:00 | 126 | 12:00 | Kachua | 138 | 8:00 | 132 | 2:00
| Sonargaon | 136 | 8:00 | 128 | 12:00 | Madanhat | 138 | 7:00 | 135 | 11:00
| Bhulta | 128 | 5:00 | 126 | 1:00 | Hathazari | 140 | 13:00 | 136 | 9:00
| Madanganj | 135 | 8:00 | 126 | 12:00 | Khulshi | 136 | 6:00 | 132 | 12:00
| Rahim steel | 134 | 1:00 | 128 | 17:00 | Halishahar | 137 | 6:00 | 134 | 9:00
| Ghorasal | 138 | 1:00 | 135 | 8:00 | Baraulia | 140 | 5:00 | 135 | 9:00
| Narsingdi | 128 | 6:00 | 126 | 18:30 | Sikalbaha | 139 | 6:00 | 132 | 18:00
| Haripur(SBU) | 134 | 1:00 | 128 | 17:00 | Dohazari | 134 | 6:00 | 128 | 18:30
| Sreenagar | 134 | 6:00 | 123 | 12:00 | Cox'sbazar | 127 | 8:00 | 92 | 10:00
| Shyampur | 132 | 6:00 | 122 | 12:00 | Chandraghona | 139 | 7:00 | 135 | 12:00
| Shitalakhya | 135 | 8:00 | 127 | 12:00 | Kaptai | 134 | 7:00 | 127 | 10:00
| Matuail | 136 | 8:00 | 128 | 12:00 | A. Khaer Stl. | 139 | 6:00 | 134 | 8:00
| Char Saidpur | 136 | 8:00 | 126 | 12:00 | Bakulia | 138 | 23:00 | 133 | 9:00
| Ullon | 133 | 3:00 | 125 | 10:00 | Julda | 138 | 23:00 | 134 | 9:00
| Hasnabad | 133 | 2:00 | 126 | 12:00 | TK Chemical | 138 | 6:00 | 134 | 9:00
| Magbazar | 136 | 4:00 | 125 | 12:00 | Modern Steel | 138 | 1:00 | 134 | 9:00
| Maniknagar | 133 | 3:00 | 126 | 12:00 | Shahmirpur | 138 | 6:00 | 134 | 8:00
| Bangabhaban | 133 | 3:00 | 126 | 12:00 | Khagrachhari | 138 | 21:00 | 133 | 19:00
| Motijheel | 133 | 3:00 | 126 | 12:00 | Matarbari | 131 | 17:00 | 118 | 19:00
| Narinda | 133 | 3:00 | 126 | 12:00 | Baroiar Hat | 138 | 7:00 | 131 | 14:00
| Kazla | 133 | 3:00 | 126 | 12:00 | Rangamati | 139 | 6:00 | 134 | 14:00
| Dhanmondi | 136 | 8:00 | 127 | 12:00 | Agrabad | 137 | 7:00 | 133 | 9:00
| Lalbag | 134 | 6:00 | 125 | 12:00 | Rampur | 137 | 6:00 | 133 | 10:00
| Madartek | 134 | 1:00 | 125 | 10:00 | Goalpara S/S | 138 | 5:00 | 135 | 12:00
| Dhaka University | 134 | 1:00 | 124 | 10:00 | Khulna Central S/S | 138 | 6:00 | 133 | 21:00
| Aftabnagar | 134 | 1:00 | 125 | 10:00 | Noapara | 137 | 6:00 | 132 | 22:00
| Fatullah | 132 | 6:00 | 122 | 12:00 | Jessore | 134 | 3:00 | 129 | 21:00
| Nawabganj | 134 | 6:00 | 125 | 12:00 | Benapol | 134 | 4:00 | 128 | 21:00
| Keraniganj | 134 | 6:00 | 126 | 12:00 | Jhenida(Old) | 133 | 1:00 | 128 | 21:00
| Banani | 134 | 3:00 | 124 | 12:00 | Bottail | 136 | 6:00 | 131 | 21:00
| Mirpur | 135 | 5:00 | 126 | 12:00 | G.K Project | 140 | 18:00 | 137 | 21:00
| Kalyanpur | 137 | 6:00 | 128 | 12:00 | Faridpur | 136 | 6:00 | 133 | 19:00
| Gulshan | 132 | 1:00 | 124 | 10:00 | Rajbari | 137 | 6:00 | 131 | 23:00
| Uttara | 137 | 6:00 | 127 | 16:00 | Madaripur | 143 | 6:00 | 138 | 14:00
| Uttara New | 136 | 4:00 | 126 | 11:00 | Shariyatpur S/S | 142 | 6:00 | 134 | 19:00
| Kamrangirchar | 133 | 4:00 | 124 | 12:00 | Gopalganj | 140 | 3:00 | 133 | 19:00
| Savar | 136 | 5:00 | 127 | 12:00 | Bagerhat | 137 | 6:00 | 131 | 18:30
| Bhasantec | 135 | 6:00 | 125 | 12:00 | Mongla | 136 | 6:00 | 131 | 20:00
| Agargaon | 136 | 6:00 | 127 | 12:00 | Satkhira | 136 | 4:00 | 128 | 21:00
| Satmosjid | 136 | 6:00 | 127 | 12:00 | Gallamari | 140 | 6:00 | 131 | 19:00
| Old Tongi | 136 | 22:00 | 127 | 18:00 | Magura | 136 | 11:00 | 127 | 21:00
| Kabirpur | 134 | 4:00 | 124 | 18:30 | Narail | 134 | 5:00 | 125 | 21:00
| Manikgonj | 132 | 4:00 | 125 | 15:00 | Chuadanga | 128 | 5:00 | 118 | 21:00
| Joydevpur | 138 | 1:00 | 132 | 10:00 | Barisal(N) | 144 | 8:00 | 136 | 18:30
| New Tongi | 136 | 3:00 | 127 | 12:00 | Barisal (S) | 143 | 5:00 | 131 | 21:00
| Kodda | 136 | 1:00 | 124 | 18:30 | Patuakhali(S) | 137 | 3:00 | 132 | 19:00
| Dhamrai | 135 | 1:00 | 0 | 6:00 | Bhandaria | 143 | 6:00 | 134 | 19:30
| Rajendrapur | 134 | 1:00 | 122 | 19:00 | Barguna | 139 | 5:00 | 132 | 18:30
| Bashundara | 134 | 1:00 | 127 | 12:00 | Jhenida(New) | 134 | 2:00 | 130 | 13:00
| Purbachal | 134 | 1:00 | 123 | 11:00 | Ishurdi | 137 | 1:00 | 134 | 7:00
| Tongi Millgate | 135 | 1:00 | 128 | 17:00 | Ruppur Paromanobik | 137 | 17:00 | 134 | 18:00
| Bashundhara Cement |  |  |  |  | Natore | 136 | 17:00 | 130 | 7:00
| Valuka | 117 | 5:00 | 107 | 7:00 | Bogra | 136 | 18:00 | 128 | 7:00
| Tangail | 129 | 4:00 | 123 | 15:00 | Noagaon | 129 | 18:00 | 119 | 7:00
| Mymensing | 120 | 5:00 | 113 | 7:00 | Rajshahi | 135 | 17:00 | 128 | 7:00
| Kishorganj | 125 | 5:00 | 119 | 1:00 | Rajshahi New | 134 | 17:00 | 127 | 7:00
| Netrokona | 117 | 5:00 | 108 | 14:00 | C.Nawabganj | 131 | 17:00 | 123 | 7:00
| Jamalpur | 129 | 2:00 | 120 | 7:00 | Amnura | 132 | 17:00 | 123 | 7:00
| Sherpur | 126 | 2:00 | 118 | 19:00 | Pabna | 136 | 1:00 | 132 | 7:00
| Srimongal | 137 | 5:00 | 132 | 18:30 | Shahjadpur | 140 | 18:30 | 135 | 7:00
| Shahjibazar | 136 | 6:00 | 130 | 15:00 | Serajganj | 133 | 1:00 | 127 | 7:00
| Fenchuganj | 138 | 8:00 | 129 | 18:30 | Niyamatpur | 127 | 17:00 | 114 | 7:00
| Khulawara | 136 | 3:00 | 130 | 16:00 | Joypurhat | 127 | 10:00 | 118 | 7:00
| Sylhet | 132 | 7:00 | 124 | 15:00 | Sherpur(Bogura) | 135 | 18:00 | 127 | 7:00
| Chatak | 132 | 7:00 | 123 | 18:30 | Mohastangor | 134 | 17:00 | 126 | 7:00
| Sunamganj | 130 | 6:00 | 120 | 18:30 | Bhangura | 137 | 1:00 | 132 | 7:00
| Biani Bazar | 132 | 7:00 | 123 | 15:00 | Rangpur | 130 | 3:00 | 120 | 7:00
| Comilla(s) | 131 | 4:00 | 125 | 18:30 | Lalmonirhat | 127 | 17:00 | 120 | 7:00
| Comilla(n) | 139 | 8:00 | 133 | 12:00 | Saidpur | 132 | 5:00 | 122 | 7:00
| Chandpur | 140 | 11:00 | 132 | 1:00 | Purbasadipur | 131 | 10:00 | 121 | 7:00
| Feni | 139 | 11:00 | 131 | 2:00 | Thakurgaon | 133 | 10:00 | 121 | 7:00
| Chowmuhani | 136 | 8:00 | 130 | 1:00 | Palashbari | 130 | 18:00 | 120 | 7:00
| Ashuganj | 137 | 7:00 | 133 | 16:00 | Barapukuria | 132 | 17:00 | 127 | 6:00
| Daudkandi | 136 | 8:00 | 127 | 12:00 | Panchagar | 135 | 10:00 | 121 | 19:00
| B.Baria | 133 | 6:00 | 127 | 20:00 | Joldhaka | 129 | 10:00 | 118 | 7:00
| Ramganj | 138 | 8:00 | 131 | 2:00 | Kurigram | 128 | 17:00 | 119 | 6:00
| Chaddagram | 140 | 8:00 | 132 | 12:00 | Mithapukur | 131 | 10:00 | 122 | 7:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-03-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 126 | 8023 | 3761 | 11784 |  |  |  | QF-LDC-11
0:30 | 70 | 7819.5 | 3563.5 | 11383 | Date: | 2022-03-21
1:00 | 14 | 7616 | 3366 | 10982
1:30 | 12 | 7470.5 | 3221 | 10691.5
2:00 | 10 | 7325 | 3076 | 10401
2:30 | 43 | 7191 | 3073.5 | 10264.5 | [5 empty] | Gen. at Eve. Peak | 13024 | 13024 MW (20:00 )
3:00 | 76 | 7057 | 3071 | 10128 | [6 empty] | 20:00
3:30 | 102 | 6915 | 3057.5 | 9972.5 | [5 empty] | Gen. at Day Peak | 11435 | 11435 MW (12:00 )
4:00 | 128 | 6773 | 3044 | 9817 | [6 empty] | 12:00
4:30 | 110 | 6721 | 2992.5 | 9713.5 | [5 empty] | Highest Generation | 13024
5:00 | 92 | 6669 | 2941 | 9610 | [6 empty] | 20:00
5:30 | 56 | 6651.5 | 2939.5 | 9591
6:00 | 20 | 6634 | 2938 | 9572
6:30 | 75 | 6648 | 3017 | 9665
7:00 | 130 | 6662 | 3096 | 9758
7:30 | 99 | 6729 | 3169 | 9898
8:00 | 68 | 6796 | 3242 | 10038
8:30 | 82 | 6977.5 | 3233 | 10210.5
9:00 | 96 | 7159 | 3224 | 10383
9:30 | 213 | 7242.5 | 3343.5 | 10586
10:00 | 330 | 7326 | 3463 | 10789
10:30 | 317 | 7459.5 | 3472.5 | 10932
11:00 | 304 | 7593 | 3482 | 11075
11:30 | 254 | 7740 | 3515 | 11255
12:00 | 204 | 7887 | 3548 | 11435
12:30 | 145 | 7975 | 3561 | 11536
13:00 | 86 | 8063 | 3574 | 11637
13:30 | 144 | 8090.5 | 3579 | 11669.5
14:00 | 202 | 8118 | 3584 | 11702
14:30 | 205 | 8198.5 | 3592.5 | 11791
15:00 | 208 | 8279 | 3601 | 11880
15:30 | 255 | 8245.5 | 3560 | 11805.5
16:00 | 302 | 8212 | 3519 | 11731
16:30 | 321 | 8111 | 3542 | 11653
17:00 | 340 | 8010 | 3565 | 11575
17:30 | 333 | 7965 | 3575.5 | 11540.5
18:00 | 326 | 7920 | 3586 | 11506
18:30 | 170 | 8341 | 3810 | 12151
19:00 | 14 | 8762 | 4034 | 12796
19:30 | 48 | 8768 | 4246 | 13014
20:00 | 34 | 8758 | 4266 | 13024 |  |  |  | Executive Engineer
20:30 | 68 | 8746 | 4174.5 | 12920.5 |  |  |  | Network Operation Division
21:00 | 102 | 8734 | 4083 | 12817
21:30 | 71 | 8651 | 4014.5 | 12665.5
22:00 | 40 | 8568 | 3946 | 12514 |  |  |  |  | Page 6 of 7
22:30 | 102 | 8354 | 3944 | 12298
23:00 | 164 | 8140 | 3942 | 12082
23:30 | 145 | 8081.5 | 3851.5 | 11933
24:00 | 126 | 8023 | 3761 | 11784
13024 MW (20:00 )
11435 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-03-21 |  | Energy |  | 272831645
[13 empty] | 2022-03-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3759 | 713 | 1741 | 100 | 3845 | 850 | 70 | 195 | 373 | 138 | 0 | 0
0:30 | 3918.5 | 715.5 | 1793 | 50 | 3452.5 | 863.5 | 70 | 157.5 | 227.5 | 135 | 0 | 0 | Date: | 2022-03-21
1:00 | 4078 | 718 | 1845 | 0 | 3060 | 877 | 70 | 120 | 82 | 132 | 0 | 0
1:30 | 4074.5 | 718 | 1854 | 0 | 2787.5 | 863 | 67.5 | 120 | 73 | 134 | 0 | 0 | [8 empty] | Total Energy | 272.8316 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 4071 | 718 | 1863 | 0 | 2515 | 849 | 65 | 120 | 64 | 136 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4058.5 | 717.5 | 1851 | 0 | 2440.5 | 849 | 50 | 120 | 48 | 130 | 0 | 0 | [8 empty] | Energy Requirement | 272.8316
3:00 | 4046 | 717 | 1839 | 0 | 2366 | 849 | 35 | 120 | 32 | 124 | 0 | 0
3:30 | 4060.5 | 717.5 | 1831 | 0 | 2224.5 | 838 | 35 | 120 | 24 | 122 | 0 | 0 | [6 empty] | Shortage
4:00 | 4075 | 718 | 1823 | 0 | 2083 | 827 | 35 | 120 | 16 | 120 | 0 | 0
4:30 | 4060.5 | 717.5 | 1811.5 | 0 | 2008 | 828 | 35 | 120 | 16 | 117 | 0 | 0
5:00 | 4046 | 717 | 1800 | 0 | 1933 | 829 | 35 | 120 | 16 | 114 | 0 | 0
5:30 | 4019.5 | 717.5 | 1762 | 0 | 1981 | 829 | 35 | 120 | 16 | 111 | 0 | 0
6:00 | 3993 | 718 | 1724 | 0 | 2029 | 829 | 35 | 120 | 16 | 108 | 0 | 0
6:30 | 3944.5 | 718 | 1766.5 | 0 | 2120.5 | 829 | 35 | 120 | 16 | 107 | 8.5 | 0 |  |  |  |  | Coal
7:00 | 3896 | 718 | 1809 | 0 | 2212 | 829 | 35 | 120 | 16 | 106 | 17 | 0
7:30 | 3883.5 | 717.5 | 1783.5 | 0 | 2355.5 | 829 | 35 | 120 | 24 | 109 | 41 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3871 | 717 | 1758 | 0 | 2499 | 829 | 35 | 120 | 32 | 112 | 65 | 0
8:30 | 3887.5 | 717 | 1729 | 0 | 2628.5 | 829 | 35 | 120 | 67 | 111 | 86.5 | 0
9:00 | 3904 | 717 | 1700 | 0 | 2758 | 829 | 35 | 120 | 102 | 110 | 108 | 0
9:30 | 3887 | 715.5 | 1756.5 | 0 | 2857 | 829.5 | 35 | 120 | 135.5 | 113 | 137 | 0
10:00 | 3870 | 714 | 1813 | 0 | 2956 | 830 | 35 | 120 | 169 | 116 | 166 | 0
10:30 | 3829 | 714.5 | 1763 | 0 | 3147 | 828.5 | 35 | 120 | 190 | 123 | 182 | 0
11:00 | 3788 | 715 | 1713 | 0 | 3338 | 827 | 35 | 120 | 211 | 130 | 198 | 0
11:30 | 3808 | 715 | 1734 | 30.5 | 3420.5 | 827.5 | 35 | 125 | 222 | 136 | 201.5 | 0
12:00 | 3828 | 715 | 1755 | 61 | 3503 | 828 | 35 | 130 | 233 | 142 | 205 | 0
12:30 | 3778.5 | 715 | 1744.5 | 146.5 | 3548.5 | 829.5 | 35 | 165 | 233 | 138 | 202.5 | 0
13:00 | 3729 | 715 | 1734 | 232 | 3594 | 831 | 35 | 200 | 233 | 134 | 200 | 0
13:30 | 3729 | 715 | 1734 | 232 | 3594 | 831 | 35 | 200 | 233 | 134 | 200 | 0
14:00 | 3729 | 715 | 1734 | 232 | 3594 | 831 | 35 | 200 | 233 | 134 | 200 | 0
14:30 | 3777.5 | 715 | 1711 | 243 | 3668 | 841.5 | 35 | 210 | 249.5 | 140 | 168 | 0
15:00 | 3826 | 715 | 1688 | 254 | 3742 | 852 | 35 | 220 | 266 | 146 | 136 | 0
15:30 | 3822 | 715 | 1651 | 253.5 | 3692.5 | 857.5 | 52.5 | 220 | 287.5 | 145 | 109 | 0
16:00 | 3818 | 715 | 1614 | 253 | 3643 | 863 | 70 | 220 | 309 | 144 | 82 | 0
16:30 | 3782 | 715 | 1583.5 | 222.5 | 3672.5 | 862.5 | 70 | 221.5 | 306 | 144 | 55.5 | 0
17:00 | 3782 | 715 | 1553 | 192 | 3702 | 862 | 70 | 223 | 303 | 144 | 29 | 0
17:30 | 3794.5 | 715 | 1537 | 144.5 | 3713.5 | 861 | 70 | 221.5 | 324 | 145 | 14.5 | 0
18:00 | 3807 | 715 | 1521 | 97 | 3725 | 860 | 70 | 220 | 345 | 146 | 0 | 0
18:30 | 3861 | 714.5 | 1548.5 | 526 | 3757 | 885 | 70 | 222 | 415 | 152 | 0 | 0
19:00 | 3915 | 714 | 1576 | 955 | 3789 | 910 | 70 | 224 | 485 | 158 | 0 | 0
19:30 | 3859 | 715 | 1591 | 978 | 3927 | 971 | 70 | 235 | 512 | 156 | 0 | 0
20:00 | 3830 | 714 | 1602 | 981 | 3960 | 954 | 70 | 235 | 522 | 156 | 0 | 0
20:30 | 3860.5 | 714 | 1609 | 878 | 3959.5 | 929 | 70 | 236.5 | 510 | 154 | 0 | 0
21:00 | 3891 | 714 | 1616 | 775 | 3959 | 904 | 70 | 238 | 498 | 152 | 0 | 0
21:30 | 3861 | 714.5 | 1621.5 | 679 | 3960 | 897 | 70 | 227 | 490.5 | 145 | 0 | 0
22:00 | 3831 | 715 | 1627 | 583 | 3961 | 890 | 70 | 216 | 483 | 138 | 0 | 0
22:30 | 3794 | 714.5 | 1662 | 380.5 | 3939.5 | 895.5 | 70 | 217.5 | 481.5 | 143 | 0 | 0
23:00 | 3757 | 714 | 1697 | 178 | 3918 | 901 | 70 | 219 | 480 | 148 | 0 | 0
23:30 | 3758 | 713.5 | 1719 | 139 | 3881.5 | 875.5 | 70 | 207 | 426.5 | 143 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34.6° C
24:00 | 3759 | 713 | 1741 | 100 | 3845 | 850 | 70 | 195 | 373 | 138 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-03-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 30 | [13 empty] | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 345944
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW PP | [9 empty] | 1 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 357555
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 15 | 19 | 20 | 20 | 20 | 19 | 15 | 9 | 3 | [9 empty] | 153090
6 | Sikalbaha 225MW CCPP (Gas) | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 140 | 131 | 143 | 139 | 142 | 132 | 131 |  | 145 | 150 | 151 | 151 | 100 | 26 | 25 | 2983527
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 8 |  | 51 | 51 | 51 | 34 | 34 | 34 |  | 232410
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 68 | 68 | 68 | 72 | 90 | 95 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2396181
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 20 |  | 200 | 200 | 200 | 170 | 130 | 100 | 100 | 939840
14 | Titas 50 MW Peaking PP | [14 empty] | 5 | 42 | 42 | 42 |  | 42 | 41 | 41 | 42 | 35 | 33 | 33 | 347960
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 219 | 219 | 220 | 220 | 228 | 180 | 180 | 229 | 226 | 220 | 207 | 217 | 200 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 180 | 169 | 178 | 190 | 4840875
18 | Kodda 300 MW PP Unit-2 (Summit) | 260 | 145 | 95 | 45 | 45 | 55 | 95 | 95 | 95 | 95 | 190 | 270 | 298 | 296 | 298 | 298 | 298 | 298 |  | 298 | 298 | 298 | 298 | 298 | 298 | 300 | 5193816
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 451636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 4803000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6787827
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 26 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 26 | 26 | 26 | 29 | 612648
33 | Ashuganj 225 MW CCPP | 222 | 210 | 190 | 208 | 214 | 220 | 225 | 223 | 218 | 216 | 181 | 155 | 146 | 177 | 171 | 170 | 187 | 205 |  | 186 | 184 | 200 | 206 | 219 | 219 | 221 | 4836000
34 | Ashuganj 450 MW CCPP(South) | 310 | 315 | 315 | 315 | 315 | 305 | 270 | 270 | 285 | 290 | 285 | 320 | 285 | 320 | 320 | 315 | 285 | 285 |  | 335 | 305 | 275 | 300 | 290 | 275 | 275 | 7282000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 260 | 260 | 260 | 260 | 340 | 270 | 270 | 300 | 270 | 305 | 305 | 300 | 270 | 270 |  | 345 | 310 | 270 | 295 | 280 | 270 | 270 | 7264000
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 55 | 30 | 30 | 30 | 30 | 48 | 48 | 48 | 48 | 48 | 50 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 843840
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 91 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 81 | 73 | 72 | 72 | 72 |  | 73 | 73 | 73 | 72 | 71 | 72 | 72 | 1540070
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 320 | 320 | 320 | 310 | 310 | 310 | 300 | 300 | 300 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7384000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 108 | 109 | 109 | 109 | 109 | 110 | 109 | 71 | 71 | 70 | 70 | 68 | 68 | 68 | 70 | 67 | 70 | 71 |  | 71 | 72 | 72 | 70 | 72 | 87 | 86 | 1943040
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 5 | 16 | 22 | 37 | 45 | 45 | 45 | 40 | 29 | 16 | 6 | 0 | [8 empty] | 310190
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 680792
46 | Shajibazar 330 MW CCPP | 266 | 266 | 263 | 268 | 268 | 269 | 262 | 266 | 266 | 265 | 265 | 267 | 265 | 260 | 261 | 265 | 265 | 266 |  | 267 | 267 | 268 | 267 | 267 | 267 | 270 | 6109000
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 60 | 61 | 1329216
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 85 | 84 | 83 | 83 | 84 | 85 | 84 |  | 85 | 86 | 89 | 89 | 89 | 89 | 89 | 2063040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245880
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242976
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 1112400
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 22 | 22 | 24 | 24 | 23 | 23 | 21 | 21 | 21 | 21 | 21 | 21 | 14 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 526104
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 275 | 285 | 280 | 290 | 285 | 290 | 290 | 270 | 300 | 260 | 300 | 290 | 300 | 310 | 315 | 290 | 265 |  | 295 | 305 | 300 | 290 | 290 | 280 | 290 | 7157500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 397 | 383 | 385 | 380 | 378 | 380 | 398 | 400 |  | 385 | 385 | 394 | 393 | 400 | 400 | 400 | 9466100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1031820
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 19 | 18 | 523920
60 | Barabkunda 22 MW PP (Regent) | [26 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 492732
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 375120
63 | Impoprt (Tripura) | 132 | 136 | 124 | 120 | 114 | 108 | 106 | 112 | 110 | 116 | 130 | 142 | 134 | 146 | 146 | 144 | 144 | 146 |  | 158 | 156 | 156 | 152 | 138 | 148 | 138 | 3208320
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 39 | 39 | 39 | 39 | 37 | 11 | 2 | 4 | 3 | 6 | 10 | 5 | 4 | 4 | 8 | 2 |  | 12 | 15 | 21 | 27 | 34 | 35 | 38 | 497280
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 451476
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 206640
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 20 | 25 | 25 | 25 | 25 | 17 | 16 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 723500
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 18 | 12 | 20 | 20 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 519420
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 20 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 23 | 23 | 15 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 26 | 27 | 28 | 28 | 28 | 28 | 539640
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 824800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792500
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 94 | 90 | 90 | 90 | 90 | 88 | 90 | 89 | 89 | 87 |  | 88 | 89 | 88 | 88 | 88 | 88 | 90 | 2175590
| Feni Lanka Power | 52 | 34 | 17 |  |  | 17 | 22 | 51 | 51 | 84 | 114 | 114 | 98 | 98 | 98 | 98 | 98 | 98 |  | 81 | 98 | 98 | 98 | 98 | 98 | 98 | 1739640
| Chowmuhani 113 MW | 89 | 88 | 88 | 87 | 89 | 89 | 88 | 88 | 88 | 88 | 91 | 97 | 97 | 102 | 105 | 105 | 105 | 105 |  | 106 | 107 | 107 | 107 | 106 | 106 | 99 | 2331840
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 108 | 108 | 108 | 111 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3371040
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 22 | 42 | 42 | 43 | 50 | 50 | 50 | 49 | 49 | 41 | 41 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 861120
79 | Kodda 150MW PP | 82 | 64 | 32 | 16 | 16 | 16 | 16 | 32 | 82 | 115 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2538240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 42 | 16 | 16 | 16 | 16 | 20 | 35 | 37 | 43 | 39 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 903034
| Gazipur 100 MW PP | 105 | 34 | 34 | 34 | 34 | 50 | 52 | 70 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1886400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | [10 empty] | 35160
| Jodiac Power | 54 | 54 | 54 | 54 | 45 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 47 | 54 | 54 | 54 | 1032800
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 105 | 110 | 94 |  | 107 | 110 | 110 | 110 | 110 | 110 | 110 | 2639552
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 255 | 275 | 265 | 255 | 290 | 235 | 280 | 250 | 275 | 285 | 285 | 275 | 275 | 260 | 260 | 190 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 5521338
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 93 | 92 | 91 | 70 | 53 | 53 | 53 | 56 | 88 | 92 | 91 | 91 | 90 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2051520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 10 | 40 | 94 | 92 | 92 | 92 | 92 | 92 | 92 |  | 100 | 100 | 100 | 100 | 88 | 88 | 88 | 1190400
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1161010
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 16 | 16 | 16 | 16 | 16 | 16 | 40 | 58 | 75 | 84 | 84 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1589040
95 | Patenga 50MW PP (Baraka) | 50 | 40 | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 14 | 37 | 46 | 43 | 37 | 37 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 876480
96 | Chattogram 108 MW PP (ECPV) | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | [13 empty] | 0 | 72000
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 0 | 0 | 0 | 0 | 0 | 1 | 15 | 15 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 943293
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 10 | 17 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 753629
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1292760
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 32 |  | 54 | 55 | 22 | 22 |  | 304 | 303 | 306 | 246 | 204 |  | 0 | 1320414
105 | Bramhangoan 100 MW PP (Aggreko) | [11 empty] | 31 | 100 | 50 | 100 | 100 | 100 | 25 |  | 100 | 100 | 100 | 100 | 100 | 50 | 0 | 954038
106 | Mymensingh 200 MW PP (United) | 182 | 191 | 192 | 192 | 193 | 193 | 193 | 193 | 193 | 193 | 182 | 180 | 188 | 189 | 188 | 188 | 188 | 189 |  | 189 | 189 | 190 | 191 | 191 | 191 | 191 | 4468800
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 30 | 100 | 30 | 100 | 98 | 70 | 25 |  | 100 | 100 | 100 | 99 | 99 | 28 | 0 | 891240
114 | Kodda 149 MW PP Unit-1 (Summit) | 133 | 134 | 129 | 100 | 100 | 114 | 118 | 127 | 134 | 134 | 134 | 121 | 117 | 129 | 133 | 135 | 118 | 122 |  | 116 | 116 | 132 | 135 | 133 | 135 | 135 | 3040704
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2108160
116 | Chandpur 200MW (Desh energy) | [7 empty] | 15 | 17 | 17 | 19 | 52 | 150 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2492640
117 | Ashuganj 150MW PP (Midland) | 142 | 140 | 140 | 140 | 142 | 142 | 140 | 122 | 140 | 142 | 143 | 147 | 147 | 145 | 130 | 130 | 125 | 130 |  | 138 | 140 | 140 | 140 | 142 | 137 | 137 | 3330400
118 | Bibiyana-III 400 MW CCPP | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 399 | 400 | 402 | 377 | 404 | 403 | 405 | 405 | 405 | 403 | 403 |  | 403 | 402 | 403 | 403 | 402 | 401 | 401 | 9615000
| Jamalpur 115 MW PP (United) | 98 | 98 | 75 | 50 | 50 | 70 | 98 | 98 | 98 | 89 | 98 | 98 | 98 | 108 | 107 | 107 | 97 | 107 |  | 108 | 108 | 108 | 108 | 108 | 108 | 109 | 2306400
| Anwara 300 MW PP (United) | 281 | 281 | 281 | 281 | 281 | 281 | 265 | 265 | 281 | 265 | 265 | 265 | 265 | 281 | 281 | 264 | 264 | 281 |  | 281 | 281 | 281 | 281 | 281 | 281 | 281 | 6523636
| Juldah unit-2 (Acorn) | 100 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 90 | 65 | 90 | 77 | 77 | 77 | 77 | 77 |  | 86 | 100 | 100 | 100 | 100 | 100 | 100 | 1557120
| Anlima Energy Ltd. | 113 | 113 | 113 | 113 | 113 | 113 | 96 | 95 | 94 | 94 | 95 | 95 | 95 | 94 | 97 | 113 | 113 | 94 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2515364
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 7 | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 33 | 35 | 35 | 17 | 489960
| Spectra Solar Plant Ltd. | [7 empty] | 9 | 19 | 26 | 31 | 32 | 30 | 27 | 20 | 12 | 4 | 0 | [8 empty] | 203865
| Chandpur 115(Doreen) | [5 empty] | 4 | 20 | 50 | 51 | 63 | 91 | 90 | 76 | 76 | 82 | 84 | 79 | 77 |  | 94 | 98 | 98 | 98 | 99 | 100 | 98 | 1480320
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 17 | 17 | 32 | 40 | 52 | 55 | 50 | 43 | 39 | 40 | 55 | 55 | 37 | 55 | 55 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 1170000
120 | Eastern Zone Total | 7616 | 7325 | 7057 | 6773 | 6669 | 6634 | 6662 | 6796 | 7159 | 7326 | 7593 | 7887 | 8063 | 8118 | 8279 | 8212 | 8010 | 7920 | 0 | 8762 | 8768 | 8758 | 8734 | 8568 | 8140 | 8023 | 186280572
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 4 |  | 7 | 31 | 40 | 32 | 32 | 32 | 2 | 135360
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 200 | 220 | 220 | 220 | 223 | 220 |  | 210 | 210 | 210 | 216 | 216 | 219 | 195 | 3918952
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 53 | 53 | 53 | 53 | 53 | 53 | 70 | 94 | 90 | 73 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 105 | 105 | 105 | 105 | 105 | 105 | 2091840
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 8 | 27 | 42 | 70 | 86 | 91 | 88 | 78 | 61 | 39 | 15 | [8 empty] | 0 | 608400
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 107 | 106 | 107 | 107 | 107 | 98 | 107 | 105 | 105 | 108 | 107 | 100 | 100 | 103 | 103 | 103 | 102 | 105 |  | 105 | 105 | 105 | 115 | 119 | 195 | 220 | 2755609
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 28 | 64 | 80 | 80 | 80 | 48 |  | 252320
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 27 | 25 | 24 | 24 | 24 | 22 | 20 | 18 | 18 | 17 | 18 | 19 | 21 | 22 | 21 | 21 | 21 | 20 |  | 28 | 27 | 28 | 28 | 27 | 28 | 28 | 548800
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [9 empty] | 75 | 98 | 98 | 20 |  |  | 0 | 248640
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 8 | 8 | [5 empty] | 9728
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 2 | 32 | 32 |  |  |  |  | 57888
146 | Bheramara HVDC | 718 | 718 | 717 | 718 | 717 | 718 | 718 | 717 | 717 | 714 | 715 | 715 | 715 | 715 | 715 | 715 | 715 | 715 |  | 714 | 715 | 714 | 714 | 715 | 714 | 713 | 17332363
147 | Bheramara 410 MW CCPP | 235 | 240 | 240 | 245 | 245 | 250 | 255 | 250 | 240 | 240 | 235 | 225 | 215 | 210 | 210 | 210 | 210 | 210 |  | 210 | 220 | 225 | 225 | 230 | 230 | 220 | 5705280
148 | Payra 1320 MW | 600 | 570 | 570 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 570 | 580 | 580 | 580 |  | 630 | 690 | 670 | 620 | 610 | 620 | 570 | 15565200
149
150 | Barapukuria TPP Unit-1 | 78 | 80 | 80 | 78 | 79 | 79 | 79 | 80 | 80 | 80 | 78 | 78 | 81 | 82 | 82 | 83 | 82 | 80 |  | 80 | 81 | 84 | 84 | 80 | 81 | 80 | 1916945
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 199 | 199 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4850700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 7 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 245540
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 4 | 3 | 1 | 0 | 0 | [8 empty] | 33180
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 4 | 4 | 3 | 4 | 4 | 3 | 3 |  | 3 | 3 | 3 | 3 | 4 | 4 | 0 | 246400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 161 | 158 | 158 | 158 | 158 | 157 | 158 | 160 | 160 | 159 | 148 | 148 | 147 | 140 | 137 | 136 | 133 | 132 |  | 132 | 132 | 132 | 132 | 133 | 132 | 134 | 3723500
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 138 | 138 | 139 | 146 | 141 | 135 | 131 | 124 | 129 | 148 | 156 | 156 | 155 | 149 | 148 | 148 | 147 |  | 146 | 146 | 145 | 147 | 147 | 144 | 143 | 3688018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 400 | 400 | 396 | 420 | 352 | 352 | 382 | 383 | 326 | 417 | 372 | 387 | 380 | 352 | 356 | 356 | 355 | 355 |  | 370 | 370 | 377 | 385 | 386 | 385 | 389 | 8990909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 5 | 5 | 5 | 5 | 7 | 5 | 16 |  | 24 | 31 | 37 | 37 | 37 | 36 | 25 | 231314
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 17 | 17 | 17 | 17 | 16 | 16 | 15 | 16 | 17 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 393360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 263934
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [10 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 545891
167 | Katakhali 50 MW Peaking PP | [11 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 36 |  | 40 | 40 | 40 | 40 | 32 | 32 | 0 | 345574
168 | Santahar 50 MW Peaking PP | [13 empty] | 12 | 28 | 32 | 28 | 28 |  | 28 | 25 | 28 | 28 | 28 | 28 | 28 | 266536
169 | Natore 52 MW PP (Rajlanka) | 24 |  |  |  |  | 8 | 8 | 24 | 24 | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 845424
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 20 | 54 | 61 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 1035208
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 5 |  | 176 | 177 | 177 | 140 | 50 | 0 | 0 | 603374
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 70 | 70 | 77 | 113 | 113 | 113 | 94 | 94 | 74 | 94 | 109 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2531712
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2072640
173 | Rangpur 20 MW GTPP | [19 empty] | 14 | 15 | 15 | 12 | 0 |  |  | 47000
175 | Saidpur 20 MW GTPP | [20 empty] | 10 | 10 | 10 | 0 |  |  | 29000
176 | Rangpur 113 MW PP (Confidence) | 113 | 70 | 70 | 34 | 34 | 34 | 103 | 113 | 104 | 113 | 113 | 113 | 106 | 112 | 103 | 27 | 108 | 111 |  | 111 | 111 | 111 | 110 | 115 | 109 | 109 | 2221862
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [8 empty] | 35779
178 | Energypac Power Venture Thakurgaon Ltd. | 91 | 18 | 18 | 18 | 18 | 18 | 55 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2156893
178